## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: September 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-09-02 |  | 2025-08-01 |  | 2024-09-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16279.02 | 2025-09-01 | 16076.4 | 2025-08-11 | 15717 | 2024-09-19 | 16794 | 2025-07-23
|  |  | 19:30 Hr. |  | 19:30 Hr. |  | 21:00 |  | 21:00 Hr.
2 | Minimum Generation (MW) | 10620.26 | 2025-09-22 | 9865.74 | 2025-08-08 | 7847 | 2024-09-14 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16279.02 | 2025-09-01 | 16076.4 | 2025-08-11 | 15717 | 2024-09-19 | 16794 | 2025-07-23
|  |  | 19:30 Hr. |  | 19:30 Hr. |  | 21:00 |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 14965.88 | 2025-09-30 | 14273.89 | 2025-08-12 | 13785 | 2024-09-19 | 14965.88 | 2025-09-30
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 16450.02 | 2025-09-01 | 16199.71 | 2025-08-11 | 16300 | 2024-09-30 | 17200 | 2024-04-29
|  |  | 19:30 Hr. |  | 19:30 Hr. |  | 20:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 15373.711 |  | 15029.8061 |  | 14156.9333 |  | - | -
7 | Average Generation (MW) at Day Peak | 13652.769 |  | 13104.8316 |  | 12483.1 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 979 | 2025-09-09 | 973 | 2025-08-29 | 910 | 2024-09-27 | 979 | 2025-09-09
|  |  | 5:00 |  | 7:30 |  | 15:30 |  | 5:00
9 | Maximum Power Import from Tripura, India (MW) | 66 | 2025-09-25 | 62 | 2025-08-18 | 104 | 2024-09-18 | 194 | 12/06/19
|  |  | 18:00 |  | 13:00 |  | 14:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1308 | 2025-09-09 | 197 | 2025-08-18 | 1973 | 2024-09-09 | 4395 | 04/10/2022
|  |  | 20:00 |  | 20:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14881 | 2025-09-09 | 15945.99 | 2025-08-18 | 14034 | 45544 | 14965 | 2024-05-16
|  |  | 20:00 |  | 20:00 |  | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 44 | 2025-09-05 | 0 | 2025-08-01 | 0 | 45549 | - | -
|  |  | 21:00 |  | 21:00 |  | 20:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 15064.21 | 2025-09-05 | 13620.22 | 2025-08-01 | 11456 | 2024-09-14 | - | -
|  |  | 21:00 |  | 21:00 |  | 20:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 318 | 2025-09-10 | 36 | 2025-08-28 | 1749 | 45545 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 14471.36 | 2025-09-10 | 13864.61 | 2025-08-28 | 12869 | 45545 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 23 | 2025-09-06 | 0 | 2025-08-01 | 0 | 45549 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 13309.84 | 2025-09-06 | 11666.46 | 2025-08-01 | 10079 | 45549 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 30 |  | 13 |  | 26 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 15 |  | 1 |  | 26 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1248.3832 |  | 1209.5845 |  | 1362.8967 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 30.8707 |  | 787.378 |  | 56.005 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1217.5125 |  | 422.2065 |  | 1306.8916 |  | - | -
23 | Net Generation of IPP (MKWH) | 2978.8553 |  | 2717.094 |  | 3540.7158 |  | - | -
23b | Net Generation by Generation Companies | 4245.3018 |  | 3051.341 |  | 2703.457
24 | Net Generation of REB (MKWH) | 44.7809 |  | 48.2344 |  | 80.3803 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 139.669 |  | 132.6744 |  | 140.2199 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 8626.1194 |  | 6371.5503 |  | 7771.6647 |  | - | -
27 | Energy Generation by Gas (MKWH) | 4025.2813 |  | 4290.1188 |  | 3600.4368 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 23.9372 |  | 12.0531 |  | 21.8892 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 1216.6848 |  | 935.2305 |  | 1317.2118 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 156.2217 |  | 162.1321 |  | 154.5809 |  | - | -
31 | Energy Generation by Solar (MKWH) | 119.0925 |  | 108.7313 |  | 92.3345 |  | - | -
31b | Energy Generation by Wind (MKWH) | 4.9805 |  | 10.2067 |  | 8.4058 |  | - | -
32 | Energy Generation by Coal (MKWH) | 3110.7922 |  | 3144.9225 |  | 2632.8107 |  | - | -
33 | Enegry Import from India (MKWH) | 1483.7987 |  | 1458.9205 |  | 1398.3326 |  | - | -
34 | Monthly Load Factor (%) | 86.5189 |  | 84.6288 |  | 81.5289 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: September 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16279.02 | 2025-09-01 | 19:30 Hr.
Generation Period
| Dhaka | MW | 5642.2
| Chattogram | MW | 1465.2
| Cumilla | MW | 1430.36
| Mymensingh | MW | 1129
| Sylhet | MW | 597
a) | Total supply in East zone | MW | 10263.76
| Khulna | MW | 1971.4
| Barisal | MW | 421.9
| Rajshahi | MW | 1719.4
| Rangpur | MW | 1144
b) | Total supply in West zone | MW | 5256.7
c) | Total supply in both zone ( a+b) | MW | 15520.46
Ref: | 27.21.0000.603.16.087.20.936 | Date: 16/10/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 1080 | 2025-09-21 | 12:00
|  | MW | 414
| b) Ghorashal end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 0 | - | -
|  | MW | 0
| b) Ghorashal end | AMPS | 1034 | 2025-09-21 | 11:00
|  | MW | 384
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 7063.388 | 2025-09-06 | N/A
| b) Ghorashal end | MWh | 0 | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0 | -
| b) Ghorashal end | MWh | 6762.253 | 2025-09-06 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 163860.366
| b) Ghorashal end | MWh | 0
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 158944.555
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1980 | 2025-09-03 | 11:00
|  | MW | 760
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Serajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur | AMPS | 2022 | 2025-09-03 | 11:00
|  | MW | 748
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Serajganj end | MWh | 7892 | 20-9-25
| b) Sreepur | MWh | 0 | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | -
| b) Sreepur | MWh | - | -
28 | Total Energy Export through EWI/ NO-2
| a)Serajganj end | MWh | 396268
| b) Sreepur | MWh | 0
29 | Total Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0
| b) Sreepur | MWh | 388431
30 | Transmission loss of EWI/ NO-2 | % | 3.33
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 3144
|  | MW | 2004
| b) Aminbazar end | AMPS | 0 | 2025-09-26 | 12:00
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 3125 | 2025-09-26 | 12:00
|  | MW | 2003
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 53870 | 2025-09-25 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 53716 | 2025-09-25
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1148794
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1144160
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.403
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Tr-1(404T) | 2025-09-01 22:52 | 2025-09-01 23:15 | 0.015972 | T | 33kv bangalgao feeder fault RET650 | 50 | 19.1667 | Power interruption
Bhaluka 132/33kV | Transformer-03 | 2025-09-06 21:20 | 2025-09-06 21:26 | 0.0041667 | T | 33 KV Bironia feeder fault. 50N/51N | 19 | 1.9 | Power interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-09-15 16:45 | 2025-09-15 17:58 | 0.050694 | T | 33 kV PBS feeder fault (feeder no 16). 50/51 N trip relay. | 46 | 55.9667 | Power interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-09-15 16:45 | 2025-09-15 17:58 | 0.050694 | T | 33 kV PBS feeder fault (feeder no 16). 50/51 N trip relay | 46 | 55.9667 | Power interruption
Bhaluka 132/33kV | Transformer-03 | 2025-09-28 08:25 | 2025-09-28 09:02 | 0.025694 | T | 33kV feeder fault(14 no.pbs feeder) 50/51N | 7 | 4.3167 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR2 | 2025-09-18 17:49 | 2025-09-18 18:27 | 0.026389 | T | Mechanical Protection trip RET 670 | 250 | 158.3333 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR1 | 2025-09-18 17:49 | 2025-09-18 18:15 | 0.018056 | T | Directional Overcurrent RET 670 | 250 | 108.3333 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-09-15 16:20 | 2025-09-15 17:45 | 0.059028 | T | 33 kv T-1 & T-3 bus fault Micom P 40 Agile | 25 | 35.4167 | Power interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2025-09-15 16:20 | 2025-09-15 17:45 | 0.059028 | T | 33 kv T-1 & T-3 bus fault Micom P40 Agile | 25 | 35.4167 | Power interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-09-15 16:20 | 2025-09-15 17:44 | 0.058333 | T | 33 kv T-1 & T-3 bus fault Micom P40 Agile | 20 | 28 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-09-18 17:36 | 2025-09-18 17:42 | 0.0041667 | T | df/dt FBCPU | 44 | 4.4 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-09-18 23:25 | 2025-09-18 23:29 | 0.0027778 | T | df/dt FBCPU | 38 | 2.5333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-09-18 23:25 | 2025-09-18 23:29 | 0.0027778 | T | df/dt FBCPU | 53 | 3.5333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-09-21 11:00 | 2025-09-21 11:24 | 0.016667 | T | df/dt | 38 | 15.2 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-09-21 11:00 | 2025-09-21 11:12 | 0.0083333 | T | df/dt | 53 | 10.6 | Power interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-09-18 15:17 | 2025-09-18 17:25 | 0.088889 | E/O | For pbs feeder no 16 | 25 | 53.3333 | Power interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-09-29 07:19 | 2025-09-29 09:23 | 0.086111 | E/O | 33 kv pbs feeder-09 (33 kv bus loop red hot) | 40 | 82.6667 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-09-24 17:49 | 2025-09-24 19:24 | 0.065972 | E/O | 132 CB maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-09-20 11:05 | 2025-09-20 12:47 | 0.070833 | E/O | Emergency s/d due to kite cotton remove ckt-1 Tower no 52. | 5 | 8.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-09-14 14:34 | 2025-09-14 18:07 | 0.14792 | E/O | Red Hot | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-09-17 13:20 | 2025-09-17 15:33 | 0.092361 | E/O | Red Hot | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2025-09-28 07:06 | 2025-09-28 07:39 | 0.022917 | E/O | Red Hot 132 kV side (CT-R phase, CB-Y phase) | 230 | 126.5 | Power interruption
Sreepur 230/132/33kV | 230/132 kV T-2 | 2025-09-28 07:46 | 2025-09-28 08:10 | 0.016667 | E/O | Red Hot 132 kV Side (CT-Y phase, CB-B phase) | 230 | 92 | Power interruption
|  |  | Total : | 0.99444 |  | Unserved Energy: |  | 902.0833
Dhaka (South) Grid Circle :
Hasnabad 132/33kV | 132kV Reserve Bus | 2025-09-22 07:20 | 2025-09-22 08:24 | 0.044444 | T | Fatullah line fault, Fatullah line trial an 132 kv bus trip at a time. Over current | 50 | 53.3333 | Power interruption
Hasnabad 230/132kV | AUTO TR-1 | 2025-09-22 07:18 | 2025-09-22 08:22 | 0.044444 | T | 132 kV bus trip O/C and E/F relay operated | 29 | 30.9333 | Power interruption
Hasnabad 230/132kV | AUTO TR-3 | 2025-09-22 07:18 | 2025-09-22 08:22 | 0.044444 | T | 132 kV bus trip O/C and E/F relay operated | 29 | 30.9333 | Power interruption
Hasnabad 230/132kV | AUTO TR-2 | 2025-09-22 07:18 | 2025-09-22 08:23 | 0.045139 | T | 132 kV bus trip O/C and E/F relay operated | 29 | 31.4167 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-09-06 10:36 | 2025-09-06 10:50 | 0.0097222 | T | Due to PBS Boorpa feeder overcurrent fault. D/R O/C & E/F Relay | 48 | 11.2 | Power interruption
Srinagar 132/33kV | Tr-01 | 2025-09-22 14:15 | 2025-09-22 16:18 | 0.085417 | T | ৩৩ কেভি ফিডারের স্কাই ওয়্যার ছিড়ে ৩৩ কেভি বাস এর উপর এসে পড়ায় ট্রান্সফরমার-০১ ট্রিপ করে। Bus-bar protection P742 relay | 15 | 30.75 | Power interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-09-10 16:02 | 2025-09-10 16:35 | 0.022917 | E/O | Nawabganj-1 Reserve Bus DS Y-Phase red hot | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-09-25 19:43 | 2025-09-25 20:06 | 0.015972 | E/O |  | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-09-10 03:48 | 2025-09-10 04:31 | 0.029861 | E/O | Corrective maintenance work for PBS 33kv Langulbanbdo feeder Y-phase source DS flashing. Work done by PBS. | 40 | 28.6667 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2025-09-16 15:05 | 2025-09-16 16:26 | 0.05625 | E/O | Due to red hot maintenance at pbs 33kv Everest feeder. | 62 | 83.7 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-09-21 13:22 | 2025-09-21 14:18 | 0.038889 | E/O | According to Direction of NLDC | 65 | 60.6667 | Power interruption
|  |  | Total : | 0.4375 |  | Unserved Energy: |  | 361.6
Chattogram Grid Circle :
Agrabad 132/33kV | MTR-02 (416T) | 2025-09-25 23:01 | 2025-09-26 00:58 | 0.08125 | T | 33KV Newmoring Feeder Trip. 50/51N Instantaneous earth fault, | 42 | 81.9 | Power interruption
Agrabad 132/33kV | MTR-01 (406T) | 2025-09-25 23:01 | 2025-09-26 00:49 | 0.075 | T | 33KV Newmoring Feeder Trip. 50/51N Instantaneous earth fault, | 42 | 75.6 | Power interruption
Halishahar 132/33kV | 415T(TR-2) | 2025-09-08 03:52 | 2025-09-08 06:35 | 0.11319 | T | BPDB 33/.4 kV Station Supply Transformer primary cable fault. Over Current | 26 | 70.6333 | Power interruption
Madunaghat 132/33kV | TR-2(517T) | 2025-09-29 09:17 | 2025-09-29 14:19 | 0.20972 | T | 33kV feeder old wasa(bpdb) is tripped, and the Y-phase loop from the bus isolator lower point to the breaker upper point is broken down. REF-615(33KV), RET-670,RET-650 | 17 | 85.5667 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2025-09-28 16:03 | 2025-09-28 16:36 | 0.022917 | E/O | chokaria 33 feeder red hot maintenance | 15 | 8.25 | Power interruption
Halishahar 132/33kV | 415T(TR-2) | 2025-09-08 13:58 | 2025-09-08 14:41 | 0.029861 | E/O | Bpdp station Transformer R Phase Blast. Now They are maintenance this phase and connection with 33kv TR-02 Secondary Breaker. For this reason need to shutdown. | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-04 | 2025-09-02 16:25 | 2025-09-02 19:04 | 0.11042 | E/O | BUS DS Redhot | 20 | 53 | Power interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-09-01 12:04 | 2025-09-01 14:15 | 0.090972 | E/O | High Temperature in DS joint all phase and CB joint. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-09-01 14:36 | 2025-09-01 14:55 | 0.013194 | E/O | CB joint point High Temperature | 0 | 0 | No interruption
TK chemical | 48/64MVA T-2(415T) | 2025-09-07 21:05 | 2025-09-07 22:10 | 0.045139 | E/O | red hot | 0 | 0 | No interruption
|  |  | Total : | 0.79167 |  | Unserved Energy: |  | 374.95
Cumilla Grid Circle :
Bibiana 400/230kV | ICT-02 | 2025-09-17 23:23 | 2025-09-18 06:42 | 0.30486 | T | PRD Trip. RTE670,Main 2 | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-02 | 2025-09-20 07:23 | 2025-09-20 17:47 | 0.43333 | T | PRD-2 TRIP RET670 MAIN -2 | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-1 | 2025-09-03 08:28 | 2025-09-03 08:52 | 0.016667 | T | REF-615,RET-670 | 34 | 13.6 | Power interruption
Cumilla(S) 132/33kV | TR-1 | 2025-09-08 16:03 | 2025-09-08 16:14 | 0.0076389 | T | 33 KV Kosba Palpara PDB feeder C.B trip REF615, RET650 | 40 | 7.3333 | Power interruption
Cumilla(S) 132/33kV | TR-1 | 2025-09-10 18:51 | 2025-09-10 19:57 | 0.045833 | T | Bagmara REB feeder fault REF615, RET650 | 37 | 40.7 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-09-25 17:43 | 2025-09-25 18:03 | 0.013889 | T | 33KV Palpara feeder fault but feeder CB did not trip. Relay DC power was not available on control panel in PDB 33KV C/R. RET 650 REF 615 | 26 | 8.6667 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-09-30 02:45 | 2025-09-30 03:35 | 0.034722 | T | 33kv Laksam REB feeder fault C.B not trip. REF-615 | 30 | 25 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-09-24 08:54 | 2025-09-24 09:36 | 0.029167 | T | 33 kv Jamuna Feeder Flashing and Trip OC EF Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-09-24 08:54 | 2025-09-24 09:36 | 0.029167 | T | 33 kv Jamuna Feeder Flashing and Trip Trip Relay, Mikro Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-09-28 12:49 | 2025-09-28 13:12 | 0.015972 | T | Thundering and 33kv Madhabpur Feeder CT Blast Trip Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-09-28 12:49 | 2025-09-28 13:12 | 0.015972 | T | Thundering and 33kv Madhabpur Feeder CT Blast Lockout Relay | 0 | 0 | No interruption
Sylhet (South) | Trafo-2 | 2025-09-06 13:14 | 2025-09-06 13:33 | 0.013194 | T | fault to connecting local grounding at moglabazar feeder. 86.1/2 , 50/51N optd. | 35 | 11.0833 | Power interruption
Sylhet 132/33kV | T1 | 2025-09-07 08:53 | 2025-09-07 09:13 | 0.013889 | T | Unknown Ins O/C at A and C Phase. | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-09-28 07:22 | 2025-09-28 07:44 | 0.015278 | T | 33kv IC-1 Feeder trip due to O/C Fault O/C | 20 | 7.3333 | Power interruption
Chowmuhani 132/33kV | TR1 | 2025-09-28 11:34 | 2025-09-28 15:00 | 0.14306 | E/O | For Circuit Breaker Replacement. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR1 | 2025-09-29 19:56 | 2025-09-29 22:40 | 0.11389 | E/O | Y Phase Red Hot Maintenance | 20 | 54.6667 | Power interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-09-03 06:40 | 2025-09-03 09:56 | 0.13611 | E/O | Emergency maintanance Works | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 401T | 2025-09-03 10:42 | 2025-09-03 12:09 | 0.060417 | E/O | Emergency maintanance Works | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 403T | 2025-09-20 11:40 | 2025-09-20 13:05 | 0.059028 | E/O | Emergency maintanance Work | 16 | 22.6667 | Power interruption
Chandpur 132/33kV | 412T (T-2) | 2025-09-09 18:11 | 2025-09-11 13:37 | 1899-12-31 19:26 | E/O | Emergency maintanance Work | 0 | 0 | No interruption
Chandpur 132/33kV | 200KVA Aux. T-2 | 2025-09-09 18:12 | 2025-09-09 18:12 | 0 | E/O | Emergency maintanance Work | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2025-09-11 13:37 | 2025-09-22 13:04 | 1900-01-09 23:27 | E/O | Emergency maintanance Work | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 | 2025-09-04 22:28 | 2025-09-04 23:33 | 0.045139 | E/O | Red hot at Lalbag feeder of PBS end under bus-02. | 38 | 41.1667 | Power interruption
Chhatak 132/33kV | T-3 | 2025-09-09 17:50 | 2025-09-09 18:39 | 0.034028 | E/O | Maintanance Oil leakage of 132 kv SF6 CB of T-3 | 0 | 0 | No interruption
Chhatak 132/33kV | T-2 | 2025-09-25 13:57 | 2025-09-25 15:10 | 0.050694 | E/O | Transformer T-2 Shutdown for tap changing. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR2-425T | 2025-09-07 14:37 | 2025-09-07 14:58 | 0.014583 | E/O | 132kV DS424BP emergency maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-04 | 2025-09-25 17:02 | 2025-09-25 19:10 | 0.088889 | E/O | 33 KV Kaliajuri Feeder bus DS and Loop maintenance | 20 | 42.6667 | Power interruption
Kachua 230/132/33kV | TR-1 | 2025-09-30 08:35 | 2025-09-30 10:28 | 0.078472 | E/O | 33 kV Source DS maintenance of PBS feeder. | 30 | 56.5 | Power interruption
Kasba 132/33kV | TR-1 | 2025-09-21 17:21 | 2025-09-21 18:00 | 0.027083 | E/O | red hot | 17 | 11.05 | Power interruption
Sreemongol 132/33kV | 132/33kv T-2 | 2025-09-17 09:23 | 2025-09-17 10:48 | 0.059028 | E/O | Emergency maintanance Works at 907 DS Loap Repairing. | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-09-17 09:23 | 2025-09-17 10:48 | 0.059028 | E/O | Emergency maintanance Works at 907 DS Loap Repairing. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-13 17:54 |  | Unserved Energy: |  | 342.4333
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2025-09-01 13:38 | 2025-09-01 14:06 | 0.019444 | T | WTI fluse Trip Lockut Relay | 15 | 7 | Power interruption
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2025-09-05 16:19 | 2025-09-05 18:57 | 0.10972 | T | WTI fluse Trip Lockout | 20 | 52.6667 | Power interruption
Khulna (C) | Tr-3 405T | 2025-09-15 19:59 | 2025-09-15 23:12 | 0.13403 | T | 33 KV BUS SEC-2 PT FUSE B PHASE BURN. INST E/F | 7 | 22.5167 | Power interruption
Khulna (C) | Tr-3 405T | 2025-09-16 00:35 | 2025-09-16 01:08 | 0.022917 | T | 33kv khalishpur feeder fault OC, OC/EF | 7 | 3.85 | Power interruption
Khulna (C) | Tr-3 405T | 2025-09-16 08:42 | 2025-09-16 09:26 | 0.030556 | T | Joragate feeder fault No relay | 0 | 0 | No interruption
Mongla 132/33kV | T-2 | 2025-09-22 03:54 | 2025-09-22 04:32 | 0.026389 | T | Auxiliary ⇨2 trip Lockout relay | 5 | 3.1667 | Power interruption
Narail 132/33kV | TR2 (413-T) | 2025-09-17 04:37 | 2025-09-17 05:12 | 0.024306 | T | Due to bird Over current | 45 | 26.25 | Power interruption
Rajbari 132/33kV | Transformer-3 | 2025-09-02 07:34 | 2025-09-02 07:57 | 0.015972 | T | 33kV feeder fault(Sajjonkanda & Goalanda feeder) O/C, 86.1, 86.2 | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-3 | 2025-09-13 04:49 | 2025-09-13 04:51 | 0.0013889 | T | Sajjankanda feeder fault. O/C | 6 | 0.2 | Power interruption
Satkhira 132/33kV | Transformer-3(T-3) | 2025-09-20 11:10 | 2025-09-20 11:10 | 0 | T | no | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2025-09-22 02:55 | 2025-09-22 03:29 | 0.023611 | E/O | Power out from bagerhat | 35 | 19.8333 | Power interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-09-08 17:42 | 2025-09-08 18:30 | 0.033333 | E/O | 33kv bus red-hot Maintenance work. | 40 | 32 | Power interruption
Satkhira 132/33kV | Transformer-3(T-3) | 2025-09-04 15:23 | 2025-09-04 17:56 | 0.10625 | E/O | Emergency maintanance Work | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-09-04 15:23 | 2025-09-04 17:53 | 0.10417 | E/O | Emergency maintanance Work | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-09-20 11:16 | 2025-09-20 13:26 | 0.090278 | E/O | Emergency maintanance Work | 34.5 | 74.75 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2025-09-20 11:24 | 2025-09-20 13:19 | 0.079861 | E/O | Emergency maintanance Work | 41.5 | 79.5417 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2025-09-30 07:10 | 2025-09-30 09:08 | 0.081944 | E/O | Red hot maintenance | 50 | 98.3333 | Power interruption
|  |  | Total : | 0.90417 |  | Unserved Energy: |  | 420.1083
HVDC Grid Circle :
BIPTC | 20DF22 | 2025-09-22 03:59 | 2025-09-22 11:15 | 0.30278 | T | Tripped | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-09-22 18:05 | 2025-09-23 11:20 | 0.71875 | T | Tripped | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-09-28 16:54 | 2025-09-29 11:16 | 0.76528 | T | Tripped | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-1 | 2025-09-03 05:00 | 2025-09-03 05:13 | 0.0090278 | T | Taragunia 33kV pbs feeder fault OC/EF | 21 | 4.55 | Power interruption
Bheramara(GK) 132/33kV | TR-2 | 2025-09-03 05:00 | 2025-09-03 05:13 | 0.0090278 | T | Taragunia 33kV pbs feeder fault OC/EF | 21 | 4.55 | Power interruption
Bheramara(GK) 132/33kV | TR-1 | 2025-09-11 13:30 | 2025-09-11 13:48 | 0.0125 | T | Taraguniya 33kV pbs feeder Fault OC/EF | 22 | 6.6 | Power interruption
Bheramara(GK) 132/33kV | TR-2 | 2025-09-11 13:30 | 2025-09-11 13:49 | 0.013194 | T | Taraguniya 33kV pbs feeder Fault OC/EF | 22 | 6.9667 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-03 | 2025-09-16 23:45 | 2025-09-17 01:08 | 0.057639 | T | OLTC Trip OLTC relay | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-03 | 2025-09-17 16:41 | 2025-09-17 21:11 | 0.1875 | T | on load tap changer trip | 0 | 0 | No interruption
Kushtia 132/33kV | T-3 | 2025-09-15 12:27 | 2025-09-15 12:50 | 0.015972 | T | Micom | 40 | 15.3333 | Power interruption
Baghabari 230/132kV | T-2 Bank | 2025-09-02 08:51 | 2025-09-02 19:43 | 0.45278 | E/O | To work on the PDB edge | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2025-09-01 23:07 | 2025-09-01 23:52 | 0.03125 | E/O | red hot remove | 16 | 12 | Power interruption
BIPTC | 20D09C 20MVA | 2025-09-08 09:01 | 2025-09-08 10:29 | 0.061111 | E/O | Shutdown is taken for emergency maintenance work on neutral grounding | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2025-09-05 19:32 | 2025-09-05 21:52 | 0.097222 | E/O | R phase red hot | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2025-09-02 07:06 | 2025-09-02 08:47 | 0.070139 | E/O | 33kV T-1 Transformer R phase DS Red Hot Maintenance. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-3 | 2025-09-14 07:16 | 2025-09-14 08:28 | 0.05 | E/O | Due to Red Hot maintenance taken by pbs | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2025-09-18 07:32 | 2025-09-18 09:11 | 0.06875 | E/O | 33kv T1A, DS red hot maintainence of B-phase. | 35 | 57.75 | Power interruption
Pabna 132/33kV | T-3 | 2025-09-07 16:03 | 2025-09-07 17:13 | 0.048611 | E/O | Red hot Maintemance work | 10 | 11.6667 | Power interruption
Pabna 132/33kV | T-1 | 2025-09-08 07:08 | 2025-09-08 08:50 | 0.070833 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 01:01 |  | Unserved Energy: |  | 119.4167
Bogura Grid Circle:
Chapai 132/33kV | T-2 (415T) | 2025-09-02 02:15 | 2025-09-02 06:29 | 0.17639 | T | Doc/DEF R- Phase | 0 | 0 | No interruption
Chapai 132/33kV | T-4 (435T) | 2025-09-02 02:15 | 2025-09-02 04:01 | 0.073611 | T | 50/51. 50/51N | 8 | 14.1333 | Power interruption
Kurigram 132/33kV | Transformer T-2 (Tr-413T) | 2025-09-30 19:15 | 2025-10-01 00:50 | 0.23264 | T | Differential Y-phase, | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2025-09-10 12:52 | 2025-09-12 11:48 | 1899-12-31 22:56 | T | underground cable kit blasted of LT Side(T-3(A)) MICOM P122 | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2025-09-16 10:57 | 2025-09-16 12:20 | 0.057639 | T | 33kv NESCO Sugarmil feeder fault. Siemens Siprotech 7SJ81 | 35 | 48.4167 | Power interruption
Saidpur 132/33kV | TR-5 (434T) | 2025-09-02 03:25 | 2025-09-02 03:33 | 0.0055556 | T | 33 kv Niamotpur-02 feeder fault (O/C + E/F). Protection relay + Backup Protection relay | 36 | 4.8 | Power interruption
Sirajganj 132/33kV | T3-(435) | 2025-09-02 01:36 | 2025-09-02 02:42 | 0.045833 | T | PBS 33 kv feeder (Pipulbaria) loop disconnect from bus. 51/50 over current. | 5 | 5.5 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2025-09-02 01:36 | 2025-09-02 02:35 | 0.040972 | T | PBS 33 kv feeder (Pipulbaria) loop disconnect from bus. no | 5 | 4.9167 | Power interruption
Thakurgaon 132/33kV | T-1(422T) | 2025-09-07 03:24 | 2025-09-07 03:50 | 0.018056 | T | 914B, 905B, 920B & 923B Trip করে T-1 ওপেন হয়ে যায়। N/A | 36 | 15.6 | Power interruption
Thakurgaon 132/33kV | T-2(412T) | 2025-09-07 03:24 | 2025-09-07 03:50 | 0.018056 | T | 914B, 905B, 920B & 923B Trip করে T-2 ওপেন হয়ে যায়। N/A | 36 | 15.6 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2025-09-10 09:55 | 2025-09-10 12:25 | 0.10417 | E/O | 33 KV underground Cable maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV | T-03 | 2025-09-17 09:45 | 2025-09-17 10:55 | 0.048611 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-09-15 10:56 | 2025-09-15 12:59 | 0.085417 | E/O | Red hot maintenance | 20 | 41 | Power interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-09-19 10:06 | 2025-09-19 12:06 | 0.083333 | E/O | For redhot maintenance work by pbs at 33kv bus section ds-02 | 16.5 | 33 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-09-01 11:12 | 2025-09-01 17:15 | 0.25208 | E/O | 33kv source DS & load DS hot spot maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-09-12 07:50 | 2025-09-12 09:20 | 0.0625 | E/O |  | 0 | 0 | No interruption
Palashbari 132/33kV | TR2-404T | 2025-09-22 11:06 | 2025-09-22 14:14 | 0.13056 | E/O | T-2 ট্রান্সফরমারের ৩৩ কেভি B phase bushing to Jac BUS twin conductor loop এর Strands কেটে যাওয়ায় তা পরিবর্তন কাজের জন্য | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) | 2025-09-09 01:38 | 2025-09-09 02:31 | 0.036806 | E/O | Red-hot maintenance at Biral-1, 33 kv Feeder | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2025-09-16 18:54 | 2025-09-16 21:10 | 0.094444 | E/O | redhot | 20 | 20.1667 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2025-09-02 07:40 | 2025-09-02 09:41 | 0.084028 | E/O | Emergency 33 kv loop conductor Maintenance at pipulbaria 33kV Feeder DS Raiser cable. | 10 | 20.1667 | Power interruption
Thakurgaon 132/33kV | T-3(432T) | 2025-09-30 13:41 | 2025-09-30 16:28 | 0.11597 | E/O | Circuit Sheild Relay ফল্টে পুড়ে যাওয়ায় টি-৩ ইনকামিং শাটডাউনে রয়েছে। উল্লেখ্য যে টি-১ ও টি-২ দিয়ে পাওয়ার স্বাভাবিক আছে। কোনো লোডশেড নাই। | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 17:20 |  | Unserved Energy: |  | 223.3
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-23 15:19 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Mirpur-01 | 2025-09-22 01:40 | 2025-09-22 02:50 | 0.048611 | T | Trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Mirpur-02 | 2025-09-22 01:40 | 2025-09-22 02:13 | 0.022917 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2025-09-06 09:35 | 2025-09-06 09:47 | 0.0083333 | T | None | 124 | 24.8 | Power interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2025-09-06 09:35 | 2025-09-06 09:54 | 0.013194 | T | Trip | 124 | 39.2667 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2025-09-06 09:44 | 2025-09-06 09:48 | 0.0027778 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2025-09-06 09:44 | 2025-09-06 09:58 | 0.0097222 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-09-06 09:46 | 2025-09-06 09:59 | 0.0090278 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2025-09-06 09:46 | 2025-09-06 09:59 | 0.0090278 | T | No signal ( Instruction from NLDC) | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-09-08 13:32 | 2025-09-08 13:42 | 0.0069444 | T | Trip | 10 | 1.6667 | Power interruption
Ghatail 132/33kV | Tangail-1 | 2025-09-18 17:50 | 2025-09-18 18:23 | 0.022917 | T | Due to 400/132 KV X-former tripped at Kaliakair Grid SS. | 60 | 33 | Power interruption
Ghatail 132/33kV | Tangail -2 | 2025-09-18 17:50 | 2025-09-18 18:32 | 0.029167 | T | Due to 400/132 KV X-former tripped at Kaliakair Grid SS. | 60 | 42 | Power interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-09-19 09:54 | 2025-09-19 10:11 | 0.011806 | T | Trip | 0 | 0 | No interruption
Netrakona 132/33kV | Mymensingh-Netrokona Ckt-2 | 2025-09-01 08:55 | 2025-09-01 09:39 | 0.030556 | T | None | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-09-25 04:57 | 2025-09-25 05:55 | 0.040278 | T | Kodda end power zero. | 8 | 7.7333 | Power interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2025-09-06 09:32 | 2025-09-06 09:50 | 0.0125 | T | OC/EF | 130 | 39 | Power interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2025-09-05 16:41 | 2025-09-05 16:46 | 0.0034722 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2025-09-14 19:32 | 2025-09-14 19:32 | 0 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-09-15 15:38 | 2025-09-15 16:50 | 0.05 | T | Trip | 90 | 108 | Power interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2025-09-25 04:55 | 2025-09-25 08:06 | 0.13264 | T | N/A | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2025-09-25 04:55 | 2025-09-25 16:35 | 0.48611 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | Capacitor Bank- 01 | 2025-09-18 15:16 | 2025-09-18 17:30 | 0.093056 | E/O | For pbs feeder no 16 | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-1 | 2025-09-17 12:11 | 2025-09-17 12:38 | 0.01875 | E/O | Tree trimming | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-1 | 2025-09-20 11:05 | 2025-09-20 12:45 | 0.069444 | E/O | Emergency s/d due to kite cotton remove ckt-1 Tower no 52. | 5 | 8.3333 | Power interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-2 | 2025-09-18 09:48 | 2025-09-18 12:34 | 0.11528 | E/O | Red Hot (Ashuganj end) | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 05:55 |  | Unserved Energy: |  | 303.8
Dhaka (South) Grid Circle :
Bhulta 400/230kV | Ghorashal-01 | 2025-09-25 04:57 | 2025-09-28 07:32 | 1900-01-02 02:35 | T | tripped | 75 | 5593.75 | Power interruption
Fatullah 132/33kV | 132 kV Madanganj | 2025-09-17 19:15 | 2025-09-17 19:36 | 0.014583 | T | tripprd | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Madanganj | 2025-09-26 01:53 | 2025-09-26 01:53 | 0 | T | tripped | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-09-17 19:16 | 2025-09-17 19:23 | 0.0048611 | T | Unknown. | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-09-19 18:26 | 2025-09-19 18:31 | 0.0034722 | T | tripped | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-09-22 05:48 | 2025-09-22 06:05 | 0.011806 | T | tripped | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-09-26 01:58 | 2025-09-26 02:09 | 0.0076389 | T | Unknown. | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-09-22 05:48 | 2025-09-22 09:48 | 0.16667 | T | unknown | 5 | 0 | No interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2025-09-17 19:15 | 2025-09-17 19:37 | 0.015278 | T | tripped | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Summit 55 MW 132 kv Ckt | 2025-09-17 19:15 | 2025-09-17 19:41 | 0.018056 | T | tripped | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2025-09-19 18:22 | 2025-09-26 02:43 | 1900-01-05 08:21 | T | CT blast Bashundhara end | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Summit 55 MW 132 kv Ckt | 2025-09-19 18:22 | 2025-09-19 18:40 | 0.0125 | T | CT Blast at Bashundhara End | 0 | 0 | No interruption
Madanganj 132/33kV | 132kV Haripur-Madanganj-Shitalakhya-Fatullah (74 nos 132kv tower) | 2025-09-26 01:56 | 2025-09-26 01:56 | 0 | T | tripped | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2025-09-26 03:01 | 2025-09-26 04:07 | 0.045833 | T | tripped | 0 | 0 | No interruption
Shitalakhya 132/33kV | 132 kV Hasnabad | 2025-09-22 07:20 | 2025-09-22 09:42 | 0.098611 | T | Hasnabad End Problem | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2025-09-30 12:31 | 2025-09-30 12:31 | 0 | T | tripped | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2025-09-30 12:31 | 2025-09-30 12:58 | 0.01875 | T | Due to Ullon Circuit-1 Tripped. | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2025-09-25 05:32 | 2025-09-28 07:33 | 1900-01-02 02:01 | E/O | Emergency maintenance work | 75 | 5551.25 | Power interruption
Fatullah 132/33kV | 132 kV Madanganj | 2025-09-26 03:32 | 2025-09-26 03:32 | 0 | E/O | Due to a trip to the relay with 21 trp and zone -1 trip, B- Phase | 0 | 0 | No interruption | #DIV/0!
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-09-22 09:48 | 2025-09-22 09:48 | 0 | E/O | Emergency maintenance work. | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2025-09-26 11:50 | 2025-09-26 17:39 | 0.24236 | E/O | Red hot on the edge of Shitallakhya. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-2 | 2025-09-21 12:53 | 2025-09-21 17:04 | 0.17431 | E/O | Bus DS finger maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2025-09-29 11:24 | 2025-09-29 13:39 | 0.09375 | E/O | Line DS red hot maintenance | 2 | 4.5 | Power interruption
Mogbazar 132/33kV | Rampura 1 | 2025-09-04 06:28 | 2025-09-04 06:52 | 0.016667 | E/O | There was a short cable twisted on 132kV Rampura Mogbazar Ckt 01 | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2025-09-04 06:32 | 2025-09-04 06:50 | 0.0125 | E/O | S/D taken by NLDC Xen Sir for removing unwanted wire by DPDC | 0 | 0 | No interruption
Shitalakhya 132/33kV | 132 kV Hasnabad | 2025-09-01 12:55 | 2025-09-01 17:50 | 0.20486 | E/O | Feeder transfer to hasnabad now new fattullah | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-2(E10) | 2025-09-15 09:19 | 2025-09-15 17:13 | 0.32917 | E/O | Maintenance Work of 132kV Shyampur Line-02 under 132/33kV Shyampur Grid SS (DPDC) . | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 2 | 2025-09-13 12:50 | 2025-09-13 14:42 | 0.077778 | E/O | maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-13 02:37 |  | Unserved Energy: |  | 11149.5
Chattogram Grid Circle :
Baroirhat 132/33kV | Hat-1 | 2025-09-09 01:21 | 2025-09-09 01:38 | 0.011806 | T | Bad weather | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2025-09-09 03:01 | 2025-09-09 03:11 | 0.0069444 | T | Bad weather | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Rampur Ckt-2 | 2025-09-22 14:33 | 2025-09-22 15:03 | 0.020833 | T | Transient Fault | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-01 | 2025-09-09 01:30 | 2025-09-09 01:39 | 0.00625 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2025-09-09 01:30 | 2025-09-09 01:39 | 0.00625 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2025-09-09 03:06 | 2025-09-09 03:09 | 0.0020833 | T | Tripped | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-09-16 12:28 | 2025-09-16 12:49 | 0.014583 | T | Fault. | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2025-09-16 12:27 | 2025-09-16 12:50 | 0.015972 | T | General Trip | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2025-09-22 09:49 | 2025-09-22 10:11 | 0.015278 | T | Tripped | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2025-09-09 05:36 | 2025-09-09 09:25 | 0.15903 | E/O | Emergency high temperature maintenance at Hathazari ckt-1 | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2025-09-09 05:53 | 2025-09-09 09:22 | 0.14514 | E/O | Emergency high temperature maintenance | 72 | 250.8 | Power interruption
Baroaulia 132/33kV | AKSPL | 2025-09-16 08:29 | 2025-09-16 08:57 | 0.019444 | E/O | As per direction NLDC Xen | 0 | 0 | No interruption | #DIV/0!
Baroaulia 132/33kV | Kulshi | 2025-09-16 08:30 | 2025-09-16 08:57 | 0.01875 | E/O | As per direction NLDC Xen | 0 | 0 | No interruption
Baroaulia 132/33kV | Kulshi | 2025-09-18 06:32 | 2025-09-18 09:47 | 0.13542 | E/O | High temperature maintenance at 132kv khulshi bay | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Baraulia Circuit-2 | 2025-09-18 06:26 | 2025-09-18 09:53 | 0.14375 | E/O | Red hot maintenance work at Baraulia s/s end. | 0 | 0 | No interruption
Shahmirpur 132/33kV | Sikalbaha-2 | 2025-09-03 11:05 | 2025-09-03 16:22 | 0.22014 | E/O | Temperature rapiddly increasing at the point of Bus DS I clamp CB end R,Y,B Phase, Line DS I clamp Y, B phase & CT clamp B phase. | 0 | 0 | No interruption
Shikalbaha 230/132kV | Interconnection-2 | 2025-09-03 15:15 | 2025-09-03 15:15 | 0 | E/O | Due to R-ph current become zero | 0 | 0 | No interruption
|  |  | Total : | 0.94167 |  | Unserved Energy: |  | 250.8
Cumilla Grid Circle :
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2025-09-12 06:53 | 2025-09-12 07:09 | 0.011111 | T | Tripped | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2025-09-30 12:41 | 2025-09-30 14:58 | 0.095139 | T | L2-L3 Fault | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-2 | 2025-09-30 12:41 | 2025-09-30 15:01 | 0.097222 | T | Tripped | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Kosba Ckt-01 | 2025-09-25 02:18 | 2025-09-25 03:00 | 0.029167 | T | Tripped | 15 | 10.5 | Power interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2025-09-26 15:16 | 2025-09-26 15:42 | 0.018056 | T | None | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-09-26 15:16 | 2025-09-26 15:42 | 0.018056 | T | For thundering distance relay tripped with phase A | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-09-20 14:10 | 2025-09-20 14:40 | 0.020833 | T | Thundering | 26 | 13 | Power interruption
Ashuganj 230/132/33kV | Cumilla(N) 230 kV Ckt-2 | 2025-09-09 20:13 | 2025-09-09 20:50 | 0.025694 | E/O | Wave trap problem. | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-09-30 16:04 | 2025-09-30 16:11 | 0.0048611 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-09-30 16:11 | 2025-09-30 16:21 | 0.0069444 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-1 | 2025-09-13 18:32 | 2025-09-14 11:24 | 0.70278 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-2 | 2025-09-13 18:32 | 2025-09-14 11:32 | 0.70833 | E/O | Emergency maint.work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-09-03 08:58 | 2025-09-03 09:36 | 0.026389 | E/O | Due to NLDC 01777760419 direction | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-09-08 07:33 | 2025-09-08 09:40 | 0.088194 | E/O | Maintenance work at Feni 132kv ss | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-09-28 18:05 | 2025-09-29 04:52 | 0.44931 | E/O | Breaker replacement for feni 132/33kv grid substation | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 07:15 |  | Unserved Energy: |  | 23.5
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-09-29 08:49 | 2025-09-29 09:09 | 0.013889 | T | Unknown | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-09-29 09:25 | 2025-09-29 09:40 | 0.010417 | T | Unknown | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-09-29 10:28 | 2025-09-29 10:28 | 0 | T | Tripped | 0 | 0 | No interruption
Bhandaria 132/33kV | Bagerhat (L3) | 2025-09-29 08:49 | 2025-09-29 09:14 | 0.017361 | T | Tripped | 39 | 16.25 | Power interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2025-09-22 02:42 | 2025-09-22 03:21 | 0.027083 | T | Tripped | 52 | 33.8 | Power interruption
Goalpara 132/33kV | Goalpara-Orion | 2025-09-22 02:42 | 2025-09-22 03:36 | 0.0375 | T | Tripped | 52 | 46.8 | Power interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2025-09-22 02:43 | 2025-09-22 04:14 | 0.063194 | T | Trip | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2025-09-22 01:12 | 2025-09-22 10:49 | 0.40069 | T | Distance trip | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2025-09-22 02:41 | 2025-09-22 04:08 | 0.060417 | T | Def.EF | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2025-09-22 02:41 | 2025-09-22 04:13 | 0.063889 | T | Distance trip | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2025-09-22 02:41 | 2025-09-22 04:52 | 0.090972 | T | Distance trip | 0 | 0 | No interruption
Narail 132/33kV | Capacitor Bank Bay | 2025-09-24 18:16 | 2025-09-24 18:16 | 0 | T | Causes by bird. | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2025-09-27 11:09 | 2025-09-27 11:22 | 0.0090278 | T | E/F, R phase | 10 | 2.1667 | Power interruption
Bhandaria 132/33kV | Barishal (L4) | 2025-09-29 08:34 | 2025-09-29 10:36 | 0.084722 | E/O | Barishal- Bhandariya 132 KV line S/D for emergency maintenance work | 40 | 81.3333 | Power interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2025-09-07 12:35 | 2025-09-07 14:31 | 0.080556 | E/O | ALDC Instruction | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-09-30 10:12 | 2025-09-30 11:28 | 0.052778 | E/O | Emergency Maintenance work at central ckt end. | 0 | 0 | No interruption
Mongla 132/33kV | 100MW ERBL Solar PS | 2025-09-22 02:58 | 2025-09-22 03:41 | 0.029861 | E/O | Power out from bagerhat | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2025-09-15 03:15 | 2025-09-15 03:15 | 0 | E/O | low voltage. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2025-09-07 12:33 | 2025-09-07 14:31 | 0.081944 | E/O | 132kV CT oil leakage(Phase-R) | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2025-09-20 11:24 | 2025-09-20 13:09 | 0.072917 | E/O | Transformer-3 burnout. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2025-09-20 11:24 | 2025-09-20 13:09 | 0.072917 | E/O | Transformer-3 burnout. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 06:29 |  | Unserved Energy: |  | 180.35
HVDC Grid Circle :
Bheramara 230/132kV | Kushti | 2025-09-18 21:59 | 2025-09-18 22:19 | 0.013889 | T | Distance, Overcorrect 86B | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia -Bheramar | 2025-09-18 21:59 | 2025-09-18 22:19 | 0.013889 | T | Earth Fault Z1 Fault ABC C Phase 2.2 kilometer | 0 | 0 | No interruption
Chuadanga 132/33kV | Jhenaidah-Chuadanga Ckt-1 | 2025-09-14 13:22 | 2025-09-14 14:09 | 0.032639 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 2 | 2025-09-18 22:46 | 2025-09-18 23:10 | 0.016667 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-09-25 04:56 | 2025-09-25 05:59 | 0.04375 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-09-25 04:56 | 2025-09-25 08:46 | 0.15972 | T | Tripped | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2025-09-18 23:16 | 2025-09-19 01:18 | 0.084722 | T | Tripped | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Pabna | 2025-09-18 23:16 | 2025-09-19 08:41 | 0.39236 | T | Thundering | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Bghabari-2 | 2025-09-18 23:25 | 2025-09-19 01:04 | 0.06875 | T | Thundering | 0 | 0 | No interruption
Ullahpara 132/33kV | Baghabari ckt | 2025-09-18 23:25 | 2025-09-19 00:39 | 0.051389 | T | Baghabari ckt Trip at Baghabari End But BKR Close on Ullapara Grid. | 0 | 0 | No interruption
Bheramara 230/132kV | GTG (NW) | 2025-09-14 09:17 | 2025-09-14 12:08 | 0.11875 | E/O | 1-20-89B DS maintenace | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-09-07 10:05 | 2025-09-07 20:18 | 0.42569 | E/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Chuadanga, 132kV Circuit-2(L8) | 2025-09-14 11:11 | 2025-09-14 13:09 | 0.081944 | E/O | Maint.work | 43 | 84.5667 | Power interruption
|  |  | Total : | 1899-12-31 12:06 |  | Unserved Energy: |  | 84.5667
Bogura Grid Circle:
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-09-05 18:21 | 2025-09-05 18:44 | 0.015972 | T | Tripped | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-09-05 18:21 | 2025-09-05 19:02 | 0.028472 | T | Tripped | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2025-09-14 11:48 | 2025-09-14 12:26 | 0.026389 | T | Zone 01 trip | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2025-09-14 11:48 | 2025-09-14 12:29 | 0.028472 | T | Zone 01 trip | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-09-19 11:05 | 2025-09-19 11:21 | 0.011111 | T | thundering | 0 | 0 | No interruption
Bogura 132/33kV | Natore-1 | 2025-09-15 12:37 | 2025-09-15 13:30 | 0.036806 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-09-29 15:45 | 2025-09-29 15:58 | 0.0090278 | T | Tripped | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-09-17 16:17 | 2025-09-18 15:07 | 0.95139 | T | Tripped | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-09-29 12:18 | 2025-09-30 12:46 | 1899-12-31 00:28 | T | Directional Earth Fault | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-2 | 2025-09-29 15:45 | 2025-09-29 15:59 | 0.0097222 | T | None | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-09-18 06:34 | 2025-09-18 06:50 | 0.011111 | T | Tripped | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-09-18 08:44 | 2025-09-18 10:10 | 0.059722 | T | Tripped | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon-1 | 2025-09-07 03:24 | 2025-09-07 04:19 | 0.038194 | T | Tripped | 48 | 44 | Power interruption
Panchagarh 132/33kV | Thakurgaon-1 | 2025-09-18 05:02 | 2025-09-18 05:18 | 0.011111 | T | Fault | 0 | 0 | No interruption
Purbasadipur 132/33kV | Thakurgaon Line-1 | 2025-09-17 16:27 | 2025-09-17 16:48 | 0.014583 | T | None | 0 | 0 | No interruption
Purbasadipur 132/33kV | Thakurgaon Line-2 | 2025-09-17 16:27 | 2025-09-17 16:55 | 0.019444 | T | None | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-09-05 18:23 | 2025-09-05 19:09 | 0.031944 | T | Fault | 0 | 0 | No interruption
Saidpur 132/33kV | 150 MW Cable Line | 2025-09-17 16:30 | 2025-09-17 17:28 | 0.040278 | T | 85/21;85/67; k861; k862. | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-1 | 2025-09-07 03:24 | 2025-09-07 04:19 | 0.038194 | T | 905 B & 920B Trip | 23 | 21.0833 | Power interruption
Thakurgaon 132/33kV | Panchagar CKT-2 | 2025-09-07 03:24 | 2025-09-07 04:19 | 0.038194 | T | 920 B & 923B Trip | 23 | 21.0833 | Power interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-1 | 2025-09-17 16:26 | 2025-09-17 16:50 | 0.016667 | T | Zone-1 | 58 | 23.2 | Power interruption
Thakurgaon 132/33kV | Panchagar CKT-1 | 2025-09-18 05:05 | 2025-09-18 05:18 | 0.0090278 | T | Zone 1 (14.59km) | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-1 | 2025-09-18 05:22 | 2025-09-18 05:58 | 0.025 | T | Zone 1 (22.12km) Breaker trip 905B & 920B | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-2 | 2025-09-12 07:32 | 2025-09-12 09:13 | 0.070139 | E/O | 230kv sub station Red hot. | 15 | 25.25 | Power interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-09-05 20:02 | 2025-09-09 12:01 | 1900-01-02 15:59 | E/O | Instructed by NLDC and Permitted by our incharge sir | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-09-13 17:44 | 2025-09-17 15:00 | 1900-01-02 21:16 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-09-27 19:06 | 2025-10-05 12:17 | 1900-01-06 17:11 | E/O | Emergency maint.work | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-1 | 2025-09-24 10:40 | 2025-09-24 16:15 | 0.23264 | E/O | Shutdown for 102B CB SF6 Gas density monitor Maintenance | 0 | 0 | No interruption
Sirajgonj 230 | SNWPCL (Unit-04) | 2025-09-04 05:46 | 2025-09-04 09:21 | 0.14931 | E/O | Redhot identified | 0 | 0 | No interruption
|  |  | Total : | 1900-01-17 05:03 |  | Unserved Energy: |  | 134.6167
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-07 14:01 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Tr-2(414T) | 2025-09-06 14:02 | 2025-09-06 15:08 | 1:06 | S/O | Project work | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-09-18 12:05 | 2025-09-19 00:57 | 12:52 | S/O | Redhot maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2025-09-07 07:45 | 2025-09-07 10:23 | 2:38 | S/O | High temperature minimize. | 0 | 0 | No interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2025-09-17 17:01 | 2025-09-17 19:36 | 2:35 | S/O | Project work | 60 | 155 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2025-09-19 07:11 | 2025-09-19 11:31 | 4:20 | S/O | Project work | 50 | 216.6667 | Power interruption
Dhamrai 132/33kV | Transformer-2 | 2025-09-24 07:15 | 2025-09-24 09:55 | 2:40 | S/O | PBS maintenance work | 60 | 160 | Power interruption
Jamalpur 132/33kV | T-4 | 2025-09-07 08:10 | 2025-09-07 08:50 | 0:40 | S/O | 33 KV Vabki feeder incoming isolator Maintenance work | 15 | 10 | Power interruption
Jamalpur 132/33kV | T-3 | 2025-09-20 20:14 | 2025-09-20 21:12 | 0:58 | S/O | Temperature rise in the y Phase of a transformer lt bushing. | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-09-10 16:08 | 2025-09-10 17:56 | 1:48 | S/O | 33 kv Radio redhot maintenance. | 62 | 111.6 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-09-13 15:38 | 2025-09-13 17:47 | 2:09 | S/O | 33 kV Red Hot Maintanence of Hi - Tec feeder | 115 | 247.25 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-09-20 07:36 | 2025-09-20 11:09 | 3:33 | S/O | 33 kV Radio Feeder Red Hot Maintanence | 65 | 230.75 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-09-03 08:54 | 2025-09-03 18:17 | 9:23 | S/O | Jack bus drop wire connection | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-09-04 12:15 | 2025-09-04 19:24 | 7:09 | S/O | Project Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-09-23 09:28 | 2025-09-23 14:57 | 5:29 | S/O | CRM test Project Work | 0 | 0 | No interruption
Kodda 132/33kV | Tr-4 (436T) | 2025-09-08 06:42 | 2025-09-08 06:50 | 0:08 | S/O | Bus shift | 0 | 0 | No interruption
Kodda 132/33kV | Tr-1 (406T) | 2025-09-08 06:56 | 2025-09-08 07:24 | 0:28 | S/O | Maintainece work | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-09-08 06:59 | 2025-09-08 10:45 | 3:46 | S/O | Maintainence work | 50 | 188.3333 | Power interruption
Kodda 132/33kV | Tr-1 (406T) | 2025-09-08 11:01 | 2025-09-08 11:52 | 0:51 | S/O | Red hot problem | 50 | 42.5 | Power interruption
Mirpur 132/33kV | T2 | 2025-09-04 06:49 | 2025-09-04 08:29 | 1:40 | S/O | Prevevtive Maintenance of Blue phase Bushing Hot spot | 0 | 0 | No interruption
New Tongi | Tr-1 (4061 | 2025-09-21 11:13 | 2025-09-21 16:21 | 5:08 | S/O | DESCO SAS System Testing and Operation | 0 | 0 | No interruption
New Tongi | Tr-2(4161 | 2025-09-22 14:49 | 2025-09-22 17:32 | 2:43 | S/O | DESCO Project work. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-09-06 10:36 | 2025-09-06 16:16 | 5:40 | S/O | Bay Extension Work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-09-07 09:17 | 2025-09-07 19:25 | 10:08 | S/O | Sreepur Bay extension work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2025-09-05 06:23 | 2025-09-05 07:41 | 1:18 | S/O | project work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-09-16 13:40 | 2025-09-16 16:37 | 2:57 | S/O | Trip Coil Change | 20 | 59 | Power interruption
|  |  | Total : | 1900-01-02 20:07 |  | Unserved Energy: |  | 1421.1
Dhaka (South) Grid Circle :
Haripur 230/132kV | 132KV Bhult | 2025-09-17 09:47 | 2025-09-17 14:24 | 4:37 | S/O | DFDR Commissioning at Bhulta 400 KV SS. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Reserve Bus | 2025-09-25 19:49 | 2025-09-25 19:49 | 0:00 | S/O | Loop Maintenance works | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2025-09-27 07:33 | 2025-09-27 14:49 | 7:16 | S/O | Auto Tr-1 Bhase tertiary cable termination maintenance work | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2025-09-27 15:22 | 2025-09-27 20:49 | 5:27 | S/O | D/S 324 B - phase Finger maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2025-09-05 07:26 | 2025-09-05 08:30 | 1:04 | S/O | High Temperature Maintenance. | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 | 2025-09-23 06:26 | 2025-09-23 08:59 | 2:33 | S/O | To built Cable Trench,by DPDC. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus1 | 2025-09-05 07:45 | 2025-09-05 12:43 | 4:58 | S/O | Aminbazar line Dismantling and re-installation work. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2025-09-12 06:23 | 2025-09-12 10:03 | 3:40 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR - 2 | 2025-09-19 06:47 | 2025-09-19 15:10 | 8:23 | S/O | ATR 2 shutdown by siemens for project work | 0 | 0 | No interruption
Mogbazar 132/33kV | GT-1 | 2025-09-26 04:48 | 2025-09-26 04:48 | 0:00 | S/O | Separate 33kv bus1 | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 | 2025-09-20 08:02 | 2025-09-20 15:50 | 7:48 | S/O | 33kV bus section maintenance work by PBS | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-09-20 08:04 | 2025-09-20 15:50 | 7:46 | S/O | 33kV bus section maintenance work by PBS | 0 | 0 | No interruption
Narshingdi 132/33kV | T-2 | 2025-09-27 09:50 | 2025-09-27 13:19 | 3:29 | S/O | PRD cable Change | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2025-09-01 05:45 | 2025-09-01 08:00 | 2:15 | S/O | for red hot at 33kV isolator (DS). | 0 | 0 | No interruption
Siddhirganj 230/132kV | MTR 2 | 2025-09-13 12:50 | 2025-09-13 14:42 | 1:52 | S/O | Oil refilled in OLTC | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-09-12 09:24 | 2025-09-12 11:41 | 2:17 | S/O | Loop Maintenance works | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2025-09-22 15:07 | 2025-09-22 16:18 | 1:11 | S/O | ৩৩ কেভি ফিডারের স্কাই ওয়্যার ছিড়ে ৩৩ কেভি বাস এর উপর এসে পড়ায় ট্রান্সফরমার-০১ ট্রিপ করে। ফলে ট্রান্সফরমার-০২ শাট ডাউন করা প্রয়োজন হয়। | 15 | 17.75 | Power interruption
|  |  | Total : | 1900-01-01 16:36 |  | Unserved Energy: |  | 17.75
Chattogram Grid Circle :
Bakulia 132/33kV | T-3 (422T) | 2025-09-18 06:22 | 2025-09-18 07:48 | 1:26 | S/O | Hot spot maintenance. | 0 | 0 | No interruption
Coxsbazar 132/33kV | 405T-T1 | 2025-09-13 06:00 | 2025-09-13 14:04 | 8:04 | S/O | TR-1 33(33kV bushing to incomer 2 cable installation ) | 46 | 371.0667 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2025-09-15 09:16 | 2025-09-16 16:39 | 31:23 | S/O | checking and maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-03 | 2025-09-05 06:20 | 2025-09-05 14:52 | 8:32 | S/O | RED HOT MAINTENANCE WORK | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 | 2025-09-17 06:10 | 2025-09-17 10:35 | 4:25 | S/O | red hot maintenance | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) | 2025-09-12 21:52 | 2025-09-12 22:58 | 1:06 | S/O | 33kV secondary bus isolator R-phase red hot maintenance work. | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) | 2025-09-13 06:16 | 2025-09-13 07:32 | 1:16 | S/O | 33/0.44kV Station supply Transformer's 33kV Bus connector Red-hot maintenance work. | 0 | 0 | No interruption
Khulshi 132/33kV | 415T (T2) | 2025-09-20 07:33 | 2025-09-20 09:33 | 2:00 | S/O | Emergency maintenance work | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-1(705T) | 2025-09-22 09:30 | 2025-09-24 10:04 | 48:34 | S/O | Maintenance works | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-2(715T) | 2025-09-24 10:21 | 2025-09-26 10:08 | 47:47 | S/O | Maintenance works | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-3(725T) | 2025-09-26 11:36 | 2025-09-28 11:15 | 47:39 | S/O | Maintenance works | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-02 | 2025-09-04 09:33 | 2025-09-04 17:38 | 8:05 | S/O | Blast wall painting work. | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-02 | 2025-09-05 09:13 | 2025-09-05 17:38 | 8:25 | S/O | Transformer blast wall working | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-02 | 2025-09-06 09:41 | 2025-09-06 17:29 | 7:48 | S/O | Project work | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-01 | 2025-09-17 16:32 | 2025-09-17 18:27 | 1:55 | S/O | PBS project work | 0 | 0 | No interruption
Rampur 230/132/33 | 132kV BUS-02 | 2025-09-14 11:33 | 2025-09-14 17:35 | 6:02 | S/O | Interlock wiring modification purpose | 0 | 0 | No interruption
Rampur 230/132/33 | TR-1 | 2025-09-25 07:18 | 2025-09-25 08:28 | 1:10 | S/O | red hot maintenance | 0 | 0 | No interruption
Rampur 230/132/33 | TR-1 | 2025-09-26 07:07 | 2025-09-26 09:18 | 2:11 | S/O | Red hot on TR-1 secondary R phase | 0 | 0 | No interruption
Shahmirpur 132/33kV | 406T | 2025-09-05 08:12 | 2025-09-05 12:11 | 3:59 | S/O | Redhot maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV | 416T | 2025-09-05 14:30 | 2025-09-05 17:27 | 2:57 | S/O | red hot maintenance work for tr 02 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-09 04:44 |  |  |  | 371.0667
Cumilla Grid Circle :
Chandina 132/33kV | TR-3 | 2025-09-23 11:28 | 2025-09-23 16:41 | 5:13 | S/O | Project work | 6 | 31.3 | Power interruption
Chandina 132/33kV | TR-2 | 2025-09-23 12:02 | 2025-09-23 14:37 | 2:35 | S/O | project work | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2025-09-09 07:34 | 2025-09-09 18:09 | 10:35 | S/O | High temperature at HT bushing ( Y phase) of T5 | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2025-09-11 07:30 | 2025-09-11 13:37 | 6:07 | S/O | Maintenance work | 5 | 30.5833 | Power interruption
Chandpur 132/33kV | 422T(T-5) | 2025-09-22 13:04 | 2025-09-22 15:32 | 2:28 | S/O | Maintenance work | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 | 2025-09-18 14:27 | 2025-09-18 15:40 | 1:13 | S/O | T-2 is in shutdown for maintenance (Red Hot) at PBS end. | 34 | 41.3667 | Power interruption
Chowmuhani 132/33kV |  | 2025-09-14 09:02 | 2025-09-14 10:55 | 1:53 | S/O | 33 KV Dotter Hat Feeder Y Phase Red Hot Maintenance at 33 KV Bus Point | 35 | 65.9167 | Power interruption
Chowmuhani 132/33kV |  | 2025-09-16 20:22 | 2025-09-16 21:55 | 1:33 | S/O | 33 KV L-Bus Feeder B Phase Red Hot Maintenance at incoming DS Point. | 45 | 69.75 | Power interruption
Chowmuhani 132/33kV |  | 2025-09-30 07:09 | 2025-09-30 09:24 | 2:15 | S/O | 33 KV L-Bus Feeder Bus DS Red Hot maintenance | 40 | 90 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-05 | 2025-09-18 21:38 | 2025-09-18 22:34 | 0:56 | S/O | 33KV Section Isolator Red Hot Removed. | 25 | 23.3333 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-09-30 07:51 | 2025-09-30 09:38 | 1:47 | S/O | Maintenance work | 60 | 107 | Power interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-09-27 08:18 | 2025-09-27 17:02 | 8:44 | S/O | For project work | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-3 | 2025-09-29 10:35 | 2025-09-29 11:07 | 0:32 | S/O | transformer maintenance work. | 10 | 5.3333 | Power interruption
Feni 132/33kV | Bus-2 | 2025-09-04 06:49 | 2025-09-04 09:01 | 2:12 | S/O | For red hot work (REB) | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) | 2025-09-17 07:17 | 2025-09-17 09:58 | 2:41 | S/O | T-2 132kV Side Hotspot Work Purpose. | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-09-25 06:40 | 2025-09-25 11:25 | 4:45 | S/O | Redhot maintenance work | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-09-13 12:50 | 2025-09-13 14:32 | 1:42 | S/O | PBS red hot maintenance | 22 | 37.4 | Power interruption
Kulaura 132/33kV | TR-2 | 2025-09-18 16:22 | 2025-09-18 17:56 | 1:34 | S/O | OTI metre replacement | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-09-23 09:00 | 2025-09-23 10:17 | 1:17 | S/O | Red hot maintenance by PBS | 25 | 32.0833 | Power interruption
Ramganj 132/33kV | Transformer-01 | 2025-09-04 07:33 | 2025-09-05 21:33 | 1899-12-31 14:00 | S/O | 33 Bus -1 Red Hot point maintenance | 40 | 1520 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2025-09-02 06:41 | 2025-09-02 08:05 | 1:24 | S/O | 33kv D/S Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-09-02 06:42 | 2025-09-02 08:02 | 1:20 | S/O | Shutdown Taken By Pdb | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-09-06 07:44 | 2025-09-06 10:47 | 3:03 | S/O | Shutdown taken by pbs | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-09-06 07:52 | 2025-09-06 10:52 | 3:00 | S/O | Shutdown taken by pbs | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-09-22 08:39 | 2025-09-22 12:22 | 3:43 | S/O | TR-06 Shutdown Bus Section-05 Taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-09-22 20:11 | 2025-09-22 21:42 | 1:31 | S/O | 33 kv Bus Redhot Maintenance | 40 | 60.6667 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2025-09-23 07:25 | 2025-09-23 08:28 | 1:03 | S/O | PDB's Redhot maintenace | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-09-13 15:16 | 2025-09-13 15:49 | 0:33 | S/O | For 33 kV GCB gas refill work. | 0 | 0 | No interruption
Sylhet (South) | Trafo-2 | 2025-09-02 06:11 | 2025-09-02 09:20 | 3:09 | S/O | Maintenance work | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2025-09-10 07:23 | 2025-09-10 08:39 | 1:16 | S/O | work of PDB | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-09-27 07:28 | 2025-09-27 08:30 | 1:02 | S/O | High temp. maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 23:06 |  |  |  | 2114.7333
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-2 (413 T) | 2025-09-22 03:05 | 2025-09-22 10:50 | 7:45 | S/O | T-2 transformer closing problem | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-2 | 2025-09-04 12:16 | 2025-09-04 13:01 | 0:45 | S/O | WZPDCL-1 ,B-Phase Bus Loop Red Hot Maintenance. | 8 | 6 | Power interruption
Barguna 132/33kV | Transformer-2 | 2025-09-24 07:49 | 2025-09-24 10:19 | 2:30 | S/O | WZPDCL Bus loop red hot maintenance | 6 | 15 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-09-02 07:20 | 2025-09-02 09:15 | 1:55 | S/O | To Remove red hot. | 30 | 57.5 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-09-24 06:13 | 2025-09-24 07:05 | 0:52 | S/O | Jhalokathi WZPDCL 33kV incoming DS Red hot Maintenance | 30 | 26 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-09-29 06:31 | 2025-09-29 08:09 | 1:38 | S/O | High temperature remedy work at different points | 0 | 0 | No interruption | 14:29
Barishal 230/132kV | T-5 | 2025-09-20 07:25 | 2025-09-20 09:47 | 2:22 | S/O | Red Hot maintenance | 30 | 71 | Power interruption
Barishal 230/132kV | T-4 | 2025-09-20 10:08 | 2025-09-20 12:07 | 1:59 | S/O | Redhot maintenance | 9 | 17.85 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2025-09-23 07:01 | 2025-09-23 13:27 | 6:26 | S/O | to change heat shrink tube of termination kit of 33kv u/g cable | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-1 | 2025-09-26 07:16 | 2025-09-26 09:37 | 2:21 | S/O | Redhot Maintenance. | 10 | 23.5 | Power interruption
Goalpara 132/33kV | T-5 | 2025-09-04 07:17 | 2025-09-04 09:16 | 1:59 | S/O | Maintenance work | 4 | 7.9333 | Power interruption
Goalpara 132/33kV | T-6 | 2025-09-04 07:17 | 2025-09-04 09:16 | 1:59 | S/O | Maintenance work | 4 | 7.9333 | Power interruption
Goalpara 132/33kV | T1 | 2025-09-04 07:17 | 2025-09-04 09:16 | 1:59 | S/O | Shutdown taken by pbs | 4 | 7.9333 | Power interruption
Goalpara 132/33kV | T-5 | 2025-09-16 14:57 | 2025-09-16 19:08 | 4:11 | S/O | Maintenance work | 9 | 37.65 | Power interruption
Goalpara 132/33kV | T-6 | 2025-09-16 14:57 | 2025-09-16 17:55 | 2:58 | S/O | Maintenance work | 9 | 26.7 | Power interruption
Goalpara 132/33kV | T1 | 2025-09-16 14:57 | 2025-09-16 19:27 | 4:30 | S/O | Maintenance work | 9 | 40.5 | Power interruption
Gopalganj 132/33kV | T1 | 2025-09-18 08:11 | 2025-09-18 09:53 | 1:42 | S/O | WZ red hot maintenance. | 20 | 34 | Power interruption
Khulna (C) | TR-1 425T | 2025-09-23 07:03 | 2025-09-23 09:02 | 1:59 | S/O | High temp point maintenance | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-09-23 09:13 | 2025-09-23 10:43 | 1:30 | S/O | for temperature reduce | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2025-09-24 07:42 | 2025-09-24 10:02 | 2:20 | S/O | temperature reduce | 0 | 0 | No interruption
Narail 132/33kV | TR1 (403-T) | 2025-09-09 07:10 | 2025-09-09 08:52 | 1:42 | S/O | 33 kV Bus extension | 20 | 34 | Power interruption
Narail 132/33kV | TR1 (403-T) | 2025-09-16 06:26 | 2025-09-16 08:36 | 2:10 | S/O | 33kv bay extension | 20 | 43.3333 | Power interruption
Narail 132/33kV | TR2 (413-T) | 2025-09-17 10:54 | 2025-09-17 13:42 | 2:48 | S/O | Auxiliary 2 Y and B jumper maintenance | 6 | 16.8 | Power interruption
Noapara 132/33kV | T-1 | 2025-09-18 10:59 | 2025-09-18 13:05 | 2:06 | S/O | due to 33kv busbar clamp &connector measuring | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-09-11 08:51 | 2025-09-11 15:07 | 6:16 | S/O | To install annunciator at 132KV & 33KV in the control panel. | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-09-12 10:02 | 2025-09-12 14:40 | 4:38 | S/O | Installation annunciator | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-09-24 08:20 | 2025-09-24 09:21 | 1:01 | S/O | Bauphal 33kv red hot maintenance work ( Amtoli+ Dashmina S/D taken by pbs) | 27.5 | 27.9583 | Power interruption
Payra 400/132/33kV | Bus-I ( 132KV Bus) | 2025-09-02 14:12 | 2025-09-02 14:33 | 0:21 | S/O | Due to Bus coupler PT Y Phase Damage MCB change. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 02:42 |  | Unserved Energy : |  | 501.5917
HVDC Grid Circle
BIPTC | 20DF22 | 2025-09-08 11:16 | 2025-09-08 11:50 | 0:34 | S/O | Shutdown is taken for maintenance work | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-09-05 06:48 | 2025-09-05 08:57 | 2:09 | S/O | 33kV bus loop change. | 15 | 32.25 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2025-09-13 07:08 | 2025-09-13 18:25 | 11:17 | S/O | Maintenance work | 40 | 451.3333 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) | 2025-09-13 07:09 | 2025-09-13 18:27 | 11:18 | S/O | Maintenance work | 40 | 452 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-09-13 07:09 | 2025-09-13 18:28 | 11:19 | S/O | Maintenance work | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-09-28 11:05 | 2025-09-28 13:02 | 1:57 | S/O | Red Hot Maintenance Work. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-09-02 06:40 | 2025-09-02 08:40 | 2:00 | S/O | 33kv busbar-1 maintenance work | 25 | 50 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2025-09-02 06:41 | 2025-09-02 08:40 | 1:59 | S/O | 33kv busbar-1 maintenance work | 25 | 49.5833 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-09-06 07:20 | 2025-09-06 16:01 | 8:41 | S/O | load Shifting T-1 from T-2 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-2 | 2025-09-06 07:30 | 2025-09-06 07:30 | 0:00 | S/O | load shifting T-1 from T-2 | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2025-09-19 09:40 | 2025-09-19 19:04 | 9:24 | S/O | Maintenance work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2025-09-20 10:03 | 2025-09-20 17:29 | 7:26 | S/O | 33 kv auxiliary transformer installation | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2025-09-20 18:38 | 2025-09-20 21:09 | 2:31 | S/O | OLTC tank oil refill | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2025-09-26 07:08 | 2025-09-26 08:29 | 1:21 | S/O | Red hot Maintenance Work | 10 | 13.5 | Power interruption
|  |  | Total : | 1900-01-01 23:56 |  | Unserved Energy : |  | 1048.6667
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) | 2025-09-01 10:42 | 2025-09-01 11:45 | 1:03 | S/O | Oil sample collection. | 0 | 0 | No interruption
Amnura 132/33kV | T-2 (416T) | 2025-09-01 11:54 | 2025-09-01 12:47 | 0:53 | S/O | Oil sample collection. | 0 | 0 | No interruption
Amnura 132/33kV | T-2 (416T) | 2025-09-28 10:25 | 2025-09-28 12:31 | 2:06 | S/O | Mondumala 33 kv ds maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2025-09-18 07:14 | 2025-09-18 09:50 | 2:36 | S/O | 33kv CT Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Station Supply-PGCB | 2025-09-27 09:53 | 2025-09-27 15:04 | 5:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-09-11 10:07 | 2025-09-11 17:12 | 7:05 | S/O | Breaker and CT maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-09-15 10:31 | 2025-09-15 18:44 | 8:13 | S/O | For maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-4 | 2025-09-21 09:35 | 2025-09-21 21:39 | 12:04 | S/O | Connection loop extension between 33 KV CT and CB. | 0 | 0 | No interruption
Chapai 132/33kV | T-4 (435T) | 2025-09-02 16:17 | 2025-09-09 21:28 | 173:11 | S/O | T-04 33 kv trip coil maintenance work | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2025-09-28 08:23 | 2025-09-28 09:20 | 0:57 | S/O | CT 132kV side high temperature maintenance | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2025-09-02 09:28 | 2025-09-02 15:17 | 5:49 | S/O | Oil leakage problem | 0 | 0 | No interruption
Saidpur 132/33kV | TR-01 | 2025-09-10 10:15 | 2025-09-10 10:15 | 0:00 | S/O | QF- GMD-39 and as the instructions of ALDC, Bogura | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 03:08 |  | Unserved Energy : |  | 0
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 886:19 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:September 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2025-09-19 06:55 | 2025-09-19 11:43 | 4:48 | S/O | Project work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2025-09-20 10:53 | 2025-09-20 14:47 | 3:54 | S/O | Maintenance work for temperature increase of C.T. (R phase). | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2025-09-22 13:07 | 2025-09-22 14:35 | 1:28 | S/O | Construction safety net remove | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-1 | 2025-09-19 06:58 | 2025-09-19 11:43 | 4:45 | S/O | scheduled Shutdown Dhamrai s/s end project works | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2025-09-20 16:03 | 2025-09-20 18:09 | 2:06 | S/O | Tree trimming. | 0 | 0 | No interruption
|  |  | Total : | 0.70903 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Bhulta 132/33kV | Haripur | 2025-09-19 06:45 | 2025-09-19 09:40 | 2:55 | S/O | DFDR Installation | 60 | 175 | Power interruption
Bhulta 132/33kV | Narsingdi | 2025-09-19 09:45 | 2025-09-19 09:45 | 0:00 | S/O | Availability of new line(bhulta 400KV to bhulta 132KV) | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Hasnabad | 2025-09-05 10:10 | 2025-09-05 15:06 | 4:56 | S/O | 0 | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-2 | 2025-09-21 12:49 | 2025-09-21 17:02 | 4:13 | S/O | From other end by NLDC | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-09-01 12:46 | 2025-09-01 19:24 | 6:38 | S/O | Shutdown has been taken to restore Fatullah & Shitalakkya ckt to it's previous condition. | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2025-09-01 12:46 | 2025-09-01 18:46 | 6:00 | S/O | Shutdown has been taken to restore Fatullah & Shitalakkya ckt to it's previous condition. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2025-09-16 10:53 | 2025-09-16 12:27 | 1:34 | S/O | Maintenance Work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2025-09-16 12:34 | 2025-09-16 12:54 | 0:20 | S/O | Maintenance work | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2025-09-20 07:14 | 2025-09-20 07:14 | 0:00 | S/O | 132kV shyampur ckt-01 overhead transmission line re-conducting work. | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2025-09-01 10:33 | 2025-09-01 13:00 | 2:27 | S/O | Shutdown Taken by EGCB For Relay testing. | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 2 | 2025-09-18 07:38 | 2025-09-18 20:30 | 12:52 | S/O | 0 | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 1 | 2025-09-19 07:51 | 2025-09-19 20:40 | 12:49 | S/O | Internal maintenance of EGCB end. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 06:44 |  | Unserved Energy: |  | 175
Chattogram Grid Circle :
Baroaulia 132/33kV | Hat-2 | 2025-09-16 07:04 | 2025-09-16 08:55 | 1:51 | S/O | Red hot work at hathazari side | 15 | 27.75 | Power interruption
BSRM 230/33kV | Cumilla Ckt-1 | 2025-09-23 06:45 | 2025-09-23 16:52 | 10:07 | S/O | Feni 230kV SS work | 0 | 0 | No interruption
BSRM 230/33kV | Cumilla Ckt-2 | 2025-09-23 06:46 | 2025-09-23 16:53 | 10:07 | S/O | Feni 230kV SS work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-02 | 2025-09-16 07:06 | 2025-09-16 09:55 | 2:49 | S/O | Red hot maintenance | 80 | 225.3333 | Power interruption
|  |  | Total : | 1899-12-31 00:54 |  | Unserved Energy: |  | 253.0833
Cumilla Grid Circle :
Chandpur 132/33kV | 33 kV T-5 section | 2025-09-09 07:34 | 2025-09-09 10:14 | 2:40 | S/O | High temperature at HT bushing ( Y phase) of T5 | 35 | 93.3333 | Power interruption
Chandpur 132/33kV | 33 kV T-2 section | 2025-09-11 07:30 | 2025-09-11 09:55 | 2:25 | S/O | Maintenance work. | 5 | 12.0833 | Power interruption
Chandpur 132/33kV | 100MW(GT) Power Plant Incomer (T4) | 2025-09-29 10:55 | 2025-09-29 15:57 | 5:02 | S/O | Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2025-09-01 10:20 | 2025-09-01 11:22 | 1:02 | S/O | Red Hot Maintenance And Conductor Change of CT to GCB Y Phase | 15 | 15.5 | Power interruption
Chowmuhani 132/33kV | TR1 | 2025-09-03 23:00 | 2025-09-04 01:30 | 2:30 | S/O | 33 KV Maijdee Feeder incoming Y Phase DS Red Hot Maintenance. | 25 | 62.5 | Power interruption
Cumilla(S) 132/33kV | Cumilla North-2 | 2025-09-18 08:19 | 2025-09-18 09:06 | 0:47 | S/O | Emergency maintenance work. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-09-27 08:31 | 2025-09-27 17:35 | 9:04 | S/O | Project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2025-09-27 08:32 | 2025-09-27 16:50 | 8:18 | S/O | Project work | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-09-08 07:30 | 2025-09-08 09:39 | 2:09 | S/O | S/D Taken for Bus coupler Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-1 | 2025-09-16 06:14 | 2025-09-16 18:43 | 12:29 | S/O | 230kV Feni LILO Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-2 | 2025-09-16 06:14 | 2025-09-16 20:48 | 14:34 | S/O | 230kV Feni LILO Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-09-27 08:22 | 2025-09-27 17:35 | 9:13 | S/O | Bus coupler GCB Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-09-28 17:58 | 2025-09-29 04:58 | 11:00 | S/O | Assalamu-alaikum Sir, Chamuhani/dagonbhuyan Ckt-01 s/down taken for pole Maintenance work | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2025-09-17 09:42 | 2025-09-17 11:33 | 1:51 | S/O | Hotspot maintenance by 86 MW | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-09-04 23:46 | 2025-09-06 01:50 | 26:04 | S/O | RHD Project Works | 0 | 0 | No interruption
Sreemongol 132/33kV | sreemangal-Shahjibazar circuit-2 | 2025-09-04 23:46 | 2025-09-06 01:50 | 26:04 | S/O | RHD Project Works. | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2025-09-02 08:44 | 2025-09-02 10:20 | 1:36 | S/O | Chhatak-Sunamgonj CKT-2 Maintenance work | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2025-09-16 15:12 | 2025-09-16 17:17 | 2:05 | S/O | Chattak-Sunamganj CKT-2 Shutdown due to system protection | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-09-20 14:25 | 2025-09-20 14:40 | 0:15 | S/O | 112B CB Maitanance | 26 | 6.5 | Power interruption
Sylhet 132/33kV | Sylhet-Sylhet (S) Ckt | 2025-09-29 08:26 | 2025-09-29 13:05 | 4:39 | S/O | Due to Under Construction GIS Building works. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-09-29 10:40 | 2025-09-29 11:54 | 1:14 | S/O | 132 KV 699 number tower nest broken job. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-09-30 08:43 | 2025-09-30 13:45 | 5:02 | S/O | Due to under Construction GIS Building Works. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 06:03 |  | Unserved Energy: |  | 189.9167
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-09-25 09:46 | 2025-09-25 10:01 | 0:15 | S/O | Shut down for Emergency Tree Trimming. | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-09-29 08:36 | 2025-09-29 10:35 | 1:59 | S/O | High temperature remedy work at different points and loop changing | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-09-12 07:07 | 2025-09-12 11:45 | 4:38 | S/O | clamp change for temperature reduce | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2025-09-16 08:35 | 2025-09-16 22:28 | 13:53 | S/O | Ordered by ALDC | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-09-30 10:12 | 2025-09-30 11:29 | 1:17 | S/O | temperature reduce | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2025-09-04 09:25 | 2025-09-04 10:57 | 1:32 | S/O | 0 | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2025-09-04 11:15 | 2025-09-04 13:12 | 1:57 | S/O | 0 | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-09-12 07:08 | 2025-09-12 11:44 | 4:36 | S/O | 0 | 0 | 0 | No interruption
Narail 132/33kV | Capacitor Bank Bay | 2025-09-25 10:06 | 2025-09-25 10:06 | 0:00 | S/O | Due to unbalance current raising need to capacitor cell test. | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2025-09-12 06:49 | 2025-09-12 11:49 | 5:00 | S/O | by aldc | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-2 | 2025-09-12 06:49 | 2025-09-12 11:50 | 5:01 | S/O | by aldc | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2025-09-16 08:36 | 2025-09-16 22:29 | 13:53 | S/O | Distance Relay Change by SPMD | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2025-09-30 10:09 | 2025-09-30 11:30 | 1:21 | S/O | ALDC Khulna Instraction | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-2 | 2025-09-30 10:09 | 2025-09-30 11:30 | 1:21 | S/O | ALDC Khulna Instraction | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2025-09-04 09:24 | 2025-09-04 10:58 | 1:34 | S/O | 0 | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2025-09-04 11:15 | 2025-09-04 13:24 | 2:09 | S/O | 0 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 12:26 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Baharampur-4 | 2025-09-01 09:51 | 2025-09-01 20:40 | 10:49 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2025-09-02 09:57 | 2025-09-02 19:35 | 9:38 | S/O | shutdown is taken from baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-09-03 08:26 | 2025-09-03 19:54 | 11:28 | S/O | Shutdown has been taken from Baharampur end. | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-09-04 08:59 | 2025-09-04 20:06 | 11:07 | S/O | Shutdown has been taken from Baharampur end. | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-09-05 08:06 | 2025-09-05 21:58 | 13:52 | S/O | 0 | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-09-06 09:35 | 2025-09-06 21:25 | 11:50 | S/O | Shutdown is taken by baharampur end. | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-09-09 09:44 | 2025-09-09 18:15 | 8:31 | S/O | 0 | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2025-09-11 10:51 | 2025-09-11 19:00 | 8:09 | S/O | Shutdown is taken from Baharampur end. | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2025-09-17 09:50 | 2025-09-17 17:42 | 7:52 | S/O | Shutdown is taken for Isolator maintenance | 0 | 0 | No interruption
Chuadanga 132/33kV | Jhenaidah-Chuadanga Ckt-2 | 2025-09-13 07:10 | 2025-09-13 20:25 | 13:15 | S/O | 0 | 0 | 0 | No interruption
Chuadanga 132/33kV | Jhenaidah-Chuadanga Ckt-1 | 2025-09-13 07:11 | 2025-09-13 18:24 | 11:13 | S/O | 0 | 100 | 1121.6667 | Power interruption
Chuadanga 132/33kV | Jhenaidah-Chuadanga Ckt-2 | 2025-09-14 11:10 | 2025-09-14 13:22 | 2:12 | S/O | Maintenance work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-09-12 09:27 | 2025-09-12 12:33 | 3:06 | S/O | Bonpara s/s Lilo | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2025-09-12 09:27 | 2025-09-12 12:33 | 3:06 | S/O | Bonpara s/s Lilo | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-09-21 10:45 | 2025-09-21 15:48 | 5:03 | S/O | LILO wok at bonpara | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2025-09-21 10:45 | 2025-09-21 15:48 | 5:03 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-09-26 06:36 | 2025-09-27 20:38 | 38:02 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Chuadanga, 132kV Circuit-2(L8) | 2025-09-13 07:13 | 2025-09-13 19:08 | 11:55 | S/O | None | 47 | 560.0833 | Power interruption
Jhenaidah 230/132kV | Jhenaidah2-Chuadanga | 2025-09-13 07:14 | 2025-09-13 07:14 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 18:11 |  | Unserved Energy: |  | 1681.75
Bogura Grid Circle :
Amnura 132/33kV | Amnura - 100MW PPP | 2025-09-08 09:59 | 2025-09-08 13:43 | 3:44 | S/O | Redhot at Chapainawabganj 100MW line bay. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2025-09-12 07:42 | 2025-09-12 17:15 | 9:33 | S/O | Maint.work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2025-09-13 07:52 | 2025-09-13 17:41 | 9:49 | S/O | project work | 0 | 0 | No interruption
Bogura 132/33kV | Natore-2 | 2025-09-29 07:55 | 2025-09-29 13:32 | 5:37 | S/O | natore ckt2 conductor change | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-09-04 14:53 | 2025-09-04 18:30 | 3:37 | S/O | Dfdr Integration | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-09-05 10:06 | 2025-09-05 16:01 | 5:55 | S/O | Dfdr Integration | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 1 | 2025-09-12 07:26 | 2025-09-12 09:01 | 1:35 | S/O | Red-hot maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-2 | 2025-09-12 07:33 | 2025-09-12 09:10 | 1:37 | S/O | Red hot maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-09-04 15:01 | 2025-09-04 15:48 | 0:47 | S/O | Partial Discharge monitor checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-09-05 10:06 | 2025-09-05 16:01 | 5:55 | S/O | Project work at Bogura 230 kv grid ss end. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2025-09-12 07:43 | 2025-09-12 17:16 | 9:33 | S/O | Aviation painting work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2025-09-13 07:53 | 2025-09-13 17:42 | 9:49 | S/O | Tower aviation painting work (Barapukuria side) | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-09-21 09:05 | 2025-09-21 20:51 | 11:46 | S/O | Partial Discharge Testing | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-09-21 09:06 | 2025-09-21 20:51 | 11:45 | S/O | Partial Discharge Testing | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-09-22 08:44 | 2025-09-22 17:19 | 8:35 | S/O | Partial discharge monitor checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-09-22 08:44 | 2025-09-22 17:19 | 8:35 | S/O | Partial discharge monitor checking | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Nia Ckt-1 | 2025-09-22 14:10 | 2025-09-22 14:10 | 0:00 | S/O | Pile casting work of terminal gantry under G to G project. | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-09-12 09:21 | 2025-09-12 12:38 | 3:17 | S/O | Requested by ALDC. | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-2 | 2025-09-12 09:26 | 2025-09-12 12:38 | 3:12 | S/O | Maint.work | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-09-21 10:48 | 2025-09-21 15:48 | 5:00 | S/O | Jumper wire connection | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-2 | 2025-09-21 10:48 | 2025-09-21 15:50 | 5:02 | S/O | Jumper wire connection | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV PPP 50 Mw | 2025-09-25 07:02 | 2025-09-25 16:12 | 9:10 | S/O | Due to x former maintenance at PDB End | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-GTPS | 2025-09-29 16:35 | 2025-09-29 18:11 | 1:36 | S/O | Piling work of G2G project | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-GTPS | 2025-09-30 09:52 | 2025-10-01 11:43 | 25:51 | S/O | Pilling Work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 17:20 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-01-26 06:39 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September 2025
| Area | Previous Month (August' 2025) |  |  |  | Current Month (September '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 16 | 7 | 56 | 79 | 35 | 12 | 30 | 77
2 | Dhaka (South) Grid Circle. | 26 | 7 | 54 | 87 | 23 | 16 | 29 | 68
3 | Chattogram Grid Circle. | 5 | 8 | 23 | 36 | 13 | 14 | 24 | 51
4 | Cumilla Grid Circle. | 20 | 15 | 62 | 97 | 21 | 24 | 53 | 98
5 | Khulna Grid Circle. | 10 | 13 | 50 | 73 | 23 | 15 | 44 | 82
6 | HVDC Grid Circle | 8 | 23 | 15 | 46 | 20 | 12 | 33 | 65
7 | Bogura Grid Circle. | 18 | 12 | 35 | 65 | 33 | 17 | 36 | 86
8 | Others
9 | Total | 103 | 85 | 295 | 483 | 168 | 110 | 249 | 527
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September 2025
| Area | Previous Month (August' 2025) |  |  |  | Current Month (September '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 165.7 | 273.5 | 1045.28 | 1484.48 | 834.55 | 371.33 | 1421.1 | 2626.98
2 | Dhaka (South) Grid Circle. | 828.2 | 87.08 | 11381.47 | 12296.75 | 5782.85 | 5728.78 | 192.75 | 11704.38
3 | Chattogram Grid Circle. | 81.43 | - | 1103.6 | 1185.03 | 313.7 | 312.05 | 624.15 | 1249.9
4 | Cumilla Grid Circle. | 7.27 | 123.8 | 503.17 | 634.24 | 137.22 | 228.72 | 2304.65 | 2670.59
5 | Khulna Grid Circle. | 69.73 | 75.77 | 1101.5 | 1247 | 214.67 | 385.79 | 501.59 | 1102.05
6 | HVDC Grid Circle | 2053.2 | 143.03 | 291.2 | 2487.43 | 38 | 165.99 | 2730.42 | 2934.41
7 | Bogura Grid Circle. | 747.51 | 44.47 | 887.66 | 1679.64 | 218.34 | 139.58 | - | 357.92
8 | Others
9 | Total | 3953.04 | 747.65 | 16313.88 | 21014.57 | 7539.33 | 7332.24 | 7774.66 | 22646.23
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 20 | 10 | 30 | 9 | 5 | 16 | 2323.18
2 | Dhaka (South) | 5031.6 | 9 | 1 | 10 | 1 | 2 | 7 | 379.35
3 | Chattogram | 2042 | 6 | 1 | 7 |  | 1 | 6 | 746.02
4 | Khulna | 2434 | 12 | 18 | 30 | 2 | 7 | 21 | 921.7
5 | HVDC | 5954.3 | 8 | 6 | 14 | 5 | 1 | 8 | 1168.09
6 | Bogura | 3145.6 | 11 | - | 11 | 3 | 1 | 7 | 223.3
7 | Cumilla | 2981 | 13 | 13 | 26 | 5 | 4 | 17 | 2457.16
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 8218.8
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.89%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.87%
4 | Khulna | 99.96%
5 | HVDC | 99.97%
6 | Bogura | 99.94%
7 | Cumilla | 99.96% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 9 | - | 9 | 4 | 3 | 2 | 303.8
2 | Dhaka (South) | 990.29 | - | 3 | 1 | 4 | - | - | 4 | 11324.5
3 | Chattogram | 917 | - | 1 | 2 | 3 | - | - | 3 | 503.88
4 | Khulna | 1238.4 | - | 5 | - | 5 | 2 | 2 | 1 | 180.35
5 | HVDC | 1325 | - | 1 | 2 | 3 | - | - | 3 | 1766.32
6 | Bogura | 1803.3 | - | 5 | - | 5 | 1 | 1 | 3 | 134.62
7 | Cumilla | 1648.16 | - | 2 | 5 | 7 | 1 | 2 | 4 | 213.42
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 14426.89
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.98%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2025-09-01 | 8 | - | 14 | 21 hr 32 min | 5 | 156 hr 05 min | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:September 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bajitpur 132/33kV | 1 | 0.015972 | 19.1667
Bhaluka 132/33kV | 4 | 0.13125 | 118.15
Kaliakoir 400/230/132kV | 2 | 0.044444 | 266.67
Kishoreganj 132/33kV | 3 | 0.17639 | 98.83
Sreepur 230/132/33kV | 5 | 0.034722 | 36.27
Bhaluka 132/33kV | 2 | 4:12 | 136
Manikganj 132/33kV | 1 | 1:42 | 8.5
Sreepur 230/132/33kV | 2 | 0:57 | 218.5
Bhaluka 132/33kV | 3 | 0.028472 | 65.73
Ghatail 132/33kV | 2 | 0.052083 | 75
Rajendrapur 132/33kV | 1 | 0:58 | 7.7333
Sreepur 230/132/33kV | 1 | 0:18 | 39
Tongi 230/132/33kV | 1 | 1:12 | 108
Manikganj 132/33kV | 1 | 1:40 | 8.3333
Bhaluka 132/33kV | 1 | 2:35 | 155
Dhamrai 132/33kV | 2 | 7:00 | 376.67
Jamalpur 132/33kV | 1 | 0.027778 | 10
Kabirpur 132/33kV | 3 | 0.3125 | 589.6
Kodda 132/33kV | 2 | 0.19236 | 230.83
Sreepur 230/132/33kV | 1 | 0.12292 | 59
Hasnabad 132/33kV | 1 | 0.044444 | 53.3333
Hasnabad 230/132kV | 3 | 0.13403 | 93.28
Sonargaon 132/33kV | 1 | 0.0097222 | 11.2
Srinagar 132/33kV | 1 | 2:03 | 30.75
Sonargaon 132/33kV | 3 | 3:00 | 173.03
Bhulta 400/230kV | 2 | 148:36 | 11145
Madanganj 132/33kV | 1 | 0.09375 | 4.5
Srinagar 132/33kV | 1 | 0.049306 | 17.75
Bhulta 132/33kV | 1 | 0.12153 | 175
Agrabad 132/33kV | 2 | 0.15625 | 157.5
Halishahar 132/33kV | 1 | 0.11319 | 70.6333
Madunaghat 132/33kV | 1 | 0.20972 | 85.5667
Dohazari 132/33kV | 1 | 0.022917 | 8.25
Hathazari 230/132/33kV | 1 | 2:39 | 53
Baroaulia 132/33kV | 1 | 3:29 | 250.8
Coxsbazar 132/33kV | 1 | 8:04 | 371.0667
Baroaulia 132/33kV | 1 | 1:51 | 27.75
Hathazari 230/132/33kV | 1 | 2:49 | 225.3333
Cumilla(S) 132/33kV | 1 | 2:51 | 95.3
Sylhet (South) | 1 | 0:19 | 11.0833
Sylhet 132/33kV | 1 | 0:22 | 7.3333
Chowmuhani 132/33kV | 1 | 2:44 | 54.6667
Brahmanbaria 132/33kV | 1 | 0.059028 | 22.6667
Chauddagram 132/33kV | 1 | 0.045139 | 41.1667
Cumilla(N) 230/132/33kV | 1 | 0.088889 | 42.6667
Kachua 230/132/33kV | 1 | 0.078472 | 56.5
Kasba 132/33kV | 1 | 0.027083 | 11.05
Muradnagar 132/33kV | 1 | 0.029167 | 10.5
Sylhet 132/33kV | 1 | 0.020833 | 13
Chandina 132/33kV | 1 | 5:13 | 31.3
Chandpur 132/33kV | 1 | 6:07 | 30.5833
Chauddagram 132/33kV | 1 | 1:13 | 41.3667
Chowmuhani 132/33kV | 3 | 5:41 | 225.67
Cumilla(N) 230/132/33kV | 2 | 2:43 | 130.33
Daudkandi 132/33kV | 1 | 0:32 | 5.3333
Kulaura 132/33kV | 2 | 2:59 | 69.48
Ramganj 132/33kV | 1 | 1899-12-31 14:00 | 1520
Shahjibazar 132/33kV | 1 | 1:31 | 60.6667
Chandpur 132/33kV | 2 | 5:05 | 105.42
Chowmuhani 132/33kV | 2 | 3:32 | 78
Sylhet 132/33kV | 1 | 0:15 | 6.5
Bagerhat 132/33kV | 2 | 3:06 | 59.67
Khulna (C) | 2 | 3:46 | 26.37
Mongla 132/33kV | 1 | 0:38 | 3.1667
Narail 132/33kV | 1 | 0:35 | 26.25
Rajbari 132/33kV | 1 | 0:02 | 0.2
Mongla 132/33kV | 1 | 0:34 | 19.8333
Patuakhali 132/33kV | 1 | 0:48 | 32
Satkhira 132/33kV | 3 | 6:03 | 252.63
Bhandaria 132/33kV | 1 | 0:25 | 16.25
Goalpara 132/33kV | 2 | 1:33 | 80.6
Patuakhali 132/33kV | 1 | 0:13 | 2.1667
Bhandaria 132/33kV | 1 | 2:02 | 81.3333
Barguna 132/33kV | 2 | 3:15 | 21
Barishal 132/33kV | 2 | 2:47 | 83.5
Barishal 230/132kV | 2 | 4:21 | 88.85
Faridpur 132/33kV | 1 | 2:21 | 23.5
Goalpara 132/33kV | 6 | 17:36 | 128.65
Gopalganj 132/33kV | 1 | 1:42 | 34
Narail 132/33kV | 3 | 6:40 | 94.13
Patuakhali 132/33kV | 1 | 1:01 | 27.9583
Bheramara(GK) 132/33kV | 4 | 1:03 | 22.67
Kushtia 132/33kV | 1 | 0:23 | 15.3333
Bhangura 132/33kV | 1 | 0:45 | 12
Jhenaidah 132/33kV | 1 | 1:39 | 57.75
Pabna 132/33kV | 1 | 1:10 | 11.6667
Jhenaidah 132/33kV | 1 | 1:58 | 84.5667
Chuadanga 132/33kV | 3 | 2:09 | 935.58
Ishurdi 132/33kV | 2 | 3:59 | 99.58
Kushtia 132/33kV | 1 | 1:21 | 13.5
Chuadanga 132/33kV | 1 | 11:13 | 1121.6667
Jhenaidah 132/33kV | 1 | 11:55 | 560.0833
Chapai 132/33kV | 1 | 1:46 | 14.1333
Purbasadipur 132/33kV | 1 | 1:23 | 48.4167
Saidpur 132/33kV | 1 | 0:08 | 4.8
Sirajganj 132/33kV | 2 | 2:05 | 10.42
Thakurgaon 132/33kV | 2 | 0:52 | 31.2
Mithapukur 132/33kV | 2 | 4:03 | 74
Purbasadipur 132/33kV | 1 | 2:16 | 20.1667
Sirajganj 132/33kV | 1 | 2:01 | 20.1667
Panchagarh 132/33kV | 1 | 0:55 | 44
Thakurgaon 132/33kV | 3 | 2:14 | 65.37
Bogura 132/33kV | 1 | 1:41 | 25.25
| 160 | 447:16 | 22645.6883
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: September 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 16 | 2025-09-28 17:00
2 | AKSML | 153 | 2025-09-09 04:00
3 | Aftabnagar | 46 | 2025-09-01 18:30
4 | Agargaon | 150 | 2025-09-01 16:00
5 | Agrabad | 110 | 2025-09-23 20:00
6 | Amnura | 38 | 2025-09-29 23:00
7 | Ashuganj | 114 | 2025-09-26 21:00
8 | BSRM | 195 | 2025-09-01 05:00
9 | Bagerhat | 89 | 2025-09-29 21:00
10 | Bajitpur | 108 | 2025-09-27 23:00
11 | Bakulia | 107 | 2025-09-24 16:00
12 | Banani | 59.4 | 2025-09-10 13:00
13 | Bangabhaban | 27 | 2025-09-07 10:00
14 | Barapukuria | 78 | 2025-09-01 22:00
15 | Barguna | 24 | 2025-09-01 20:00
16 | Barishal | 133 | 2025-09-10 12:00
17 | Barishal-230 | 146 | 2025-09-28 01:00
18 | Baroaulia | 84 | 2025-09-20 10:00
19 | Baroirhat | 83 | 2025-09-25 18:30
20 | Bashundhara | 229 | 2025-09-01 15:00
21 | BashundharaCement | 12 | 2025-09-15 15:00
22 | Beanibazar | 92 | 2025-09-26 22:00
23 | Benapole | 74 | 2025-09-08 22:00
24 | Bhaluka | 162 | 2025-09-29 19:30
25 | Bhandaria | 88 | 2025-09-22 13:00
26 | Bhangura | 44 | 2025-09-01 21:00
27 | Bheramara(GK) | 78 | 2025-09-01 22:00
28 | Bhulta | 224 | 2025-09-29 19:30
29 | Bog-Sherpur | 86 | 2025-09-01 23:00
30 | Bogura | 190 | 2025-09-25 19:30
31 | Borhanuddin | 227 | 2025-09-07 19:00
32 | Brahmanbaria | 152 | 2025-09-01 20:00
33 | Cantonment | 162 | 2025-09-01 15:00
34 | Chandina | 43.53 | 2025-09-09 23:00
35 | Chandpur | 94 | 2025-09-09 00:00
36 | Chandraghona | 44 | 2025-09-20 19:00
37 | Chapai | 78 | 2025-09-01 23:00
38 | Charsaidpur | 42 | 2025-09-01 00:00
39 | Chauddagram | 84 | 2025-09-30 18:00
40 | Chhatak | 48 | 2025-09-22 00:00
41 | Chowmuhani | 205 | 2025-09-24 22:00
42 | Chuadanga | 136 | 2025-09-01 22:00
43 | Coxsbazar | 151 | 2025-09-30 14:00
44 | Cumilla(N) | 156 | 2025-09-03 19:00
45 | Cumilla(S) | 172 | 2025-09-25 18:30
46 | Daganbhuiyan | 0 | 2025-09-01 00:00
47 | Daudkandi | 162 | 2025-09-24 20:00
48 | DhakaUniversity | 114 | 2025-09-21 13:00
49 | Dhamrai | 140 | 2025-09-11 09:00
50 | Dhanmondi | 154.3 | 2025-09-03 13:00
51 | Dohazari | 118 | 2025-09-06 19:00
52 | Faridpur | 198 | 2025-09-01 22:00
53 | Fatullah | 122 | 2025-09-29 11:00
54 | Fenchuganj | 53 | 2025-09-21 20:00
55 | Feni | 132 | 2025-09-29 20:00
56 | GPH | 100 | 2025-09-23 01:00
57 | Ghatail | 98 | 2025-09-05 19:00
58 | Ghorashal | 22 | 2025-09-21 15:00
59 | Ghorashal-230 | 107 | 2025-09-30 20:00
60 | Goalpara | 42 | 2025-09-01 19:30
61 | Gollamari | 114 | 2025-09-08 23:00
62 | Gopalganj | 120 | 2025-09-21 18:30
63 | Gulshan | 144 | 2025-09-01 15:00
64 | Halishahar | 85 | 2025-09-26 01:00
65 | HaripurSBU | 171 | 2025-09-04 16:00
66 | Hasnabad | 107 | 2025-09-25 18:30
67 | Hathazari | 95 | 2025-09-30 20:00
68 | Ishurdi | 91 | 2025-09-01 19:00
69 | Jaldhaka | 98 | 2025-09-01 19:30
70 | Jamalpur | 139 | 2025-09-02 00:00
71 | Jashore | 164 | 2025-09-08 19:30
72 | Jhenaidah | 155 | 2025-09-24 21:00
73 | Joydebpur | 172 | 2025-09-21 19:00
74 | Joypurhat | 77 | 2025-09-06 20:00
75 | Juldah | 19.5 | 2025-09-20 11:00
76 | KSRM | 65 | 2025-09-15 11:00
77 | Kabirpur | 274 | 2025-09-08 11:00
78 | Kachua | 110 | 2025-09-05 21:00
79 | Kallyanpur | 123 | 2025-09-07 00:00
80 | Kalurghat | 44 | 2025-09-09 15:00
81 | Kamrangirchar | 85 | 2025-09-10 18:30
82 | Kaptai | N/A | N/A
83 | Kasba | 42 | 2025-09-01 20:00
84 | Kazla | 123 | 2025-09-03 19:30
85 | Keranigonj | 105 | 2025-09-07 19:30
86 | Khagrachori | 38 | 2025-09-01 18:30
87 | Khulna | 92 | 2025-09-29 13:00
88 | Khulshi | 210 | 2025-09-11 14:00
89 | Kishoreganj | 147 | 2025-09-02 20:00
90 | Kodda | 322 | 2025-09-16 18:30
91 | Kulaura | 63 | 2025-09-02 18:30
92 | Kurigram | 76 | 2025-09-02 21:00
93 | Kushtia | 182 | 2025-09-13 18:30
94 | Laksam | 46 | 2025-09-05 23:00
95 | Lakshmipur | 41 | 2025-09-06 23:00
96 | Lalbag | 65 | 2025-09-25 13:00
97 | Lalmonirhat | 74 | 2025-09-01 19:00
98 | MI_Cement | 19 | 2025-09-30 10:00
99 | Madanganj | 45 | 2025-09-29 00:00
100 | Madaripur | 133 | 2025-09-01 21:00
101 | Madartek | 110 | 2025-09-01 22:00
102 | Madunaghat | 70 | 2025-09-14 18:30
103 | Magura | 76 | 2025-09-01 19:30
104 | Mahasthangarh | 94 | 2025-09-02 00:00
105 | Maijdee | 24 | 2025-09-27 22:00
106 | Manikganj | 139 | 2025-09-01 19:30
107 | Maniknagar | 74 | 2025-09-24 14:00
108 | Matarbari | 59 | 2025-09-08 19:00
109 | Matuail | 78 | 2025-09-21 12:00
110 | Metrorail_Motijheel | N/A | N/A
111 | Metrorail_Uttara | N/A | N/A
112 | Millgate | 140 | 2025-09-01 15:00
113 | Mirpur | 141 | 2025-09-09 11:00
114 | Mirsorai | 100 | 2025-09-21 04:00
115 | Mirzapur | 50 | 2025-09-01 17:00
116 | Mithapukur | 84 | 2025-09-01 19:00
117 | Modern | N/A | N/A
118 | Mogbazar | 125.8 | 2025-09-01 17:00
119 | Mongla | 50 | 2025-09-24 11:00
120 | Motijheel | 51 | 2025-09-01 18:30
121 | Muktagacha | 45 | 2025-09-26 08:00
122 | Munshiganj | 127 | 2025-09-11 00:00
123 | Muradnagar | 46 | 2025-09-01 22:00
124 | Mymensingh | 230 | 2025-09-02 22:00
125 | Naogaon | 157 | 2025-09-01 22:00
126 | Narail | 66 | 2025-09-01 19:00
127 | Narinda | 84 | 2025-09-08 13:00
128 | Narshingdi | 198 | 2025-09-30 21:00
129 | Natore | 169 | 2025-09-01 22:00
130 | Nawabganj | 70.8 | 2025-09-10 20:00
131 | Netrakona | 163 | 2025-09-30 18:30
132 | New | 82 | 2025-09-03 16:00
133 | Niamatpur | 86 | 2025-09-01 22:00
134 | Noapara | 50 | 2025-09-01 19:30
135 | PHP | 9 | 2025-09-01 13:00
136 | Pabna | 142 | 2025-09-01 19:30
137 | Palashbari | 139 | 2025-09-29 19:00
138 | Panchagarh | 70 | 2025-09-01 22:00
139 | Patiya | 55 | 2025-09-20 14:00
140 | Patuakhali | 79 | 2025-09-20 01:00
141 | Payra | 40 | 2025-09-19 22:00
142 | Postogola | 74 | 2025-09-24 13:00
143 | Purbachal | 26 | 2025-09-01 22:00
144 | Purbasadipur | 139 | 2025-09-01 19:30
145 | Rahanpur | 45 | 2025-09-01 22:00
146 | Rahim | 53 | 2025-09-10 17:00
147 | Rajbari | 97 | 2025-09-25 19:00
148 | Rajendrapur | 144 | 2025-09-02 18:30
149 | Rajshahi | 126 | 2025-09-02 00:00
150 | Rajshahi-230 | 114 | 2025-09-01 21:00
151 | Ramganj | 124 | 2025-09-25 21:00
152 | Rampur | 53 | 2025-09-12 21:00
153 | Rangamati | 21 | 2025-09-17 18:30
154 | Rangpur | 166 | 2025-09-22 18:30
155 | Ruppur | 9.8 | 2025-09-10 09:00
156 | SSM | 17 | 2025-09-17 02:00
157 | Saidpur | 117 | 2025-09-01 19:00
158 | Satkhira | 140 | 2025-09-01 19:00
159 | Satmasjid | 115 | 2025-09-10 18:30
160 | Savar | 255 | 2025-09-04 16:00
161 | SevenRings | 21.07 | 2025-09-09 16:00
162 | ShahCement | 39 | 2025-09-04 19:00
163 | Shahjadpur | 99 | 2025-09-01 19:30
164 | Shahjibazar | 152 | 2025-09-03 22:00
165 | Shahmirpur | 69 | 2025-09-03 00:00
166 | Shariatpur | 102 | 2025-09-30 22:00
167 | Sherpur | 154 | 2025-09-01 00:00
168 | Shikalbaha | 30 | 2025-09-25 19:00
169 | Shitalakhya | 95 | 2025-09-25 16:00
170 | Sholosohor | 53 | 2025-09-29 12:00
171 | Shyampur | 176 | 2025-09-06 10:00
172 | Siddhirganj | 135 | 2025-09-10 15:00
173 | Sirajganj | 134 | 2025-09-01 20:00
174 | Sonargaon | 160 | 2025-09-29 18:00
175 | Sreemongol | 96 | 2025-09-26 18:00
176 | Sreepur | 121 | 2025-09-27 19:00
177 | Srinagar | 57 | 2025-09-10 19:30
178 | Sunamganj | 67 | 2025-09-24 21:00
179 | Sylhet | 62 | 2025-09-27 20:00
180 | Sylhet-132 | 157 | 2025-09-22 18:00
181 | TK | 45 | 2025-09-01 18:30
182 | Tangail | 188 | 2025-09-30 23:00
183 | Taraganj | 26 | 2025-09-01 19:30
184 | Thakurgaon | 122 | 2025-09-01 21:00
185 | Tongi | 146 | 2025-09-21 15:00
186 | Ullahpara | 51 | 2025-09-22 18:30
187 | Ullon | 69 | 2025-09-01 22:00
188 | Uttara | 103 | 2025-09-04 13:00
189 | UttaraNew | 72 | 2025-09-01 21:00
190 | Zigatola | 82 | 2025-09-06 23:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: September 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5904.79 | 2025-09-04 | 16:00
Chattogram | 1657.57 | 2025-09-25 | 18:00
Cumilla | 1585.64 | 2025-09-24 | 23:00
Mymensingh | 1224 | 2025-09-01 | 0:00
Sylhet | 729 | 2025-09-21 | 20:00
Khulna | 1992 | 2025-09-08 | 22:00
Barishal | 584 | 2025-09-07 | 19:00
Rajshahi | 1771 | 2025-09-01 | 22:00
Rangpur | 1157 | 2025-09-01 | 22:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 391 | 2025-09-22 07:00 | 347 | 2025-09-04 14:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 409 | 2025-09-12 17:00 | 340 | 2025-09-01 13:00
4 | Bibiana | 400 | 390 | 2025-09-22 07:00 | 374 | 2025-09-10 22:00
5 | BIPTC | 400 | 407 | 2025-09-21 09:00 | 385 | 2025-09-01 15:00
6 | Bogura | 400 | 405 | 2025-09-30 18:00 | 361 | 2025-09-04 23:00
7 | Gopalganj | 400 | 404 | 2025-09-22 07:00 | 376 | 2025-09-24 22:00
8 | Kaliakoir | 400 | 381 | 2025-09-22 07:00 | 354 | 2025-09-30 12:00
9 | Madunaghat | 400 | 396 | 2025-09-25 18:00 | 383 | 2025-09-08 12:00
10 | Meghnaghat | 400 | 393 | 2025-09-22 07:00 | 367 | 2025-09-03 12:00
11 | Payra | 400 | 417 | 2025-09-22 07:00 | 398 | 2025-09-24 21:00
12 | Rahanpur | 400 | 414 | 2025-09-30 17:00 | 382 | 2025-09-20 18:30
13 | Rampal | 400 | 408 | 2025-09-22 07:00 | 384 | 2025-09-24 19:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 236 | 2025-09-13 07:00 | 210 | 2025-09-27 19:30
2 | AKSML | 230 | 236 | 2025-09-10 19:00 | 221 | 2025-09-01 11:00
3 | Aminbazar | 230 | 237 | 2025-09-22 07:00 | 211 | 2025-09-04 09:00
4 | Ashuganj | 230 | 239 | 2025-09-10 02:00 | 215 | 2025-09-20 21:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 236 | 2025-09-02 00:00 | 223 | 2025-09-19 21:00
7 | Barapukuria | 230 | 229 | 2025-09-09 11:00 | 229 | 2025-09-09 11:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 234 | 2025-09-22 07:00 | 217 | 2025-09-06 23:00
10 | Bheramara | 230 | 235 | 2025-09-05 08:00 | 221 | 2025-09-19 23:00
11 | Bhulta | 230 | 235 | 2025-09-22 07:00 | 206 | 2025-09-04 12:00
12 | Bibiana | 230 | 231 | 2025-09-22 07:00 | 218 | 2025-09-01 18:30
13 | BIPTC | 230 | 238 | 2025-09-17 05:00 | 221 | 2025-09-17 23:00
14 | Bogura | 230 | 244 | 2025-09-09 12:00 | 220 | 2025-09-22 22:00
15 | Bogura-400 | 230 | 242 | 2025-09-09 12:00 | 220 | 2025-09-20 18:30
16 | Borhanuddin | 230 | 237 | 2025-09-22 07:00 | 224 | 2025-09-06 21:00
17 | BSRM | 230 | 234 | 2025-09-09 19:30 | 216 | 2025-09-03 12:00
18 | Cumilla(N) | 230 | 230 | 2025-09-22 07:00 | 211 | 2025-09-04 10:00
19 | Faridpur | 230 | 233 | 2025-09-22 08:00 | 213 | 2025-09-06 23:00
20 | Fenchuganj | 230 | 233 | 2025-09-10 20:00 | 219 | 2025-09-04 15:00
21 | Ghorashal | 230 | 235 | 2025-09-11 21:00 | 220 | 2025-09-01 13:00
22 | Ghorashal-230 | 230 | 232 | 2025-09-22 07:00 | 207 | 2025-09-03 12:00
23 | Gopalganj | 230 | 233 | 2025-09-22 07:00 | 216 | 2025-09-23 21:00
24 | GPH | 230 | 234 | 2025-09-10 01:00 | 221 | 2025-09-03 12:00
25 | Haripur | 230 | 231 | 2025-09-22 07:00 | 209 | 2025-09-27 10:00
26 | Hasnabad | 230 | 230 | 2025-09-22 06:00 | 210 | 2025-09-03 11:00
27 | Hathazari | 230 | 235 | 2025-09-25 00:00 | 219 | 2025-09-23 10:00
28 | Ishurdi | 230 | 238 | 2025-09-17 05:00 | 223 | 2025-09-04 12:00
29 | Jhenaidah | 230 | 234 | 2025-09-05 09:00 | 214 | 2025-09-25 20:00
30 | Kachua | 230 | 227 | 2025-09-21 16:00 | 206 | 2025-09-22 11:00
31 | Kaliakoir | 230 | 239 | 2025-09-22 07:00 | 213 | 2025-09-04 10:00
32 | Keranigonj | 230 | 233 | 2025-09-22 07:00 | 208 | 2025-09-04 10:00
33 | Khulna(S) | 230 | 234 | 2025-09-02 06:00 | 214 | 2025-09-23 18:30
34 | Madunaghat | 230 | 237 | 2025-09-08 09:00 | 226 | 2025-09-03 11:00
35 | Madunaghat-400 | 230 | 237 | 2025-09-09 20:00 | 226 | 2025-09-03 11:00
36 | Maniknagar | 230 | 230 | 2025-09-22 07:00 | 206 | 2025-09-04 12:00
37 | Meghnaghat | 230 | 233 | 2025-09-22 08:00 | 216 | 2025-09-04 11:00
38 | Meghnaghat-400 | 230 | 233 | 2025-09-22 07:00 | 212 | 2025-09-03 12:00
39 | Mirsorai | 230 | 237 | 2025-09-09 19:30 | 218 | 2025-09-01 11:00
40 | Rajshahi | 230 | 233 | 2025-09-02 02:00 | 215 | 2025-09-19 22:00
41 | Rampal | 230 | 236 | 2025-09-11 09:00 | 215 | 2025-09-25 22:00
42 | Rampur | 230 | N/A | N/A | N/A | N/A
43 | Rampura | 230 | 233 | 2025-09-22 07:00 | 202 | 2025-09-01 11:00
44 | Shikalbaha | 230 | 237 | 2025-09-09 19:00 | 222 | 2025-09-22 23:00
45 | Shyampur | 230 | 232 | 2025-09-22 07:00 | 208 | 2025-09-04 10:00
46 | Siddhirganj | 230 | 231 | 2025-09-22 06:00 | 209 | 2025-09-04 10:00
47 | Sirajgonj | 230 | 241 | 2025-09-02 | 230 | 2025-09-22 23:00
48 | Sreepur | 230 | 231 | 2025-09-22 07:00 | 215 | 2025-09-04 09:00
49 | Tongi | 230 | 232 | 2025-09-26 05:00 | 207 | 2025-09-03 12:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 143 | 2025-09-25 05:00 | 114 | 2025-09-25 10:00
2 | Agargaon | 132 | 142 | 2025-09-22 07:00 | 122 | 2025-09-01 11:00
3 | Agrabad | 132 | 136 | 2025-09-26 01:00 | 134 | 2025-09-10 19:00
4 | AKS | 132 | 133 | 2025-09-26 01:00 | 124 | 2025-09-01 11:00
5 | Aminbazar | 132 | 140 | 2025-09-22 07:00 | 122 | 2025-09-04 09:00
6 | Amnura | 132 | 140 | 2025-09-30 17:00 | 122 | 2025-09-19 22:00
7 | Ashuganj | 132 | 143 | 2025-09-22 07:00 | 132 | 2025-09-01 18:30
8 | Bagerhat | 132 | 136 | 2025-09-02 07:00 | 115 | 2025-09-23 23:00
9 | Bajitpur | 132 | 133 | 2025-09-12 17:00 | 116 | 2025-09-01 18:30
10 | Bakulia | 132 | 160 | 2025-09-15 14:00 | 126 | 2025-09-03 10:00
11 | Banani | 132 | 138 | 2025-09-09 19:30 | 118 | 2025-09-01 11:00
12 | Bangabhaban | 132 | 140 | 2025-09-22 07:00 | 120 | 2025-09-10 00:00
13 | Barapukuria | 132 | 140 | 2025-09-05 18:30 | 122 | 2025-09-25 19:30
14 | Barguna | 132 | 141 | 2025-09-10 09:00 | 129 | 2025-09-19 23:00
0 | Barishal | 132 | 138 | 2025-09-10 18:00 | 124 | 2025-09-24 23:00
16 | Barishal-230 | 132 | 139 | 2025-09-22 07:00 | 120 | 2025-09-09 05:00
17 | Baroaulia | 132 | 135 | 2025-09-09 19:00 | 120 | 2025-09-01 10:00
18 | Baroirhat | 132 | 132 | 2025-09-30 17:00 | 114 | 2025-09-05 00:00
19 | Bashundhara | 132 | 139 | 2025-09-10 05:00 | 116 | 2025-09-03 12:00
20 | BashundharaCement | 132 | 135 | 2025-09-22 08:00 | 120 | 2025-09-04 10:00
21 | Beanibazar | 132 | 129 | 2025-09-28 07:00 | 117 | 2025-09-01 18:30
22 | Benapole | 132 | 136 | 2025-09-01 22:00 | 116 | 2025-09-08 23:00
23 | Bhaluka | 132 | 137 | 2025-09-06 10:00 | 118 | 2025-09-01 18:30
24 | Bhandaria | 132 | 137 | 2025-09-22 07:00 | 115 | 2025-09-23 18:30
25 | Bhangura | 132 | 135 | 2025-09-02 00:00 | 125 | 2025-09-19 23:00
26 | Bheramara | 132 | 137 | 2025-09-02 01:00 | 127 | 2025-09-17 18:30
27 | Bheramara(GK) | 132 | 138 | 2025-09-12 17:00 | 126 | 2025-09-19 22:00
28 | Bhulta | 132 | 130 | 2025-09-22 08:00 | 115 | 2025-09-04 09:00
29 | Bog-Sherpur | 132 | 135 | 2025-09-02 02:00 | 122 | 2025-09-22 22:00
30 | Bogura | 132 | 138 | 2025-09-09 12:00 | 123 | 2025-09-22 22:00
31 | Bogura-230 | 132 | 138 | 2025-09-09 12:00 | 123 | 2025-09-20 00:00
32 | Brahmanbaria | 132 | 137 | 2025-09-12 08:00 | 122 | 2025-09-01 18:30
33 | Cantonment | 132 | 142 | 2025-09-22 07:00 | 121 | 2025-09-01 11:00
34 | Chandina | 132 | 134 | 2025-09-22 06:00 | 120 | 2025-09-05 11:00
35 | Chandpur | 132 | 136 | 2025-09-29 18:00 | 117 | 2025-09-03 15:00
36 | Chandraghona | 132 | 136 | 2025-09-09 18:00 | 128 | 2025-09-01 11:00
37 | Chapai | 132 | 140 | 2025-09-30 17:00 | 126 | 2025-09-21 00:00
39 | Charsaidpur | 132 | 138 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
40 | Chauddagram | 132 | 130 | 2025-09-21 16:00 | 113 | 2025-09-05 00:00
41 | Chhatak | 132 | 129 | 2025-09-30 21:00 | 111 | 2025-09-01 18:30
42 | Chowmuhani | 132 | 130 | 2025-09-25 17:00 | 107 | 2025-09-01 15:00
43 | Chuadanga | 132 | 138 | 2025-09-05 08:00 | 116 | 2025-09-01 19:00
44 | Coxsbazar | 132 | 128 | 2025-09-21 06:00 | 106 | 2025-09-06 21:00
45 | Cumilla(N) | 132 | 134 | 2025-09-22 05:00 | 120 | 2025-09-01 18:30
46 | Cumilla(S) | 132 | 134 | 2025-09-25 05:00 | 126 | 2025-09-09 13:00
47 | Daganbhuiyan | 132 | 130 | 2025-09-28 15:00 | 111 | 2025-09-02 15:00
48 | Daudkandi | 132 | 133 | 2025-09-22 06:00 | 112 | 2025-09-05 00:00
49 | DhakaUniversity | 132 | 142 | 2025-09-25 05:00 | 118 | 2025-09-01 11:00
50 | Dhamrai | 132 | 140 | 2025-09-22 08:00 | 120 | 2025-09-01 11:00
51 | Dhanmondi | 132 | 139 | 2025-09-09 19:30 | 118.7 | 2025-09-01 11:00
52 | Dohazari | 132 | 134 | 2025-09-25 13:00 | 119 | 2025-09-18 15:00
53 | Faridpur | 132 | 138 | 2025-09-22 08:00 | 126 | 2025-09-06 23:00
54 | Fatullah | 132 | 139 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
55 | Fenchuganj | 132 | 137 | 2025-09-13 06:00 | 127 | 2025-09-01 18:30
56 | Feni | 132 | 130 | 2025-09-25 17:00 | 112 | 2025-09-05 00:00
57 | Ghatail | 132 | 135 | 2025-09-18 18:30 | 114 | 2025-09-19 00:00
58 | Ghorashal | 132 | 141 | 2025-09-22 07:00 | 126 | 2025-09-03 10:00
59 | Goalpara | 132 | 140 | 2025-09-06 09:00 | 123 | 2025-09-23 19:00
60 | Gollamari | 132 | 139 | 2025-09-02 06:00 | 125 | 2025-09-24 18:30
61 | Gopalganj | 132 | 138 | 2025-09-22 07:00 | 124 | 2025-09-23 19:00
62 | Gopalganj-400 | 132 | 140 | 2025-09-22 07:00 | 128 | 2025-09-23 19:00
63 | Gulshan | 132 | 139 | 2025-09-09 20:00 | 118 | 2025-09-01 11:00
64 | Halishahar | 132 | 136 | 2025-09-09 19:30 | 125 | 2025-09-03 12:00
65 | Haripur | 132 | 137 | 2025-09-22 07:00 | 121 | 2025-09-04 10:00
66 | HaripurSBU | 132 | 134 | 2025-09-22 08:00 | 121 | 2025-09-04 10:00
67 | Hasnabad | 132 | 136 | 2025-09-22 05:00 | 123 | 2025-09-04 12:00
68 | Hathazari | 132 | 136 | 2025-09-10 17:00 | 127 | 2025-09-03 12:00
69 | Ishurdi | 132 | 139 | 2025-09-02 02:00 | 129 | 2025-09-17 18:30
70 | Jaldhaka | 132 | 138 | 2025-09-05 19:00 | 113 | 2025-09-25 19:30
71 | Jamalpur | 132 | 134 | 2025-09-01 17:00 | 112 | 2025-09-02 07:00
72 | Jashore | 132 | 139 | 2025-09-15 06:00 | 118 | 2025-09-23 18:30
73 | Jhenaidah | 132 | 139 | 2025-09-02 05:00 | 116 | 2025-09-18 18:30
74 | Jhenaidah-230 | 132 | 140 | 2025-09-05 08:00 | 124 | 2025-09-23 18:30
75 | Joydebpur | 132 | 144 | 2025-09-01 23:00 | 118 | 2025-09-01 11:00
76 | Joypurhat | 132 | 130 | 2025-09-09 12:00 | 112 | 2025-09-22 22:00
77 | Juldah | 132 | 137 | 2025-09-26 01:00 | 126 | 2025-09-03 10:00
78 | Kabirpur | 132 | 140 | 2025-09-02 00:00 | 114 | 2025-09-04 12:00
79 | Kachua | 132 | 136 | 2025-09-21 16:00 | 118 | 2025-09-02 15:00
80 | Kaliakoir | 132 | 140 | 2025-09-22 08:00 | 123 | 2025-09-03 11:00
81 | Kallyanpur | 132 | 137 | 2025-09-22 05:00 | 122 | 2025-09-04 10:00
82 | Kalurghat | 132 | 137 | 2025-09-09 19:30 | 127 | 2025-09-01 11:00
83 | Kamrangirchar | 132 | 139 | 2025-09-22 07:00 | 123 | 2025-09-01 15:00
84 | Kaptai | 132 | N/A | N/A | N/A | N/A
85 | Kasba | 132 | 132 | 2025-09-22 06:00 | 115 | 2025-09-01 18:30
86 | Kazla | 132 | 140 | 2025-09-22 08:00 | 122 | 2025-09-04 13:00
87 | Keranigonj | 132 | 139 | 2025-09-17 06:00 | 124 | 2025-09-01 11:00
88 | Khagrachori | 132 | 134 | 2025-09-09 18:00 | 126 | 2025-09-01 11:00
89 | Khulna | 132 | 139 | 2025-09-22 07:00 | 124 | 2025-09-10 23:00
90 | Khulna(S) | 132 | 140 | 2025-09-05 17:00 | 124 | 2025-09-23 18:30
91 | Khulshi | 132 | 134 | 2025-09-25 23:00 | 124 | 2025-09-03 10:00
92 | Kishoreganj | 132 | 131 | 2025-09-14 09:00 | 114 | 2025-09-01 18:30
93 | Kodda | 132 | 137 | 2025-09-01 23:00 | 116 | 2025-09-29 11:00
94 | KSRM | 132 | 136 | 2025-09-09 20:00 | 125 | 2025-09-07 12:00
95 | Kulaura | 132 | 135 | 2025-09-15 16:00 | 126 | 2025-09-01 18:30
96 | Kurigram | 132 | 133 | 2025-09-09 11:00 | 112 | 2025-09-21 18:30
97 | Kushtia | 132 | 136 | 2025-09-02 01:00 | 121 | 2025-09-17 18:30
98 | Laksam | 132 | 134 | 2025-09-22 07:00 | 115 | 2025-09-03 15:00
99 | Lakshmipur | 132 | 129 | 2025-09-28 15:00 | 102 | 2025-09-06 22:00
100 | Lalbag | 132 | 138 | 2025-09-05 08:00 | 123 | 2025-09-01 18:30
101 | Lalmonirhat | 132 | 131 | 2025-09-09 10:00 | 112 | 2025-09-21 18:30
102 | Madanganj | 132 | 137 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
103 | Madaripur | 132 | 139 | 2025-09-22 07:00 | 126 | 2025-09-23 19:00
104 | Madartek | 132 | 139 | 2025-09-10 06:00 | 117 | 2025-09-01 11:00
105 | Madunaghat | 132 | 137 | 2025-09-10 19:00 | 125 | 2025-09-22 21:00
106 | Magura | 132 | 137 | 2025-09-02 05:00 | 120 | 2025-09-01 19:00
107 | Mahasthangarh | 132 | 136 | 2025-09-09 12:00 | 120 | 2025-09-20 22:00
108 | Maijdee | 132 | 129 | 2025-09-28 15:00 | 104 | 2025-09-06 22:00
109 | Manikganj | 132 | 131 | 2025-09-01 23:00 | 114 | 2025-09-04 10:00
110 | Maniknagar | 132 | 140 | 2025-09-22 07:00 | 122 | 2025-09-03 12:00
111 | Matarbari | 132 | 127 | 2025-09-11 05:00 | 106 | 2025-09-06 19:00
112 | Matuail | 132 | 136 | 2025-09-22 07:00 | 121 | 2025-09-04 10:00
113 | Millgate | 132 | 136 | 2025-09-22 07:00 | 118 | 2025-09-04 10:00
114 | Mirpur | 132 | 138 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
115 | Mirzapur | 132 | 136 | 2025-09-02 01:00 | 120 | 2025-09-03 12:00
116 | Mithapukur | 132 | 136 | 2025-09-09 13:00 | 117 | 2025-09-25 19:30
117 | MI_Cement | 132 | 137 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
118 | Modern | 132 | N/A | N/A | N/A | N/A
119 | Mogbazar | 132 | 139 | 2025-09-07 04:00 | 121 | 2025-09-01 11:00
120 | Mongla | 132 | 137 | 2025-09-22 04:00 | 117 | 2025-09-24 19:00
121 | Motijheel | 132 | 140 | 2025-09-22 07:00 | 122 | 2025-09-04 12:00
122 | Muktagacha | 132 | 133 | 2025-09-20 09:00 | 112 | 2025-09-14 20:00
123 | Munshiganj | 132 | 135 | 2025-09-22 06:00 | 120 | 2025-09-04 10:00
124 | Muradnagar | 132 | 132 | 2025-09-22 06:00 | 114 | 2025-09-07 00:00
125 | Mymensingh | 132 | 134 | 2025-09-20 10:00 | 134 | 2025-09-20 10:00
126 | Naogaon | 132 | 133 | 2025-09-02 02:00 | 115 | 2025-09-22 22:00
127 | Narail | 132 | 138 | 2025-09-02 06:00 | 117 | 2025-09-23 18:30
128 | Narinda | 132 | 0 | 2025-09-01 00:00 | N/A | N/A
129 | Narshingdi | 132 | 140 | 2025-09-09 20:00 | 114 | 2025-09-09 10:00
130 | Natore | 132 | 135 | 2025-09-02 02:00 | 117 | 2025-09-19 23:00
131 | Nawabganj | 132 | 140 | 2025-09-22 06:00 | 123 | 2025-09-01 15:00
132 | Netrakona | 132 | 128 | 2025-09-14 06:00 | 105 | 2025-09-02 18:30
133 | New | 132 | 136 | 2025-09-12 17:00 | 119 | 2025-09-01 19:00
134 | Niamatpur | 132 | 141 | 2025-09-30 17:00 | 129 | 2025-09-19 22:00
135 | Noapara | 132 | 137 | 2025-09-01 22:00 | 121 | 2025-09-23 18:30
136 | Pabna | 132 | 136 | 2025-09-02 01:00 | 125 | 2025-09-17 19:00
137 | Palashbari | 132 | 133 | 2025-09-09 13:00 | 115 | 2025-09-22 22:00
139 | Panchagarh | 132 | 140 | 2025-09-16 18:00 | 115 | 2025-09-07 08:00
140 | Patiya | 132 | 136 | 2025-09-25 17:00 | 124 | 2025-09-01 09:00
141 | Patuakhali | 132 | 142 | 2025-09-10 07:00 | 129 | 2025-09-22 23:00
142 | Payra | 132 | 137 | 2025-09-01 02:00 | 131 | 2025-09-23 19:00
143 | PHP | 132 | 131 | 2025-09-30 17:00 | 113 | 2025-09-05 00:00
144 | Postogola | 132 | 139 | 2025-09-22 07:00 | 123 | 2025-09-04 10:00
145 | Purbachal | 132 | 139 | 2025-09-10 04:00 | 117 | 2025-09-01 11:00
146 | Purbasadipur | 132 | 138 | 2025-09-05 19:00 | 115 | 2025-09-27 12:00
147 | Rahanpur | 132 | 141 | 2025-09-28 17:00 | 130 | 2025-09-20 22:00
148 | Rahanpur-400 | 132 | 141 | 2025-09-28 17:00 | 131 | 2025-09-04 23:00
149 | Rahim | 132 | 137 | 2025-09-22 07:00 | 121 | 2025-09-03 12:00
150 | Rajbari | 132 | 138 | 2025-09-02 19:00 | 122 | 2025-09-24 12:00
151 | Rajendrapur | 132 | 141 | 2025-09-09 19:30 | 117 | 2025-09-22
152 | Rajshahi | 132 | 134 | 2025-09-02 01:00 | 121 | 2025-09-16 06:00
153 | Rajshahi-230 | 132 | 134 | 2025-09-02 02:00 | 121 | 2025-09-19 23:00
154 | Ramganj | 132 | 132 | 2025-09-29 18:00 | 109 | 2025-09-19 20:00
155 | Rampur | 132 | 136 | 2025-09-26 01:00 | 124 | 2025-09-03 12:00
156 | Rampura | 132 | 139 | 2025-09-09 20:00 | 118 | 2025-09-01 11:00
157 | Rangamati | 132 | 135 | 2025-09-09 18:00 | 126 | 2025-09-02 17:00
158 | Rangpur | 132 | 135 | 2025-09-09 11:00 | 118 | 2025-09-21 19:00
159 | Ruppur | 132 | 139 | 2025-09-12 17:00 | 128 | 2025-09-17 19:00
160 | Saidpur | 132 | 136 | 2025-09-01 18:30 | 116 | 2025-09-26 19:00
161 | Satkhira | 132 | 137 | 2025-09-02 04:00 | 117 | 2025-09-01 19:00
162 | Satmasjid | 132 | 142 | 2025-09-22 07:00 | 121 | 2025-09-16 11:00
163 | Savar | 132 | 137 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
164 | SevenRings | 132 | 140 | 2025-09-22 07:00 | 123 | 2025-09-26 09:00
165 | ShahCement | 132 | 138 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
166 | Shahjadpur | 132 | 140 | 2025-09-02 03:00 | 130 | 2025-09-04 12:00
167 | Shahjibazar | 132 | 137 | 2025-09-15 17:00 | 123 | 2025-09-01 18:30
168 | Shahmirpur | 132 | 137 | 2025-09-26 01:00 | 125 | 2025-09-03 14:00
169 | Shariatpur | 132 | 137 | 2025-09-22 06:00 | 123 | 2025-09-23 22:00
170 | Sherpur | 132 | 132 | 2025-09-04 18:30 | 108 | 2025-09-29 22:00
171 | Shikalbaha | 132 | 126 | 2025-09-25 19:00 | 117 | 2025-09-18 12:00
172 | Shikalbaha-230 | 132 | 138 | 2025-09-25 18:30 | 126 | 2025-09-18 14:00
173 | Shitalakhya | 132 | 138 | 2025-09-06 01:00 | 120 | 2025-09-04 10:00
174 | Sholosohor | 132 | 136 | 2025-09-09 18:00 | 129 | 2025-09-18 12:00
175 | Shyampur | 132 | 139 | 2025-09-22 07:00 | 122 | 2025-09-04 10:00
176 | Shyampur-230 | 132 | 139 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
177 | Siddhirganj | 132 | 134 | 2025-09-22 08:00 | 121 | 2025-09-04 10:00
178 | Sirajganj | 132 | 134 | 2025-09-02 02:00 | 119 | 2025-09-02 14:00
179 | Sonargaon | 132 | 136 | 2025-09-22 07:00 | 120 | 2025-09-01 11:00
180 | Sreemongol | 132 | 135 | 2025-09-15 17:00 | 122 | 2025-09-05 00:00
181 | Sreepur | 132 | 134 | 2025-09-02 00:00 | 124 | 2025-09-22 23:00
182 | Srinagar | 132 | 140 | 2025-09-22 06:00 | 123 | 2025-09-22 12:00
183 | SSM | 132 | 138 | 2025-09-09 22:00 | 130 | 2025-09-01 13:00
184 | Sunamganj | 132 | 126 | 2025-09-12 06:00 | 111 | 2025-09-01 18:30
185 | Sylhet | 132 | 130 | 2025-09-15 08:00 | 119 | 2025-09-01 18:00
186 | Sylhet-132 | 132 | 129 | 2025-09-13 07:00 | 118 | 2025-09-01 16:00
187 | Tangail | 132 | 135 | 2025-09-02 01:00 | 115 | 2025-09-30 12:00
188 | Taraganj | 132 | 134 | 2025-09-09 11:00 | 116 | 2025-09-26 19:00
189 | Thakurgaon | 132 | 138 | 2025-09-01 18:30 | 114 | 2025-09-07 08:00
190 | TK | 132 | 136 | 2025-09-09 18:00 | 127 | 2025-09-02 15:00
191 | Tongi | 132 | 136 | 2025-09-12 04:00 | 122 | 2025-09-03 10:00
192 | Ullahpara | 132 | 136 | 2025-09-02 03:00 | 120 | 2025-09-22 02:00
193 | Ullon | 132 | 139 | 2025-09-09 20:00 | 118 | 2025-09-01 11:00
194 | Uttara | 132 | 137 | 2025-09-22 08:00 | 120 | 2025-09-04 10:00
195 | UttaraNew | 132 | 135 | 2025-09-22 07:00 | 120 | 2025-09-04 10:00
196 | Zigatola | 132 | 140 | 2025-09-22 06:00 | 124 | 2025-09-01 12:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: September 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 21-09-2025 | 11:00 | 403 | 204 | 86.8637
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 20-09-2025 | 22:00 | 357 | 154 | 74.7691
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 21-09-2025 | 11:00 | 397 | 198 | 85.3146
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 2025-01-09 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 25-09-2025 | 09:00 | 350 | 97 | 69.8448
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 25-09-2025 | 09:00 | 350 | 97 | 69.8448
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 20-09-2025 | 17:00 | 280 | 65 | 55.278
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 02-09-2025 | 01:00 | 189 | 72 | 38.8942
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 22-09-2025 | 23:00 | 418 | 31 | 55.8864
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 22-09-2025 | 23:00 | 418 | 31 | 55.8864
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 22-09-2025 | 23:00 | 418 | 31 | 55.8864
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 26-09-2025 | 1:00 | 177 | 64 | 57.9124
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 26-09-2025 | 1:00 | 177 | 64 | 57.9124
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 26-09-2025 | 1:00 | 197 | 64 | 63.7339
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 26-09-2025 | 1:00 | 286 | 55 | 38.8321
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 18-09-2025 | 18:00 | 327 | 158 | 69.8405
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 18-09-2025 | 18:00 | 327 | 158 | 69.8405
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 26-09-2025 | 02:00 | 303 | 44 | 94.2086
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 26-09-2025 | 02:00 | 303 | 44 | 94.2086
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 06-09-2025 | 08:00 | 392 | 135 | 55.2793
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 03-09-2025 | 16:00 | 388 | 152 | 55.5615
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 03-09-2025 | 16:00 | 388 | 152 | 55.5615
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 19-09-2025 | 12:00 | 448 | 117 | 61.7368
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 21-09-2025 | 11:00 | 439 | 138 | 61.3572
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 |  |  |  |  | 0
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 11-09-2025 | 20:00 | 425 | 70 | 82.8319
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 11-09-2025 | 20:00 | 420 | 70 | 81.8833
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 19-09-2025 | 22:00 | -69 | 25 | 22.5813
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 19-09-2025 | 22:00 | 69 | 25 | 22.5813
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 30-09-2025 | 22:00 | 122 | 33 | 24.3047
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 30-09-2025 | 22:00 | 122 | 33 | 24.3047
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 01-09-2025 | 16:00 | 211 | 92 | 76.7282
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 01-09-2025 | 16:00 | 211 | 92 | 76.7282
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 21-09-2025 | 09:00 | 176 | 53 | 81.692
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 21-09-2025 | 09:00 | 176 | 33 | 79.5853
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 21-09-2025 | 09:00 | 176 | 53 | 81.692
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 25-09-2025 | 14:00 | 200 | 110 | 76.0847
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 06-09-2025 | 19:00 | 240 | 40 | 81.1035
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 02-09-2025 | 13:00 | 162 | 63 | 57.9396
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 15-09-2025 | 19:30 | 144 | 48 | 67.4619
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 05-09-2025 | 18:30 | 202 | 64 | 94.1761
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 23-09-2025 | 19:00 | 190 | 76 | 90.9495
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 23-09-2025 | 19:00 | 247 | 68 | 85.3965
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 25-09-2025 | 23:00 | 135 | 39 | 46.8402
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 25-09-2025 | 23:00 | 135 | 39 | 46.8402
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 20-09-2025 | 19:00 | -134 | -24 | 60.5032
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 20-09-2025 | 19:00 | -134 | -24 | 60.5032
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 08-09-2025 | 02:00 | 177 | 41 | 80.7496
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 08-09-2025 | 02:00 | 177 | 41 | 80.7496
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 08-09-2025 | 02:00 | 238 | 58 | 81.6551
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 08-09-2025 | 02:00 | 238 | 58 | 81.6551
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 06-09-2025 | 21:00 | 173 | 62 | 81.6775
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 06-09-2025 | 21:00 | 172 | 60 | 80.9621
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 06-09-2025 | 21:00 | 183 | 63 | 86.0181
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 01-09-2025 | 19:00 | 193 | 79 | 69.5142
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 01-09-2025 | 19:00 | 243 | 101 | 87.718
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 23-09-2025 | 01:00 | 99 | 0 | 79.2
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 23-09-2025 | 01:00 | 99 | 0 | 79.2
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 11-09-2025 | 03:00 | 127 | 84 | 67.6739
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 22-09-2025 | 00:00 | 117 | 65 | 59.4859
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 22-09-2025 | 00:00 | 110 | 70 | 57.9485
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 27-09-2025 | 18:30 | 88 | 37 | 42.4276
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 27-09-2025 | 11:00 | 98 | 50 | 48.897
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 27-09-2025 | 11:00 | 98 | 50 | 48.897
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 02-09-2025 | 19:00 | 104 | 74 | 85.0934
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-09-2025 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 02-09-2025 | 19:00 | 104 | 74 | 85.0934
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 23-09-2025 | 15:00 | 101 | 49 | 74.8391
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 20-09-2025 | 19:00 | 122 | 67 | 61.8609
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 11-09-2025 | 22:00 | 115 | 51 | 55.9117
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 20-09-2025 | 19:30 | 119 | 68 | 60.9148
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 01-09-2025 | 19:00 | -214 | 55 | 73.6516
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 01-09-2025 | 19:00 | -214 | 55 | 73.6516
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 21-09-2025 | 04:00 | 200 | 158 | 84.9601
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 07-09-2025 | 20:00 | 215 | 69 | 75.2669
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 08-09-2025 | 00:00 | 216 | 65 | 75.1894
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-09-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 07-09-2025 | 22:00 | 157 | 55 | 73.9356
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 07-09-2025 | 22:00 | 157 | 55 | 73.9356
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 07-09-2025 | 22:00 | 204 | 65 | 71.3684
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 25-09-2025 | 18:00 | 144 | 7 | 48.0567
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 23-09-2025 | 14:00 | 136 | 14 | 45.5729
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 25-09-2025 | 18:00 | 144 | 7 | 48.0567
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 03-09-2025 | 13:00 | 168 | 71 | 60.7957
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 03-09-2025 | 13:00 | 168 | 71 | 60.7957
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 13-09-2025 | 13:00 | 136 | 36 | 46.8947
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 13-09-2025 | 13:00 | 136 | 36 | 46.8947
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-09-2025 | 00:00 | 1 | 1 | 0.4714
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-09-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 01-09-2025 | 15:00 | 309 | 59 | 69.9072
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 01-09-2025 | 15:00 | 309 | 59 | 69.9072
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 01-09-2025 | 15:00 | 309 | 59 | 69.9072
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 10-09-2025 | 19:30 | 232 | 138 | 89.9802
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 10-09-2025 | 19:30 | 232 | 138 | 89.9802
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 01-09-2025 | 00:00 | 154 | 62 | 55.3373
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 01-09-2025 | 00:00 | 154 | 62 | 55.3373
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 13-09-2025 | 14:00 | 112 | 1 | 37.3348
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 16-09-2025 | 11:00 | 111 | 6 | 37.054
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 29-09-2025 | 18:00 | 264 | 114 | 95.8541
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 29-09-2025 | 18:00 | 264 | 114 | 95.8541
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 04-09-2025 | 18:30 | 204 | 35 | 91.9914
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 04-09-2025 | 18:30 | 187 | 44 | 85.3808
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 04-09-2025 | 18:30 | 187 | 44 | 85.3808
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: September 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: September 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-09-01 | 16279.02 | 16450.02 | 164 | 19:30 Hr. | 10 | 10 | 10 | 100 | 34 | 0 | 0 | 0 | 0 | - | 2025-09-01 | 14612.8 | 14612.8 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-02 | 15840.88 | 16000.88 | 153 | 19:30 Hr. | 25 | 0 | 20 | 108 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-02 | 13872.72 | 13872.72 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-03 | 15794.29 | 15952.29 | 151 | 21:00 Hr. | 10 | 0 | 10 | 131 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-03 | 14349.13 | 14349.13 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-04 | 15986.38 | 16140.38 | 147 | 19:30 Hr. | 25 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-04 | 14408.28 | 14444.86 | 35 | 12:00 Hr. | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | -
2025-09-05 | 15064.21 | 15110.19 | 44 | 21:00 Hr. | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-05 | 13016.81 | 13016.81 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-06 | 15974.65 | 16021.65 | 45 | 21:00 Hr. | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-06 | 13309.84 | 13333.88 | 23 | 12:00 Hr. | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | -
2025-09-07 | 15966.54 | 16020.88 | 52 | 20:00 Hr. | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-07 | 14283.62 | 14283.62 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-08 | 15756.03 | 16300.19 | 473 | 20:00 Hr. | 180 | 15 | 85 | 135 | 58 | 0 | 0 | 0 | 0 | - | 2025-09-08 | 14613.55 | 14794.34 | 173 | 12:00 Hr. | 15 | 28 | 60 | 70 | 0 | 0 | 0 | 0 | 0 | -
2025-09-09 | 14881.02 | 16248.02 | 1308 | 20:00 Hr. | 265 | 120 | 203 | 185 | 125 | 160 | 25 | 100 | 125 | - | 2025-09-09 | 14129 | 14400 | 259 | 11:00 Hr. | 148 | 31 | 25 | 55 | 0 | 0 | 0 | 0 | 0 | -
2025-09-10 | 15636.36 | 16249.78 | 587 | 21:00 Hr. | 120 | 80 | 95 | 112 | 0 | 0 | 0 | 85 | 95 | - | 2025-09-10 | 14471.36 | 14803.36 | 318 | 12:00 Hr. | 170 | 10 | 30 | 78 | 0 | 0 | 0 | 0 | 30 | - | 0
2025-09-11 | 15713.13 | 15930.13 | 208 | 19:30 Hr. | 15 | 10 | 8 | 175 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-11 | 14301.77 | 14301.77 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-12 | 14647.37 | 14750.83 | 99 | 21:00 Hr. | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-12 | 12586.15 | 12586.15 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-13 | 15272.87 | 15669.79 | 286 | 19:30 Hr. | 0 | 0 | 10 | 126 | 0 | 30 | 10 | 75 | 35 | - | 2025-09-13 | 13695.18 | 13695.18 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-14 | 14578.22 | 14720.34 | 136 | 19:00 Hr. | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-14 | 13024.44 | 13024.44 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-15 | 14088.43 | 14190.84 | 98 | 19:30 Hr. | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-15 | 12975.28 | 13028.28 | 51 | 12:00 Hr. | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | -
2025-09-16 | 13947.53 | 14000.83 | 51 | 19:30 Hr. | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-16 | 12591.47 | 12591.47 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-17 | 14615.45 | 14700.1 | 81 | 19:30 Hr. | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-17 | 13230.59 | 13230.59 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-18 | 15244.7 | 15400.7 | 149 | 20:00 Hr. | 10 | 0 | 20 | 119 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-18 | 13505.01 | 13505.01 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-19 | 14400.89 | 14460.89 | 57 | 21:00 Hr. | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-19 | 12261.24 | 12261.24 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-20 | 15651 | 15789.99 | 133 | 19:30 Hr. | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-20 | 12518.87 | 12518.87 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-21 | 16133.4 | 16280.4 | 141 | 19:30 Hr. | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-21 | 13916.94 | 13916.94 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-22 | 14954.9 | 15105.38 | 144 | 19:00 Hr. | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-22 | 12908.12 | 12908.12 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-23 | 15753.9 | 16030.83 | 265 | 21:00 Hr. | 50 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-23 | 13470.7 | 13525.7 | 53 | 12:00 Hr. | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-09-24 | 15499.84 | 15899.84 | 383 | 21:00 Hr. | 15 | 0 | 0 | 180 | 0 | 0 | 0 | 145 | 43 | - | 2025-09-24 | 13853.47 | 13963.47 | 105 | 12:00 Hr. | 65 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | -
2025-09-25 | 15845.02 | 16220.18 | 359 | 21:00 Hr. | 100 | 0 | 20 | 150 | 50 | 0 | 0 | 0 | 39 | - | 2025-09-25 | 14136.25 | 14423.25 | 275 | 12:00 Hr. | 175 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | -
2025-09-26 | 15013.7 | 15120.29 | 102 | 21:00 Hr. | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-26 | 12947.92 | 12982.41 | 33 | 12:00 Hr. | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | -
2025-09-27 | 15939.35 | 16091.35 | 145 | 21:00 Hr. | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | - | 2025-09-27 | 13325.67 | 13359.67 | 33 | 12:00 Hr. | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | -
2025-09-28 | 15270.73 | 15950.26 | 650 | 21:00 Hr. | 75 | 0 | 115 | 120 | 50 | 45 | 0 | 140 | 105 | - | 2025-09-28 | 14012 | 14080 | 65 | 12:00 Hr. | 25 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | -
2025-09-29 | 15782.36 | 16100.36 | 304 | 20:00 Hr. | 22 | 0 | 0 | 75 | 5 | 80 | 0 | 68 | 54 |  | 2025-09-29 | 14279.71 | 14556.71 | 265 | 12:00 Hr. | 125 | 0 | 25 | 115 | 0 | 0 | 0 | 0 | 0 | -
2025-09-30 | 15679.16 | 15771.16 | 88 | 20:00 Hr. | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 |  | 2025-09-30 | 14965.88 | 15102.78 | 131 | 12:00 Hr. | 75 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: September 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16279.02 | 2025-09-01 | 19:30 Hr.
2 | Maximum Day Peak Genaration | MW | 14965.88 | 2025-09-30 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 16450.02 | 2025-09-01 | 19:30 Hr.
4 | Minimum Generation | MW | 10620.26 | 2025-09-22 | 08:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 15373.711 | - | -
6 | Average of the daily day peak Genaration | MW | 13652.769 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1308 | 2025-09-09 | 20:00 Hr.
8 | Minimum load shed | MW | 44 | 2025-09-05 | 21:00 Hr.
9 | Total nos. of load shed days | Day | 30 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 233.4333 | - | -
11 | Total Generation | MkWh | 10140.7888 | - | -
12 | Total Generation by BPDB | MkWh | 1248.3832 | % of total Gen. | 12.31%
13 | Total Generation by IPP | MkWh | 2978.8553 | '' | 29.37%
14 | A) Total Generation by Generation Companies | MkWh | 4245.3018 | '' | 41.86%
| B) Total Generation by REB | MkWh | 44.7809 | " | 0.4416%
| C) Total Generation by RENTAL | MkWh | 139.669 | " | 1.377%
| D) Total Imported from India (BIPTC) | MkWh | 654.3178 | " | 6.452%
| E) Total Imported from Tripura, India (A.C) | MkWh | 31.4235 | " | 0.3099%
| F) Total Imported from Nepal | MkWh | 27.36 | " | 0.2698%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 770.6974 | " | 7.6%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4025.2813 | % of total Gen. | 39.69%
| B) Oil | MkWh | 1240.622 | '' | 12.23%
| C) Hydro | MkWh | 156.2217 | '' | 1.541%
| D) Solar | MkWh | 119.0925 | '' | 1.174%
| E) Coal | MkWh | 3110.7922 | '' | 30.68%
| F) BIPTC (Import from India) | MkWh | 654.3178 | '' | 6.452%
| G) A.C (Import from Tripura, India) | MkWh | 31.4235 | '' | 0.3099%
| H) Total Imported from Nepal | MkWh | 27.36 | '' | 0.2698%
| I) Adani (Import from India) | MkWh | 770.6974 | '' | 7.6%
| J) Wind | MkWh | 4.9805 | '' | 0.04911%
16 | Maximun of the daily total Generation . | MkWh | 356.6746 | 2025-09-07
17 | Monthly Load factor | % | 86.5189 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 65549.529 | - | -
| A) Gas | M.Taka | 14461.5848 | - | -
| B) Coal | M.Taka | 18135.0944 | - | -
| C) HFO | M.Taka | 22458.3174 | - | -
| D) HSD | M.Taka | 0 | - | -
| E) Hydro | M.Taka | 15.6222 | - | -
| F) Solar | M.Taka | 1785.6043 | - | -
| G) Total Import | M.Taka | 8619.8936 | - | -
| H) Wind | M.Taka | 73.4123 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2603.8275 | 2025-09-10
| A) Gas | M.Taka | 519.1446 | 2025-09-13
| B) Coal | M.Taka | 640.6627 | 2025-09-30
| C) HFO | M.Taka | 1223.5896 | 2025-09-10
| D) HSD | M.Taka | 0 | 2025-09-01 | -
| E) Hydro | M.Taka | 0.53353 | 2025-09-15 | -
| F) Solar | M.Taka | 83.2758 | 2025-09-01 | -
| G) Total Import | M.Taka | 339.5974 | 2025-09-07
| H) Wind | M.Taka | 9.7992 | 2025-09-02
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.4639
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.6477
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 105.76 | 30/09/2025 | 06:00
b) | Actual | FT (MSL) | 108.04 | 30/09/2025 | 06:00
22 | Peak Genaration of September 2024 | MW | 15717 | 2024-09-19 | 21:00
23 | Peak Demand of September 2024 | MW | 16300 | 2024-09-30 | 20:00
24 | Maximum peak Generation recorded upto 30/09/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 30/09/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 30/09/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [31 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [6 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [7 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [38 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [7 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | [13 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [31 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [28 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [5 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [10 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | [6 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | [16 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [36 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 |  | 50 | 24 | 24 | 50
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [20 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: September 2025
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | [6 empty] | √ | √
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | [6 empty] | √ | [6 empty] | √ | [6 empty] | √ | √ | √ |  |  |  |  | √
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 |  |  | √ | [14 empty] | √ |  |  | √ |  | √
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | [7 empty] | √ | [12 empty] | √ | √ | [5 empty] | √
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [7 empty] | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | [5 empty] | √
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 |  |  | √
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Zodiac 54 MW | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | [17 empty] | √
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | √ | √ | √ | √ | √ | [12 empty] | √ | √ | √ | √ | √ | √
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 |  |  | √ | √ | [13 empty] | √ |  |  | √ | √ | √ | √ | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 |  |  | √ | [14 empty] | √ |  |  | √ |  | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 |  |  | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 |  |  |  | √ | √ | √ | √ | [10 empty] | √ |  |  | √ | √ | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| Meghnaghat CCPP(Summit)-2 | IPP |  | 583 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| United Payra Power Ltd. | IPP |  | 150 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| Mirsharai 150 MW | IPP | HFO/Gas | 150 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | [10 empty] | √ | √ | √ | √ |  |  |  | √
| Jangalia 52 MW PP (Lakdanavi) | [19 empty] | √
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622