## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-10-2025 | during | 29-10-2025 | during | 29-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 353 | 310 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 47 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 45 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 135 | 149.36 | 149.36 | 45 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35.01 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 14 | 24 | 24 | 24 | 24 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 277 | 293 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 117 | 131 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 126 | 162 | 162 | 108 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 310 | 310 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 70 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 2020 | 2350 | 5595.4 | 5565.4 | 4579.88 | 4832.89
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 230 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 220 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 17 | 17 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 67 | 70 | 70 | 70 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 35 | 35 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 27 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 83 | 103 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.25 | 0 | 3.23 | 0 | 3.23 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 66 | 84 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 72 | 159.86 | 159.86 | 17 | 159 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1230 | 1160 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 2560.25 | 2754.5 | 3690.95 | 3683.72 | 2832.73 | 2967.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 338 | 352 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 191 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 397 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 37 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 45 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 107 | 130 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 20 | 35 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 103 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 54 | 109 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 46 | 78 | 160 | 160 | 88 | 88 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 106 | 94 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1430 | 1772 | 2607.86 | 2542.86 | 2282.86 | 2226.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-10-2025 | during | 29-10-2025 | during | 29-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 73 | 73 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 47 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 49 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.98 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 229.98 | 187 | 377.1 | 330 | 323.6 | 276.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 140 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 78 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 159 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 9 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 312 | 325 | 325 | 325 | 325 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1130 | 1100 | 1218 | 1218 | 1169 | 1169
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 904 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 51 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 376 | 383 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 55 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1006 | 1221 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2378 | 2634 | 2393 | 2318 | 1632 | 1557
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 302 | 503 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 110 | 110 | 110 | 116 | 116 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1004 | 1140 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 10 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 170 | 170 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1806.57 | 2263 | 2147 | 2146 | 1962 | 1961
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54.8 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 202 | 157 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 410 | 395 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.76 | 0 | 5.52 | 0 | 5.52 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1011.18 | 995.38 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.86 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 98 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1816.6 | 1940.58 | 3187.39 | 3020.87 | 2574.61 | 2408.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 110 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 176 | 0 | 156.73 | 0 | 156.73 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 232.1 | 205 | 419.93 | 228 | 399.93 | 208
System Total |  |  |  |  | 28823.2 | 28364.095 | 13603.5 | 15206.08 | 21636.63 | 21052.85 | 17756.61 | 17606.84
Forecast Scenario (29-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14800 |  | 0 |  | 14800
|  |  |  | 1:00 | 14200 |  | 0 |  | 14200
|  |  |  | 2:00 | 13770 |  | 0 |  | 13770
|  |  |  | 3:00 | 13390 |  | 0 |  | 13390
|  |  |  | 4:00 | 12850 |  | 0 |  | 12850
|  |  |  | 5:00 | 12620 |  | 0 |  | 12620
|  |  |  | 6:00 | 12430 |  | 0 |  | 12430
|  |  |  | 7:00 | 12500 |  | 0 |  | 12500
|  |  |  | 8:00 | 12380 |  | 0 |  | 12380
|  |  |  | 9:00 | 12750 |  | 0 |  | 12750
|  |  |  | 10:00 | 13000 |  | 0 |  | 13000
|  |  |  | 11:00 | 13400 |  | 0 |  | 13400
|  |  |  | 12:00 | 13910 |  | 0 |  | 13910
|  |  |  | 13:00 | 14290 |  | 0 |  | 14290
|  |  |  | 14:00 | 14270 |  | 0 |  | 14270
|  |  |  | 15:00 | 14320 |  | 0 |  | 14320
|  |  |  | 16:00 | 14030 |  | 0 |  | 14030
|  |  |  | 17:00 | 13970 |  | 0 |  | 13970
|  |  |  | 18:00 | 15300 |  | 0 |  | 15300
|  |  |  | 18:30 | 15450 |  | 0 |  | 15450
|  |  |  | 19:00 | 15450 |  | 0 |  | 15450
|  |  |  | 19:30 | 15470 |  | 0 |  | 15470
|  |  |  | 20:00 | 15400 |  | 0 |  | 15400
|  |  |  | 21:00 | 15300 |  | 0 |  | 15300
|  |  |  | 22:00 | 15200 |  | 0 |  | 15200
|  |  |  | 23:00 | 15000 |  | 0 |  | 15000
Probable Maximum Temperature: |  |  | 32.50°C
Probable Maximum Demand at Day Peak: |  |  | 13910.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15470.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15470.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 334.53 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:05 hrs on 29-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-10-2025 | [28 empty] | Date: | 28-10-2025 | [28 empty] | Date: | 28-10-2025 | [28 empty] | Date: | 28-10-2025 | [28 empty] | Date: | 28-10-2025 | [14 empty] | Date: | 28-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 20 | 133 | 45 | 293 | 55 | 0 | 54 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 20 | 22 | 0 | 310 | 94 | 16 | 98 | 0 | 0 | 64 | 60 | 17 | 12 | 12 | 0 | 220 | 0 | 31 | 650 | 17 | 0 | 0 | 25.5 | 0 | 223 | 0 | 0 | 0 | 1169 | 0 | 51 | 133 | 0 | 397 | 353 | 0 | 45 | 0 | 31 | 34 | 103 | 198 | 0 | 17 | 46 | 82 | 43 | 0 | 35 | 315 | 0 | 312 | 0 | 67 | 156 | 10 | 0 | 81 | 30 | 0 | 16 | 162 | 17 | 48 | 48 | 104 | 0 | 0 | 6 | 7653.5 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 1474.45 | 0 | 48 | 0 | 0 | 70 | 0 | 88 | 21 | 0 | 0 | 0 | 25 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 371 | 1178 | 10 | 6993.45 | 14646.95 | 104.23
01:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 17 | 132 | 45 | 245 | 30 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 310 | 92 | 16 | 80 | 0 | 0 | 64 | 45 | 0 | 12 | 12 | 0 | 220 | 0 | 35 | 650 | 17 | 0 | 0 | 8 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 138 | 0 | 397 | 355 | 0 | 45 | 0 | 31 | 53 | 103 | 199 | 0 | 17 | 46 | 82 | 43 | 0 | 35 | 315 | 0 | 312 | 0 | 67 | 158 | 10 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 106 | 0 | 0 | 6 | 7403 | 903 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 1475.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 356 | 1222 | 0 | 6645.69 | 14048.69 | 104.22
02:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 17 | 107 | 30 | 145 | 30 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 310 | 60 | 16 | 59 | 0 | 0 | 64 | 23 | 0 | 12 | 12 | 0 | 220 | 0 | 35 | 650 | 17 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 80 | 0 | 397 | 355 | 0 | 46 | 0 | 31 | 69 | 103 | 170 | 0 | 17 | 45 | 82 | 25 | 0 | 35 | 310 | 0 | 312 | 0 | 67 | 156 | 7 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 48 | 48 | 111 | 0 | 0 | 6 | 7084 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1144 | 0 | 1465.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 300 | 1222 | 0 | 6537.3 | 13621.3 | 104.21
03:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 17.5 | 17 | 96 | 30 | 145 | 15 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 14.5 | 22 | 0 | 330 | 61 | 16 | 50 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 35 | 650 | 17 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1168 | 0 | 51 | 50 | 0 | 397 | 350 | 0 | 45 | 0 | 31 | 69 | 104 | 85 | 0 | 17 | 47 | 76 | 25 | 0 | 35 | 315 | 0 | 312 | 0 | 67 | 158 | 7 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 48 | 48 | 111 | 0 | 0 | 6 | 6919 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1156 | 0 | 1377.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 303 | 1120 | 0 | 6344.89 | 13263.89 | 104.2
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 17.5 | 17 | 96 | 30 | 95 | 15 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 310 | 0 | 16 | 24 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 35 | 650 | 17 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1160 | 0 | 51 | 12 | 0 | 397 | 355 | 0 | 45 | 0 | 31 | 54 | 104 | 51 | 0 | 17 | 15 | 76 | 0 | 0 | 35 | 310 | 0 | 312 | 0 | 67 | 157 | 7 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 111 | 0 | 0 | 6 | 6567 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 0 | 1271.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 303 | 1090 | 0 | 6161.17 | 12728.17 | 104.19
05:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 17 | 96 | 30 | 95 | 0 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 35 | 650 | 17 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1142 | 0 | 51 | 12 | 0 | 397 | 355 | 0 | 46 | 0 | 28 | 41 | 103 | 51 | 0 | 17 | 14 | 72 | 0 | 0 | 36 | 305 | 0 | 312 | 0 | 67 | 151 | 7 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 111 | 0 | 0 | 6 | 6528 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 1263.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 303 | 1011 | 0 | 5994.94 | 12522.94 | 104.18
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 17 | 97 | 30 | 245 | 0 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 230 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1100 | 0 | 51 | 45 | 0 | 398 | 356 | 0 | 46 | 0 | 30 | 34 | 104 | 52 | 0 | 17 | 0 | 70 | 0 | 0 | 36 | 315 | 0 | 312 | 0 | 67 | 157 | 7 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 111 | 0 | 0 | 6 | 6596 | 903 | 340 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1023 | 0 | 1259.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 304 | 905 | 0 | 5739.24 | 12335.24 | 104.17
07:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 123 | 30 | 261 | 0 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 3 | 17 | 20.5 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 0.6 | 230 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1052 | 3 | 51 | 80 | 0 | 397 | 355 | 0 | 46 | 0 | 34 | 16 | 104 | 17 | 0 | 17 | 0 | 64 | 0 | 8 | 0 | 315 | 0 | 312 | 0 | 67 | 156 | 7 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 102 | 0 | 5.67 | 6 | 6553.77 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 982 | 0 | 1227.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.08 | 9 | 0 | 0 | 5.5 | 160 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0.52 | 0 | 0 | 30 | 3 | 0 | 0 | 0 | 0 | 0.6 | 19 | 0.06 | 0 | 170 | 110 | 220 | 0 | 304 | 922 | 0 | 5851.31 | 12405.08 | 104.16
08:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 131 | 45 | 261 | 4 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 11 | 35 | 17.5 | 22 | 0 | 310 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.34 | 230 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1005 | 6 | 51 | 100 | 0 | 350 | 320 | 0 | 45 | 0 | 34 | 15 | 102 | 15 | 0 | 17 | 0 | 60 | 0 | 35 | 0 | 310 | 0 | 312 | 0 | 67 | 153 | 7 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 48 | 48 | 104 | 1 | 18.52 | 6 | 6489.36 | 903 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 910 | 0 | 1167.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.77 | 36 | 0 | 0 | 22.85 | 157 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 1.87 | 0 | 0 | 35 | 13 | 20 | 0 | 0 | 0 | 3.4 | 71 | 0.21 | 0 | 170 | 110 | 220 | 0 | 303 | 850 | 0 | 5745.08 | 12234.44 | 104.15
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 131 | 45 | 261 | 15 | 17 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 20 | 35 | 20 | 22 | 0 | 325 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.28 | 230 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1015 | 15 | 51 | 112 | 0 | 393 | 344 | 0 | 45 | 0 | 34 | 16 | 100 | 16 | 0 | 17 | 0 | 46 | 0 | 51 | 0 | 315 | 0 | 312 | 0 | 67 | 160 | 7 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 48 | 48 | 104 | 1 | 31.13 | 6 | 6713.41 | 903 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53.32 | 912 | 0 | 1107.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.46 | 60 | 0 | 0 | 37.82 | 173 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 3.17 | 0 | 0 | 35 | 21 | 34 | 0 | 0 | 0 | 4.1 | 125 | 0.42 | 0 | 170 | 110 | 220 | 0 | 303 | 850 | 0 | 5884.17 | 12597.58 | 104.13
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 131 | 45 | 277 | 15 | 27 | 35 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 24 | 52 | 5 | 0 | 0 | 318 | 2 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.91 | 230 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1095 | 15 | 51 | 110 | 0 | 395 | 342 | 0 | 44 | 0 | 33 | 18 | 100 | 24 | 0 | 15 | 0 | 44 | 0 | 61 | 0 | 315 | 0 | 312 | 0 | 67 | 157 | 7 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 49 | 48 | 73 | 2 | 38.85 | 6 | 6831.76 | 903 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 986 | 0 | 1054.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.66 | 83 | 0 | 0 | 48.35 | 172 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 4.14 | 0 | 0 | 35 | 28 | 0 | 0 | 0 | 0 | 5.5 | 151 | 0.55 | 0 | 170 | 110 | 220 | 0 | 303 | 900 | 0 | 6076.75 | 12908.51 | 104.11
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 17 | 17 | 131 | 45 | 277 | 18 | 35 | 68 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 28 | 52 | 18 | 0 | 0 | 320 | 28 | 16 | 83 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.21 | 230 | 0 | 2 | 650 | 17 | 0 | 0 | 1 | 0 | 214 | 0 | 0 | 0 | 1115 | 18 | 51 | 113 | 0 | 395 | 341 | 0 | 45 | 0 | 33 | 41 | 99 | 54 | 0 | 15 | 53 | 42 | 0 | 69 | 0 | 320 | 0 | 312 | 0 | 67 | 159 | 7 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 73 | 2 | 42.88 | 6 | 7129.09 | 904 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52 | 1020 | 0 | 1003.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.68 | 91 | 0 | 0 | 55.09 | 177 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 4.77 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 6 | 146 | 0.54 | 0 | 170 | 110 | 220 | 0 | 301 | 992 | 0 | 6131.02 | 13260.11 | 104.09
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 17 | 117 | 45 | 277 | 47 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 52 | 19 | 22 | 0 | 310 | 66 | 16 | 83 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.25 | 230 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 1230 | 17 | 51 | 107 | 0 | 393 | 338 | 0 | 45 | 0 | 33 | 34 | 98 | 54 | 0 | 15 | 106 | 46 | 34 | 56 | 20 | 315 | 0 | 312 | 0 | 67 | 157 | 7 | 0 | 80 | 30 | 0 | 0 | 162 | 17 | 49 | 47 | 73 | 2 | 35.98 | 6 | 7370.23 | 903 | 376 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 1006 | 0 | 1011.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.8 | 98 | 0 | 0 | 36.86 | 202 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 3.76 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 5.1 | 176 | 0.57 | 0 | 170 | 110 | 220 | 0 | 302 | 1004 | 0 | 6233.27 | 13603.5 | 104.07
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 17 | 131 | 45 | 277 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 29 | 52 | 19 | 22 | 0 | 310 | 94 | 16 | 88 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.79 | 230 | 0 | 5 | 650 | 17 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1228 | 17 | 51 | 112 | 0 | 395 | 347 | 0 | 45 | 0 | 33 | 35 | 98 | 52 | 0 | 15 | 98 | 82 | 34 | 65 | 27 | 320 | 0 | 312 | 0 | 67 | 156 | 7 | 0 | 80 | 30 | 0 | 0 | 161 | 17 | 49 | 47 | 73 | 2 | 36.88 | 6 | 7489.67 | 903 | 378 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83.68 | 1112 | 0 | 1009.17 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 50.33 | 81 | 0 | 0 | 37.23 | 198 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 4.54 | 0 | 0 | 70 | 31 | 60 | 0 | 0 | 0 | 5.8 | 160 | 0.58 | 0 | 170 | 110 | 220 | 0 | 303 | 1058 | 0 | 6473.33 | 13963 | 104.06
14:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 17 | 17 | 131 | 45 | 277 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 24 | 52 | 12 | 22 | 0 | 330 | 91 | 16 | 93 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 2.42 | 222 | 0 | 3 | 650 | 17 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1226 | 16 | 51 | 110 | 0 | 393 | 339 | 0 | 41 | 0 | 30 | 34 | 98 | 51 | 0 | 15 | 102 | 72 | 43 | 12 | 27 | 315 | 0 | 312 | 0 | 67 | 152 | 7 | 0 | 80 | 30 | 0 | 0 | 161 | 17 | 49 | 47 | 73 | 2 | 12.94 | 6 | 7350.36 | 903 | 378 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72.68 | 1125 | 0 | 1006.64 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 37.5 | 54 | 0 | 0 | 27.28 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.82 | 0 | 0 | 95 | 24 | 75 | 0 | 0 | 0 | 4.8 | 131 | 0.4 | 0 | 170 | 110 | 220 | 0 | 355 | 1062 | 0 | 6562.12 | 13912.48 | 104.05
15:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 17 | 17 | 131 | 44 | 277 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 14 | 52 | 14 | 22 | 0 | 330 | 91 | 16 | 95 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 1.65 | 222 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1224 | 10 | 51 | 110 | 0 | 406 | 340 | 0 | 37 | 0 | 33 | 35 | 97 | 51 | 0 | 15 | 94 | 76 | 43 | 14 | 27 | 310 | 0 | 312 | 0 | 67 | 153 | 7 | 0 | 80 | 30 | 0 | 0 | 162 | 17 | 49 | 47 | 73 | 1 | 20.84 | 6 | 7342.49 | 903 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 1147 | 0 | 1008 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 52.2 | 23.87 | 43 | 0 | 0 | 32.56 | 178 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 2.13 | 0 | 0 | 95 | 17 | 105 | 0 | 0 | 0 | 3.1 | 90 | 0.37 | 0 | 170 | 110 | 220 | 0 | 353 | 1078 | 0 | 6565.23 | 13907.72 | 104.04
16:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 17 | 17 | 131 | 44 | 293 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 52 | 19 | 22 | 0 | 310 | 89 | 16 | 94 | 0 | 0 | 8 | 0 | 0 | 12 | 12 | 0.52 | 222 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 108 | 0 | 410 | 344 | 0 | 36 | 0 | 33 | 34 | 98 | 37 | 0 | 15 | 98 | 82 | 43 | 9 | 27 | 310 | 0 | 312 | 0 | 67 | 153 | 7 | 0 | 80 | 30 | 0 | 0 | 161 | 17 | 48 | 48 | 73 | 1 | 7.92 | 6 | 7324.44 | 904 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 1143 | 0 | 1008 | 0 | 0 | 0 | 0 | 113 | 0 | 8 | 0 | 52.2 | 7.41 | 15 | 0 | 0 | 12.1 | 161 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0.89 | 0 | 0 | 95 | 7 | 106 | 0 | 0 | 0 | 1.5 | 41 | 0.04 | 0 | 170 | 110 | 180 | 0 | 354 | 1078 | 0 | 6330.14 | 13654.58 | 104.03
17:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35.9 | 17 | 116 | 73 | 293 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 19.5 | 22 | 0 | 310 | 89 | 16 | 95 | 0 | 0 | 16 | 7 | 2 | 12 | 12 | 0.06 | 221 | 0 | 2 | 650 | 35 | 0 | 0 | 15 | 0 | 214 | 0 | 0 | 0 | 1212 | 0 | 51 | 108 | 0 | 410 | 344 | 0 | 40 | 0 | 33 | 44 | 98 | 17 | 0 | 15 | 102 | 72 | 43 | 8 | 34 | 315 | 0 | 312 | 0 | 67 | 155 | 7 | 0 | 80 | 30 | 0 | 0 | 161 | 17 | 50 | 57 | 73 | 0 | 0.98 | 6 | 7388.44 | 903 | 376 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1116 | 0 | 1001 | 0 | 40 | 0 | 0 | 113 | 0 | 8 | 0 | 52.2 | 0.26 | 3 | 12 | 0 | 1.31 | 164 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.12 | 0 | 0 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 170 | 110 | 180 | 0 | 300 | 1078 | 0 | 6223.89 | 13612.33 | 104.02
18:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 50.7 | 17 | 119 | 135 | 293 | 55 | 35 | 126 | 0 | 280 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 19.5 | 22 | 0 | 310 | 94 | 16 | 97 | 0 | 0 | 50 | 33 | 35 | 12 | 12 | 0 | 220 | 0 | 5 | 650 | 145 | 0 | 0 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1182 | 0 | 51 | 117 | 0 | 385 | 343 | 0 | 41 | 0 | 37 | 51 | 102 | 17 | 0 | 15 | 95 | 80 | 43 | 0 | 34 | 315 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 80 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 73 | 0 | 0 | 3 | 7873.7 | 903 | 377 | 0 | 33 | 6 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 0 | 1003 | 0 | 32 | 0 | 35 | 113 | 0 | 87 | 15 | 52.2 | 0 | 0 | 25 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 170 | 110 | 220 | 0 | 502 | 1064 | 10 | 6719.2 | 14592.9 | 104.01
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 46.3 | 35 | 120 | 135 | 293 | 55 | 55 | 126 | 0 | 320 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 340 | 86 | 16 | 89 | 0 | 0 | 50 | 67 | 35 | 12 | 12 | 0 | 218 | 0 | 9 | 650 | 145 | 0 | 0 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 0 | 410 | 350 | 0 | 44 | 0 | 37 | 76 | 103 | 17 | 0 | 15 | 95 | 84 | 43 | 0 | 34 | 310 | 0 | 312 | 0 | 67 | 146 | 9 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 73 | 0 | 0 | 6 | 8066.8 | 903 | 378 | 0 | 41 | 26 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 1001 | 0 | 41 | 0 | 35 | 113 | 0 | 95 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 170 | 110 | 220 | 0 | 500 | 1066 | 10 | 6926.2 | 14993 | 104
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 43.5 | 35 | 131 | 135 | 293 | 55 | 55 | 126 | 0 | 320 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 20 | 15 | 0 | 340 | 88 | 16 | 89 | 0 | 0 | 50 | 67 | 35 | 12 | 12 | 0 | 218 | 0 | 18 | 650 | 145 | 0 | 0 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 129 | 0 | 410 | 348 | 14 | 45 | 0 | 34 | 90 | 103 | 100 | 0 | 17 | 99 | 88 | 43 | 0 | 34 | 310 | 0 | 312 | 0 | 67 | 150 | 9 | 0 | 77 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 73 | 0 | 0 | 0 | 8184 | 904 | 381 | 0 | 37 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 994 | 0 | 41 | 0 | 35 | 113 | 0 | 95 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 95 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 170 | 110 | 220 | 0 | 504 | 1066 | 10 | 6973.2 | 15157.2
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 44.6 | 35 | 125 | 135 | 293 | 55 | 55 | 126 | 0 | 320 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 20 | 19 | 0 | 340 | 84 | 16 | 91 | 0 | 0 | 50 | 67 | 35 | 12 | 12 | 0 | 220 | 0 | 22 | 650 | 145 | 0 | 0 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 0 | 403 | 349 | 80 | 45 | 0 | 34 | 91 | 103 | 98 | 0 | 17 | 96 | 84 | 43 | 0 | 35 | 305 | 0 | 312 | 0 | 67 | 149 | 9 | 0 | 77 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 73 | 0 | 0 | 0 | 8233.1 | 904 | 380 | 0 | 37 | 64 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 997 | 0 | 41 | 0 | 35 | 113 | 0 | 95 | 32 | 52.2 | 0 | 0 | 25 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 95 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 170 | 110 | 220 | 0 | 504 | 1077 | 10 | 6957.2 | 15190.3 | 103.99
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 45 | 35 | 131 | 135 | 293 | 55 | 35 | 126 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 14 | 22 | 0 | 310 | 84 | 16 | 103 | 0 | 0 | 50 | 67 | 35 | 12 | 12 | 0 | 221 | 0 | 27 | 650 | 72 | 0 | 0 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 130 | 0 | 397 | 352 | 191 | 45 | 0 | 37 | 90 | 103 | 109 | 0 | 17 | 94 | 78 | 43 | 0 | 35 | 305 | 0 | 312 | 0 | 67 | 140 | 9 | 0 | 78 | 30 | 0 | 0 | 159 | 17 | 49 | 48 | 73 | 0 | 0 | 0 | 8163.5 | 904 | 383 | 0 | 37 | 51 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1221 | 0 | 995.38 | 0 | 41 | 0 | 35 | 113 | 0 | 95 | 32 | 52.2 | 0 | 0 | 25 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 95 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 170 | 110 | 220 | 0 | 503 | 1140 | 10 | 7042.58 | 15206.08 | 103.98
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 45.3 | 19 | 131 | 45 | 293 | 55 | 35 | 126 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 20.5 | 22 | 0 | 315 | 82 | 16 | 104 | 0 | 0 | 50 | 67 | 35 | 12 | 12 | 0 | 221 | 0 | 32 | 650 | 17 | 0 | 0 | 25.5 | 0 | 223 | 0 | 0 | 0 | 1163 | 0 | 51 | 133 | 0 | 397 | 300 | 100 | 25 | 0 | 37 | 74 | 103 | 114 | 0 | 17 | 105 | 84 | 43 | 0 | 35 | 300 | 0 | 312 | 0 | 67 | 143 | 9 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 76 | 0 | 0 | 0 | 7882.3 | 903 | 385 | 0 | 37 | 45 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 1015.67 | 0 | 41 | 0 | 35 | 113 | 0 | 95 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 95 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 170 | 110 | 220 | 0 | 503 | 1175 | 10 | 7060.87 | 14943.17 | 103.97
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 28 | 17 | 131 | 45 | 293 | 55 | 35 | 54 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 35 | 20.5 | 22 | 0 | 310 | 91 | 16 | 104 | 0 | 0 | 50 | 67 | 17 | 12 | 12 | 0 | 221 | 0 | 34 | 650 | 17 | 0 | 0 | 25.5 | 0 | 223 | 0 | 0 | 0 | 1162 | 0 | 51 | 138 | 0 | 397 | 300 | 58 | 38 | 0 | 37 | 47 | 103 | 127 | 0 | 17 | 107 | 86 | 43 | 0 | 35 | 310 | 0 | 312 | 0 | 67 | 148 | 9 | 0 | 78 | 30 | 0 | 0 | 159 | 17 | 49 | 47 | 74 | 0 | 0 | 0 | 7648 | 902 | 375 | 0 | 36 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1019.99 | 0 | 40 | 0 | 35 | 113 | 0 | 95 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 170 | 110 | 220 | 0 | 503 | 1152 | 10 | 7039.39 | 14687.39 | 103.96
Total KWH | 0 | 1406400 | 481440 | 0 | 0 | 0 | 0 | 0 | 8056800 | 0 | 0 | 520200 | 502920 | 2948976 | 1332480 | 6112145 | 888887 | 530532 | 1579680 | 0 | 7198000 | 0 | 0 | 0 | 135715 | 6263948 | 0 | 0 | 188888 | 1369200 | 450000 | 487800 | 0 | 7835454.55 | 1433945 | 308618 | 1664640 | 0 | 5280 | 644285 | 516233 | 241483 | 300480 | 292800 | 20641 | 5344409 | 0 | 428640 | 15723636.36 | 757745 | 0 | 0 | 259965 | 0 | 5319207 | 0 | 0 | 0 | 27785452 | 115020 | 1208792 | 2509090 | 0 | 9548000 | 8585900 | 444000 | 1023360 | 0 | 806760 | 1121280 | 2426694 | 1695840 | 0 | 403920 | 1559520 | 1701120 | 635885 | 365073 | 603888 | 7638000 | 0 | 7845000 | 0 | 1587120 | 3694009 | 205992 | 0 | 1914240 | 719904 | 0 | 0 | 3791460 | 427680 | 1177200 | 1161600 | 2024640 | 12100 | 254250 | 114240 | 176658501.91 | 21882181 | 9088416 | 0 | 208800 | 221952 | 912000 | 0 | 0 | 0 | 0 | 0 | 524160 | 26625450 | 0 | 26829818 | 0 | 303389 | 0 | 234048 | 1251456 | 0 | 669424 | 144834 | 506165 | 323862 | 571840 | 178630 | 0 | 350256 | 4106545 | 0 | 0 | 0 | 0 | 0 | 9056145 | 0 | 30060 | 0 | 0 | 1332652 | 204502 | 1438262 | 0 | 0 | 0 | 39831.12 | 1116000 | 3550 | 685632 | 4124000 | 2634000 | 5318070 | 0 | 8784576 | 26162909.09 | 76800 | 155940215.21 | 332598717.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13603.5 | MW | 12:00 Hr. | Energy Generated |  |  | 332.5987 |  | MKWHr.
| Day Peak Demand |  |  | 13814.5 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.435 |  | MKWHr.
| Evening Peak Generation |  |  | 15206.08 | MW | 21:00 Hr. | Energy Demand |  |  | 336.0337 |  | MKWHr.
| Evening Peak Demand |  |  | 15550.12 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.7 |  | °C
| Minimum Generation of the Day |  |  | 12234.44 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 876.78 |  | MMCFD
| Maximum Generation of the Day |  |  | 15206.08 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.7856 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.292 | 0 | 17.8086 | 0 | 0 | 0.18889 | 0 | 0 | 48.2895 | Gas | 120.1108 | Gas | 424396036.4135
| Chattogram Zone |  |  | 5.7478 | 43.5091 | 6.4202 | 0 | 5.3444 | 0.13566 | 0 | 0.00528 | 61.1625 | Coal | 109.206 | Coal | 691967024.891
| Cumilla Zone |  |  | 24.4474 | 0 | 8.1255 | 0 | 0 | 0.36507 | 1.7011 | 0 | 34.6391 | HFO | 42.487 | HFO | 769559151.96
| Mymensingh Zone |  |  | 2.0246 | 0 | 2.8807 | 0 | 0 | 0.26635 | 0 | 0 | 5.1717 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3957 | Hydro | 5.3444 | Hydro | 534440.9
| Khulna Zone |  |  | 9.0884 | 26.6255 | 0.43075 | 0 | 0 | 0.52416 | 22.7942 | 0 | 59.463 | Solar | 4.12 | Solar | 66397665.6992
| Barishal Zone |  |  | 7.9521 | 39.0715 | 0.76243 | 0 | 0 | 0.00355 | 0 | 0 | 47.7895 | Import | 51.3251 | Import | 303934402.19
| Rajshahi Zone |  |  | 13.1627 | 0 | 3.2879 | 0 | 0 | 1.276 | 26.8298 | 0 | 44.5565 | Wind | 0.00528 | Wind | 77668.8
| Rangpur Zone |  |  | 0 | 0 | 2.7709 | 0 | 0 | 1.3603 | 0 | 0 | 4.1312
| Total |  |  | 120.1108 | 109.206 | 42.487 | 0 | 5.3444 | 4.12 | 51.3251 | 0.00528 | 332.5987
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 424396036.4135 |  | Hydro | 534440.9
|  |  |  | Coal | 691967024.891 |  | Solar | 66397665.6992
|  |  |  | HFO | 769559151.96 |  | Import | 303934402.19
|  |  |  | HSD | 0 |  | Wind | 77668.8
[5 empty] | Total: | 225,68,66,390 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8822 | Peak Hr Flow | 904.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50915654.61 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.8298 | Peak Hr Flow | 995.38 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2325 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7011 | Peak Hr Flow | 78.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2646 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.4131 | Peak Hr Flow | 1977.38 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5429
|  |  |  | Chattogram |  | 10 |  | 1541
|  |  |  | Cumilla |  | 0 |  | 1436
|  |  |  | Mymensingh |  | 100 |  | 1168
|  |  |  | Sylhet |  | 0 |  | 653
|  |  |  | Khulna |  | 0 |  | 1721
|  |  |  | Barishal |  | 0 |  | 458
|  |  |  | Rajshahi |  | 0 |  | 1445
|  |  |  | Rangpur |  | 0 |  | 825
|  |  |  | Total |  | 110 |  | 14676
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:14 | 15:50 | Noapara 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance
| 08:14 |  | Bagabari-71-----Bera 132 KV ckt S/D. (upto tower No. 268).
| 08:15 | 15:50 | Noapara 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance
| 08:24 | 15:19 | Ishwardi-Rooppur 132kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to Maintenance
work at Ruppur substation and from Ruppur 132/11kV end Due to Annual Maintenance
| 08:39 | 12:40 | Mirsorai 230/33kV S/S 150 MW Power Station -01 Scheduled S/D Due to Annual maintenance
| 08:43 | 16:28 | Bogura 230/132kV S/S T-03 HT Scheduled S/D Due to Annual Maintenance
| 08:43 | 16:28 | Bogura 230/132kV S/S T-03 LT Scheduled S/D Due to Annual Maintenance
| 08:52 |  | At Bhola GT P/S,(120/140)MVA Transformer S/D is withdrawn.
| 09:07 | 17:26 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance
| 09:15 | 16:15 | Lalmonirhat 132/33kV S/S T-1 (425T) LT Scheduled S/D Due to Annual maintenance.
| 09:24 | 15:38 | Bagerhat-Bhandaria 132 kV Ckt-1 Project Work S/D from Bagerhat 132/33kV end Due to DWZTGE
Project piling work
| 09:31 | 21:05 | Gopalganj 400/132kV S/S 400kV Rooppur Project Work S/D Due to None
| 09:45 | 17:25 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to Due to annual maintenance .
|  | 09:55 | Kalurghat 132/33kV S/S TRFO-02(516T) LT is restored.
| 10:12 | 14:30 | Meghnaghat 400/230kV S/S 400 kV Bus -02 Project Work S/D
|  | 10:16 | Madaripur 132/33kV S/S 33 KV BUS is restored.
|  | 10:30 | Goalpara 132/33kV S/S T-6 HT is restored.
| 10:32 | 13:52 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Scheduled S/D Due to 33 kv bushing maintenance
| 10:32 | 13:52 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Scheduled S/D Due to 33 kv bushing maintenance
|  | 10:34 | Goalpara 132/33kV S/S T-6 LT is restored.
| 10:46 | 13:24 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 10:46 | 13:22 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to 33 kv CT & PT Test By
PBS
| 11:47 | 12:00 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Tap change
| 12:00 |  | Day Peak Generation: 13599 MW.
| 12:15 | 15:25 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to 33 kV feeder | [7 empty] | 11.0MW load
|  |  | extension | [7 empty] | interrup.
| 12:15 | 15:24 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to 33 kV feeder | [7 empty] | 11.0MW load
|  |  | extension | [7 empty] | interrup.
| 12:46 | 15:47 | Mirsorai 230/33kV S/S 150 MW Power Station -02 Scheduled S/D Due to annual maintenance
| 13:56 |  | Satiya - Bera 132V ckt S/D.(Bera line disconnected from Bagabari line.
| 15:31 |  | Ghorashal AIS - Regent power ckt was switched on at 15:31hr. and tripped at 20:57hr. due
to blue phase LA burst at Regent end.
| 16:11 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Tripped showing Lockout Relay,
Distance Relay relays Due to None
|  | 16:26 | Sholosohor 132/33kV S/S TRAFO-01 HT is restored.
|  | 16:27 | Sholosohor 132/33kV S/S TRAFO-01 LT is restored.
|  | 16:30 | Barishal 132/33kV S/S 132 kV Capacitor Bank is restored.
|  | 16:49 | Chauddagram-Cumilla(S) 132 kV Ckt-2 is restored.
|  | 17:12 | Patuakhali 132/33kV S/S 415T (T-2) HT is restored.
|  | 17:13 | Patuakhali 132/33kV S/S 415T (T-2) LT is restored.
|  | 17:15 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
|  | 18:16 | Madaripur 132/33kV S/S T2-415T LT is restored.
|  | 18:16 | Madaripur 132/33kV S/S T2-415T HT is restored.
| 18:58 |  | Satiya - Bera 132V ckt syn.(Bera line disconnected from Bagabari line.
| 19:24 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 21:00 |  | Evening Peak Generation: 15205 MW.
| 06:00 |  | Minimum Generation is 12294 MW
| 06:21 |  | Rampura - Bashundhara L-1 was shut down due to Red Hot maintenance at Rampura End.
| 06:44 |  | Feni (New) - Dagonbhuyan (via)- Chowmuhuni line was shut down due to project work.
| 06:44 |  | Feni (New) - Chowmuhuni line was shut down for project work (LILO at Dagonbhuyan).
| 06:44 |  | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Chowmuhani 132/33kV end Due to Project
Work
| 06:44 |  | Chowmuhani-Feni 132 kV Ckt-2 Project Work S/D from Chowmuhani 132/33kV end Due to Project
Work
| 07:09 |  | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to Redhot maintenance
| 07:13 |  | Sholosohor 132/33kV S/S TRAFO-02 LT Scheduled S/D Due to Annual Maintenance
| 07:14 |  | Patuakhali 132/33kV S/S 425T (T-3) LT Scheduled S/D Due to Maintenance work-25
| 07:14 |  | Sholosohor 132/33kV S/S TRAFO-02 HT Scheduled S/D Due to Annual Maintenance
| 07:15 |  | Patuakhali 132/33kV S/S 425T (T-3) HT Scheduled S/D Due to Maintenance work-25
| 07:22 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to Annual
Maintenance work. and from Sylhet 132/33kV end Due to Due to Yearly Maintenance
| 07:22 |  | Kodda 132/33kV S/S Bus-2 Scheduled S/D
| 07:40 |  | Chauddagram-Cumilla(S) 132 kV Ckt-2 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual maintenance and from Chauddagram 132/33kV end Due to yearly maintanence. ( Line )
| 07:42 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For 33/11kv T-1 transformer incomming | [7 empty] | 38.0MW load
|  |  | isolator maintenance by bpdb. | [7 empty] | interrup.
| 07:42 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For 33/11 kv T-1 transformer | [7 empty] | 38.0MW load
|  |  | incomming isolator maintenance by bpdb | [7 empty] | interrup.
| 07:45 |  | Madaripur 132/33kV S/S T3-426T HT Scheduled S/D Due to Annual maintenance
| 07:45 |  | Madaripur 132/33kV S/S T3-426T LT Scheduled S/D Due to Annual maintenance
| 07:46 |  | Madaripur 132/33kV S/S 33 KV BUS Scheduled S/D Due to 33 kv bus section-3 shut down taken | [7 empty] | 15.0MW load
|  |  | by Madaripur pbs for manitenance work | [7 empty] | interrup.
| 07:51 |  | Lalmonirhat 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Anual Maintanance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 310 | 8056800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7198000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 888887 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6263948 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45 | 520200 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 135 | 1332480 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 530532 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 135715 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14 | 450000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 487800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 481440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 6112145 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2948976 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1406400 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1579680 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 188888 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 502920 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 310 | 7835454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1369200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2350 | 48289465.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 259965 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115020 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5344409 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5319207 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 516233 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 644285 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 300480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 428640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 103 | 1664640 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 308618 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 241483 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 292800 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 84 | 1433945 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 72 | 757745 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 27785452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 5280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15723636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2754.5 | 61162479.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 352 | 8585900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 191 | 444000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 397 | 9548000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 806760 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 45 | 1023360 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1208792 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 2509090 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 603888 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2426694 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 109 | 1695840 | -
| Import (Tripura) |  | Import | 0 | 160 | 78 | 1701120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 635885 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 403920 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 94 | 1559520 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1121280 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 365073 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1772 | 34639122
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 73 | 2024640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1161600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 49 | 1177200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 254250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 114240 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 427680 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 187 | 5171710
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1587120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3694009 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719904 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1914240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 159 | 3791460 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 9 | 205992 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7638000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 312 | 7845000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1100 | 27395725
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 21882181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 208800 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 51 | 221952 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 383 | 9088416 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 524160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1221 | 26625450 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2634 | 59462959
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 8784576 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 685632 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2634000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1140 | 26162909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5318070 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 10 | 76800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 170 | 4124000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3550 | -
Barishal Area Total |  |  |  |  | 2858 | 2263 | 47789537.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 323862 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 303389 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 144834 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 157 | 4106545 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 395 | 9056145 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 178630 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 506165 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 669424 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1251456 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 234048 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 995.38 | 26829818 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 350256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 571840 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1940.58 | 44556472
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 1438262 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39831.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1332652 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 204502 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1116000 | -
Rangpur Area Total |  |  |  |  | 950 | 205 | 4131247.12
Eastern Grid Total |  |  |  |  | 17383.855 | 8163.5 | 176658501.91
Western Grid Total |  |  |  |  | 10980.24 | 7042.58 | 155940215.21
National Grid Total |  |  |  |  | 28364.095 | 15206.08 | 332598717.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-10-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10117.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4448.3 | MW
i) Dhaka area |  |  | 5429.32 |  | MW | i) Khulna area |  |  |  | 1721 | MW
ii) Chattogram area |  |  | 1531 |  | MW | ii) Barishal area |  |  |  | 457.5 | MW
iii) Cumilla area |  |  | 1436.32 |  | MW | iii) Rajshahi area |  |  |  | 1444.8 | MW
iv) Mymensingh area |  |  | 1068 |  | MW | iv) Rangpur area |  |  |  | 825 | MW
v) Sylhet area |  |  | 653 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14565.94 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 82 | 20:00 | 133 | Niamatpur | 78 | 21:00
2 | AKSML | 164 | 13:00 | 68 | Ishurdi | 73 | 21:00 | 134 | Noapara | 50 | 13:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jaldhaka | 64 | 18:00 | 135 | PHP | 5 | 12:00
4 | Agargaon | 135 | 13:00 | 70 | Jamalpur | 103 | 07:00 | 136 | Pabna | 101 | 18:00
5 | Agrabad | 110 | 18:30 | 71 | Jashore | 139 | 18:30 | 137 | Palashbari | 104 | 19:00
6 | Amnura | 34 | 18:00 | 72 | Jhenaidah | 127 | 19:00 | 138 | Panchagarh | 45 | 21:00
7 | Ashuganj | 91 | 23:00 | 73 | Joydebpur | 158 | 18:30 | 139 | Patiya | 10.5 | 20:00
8 | BSRM | 209 | 00:00 | 74 | Joypurhat | 66 | 22:00 | 140 | Patuakhali | 69.5 | 20:00
9 | Bagerhat | 83 | 22:00 | 75 | Juldah | 17 | 17:00 | 141 | Payra | 32 | 18:00
10 | Bajitpur | 80 | 20:00 | 76 | KSRM | 32 | 17:00 | 142 | Postogola | 71 | 00:00
11 | Bakulia | 105 | 19:00 | 77 | Kabirpur | 252 | 19:00 | 143 | Purbachal | 23 | 18:00
12 | Banani | 54 | 11:00 | 78 | Kachua | 88 | 00:00 | 144 | Purbasadipur | 117 | 18:00
13 | Bangabhaban | 28 | 11:00 | 79 | Kallyanpur | 108 | 13:00 | 145 | Rahanpur | 33 | 20:00
14 | Barapukuria | 61 | 21:00 | 80 | Kalurghat | 42 | 00:00 | 146 | Rahim | 39 | 09:00
15 | Barguna | 22 | 22:00 | 81 | Kamrangirchar | 80 | 12:00 | 147 | Rajbari | 81 | 18:30
16 | Barishal | 115 | 19:30 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 134 | 19:30
17 | Barishal-230 | 84 | 00:00 | 83 | Kasba | 38 | 21:00 | 149 | Rajshahi | 104 | 20:00
18 | Baroaulia | 77 | 09:00 | 84 | Kazla | 103 | 18:00 | 150 | Rajshahi-230 | 90 | 13:00
19 | Baroirhat | 69 | 20:00 | 85 | Keranigonj | 85 | 19:00 | 151 | Ramganj | 114 | 00:00
20 | Bashundhara | 221 | 12:00 | 86 | Khagrachori | 34 | 18:00 | 152 | Rampur | 46 | 23:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulna | 74 | 13:00 | 153 | Rangamati | 17 | 19:00
22 | Beanibazar | 80 | 19:00 | 88 | Khulshi | 194 | 16:00 | 154 | Rangpur | 125 | 21:00
23 | Benapole | 59 | 13:00 | 89 | Kishoreganj | 128 | 21:00 | 155 | Ruppur | 8.4 | 15:00
24 | Bhaluka | 152 | 20:00 | 90 | Kodda | 291 | 09:00 | 156 | SSM | 5 | 07:00
25 | Bhandaria | 62 | 22:00 | 91 | Kulaura | 51 | 19:00 | 157 | Saidpur | 90 | 14:00
26 | Bhangura | 36 | 20:00 | 92 | Kurigram | 50 | 07:00 | 158 | Satkhira | 133 | 22:00
27 | Bheramara(GK) | 63 | 19:00 | 93 | Kushtia | 146 | 18:00 | 159 | Satmasjid | 107 | 18:00
28 | Bhulta | 221 | 12:00 | 94 | Laksam | 34 | 00:00 | 160 | Savar | 225 | 19:30
29 | Bog-Sherpur | 62 | 20:00 | 95 | Lakshmipur | 32 | 00:00 | 161 | SevenRings | 18.02 | 21:00
30 | Bogura | 164 | 21:00 | 96 | Lalbag | 62 | 12:00 | 162 | ShahCement | 12 | 00:00
31 | Borhanuddin | 95 | 18:00 | 97 | Lalmonirhat | 47 | 18:00 | 163 | Shahjadpur | 85 | 21:00
32 | Brahmanbaria | 141 | 20:00 | 98 | MI_Cement | 16.3 | 03:00 | 164 | Shahjibazar | 132 | 21:00
33 | Cantonment | 164 | 18:00 | 99 | Madanganj | 44 | 00:00 | 165 | Shahmirpur | 64 | 02:00
34 | Chandina | 15.22 | 22:00 | 100 | Madaripur | 108 | 23:00 | 166 | Shariatpur | 89 | 21:00
35 | Chandpur | 80 | 22:00 | 101 | Madartek | 100 | 23:00 | 167 | Sherpur | 112 | 00:00
36 | Chandraghona | 37 | 20:00 | 102 | Madunaghat | 60 | 19:30 | 168 | Shikalbaha | 29 | 23:00
37 | Chapai | 68 | 21:00 | 103 | Magura | 66 | 18:00 | 169 | Shitalakhya | 87.7 | 15:00
38 | Charsaidpur | 33 | 04:00 | 104 | Mahasthangarh | 68 | 20:00 | 170 | Sholosohor | 48 | 18:30
39 | Chauddagram | 71 | 19:30 | 105 | Maijdee | 38 | 00:00 | 171 | Shyampur | 108 | 13:00
40 | Chhatak | 38 | 19:30 | 106 | Manikganj | 131 | 18:30 | 172 | Siddhirganj | 124 | 15:00
41 | Chowmuhani | 164 | 00:00 | 107 | Maniknagar | 66 | 13:00 | 173 | Sirajganj | 115 | 19:00
42 | Chuadanga | 110 | 19:30 | 108 | Matarbari | 53 | 21:00 | 174 | Sonargaon | 124 | 19:00
43 | Coxsbazar | 145 | 19:30 | 109 | Matuail | 74 | 15:00 | 175 | Sreemongol | 88 | 19:00
44 | Cumilla(N) | 152 | 12:00 | 110 | Metrorail_Motijheel | 35 | 10:00 | 176 | Sreepur | 117 | 18:30
45 | Cumilla(S) | 154 | 18:00 | 111 | Metrorail_Uttara | 9 | 09:00 | 177 | Srinagar | 49.6 | 21:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 132 | 12:00 | 178 | Sunamganj | 63 | 19:00
47 | Daudkandi | 162 | 19:30 | 113 | Mirpur | 145 | 12:00 | 179 | Sylhet | 52 | 18:30
48 | DhakaUniversity | 71 | 12:00 | 114 | Mirsorai | 11 | 15:00 | 180 | Sylhet-132 | 133 | 18:30
49 | Dhamrai | 126 | 19:00 | 115 | Mirzapur | 43 | 12:00 | 181 | TK | 24 | 00:00
50 | Dhanmondi | 120.4 | 13:00 | 116 | Mithapukur | 50 | 19:00 | 182 | Tangail | 158 | 00:00
51 | Dohazari | 104 | 19:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 20 | 18:00
52 | Faridpur | 174 | 18:00 | 118 | Mogbazar | 106.5 | 16:00 | 184 | Thakurgaon | 90 | 18:00
53 | Fatullah | 121 | 15:00 | 119 | Mongla | 48 | 12:00 | 185 | Tongi | 121 | 09:00
54 | Fenchuganj | 43 | 19:00 | 120 | Motijheel | 74 | 13:00 | 186 | Ullahpara | 40 | 20:00
55 | Feni | 118 | 21:00 | 121 | Muktagacha | 28 | 00:00 | 187 | Ullon | 72 | 19:30
56 | GPH | 78 | 13:00 | 122 | Munshiganj | 111 | 23:00 | 188 | Uttara | 109 | 13:00
57 | Ghatail | 64 | 00:00 | 123 | Muradnagar | 43 | 19:00 | 189 | UttaraNew | 22 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 209 | 20:00 | 190 | Zigatola | 77 | 13:00
59 | Ghorashal-230 | 106 | 00:00 | 125 | Naogaon | 113 | 00:00
60 | Goalpara | 40 | 00:00 | 126 | Narail | 58 | 18:30
61 | Gollamari | 94 | 23:00 | 127 | Narinda | 76 | 13:00
62 | Gopalganj | 100 | 22:00 | 128 | Narshingdi | 188 | 19:00
63 | Gulshan | 136 | 12:00 | 129 | Natore | 143 | 21:00
64 | Halishahar | 86 | 11:00 | 130 | Nawabganj | 47.2 | 22:00
65 | HaripurSBU | 153 | 11:00 | 131 | Netrakona | 110 | 13:00
66 | Hasnabad | 103 | 20:00 | 132 | New | 62 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14646.95 | 59 |  | 14708.61
1:00 | 14048.69 | 51 |  | 14101.69
2:00 | 13621.3 | 48 |  | 13671.3
3:00 | 13263.89 | 27 |  | 13291.89
4:00 | 12728.17 | 22 |  | 12751.17
5:00 | 12522.94 | 0 |  | 12522.94
6:00 | 12335.24 | 0 |  | 12335.24
7:00 | 12405.08 | 0 |  | 12405.08
8:00 | 12234.44 | 44 |  | 12280.42
9:00 | 12597.58 | 53 |  | 12652.97
10:00 | 12908.51 | 0 |  | 12908.51
11:00 | 13260.11 | 47 |  | 13309.23
12:00 | 13603.5 | 202 |  | 13814.5
13:00 | 13963 | 222 |  | 14195
14:00 | 13912.48 | 251 |  | 14174.78
15:00 | 13907.72 | 302 |  | 14223.31
16:00 | 13654.58 | 266 |  | 13932.55
17:00 | 13612.33 | 249 |  | 13872.54
18:00 | 14592.9 | 582 |  | 15201.09
19:00 | 14993 | 437 |  | 15449.67
19:30 | 15157.2 | 376 |  | 15550.12
20:00 | 15190.3 | 202 |  | 15401.39
21:00 | 15206.08 | 110 |  | 15321.03
22:00 | 14943.17 | 123 |  | 15072.17
23:00 | 14687.39 | 138 |  | 14831.39
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7653.5 | 6993.45 | 14646.95 | DAILY GENERATION CURVE
00:30 | 7528.25 | 6819.57 | 14347.82
01:00 | 7403 | 6645.69 | 14048.69 | 28-10-2025
01:30 | 7243.5 | 6591.495 | 13834.995
02:00 | 7084 | 6537.3 | 13621.3
02:30 | 7001.5 | 6441.095 | 13442.595
03:00 | 6919 | 6344.89 | 13263.89
03:30 | 6743 | 6253.03 | 12996.03
04:00 | 6567 | 6161.17 | 12728.17
04:30 | 6547.5 | 6078.055 | 12625.555
05:00 | 6528 | 5994.94 | 12522.94
05:30 | 6562 | 5867.09 | 12429.09
06:00 | 6596 | 5739.24 | 12335.24
06:30 | 6574.885 | 5795.275 | 12370.16
07:00 | 6553.77 | 5851.31 | 12405.08
07:30 | 6521.565 | 5798.195 | 12319.76
08:00 | 6489.36 | 5745.08 | 12234.44
08:30 | 6601.385 | 5814.625 | 12416.01
09:00 | 6713.41 | 5884.17 | 12597.58
09:30 | 6772.585 | 5980.46 | 12753.045
10:00 | 6831.76 | 6076.75 | 12908.51
10:30 | 6980.425 | 6103.885 | 13084.31
11:00 | 7129.09 | 6131.02 | 13260.11
11:30 | 7249.66 | 6182.145 | 13431.805
12:00 | 7370.23 | 6233.27 | 13603.5
12:30 | 7429.95 | 6353.3 | 13783.25
13:00 | 7489.67 | 6473.33 | 13963
13:30 | 7420.015 | 6517.725 | 13937.74
14:00 | 7350.36 | 6562.12 | 13912.48
14:30 | 7346.425 | 6563.675 | 13910.1
15:00 | 7342.49 | 6565.23 | 13907.72
15:30 | 7333.465 | 6447.685 | 13781.15
16:00 | 7324.44 | 6330.14 | 13654.58
16:30 | 7356.44 | 6277.015 | 13633.455
17:00 | 7388.44 | 6223.89 | 13612.33
17:30 | 7631.07 | 6471.545 | 14102.615
18:00 | 7873.7 | 6719.2 | 14592.9
18:30 | 7970.25 | 6822.7 | 14792.95
19:00 | 8066.8 | 6926.2 | 14993
19:30 | 8184 | 6973.2 | 15157.2
20:00 | 8233.1 | 6957.2 | 15190.3
20:30 | 8198.3 | 6999.89 | 15198.19 |  | Executive Engineer
21:00 | 8163.5 | 7042.58 | 15206.08 |  | Network Operation Division
21:30 | 8022.9 | 7051.725 | 15074.625
22:00 | 7882.3 | 7060.87 | 14943.17
22:30 | 7765.15 | 7050.13 | 14815.28
23:00 | 7648 | 7039.39 | 14687.39

## En-Curve
QF-LDC-12
Date | 28-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3473 | 1558 | 903 | 38 | 82 | 1474.45 | 220 | 4690 | 0 | 542 | 1666.5 | 0 | 0 | 0 | 59 | DAILY ENERGY CURVE
00:30 | 3432.5 | 1561.25 | 903 | 38 | 82 | 1475.07 | 220 | 4699 | 0 | 395.5 | 1541.5 | 0 | 0 | 0 | 55 | 28-10-2025
01:00 | 3392 | 1564.5 | 903 | 38 | 82 | 1475.69 | 220 | 4708 | 0 | 249 | 1416.5 | 0 | 0 | 0 | 51
01:30 | 3394 | 1560 | 903 | 38 | 82 | 1470.495 | 220 | 4677 | 0 | 230 | 1260.5 | 0 | 0 | 0 | 49.5 | Energy Generated | 332.5987 |  | MKWHr
02:00 | 3396 | 1555.5 | 903 | 38 | 82 | 1465.3 | 220 | 4646 | 0 | 211 | 1104.5 | 0 | 0 | 0 | 48 | Energy not Served | 3.435 |  | MKWHr
02:30 | 3412.5 | 1565.5 | 903 | 38 | 79 | 1421.595 | 220 | 4606.5 | 0 | 192.5 | 1004 | 0 | 0 | 0 | 37.5 | Total Energy Requirement | 336.0337 |  | MKWHr
03:00 | 3429 | 1575.5 | 903 | 38 | 76 | 1377.89 | 220 | 4567 | 0 | 174 | 903.5 | 0 | 0 | 0 | 27
03:30 | 3394 | 1565.5 | 903 | 38 | 76 | 1324.53 | 220 | 4545.5 | 0 | 174 | 755.5 | 0 | 0 | 0 | 24.5
04:00 | 3359 | 1555.5 | 903 | 38 | 76 | 1271.17 | 220 | 4524 | 0 | 174 | 607.5 | 0 | 0 | 0 | 22
04:30 | 3377 | 1530.5 | 903 | 38 | 74 | 1267.555 | 220 | 4460 | 0 | 174.5 | 581 | 0 | 0 | 0 | 11
05:00 | 3395 | 1505.5 | 903 | 38 | 72 | 1263.94 | 220 | 4396 | 0 | 175 | 554.5 | 0 | 0 | 0 | 0
05:30 | 3373 | 1513.5 | 903 | 38 | 71 | 1261.59 | 225 | 4274 | 0 | 150 | 620 | 0 | 0 | 0 | 0
06:00 | 3351 | 1521.5 | 903 | 38 | 70 | 1259.24 | 230 | 4152 | 0 | 125 | 685.5 | 0 | 0 | 0 | 0
06:30 | 3370.5 | 1541.5 | 903 | 38 | 67 | 1243.395 | 230 | 4116 | 36.015 | 120.5 | 703.75 | 0 | 0 | 0.5 | 0
07:00 | 3390 | 1561.5 | 903 | 38 | 64 | 1227.55 | 230 | 4080 | 72.03 | 116 | 722 | 0 | 0 | 1 | 0
07:30 | 3309.5 | 1538.5 | 903 | 38 | 62 | 1197.765 | 230 | 3984 | 173.995 | 132.5 | 750 | 0 | 0 | 0.5 | 22
08:00 | 3229 | 1515.5 | 903 | 38 | 60 | 1167.98 | 230 | 3888 | 275.96 | 149 | 778 | 0 | 0 | 0 | 44
08:30 | 3284.5 | 1530.25 | 903 | 38 | 53 | 1137.93 | 230 | 3894 | 365.83 | 153 | 826.5 | 0 | 0 | 0 | 48.5
09:00 | 3340 | 1545 | 903 | 38 | 46 | 1107.88 | 230 | 3900 | 455.7 | 157 | 875 | 0 | 0 | 0 | 53
09:30 | 3350 | 1520 | 903 | 38 | 45 | 1081.215 | 230 | 4002 | 518.33 | 165.5 | 900 | 0 | 0 | 0 | 26.5
10:00 | 3360 | 1495 | 903 | 38 | 44 | 1054.55 | 230 | 4104 | 580.96 | 174 | 925 | 0 | 0 | 0 | 0
10:30 | 3364.5 | 1506.5 | 903.5 | 38 | 43 | 1029.245 | 230 | 4176 | 592.565 | 174 | 1027 | 0 | 0 | 0 | 23.5
11:00 | 3369 | 1518 | 904 | 38 | 42 | 1003.94 | 230 | 4248 | 604.17 | 174 | 1129 | 0 | 0 | 0 | 47
11:30 | 3395 | 1520.5 | 903.5 | 38 | 44 | 1007.56 | 230 | 4305 | 597.245 | 184 | 1207 | 0 | 0 | 0 | 124.5
12:00 | 3421 | 1523 | 903 | 38 | 46 | 1011.18 | 230 | 4362 | 590.32 | 194 | 1285 | 0 | 0 | 0 | 202
12:30 | 3414.5 | 1526.5 | 903 | 38 | 64 | 1010.175 | 230 | 4441.5 | 598.575 | 197.5 | 1359.5 | 0 | 0 | 0 | 212
13:00 | 3408 | 1530 | 903 | 38 | 82 | 1009.17 | 230 | 4521 | 606.83 | 201 | 1434 | 0 | 0 | 0 | 222
13:30 | 3397 | 1529 | 903 | 38 | 77 | 1007.905 | 226 | 4554.5 | 515.835 | 192.5 | 1495.5 | 0 | 0 | 1.5 | 236.5
14:00 | 3386 | 1528 | 903 | 38 | 72 | 1006.64 | 222 | 4588 | 424.84 | 184 | 1557 | 0 | 0 | 3 | 251
14:30 | 3365 | 1524.5 | 903 | 38 | 74 | 1007.32 | 222 | 4605 | 373.68 | 183.5 | 1612.1 | 0 | 0 | 2 | 276.5
15:00 | 3344 | 1521 | 903 | 38 | 76 | 1008 | 222 | 4622 | 322.52 | 183 | 1667.2 | 0 | 0 | 1 | 302
15:30 | 3336.5 | 1493 | 903.5 | 38 | 79 | 1008 | 222 | 4620.5 | 218.95 | 191 | 1670.2 | 0 | 0 | 0.5 | 284
16:00 | 3329 | 1465 | 904 | 38 | 82 | 1008 | 222 | 4619 | 115.38 | 199 | 1673.2 | 0 | 0 | 0 | 266
16:30 | 3335.5 | 1470.75 | 903.5 | 38 | 77 | 1004.5 | 221.5 | 4572.5 | 68.055 | 250.5 | 1691.65 | 0 | 0 | 0 | 257.5
17:00 | 3342 | 1476.5 | 903 | 38 | 72 | 1001 | 221 | 4526 | 20.73 | 302 | 1710.1 | 0 | 0 | 0 | 249
17:30 | 3356.5 | 1498.5 | 903 | 38 | 76 | 1002 | 220.5 | 4623.5 | 10.365 | 503.5 | 1870.75 | 0 | 0 | 0 | 415.5
18:00 | 3371 | 1520.5 | 903 | 38 | 80 | 1003 | 220 | 4721 | 0 | 705 | 2031.4 | 0 | 0 | 0 | 582
18:30 | 3371.5 | 1552.25 | 903 | 38 | 82 | 1002 | 219 | 4769 | 0 | 760.5 | 2095.7 | 0 | 0 | 0 | 509.5
19:00 | 3372 | 1584 | 903 | 38 | 84 | 1001 | 218 | 4817 | 0 | 816 | 2160 | 0 | 0 | 0 | 437
19:30 | 3387 | 1592 | 904 | 38 | 88 | 994 | 218 | 4834 | 0 | 826 | 2276.2 | 0 | 0 | 0 | 376
20:00 | 3393 | 1594 | 904 | 38 | 84 | 997 | 220 | 4841 | 0 | 853 | 2266.3 | 0 | 0 | 0 | 202
20:30 | 3469.5 | 1566 | 904 | 38 | 81 | 996.19 | 220.5 | 4842.5 | 0 | 846.5 | 2234 | 0 | 0 | 0 | 156
21:00 | 3546 | 1538 | 904 | 38 | 78 | 995.38 | 221 | 4844 | 0 | 840 | 2201.7 | 0 | 0 | 0 | 110
21:30 | 3466 | 1535.25 | 903.5 | 38 | 81 | 1005.525 | 221 | 4867.5 | 0 | 791 | 2165.85 | 0 | 0 | 0 | 116.5
22:00 | 3386 | 1532.5 | 903 | 38 | 84 | 1015.67 | 221 | 4891 | 0 | 742 | 2130 | 0 | 0 | 0 | 123
22:30 | 3362.5 | 1545 | 902.5 | 38 | 85 | 1017.83 | 221 | 4881.1 | 0 | 686.5 | 2075.85 | 0 | 0 | 0 | 130.5
23:00 | 3339 | 1557.5 | 902 | 38 | 86 | 1019.99 | 221 | 4871.2 | 0 | 631 | 2021.7 | 0 | 0 | 0 | 138
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 08:00 | 368 | 18:30 | Payra | 411 | 09:00 | 404 | 23:00
Ashuganj | 402 | 06:00 | 396 | 11:00 | Rahanpur | 406 | 15:00 | 395 | 01:00
Bhulta | 403 | 06:00 | 372 | 11:00 | Rampal | 404 | 06:00 | 390 | 00:00
Bibiana | 388 | 06:00 | 380 | 09:00
BIPTC | 403 | 06:00 | 395 | 11:00
Bogura | 393 | 15:00 | 381 | 01:00
Gopalganj | 395 | 06:00 | 381 | 19:00
Kaliakoir | 375 | 06:00 | 359 | 16:00
Madunaghat | 395 | 18:00 | 388 | 10:00
Meghnaghat | 383 | 06:00 | 374 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 06:00 | 218 | 11:00 | Kaliakoir | 234 | 06:00 | 223 | 11:00
AKSML | 232 | 18:00 | 224 | 10:00 | Keranigonj | 225 | 06:00 | 215 | 11:00
Aminbazar | 229 | 09:00 | 218 | 11:00 | Khulna(S) | 232 | 09:00 | 221 | 18:30
Ashuganj | 230 | 06:00 | 217 | 11:00 | Madunaghat | 233 | 18:00 | 227 | 10:00
Ashuganj-400 | 230 | 06:00 | 217 | 11:00 | Madunaghat-400 | 234 | 19:00 | 228 | 10:00
Baghabari | 234 | 05:00 | 225 | 12:00 | Maniknagar | 218 | 05:00 | 210 | 11:00
Barapukuria | 223 | 19:30 | 202 | 11:00 | Meghnaghat | 225 | 03:00 | 219 | 13:00
Barapukuria-230 | 223 | 19:30 | 202 | 11:00 | Meghnaghat-400 | 222 | 06:00 | 215 | 11:00
Barishal | 233 | 07:00 | 224 | 00:00 | Mirsorai | 232 | 18:30 | 219 | 10:00
Bheramara | 235 | 04:00 | 224 | 12:00 | Rajshahi | 234 | 04:00 | 222 | 12:00
Bhulta | 230 | 06:00 | 211 | 10:00 | Rampal | 231 | 06:00 | 220 | 18:30
Bibiana | 228 | 04:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 04:00 | 225 | 12:00 | Rampura | 228 | 06:00 | 208 | 11:00
Bogura | 239 | 15:00 | 231 | 01:00 | Shikalbaha | 232 | 18:00 | 224 | 10:00
Bogura-400 | 239 | 15:00 | 232 | 01:00 | Shyampur | 223 | 06:00 | 214 | 11:00
Borhanuddin | 237 | 08:00 | 230 | 00:00 | Siddhirganj | 218 | 05:00 | 212 | 10:00
BSRM | 230 | 18:30 | 219 | 10:00 | Sirajgonj | 239 | 06:00 | 233 | 11:00
Cumilla(N) | 224 | 06:00 | 216 | 10:00 | Sreepur | 225 | 06:00 | 217 | 11:00
Faridpur | 231 | 06:00 | 221 | 00:00 | Tongi | 228 | 07:00 | 219 | 09:00
Fenchuganj | 229 | 06:00 | 224 | 17:00
Ghorashal | 230 | 05:00 | 220 | 08:00
Ghorashal-230 | 228 | 06:00 | 213 | 11:00
Gopalganj | 232 | 06:00 | 224 | 00:00
GPH | 228 | 20:00 | 222 | 10:00
Haripur | 219 | 06:00 | 212 | 11:00
Hasnabad | 223 | 04:00 | 214 | 12:00
Hathazari | 231 | 18:00 | 223 | 00:00
Ishurdi | 237 | 04:00 | 227 | 12:00
Jhenaidah | 232 | 06:00 | 220 | 19:30
Kachua | 226 | 18:00 | 220 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 06:00 | 125 | 11:00 | Lalmonirhat | 131 | 05:00 | 120 | 12:00
Agargaon | 133 | 06:00 | 126 | 11:00 | Madanganj | 130 | 05:00 | 126 | 10:00
Agrabad | 131 | 18:00 | 127 | 10:00 | Madaripur | 135 | 06:00 | 129 | 00:00
AKS | 131 | 18:00 | 126 | 07:00 | Madartek | 138 | 05:00 | 124 | 11:00
Aminbazar | 134 | 06:00 | 128 | 10:00 | Madunaghat | 135 | 18:00 | 131 | 10:00
Amnura | 136 | 05:00 | 127 | 12:00 | Magura | 136 | 06:00 | 125 | 19:30
Ashuganj | 138 | 06:00 | 133 | 00:00 | Mahasthangarh | 132 | 05:00 | 125 | 12:00
Bagerhat | 129 | 08:00 | 117 | 18:30 | Maijdee | 131 | 17:00 | 125 | 00:00
Bajitpur | 127 | 08:00 | 123 | 11:00 | Manikganj | 133 | 06:00 | 124 | 11:00
Bakulia | 133 | 19:00 | 128 | 10:00 | Maniknagar | 131 | 05:00 | 125 | 10:00
Banani | 140 | 06:00 | 125 | 11:00 | Matarbari | 116 | 16:00 | 108 | 21:00
Bangabhaban | 132 | 06:00 | 125 | 11:00 | Matuail | 127 | 06:00 | 123 | 10:00
Barapukuria | 136 | 19:00 | 122 | 11:00 | Metrorail_Motijheel | 131 | 05:00 | 125 | 10:00
Barguna | 135 | 08:00 | 131 | 20:00 | Metrorail_Uttara | 136 | 05:00 | 129 | 11:00
Barishal | 134 | 07:00 | 127 | 00:00 | Millgate | 137 | 06:00 | 128 | 11:00
Barishal-230 | 133 | 06:00 | 126 | 00:00 | Mirpur | 133 | 05:00 | 126 | 10:00
Baroaulia | 133 | 18:00 | 128 | 10:00 | Mirzapur | 131 | 06:00 | 124 | 13:00
Baroirhat | 132 | 18:00 | 127 | 00:00 | Mithapukur | 133 | 00:00 | 123 | 11:00
Bashundhara | 140 | 06:00 | 127 | 11:00 | MI_Cement | 126 | 05:00 | 122 | 10:00
BashundharaCement | 130 | 05:00 | 126 | 10:00 | Modern | 0 | 00:00 | 0 | 00:00
Beanibazar | 128 | 08:00 | 124 | 00:00 | Mogbazar | 142 | 06:00 | 125 | 11:00
Benapole | 133 | 06:00 | 120 | 13:00 | Mongla | 128 | 08:00 | 118 | 17:00
Bhaluka | 128 | 18:00 | 120 | 11:00 | Motijheel | 132 | 06:00 | 125 | 10:00
Bhandaria | 130 | 09:00 | 119 | 00:00 | Muktagacha | 134 | 06:00 | 120 | 12:00
Bhangura | 134 | 05:00 | 129 | 11:00 | Munshiganj | 125 | 03:00 | 122 | 10:00
Bheramara | 138 | 03:00 | 134 | 11:00 | Muradnagar | 126 | 06:00 | 120 | 10:00
Bheramara(GK) | 139 | 05:00 | 134 | 12:00 | Mymensingh | 134 | 06:00 | 11 | 14:00
Bhulta | 123 | 01:00 | 120 | 11:00 | Naogaon | 132 | 18:00 | 123 | 12:00
Bog-Sherpur | 134 | 06:00 | 127 | 12:00 | Narail | 136 | 05:00 | 126 | 18:30
Bogura | 135 | 06:00 | 128 | 12:00 | Narinda | 131 | 05:00 | 125 | 10:00
Bogura-230 | 135 | 15:00 | 129 | 11:00 | Narshingdi | 130 | 06:00 | 117 | 00:00
Brahmanbaria | 131 | 06:00 | 8 | 07:00 | Natore | 135 | 06:00 | 129 | 12:00
Cantonment | 133 | 06:00 | 125 | 12:00 | Nawabganj | 133 | 06:00 | 125 | 16:00
Chandina | 129 | 06:00 | 125 | 11:00 | Netrakona | 120 | 19:00 | 114 | 13:00
Chandpur | 136 | 19:30 | 129 | 08:00 | New | 137 | 04:00 | 129 | 11:00
Chandraghona | 135 | 18:00 | 132 | 02:00 | Niamatpur | 138 | 15:00 | 135 | 00:00
Chapai | 136 | 05:00 | 134 | 00:00 | Noapara | 133 | 05:00 | 123 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 126 | 06:00 | 123 | 10:00 | Pabna | 136 | 04:00 | 130 | 12:00
Chauddagram | 130 | 17:00 | 126 | 00:00 | Palashbari | 131 | 16:00 | 121 | 12:00
Chhatak | 127 | 06:00 | 120 | 19:00 | Panchagarh | 138 | 19:00 | 124 | 11:00
Chowmuhani | 130 | 17:00 | 126 | 00:00 | Patiya | 131 | 18:00 | 127 | 01:00
Chuadanga | 135 | 06:00 | 123 | 19:30 | Patuakhali | 136 | 09:00 | 132 | 15:00
Coxsbazar | 117 | 15:00 | 108 | 19:30 | Payra | 136 | 05:00 | 134 | 00:00
Cumilla(N) | 130 | 06:00 | 125 | 11:00 | PHP | 132 | 18:00 | 126 | 04:00
Cumilla(S) | 130 | 03:00 | 125 | 10:00 | Postogola | 132 | 06:00 | 126 | 11:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 140 | 06:00 | 125 | 11:00
Daudkandi | 122 | 06:00 | 117 | 00:00 | Purbasadipur | 134 | 18:30 | 121 | 11:00
DhakaUniversity | 138 | 05:00 | 125 | 11:00 | Rahanpur | 139 | 15:00 | 136 | 00:00
Dhamrai | 133 | 05:00 | 126 | 11:00 | Rahanpur-400 | 139 | 05:00 | 136 | 01:00
Dhanmondi | 140 | 06:00 | 126 | 11:00 | Rahim | 126 | 04:00 | 123 | 10:00
Dohazari | 128 | 19:00 | 122 | 05:00 | Rajbari | 135 | 08:00 | 128 | 00:00
Faridpur | 136 | 06:00 | 130 | 00:00 | Rajendrapur | 134 | 18:00 | 121 | 11:00
Fatullah | 136 | 06:00 | 125 | 11:00 | Rajshahi | 134 | 03:00 | 128 | 12:00
Fenchuganj | 135 | 06:00 | 131 | 21:00 | Rajshahi-230 | 134 | 04:00 | 128 | 12:00
Feni | 130 | 15:00 | 125 | 00:00 | Ramganj | 131 | 19:30 | 126 | 05:00
Ghatail | 130 | 06:00 | 119 | 14:00 | Rampur | 132 | 18:00 | 127 | 10:00
Ghorashal | 138 | 06:00 | 130 | 11:00 | Rampura | 140 | 06:00 | 126 | 11:00
Goalpara | 133 | 06:00 | 125 | 00:00 | Rangamati | 135 | 18:30 | 130 | 10:00
Gollamari | 133 | 06:00 | 125 | 18:30 | Rangpur | 134 | 15:00 | 123 | 11:00
Gopalganj | 133 | 06:00 | 127 | 00:00 | Ruppur | 138 | 04:00 | 134 | 11:00
Gopalganj-400 | 138 | 07:00 | 131 | 00:00 | Saidpur | 133 | 14:00 | 120 | 11:00
Gulshan | 139 | 06:00 | 125 | 11:00 | Satkhira | 130 | 06:00 | 118 | 22:00
Halishahar | 132 | 18:00 | 30 | 06:00 | Satmasjid | 133 | 06:00 | 126 | 11:00
Haripur | 127 | 06:00 | 123 | 12:00 | Savar | 132 | 05:00 | 126 | 10:00
HaripurSBU | 127 | 06:00 | 123 | 11:00 | SevenRings | 137 | 06:00 | 129 | 11:00
Hasnabad | 133 | 04:00 | 126 | 11:00 | ShahCement | 126 | 06:00 | 123 | 10:00
Hathazari | 135 | 18:00 | 128 | 20:00 | Shahjadpur | 136 | 05:00 | 133 | 11:00
Ishurdi | 139 | 03:00 | 134 | 12:00 | Shahjibazar | 132 | 01:00 | 126 | 00:00
Jaldhaka | 131 | 15:00 | 118 | 11:00 | Shahmirpur | 133 | 18:00 | 128 | 10:00
Jamalpur | 130 | 06:00 | 116 | 13:00 | Shariatpur | 134 | 06:00 | 127 | 00:00
Jashore | 134 | 06:00 | 120 | 13:00 | Sherpur | 125 | 06:00 | 111 | 13:00
Jhenaidah | 137 | 06:00 | 126 | 18:00 | Shikalbaha | 124 | 18:00 | 118 | 10:00
Jhenaidah-230 | 137 | 06:00 | 128 | 19:30 | Shikalbaha-230 | 135 | 18:00 | 130 | 07:00
Joydebpur | 134 | 07:00 | 126 | 11:00 | Shitalakhya | 132 | 06:00 | 122 | 10:00
Joypurhat | 130 | 06:00 | 121 | 12:00 | Sholosohor | 134 | 18:00 | 130 | 10:00
Juldah | 132 | 17:00 | 128 | 10:00 | Shyampur | 134 | 06:00 | 128 | 11:00
Kabirpur | 135 | 06:00 | 126 | 09:00 | Shyampur-230 | 136 | 06:00 | 130 | 10:00
Kachua | 134 | 18:00 | 129 | 09:00 | Siddhirganj | 127 | 05:00 | 123 | 11:00
Kaliakoir | 135 | 06:00 | 129 | 07:00 | Sirajganj | 132 | 06:00 | 126 | 12:00
Kallyanpur | 133 | 04:00 | 128 | 10:00 | Sonargaon | 125 | 04:00 | 121 | 10:00
Kalurghat | 135 | 18:00 | 131 | 09:00 | Sreemongol | 132 | 06:00 | 126 | 19:30
Kamrangirchar | 133 | 06:00 | 125 | 11:00 | Sreepur | 130 | 06:00 | 124 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 133 | 05:00 | 126 | 11:00
Kasba | 126 | 06:00 | 120 | 10:00 | SSM | 135 | 18:00 | 132 | 01:00
Kazla | 130 | 04:00 | 124 | 11:00 | Sunamganj | 126 | 15:00 | 118 | 19:00
Keranigonj | 133 | 06:00 | 127 | 10:00 | Sylhet | 129 | 06:00 | 125 | 19:00
Khagrachori | 133 | 19:00 | 129 | 12:00 | Sylhet-132 | 129 | 06:00 | 126 | 19:30
Khulna | 132 | 06:00 | 123 | 19:30 | Tangail | 127 | 03:00 | 119 | 13:00
Khulna(S) | 133 | 06:00 | 125 | 19:00 | Taraganj | 133 | 00:00 | 122 | 12:00
Khulshi | 131 | 18:00 | 126 | 10:00 | Thakurgaon | 137 | 19:00 | 120 | 11:00
Kishoreganj | 127 | 06:00 | 121 | 11:00 | TK | 135 | 18:00 | 130 | 13:00
Kodda | 135 | 06:00 | 124 | 09:00 | Tongi | 136 | 04:00 | 132 | 11:00
KSRM | 134 | 18:00 | 128 | 10:00 | Ullahpara | 134 | 04:00 | 128 | 11:00
Kulaura | 134 | 07:00 | 130 | 19:00 | Ullon | 138 | 04:00 | 125 | 11:00
Kurigram | 131 | 15:00 | 120 | 11:00 | Uttara | 132 | 05:00 | 125 | 11:00
Kushtia | 136 | 06:00 | 130 | 12:00 | UttaraNew | 136 | 05:00 | 129 | 11:00
Laksam | 133 | 18:30 | 121 | 05:00 | Zigatola | 133 | 06:00 | 126 | 11:00
Lakshmipur | 131 | 17:00 | 126 | 00:00
Lalbag | 131 | 04:00 | 125 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division