## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-10-2025 | during | 30-10-2025 | during | 30-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 90 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 301 | 304 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 45.6 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35.01 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20 | 24 | 24 | 24 | 24 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 15 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 260 | 293 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 118 | 133 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 126 | 162 | 162 | 108 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 0 | 0 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 310 | 310 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1964 | 2445.6 | 5795.4 | 5795.4 | 4726.24 | 4833.25
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 219 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 221 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 36 | 0 | 0 | 70 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 17 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 89 | 104 | 0 | 0 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.2 | 0 | 3.24 | 0 | 3.24 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 41 | 110 | 110 | 100 | 100 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 91 | 86 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 15 | 159.86 | 159.86 | 17 | 159 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1177 | 1224 | 1224 | 1224 | 1224 | DCT
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 2558.2 | 2733.5 | 3492.96 | 3489.72 | 2889.74 | 3028.5
| Ashuganj TPP Unit- 3, 4 | Gas | APSCL | 1*150+1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 92 | 220 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 400 | 285 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 27 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 46 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 0 | 0 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 110 | 135 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 20 | 21 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 104 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 217 | 172 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 82 | 160 | 160 | 88 | 88 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 8 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 8 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 106 | 14 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 83 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1677 | 1547 | 2556.86 | 2491.86 | 2282.86 | 2226.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-10-2025 | during | 30-10-2025 | during | 30-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 67 | 38 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 46 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 49 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.37 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 224.37 | 150 | 377.1 | 330 | 323.6 | 276.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 0 | 0 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 146 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 78 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 10 | 0 | 0 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 312 | 325 | 325 | 325 | 325 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1121 | 1103 | 1072 | 1072 | 1152 | 1152
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 930 | 929 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 67 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 352 | 270 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 26.38 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 858 | 1112 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2204.38 | 2456 | 2389 | 2314 | 1634 | 1559
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 304 | 400 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 57 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 10 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 160 | 160 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1844.55 | 2077 | 2147 | 2146 | 2006 | 2005
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 24.5 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 173 | 168 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 336 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 1 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.47 | 0 | 5.52 | 0 | 5.52 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1141 | 1204 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.17 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1929.14 | 1983 | 2484.51 | 2317.99 | 1934.51 | 1767.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 60 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.1 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 14 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 95 | 0 | 138.82 | 0 | 138.82 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 171.1 | 183 | 422.62 | 248 | 382.62 | 208
System Total |  |  |  |  | 28823.2 | 28364.095 | 13693.74 | 14678.1 | 20737.45 | 20204.97 | 17331.57 | 17057.1
Forecast Scenario (30-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13400 |  | 0 |  | 13400
|  |  |  | 1:00 | 12850 |  | 0 |  | 12850
|  |  |  | 2:00 | 12480 |  | 0 |  | 12480
|  |  |  | 3:00 | 12160 |  | 0 |  | 12160
|  |  |  | 4:00 | 11670 |  | 0 |  | 11670
|  |  |  | 5:00 | 11500 |  | 0 |  | 11500
|  |  |  | 6:00 | 11380 |  | 0 |  | 11380
|  |  |  | 7:00 | 11500 |  | 0 |  | 11500
|  |  |  | 8:00 | 11430 |  | 0 |  | 11430
|  |  |  | 9:00 | 11870 |  | 0 |  | 11870
|  |  |  | 10:00 | 12180 |  | 0 |  | 12180
|  |  |  | 11:00 | 12640 |  | 0 |  | 12640
|  |  |  | 12:00 | 13200 |  | 0 |  | 13200
|  |  |  | 13:00 | 13550 |  | 0 |  | 13550
|  |  |  | 14:00 | 13500 |  | 0 |  | 13500
|  |  |  | 15:00 | 13520 |  | 0 |  | 13520
|  |  |  | 16:00 | 13190 |  | 0 |  | 13190
|  |  |  | 17:00 | 13100 |  | 0 |  | 13100
|  |  |  | 18:00 | 14400 |  | 0 |  | 14400
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 14620 |  | 0 |  | 14620
|  |  |  | 19:30 | 14680 |  | 0 |  | 14680
|  |  |  | 20:00 | 14530 |  | 0 |  | 14530
|  |  |  | 21:00 | 14450 |  | 0 |  | 14450
|  |  |  | 22:00 | 14200 |  | 0 |  | 14200
|  |  |  | 23:00 | 13960 |  | 0 |  | 13960
Probable Maximum Temperature: |  |  | 30.90°C
Probable Maximum Demand at Day Peak: |  |  | 13200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14680.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14680.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 311.28 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:31 hrs on 30-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-10-2025 | [28 empty] | Date: | 29-10-2025 | [28 empty] | Date: | 29-10-2025 | [28 empty] | Date: | 29-10-2025 | [28 empty] | Date: | 29-10-2025 | [14 empty] | Date: | 29-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 21.5 | 17 | 133 | 45 | 293 | 55 | 0 | 54 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 310 | 96 | 16 | 105 | 0 | 0 | 50 | 60 | 17 | 12 | 12 | 0 | 221 | 0 | 34 | 650 | 17 | 0 | 0 | 25.5 | 0 | 226 | 0 | 0 | 0 | 1166 | 0 | 51 | 137 | 0 | 397 | 300 | 11 | 44 | 0 | 37 | 34 | 103 | 188 | 0 | 19 | 112 | 84 | 43 | 0 | 36 | 325 | 0 | 312 | 0 | 68 | 156 | 9 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 88 | 0 | 0 | 0 | 7641 | 903 | 375 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 1028.05 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 95 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 170 | 110 | 220 | 0 | 503 | 1118 | 10 | 6811.25 | 14452.25 | 103.95
01:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17.5 | 17 | 133 | 45 | 293 | 55 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 310 | 91 | 16 | 104 | 0 | 0 | 39 | 60 | 0 | 12 | 12 | 0 | 221 | 0 | 34 | 650 | 17 | 0 | 0 | 25.5 | 0 | 226 | 0 | 0 | 0 | 1155 | 0 | 51 | 140 | 0 | 397 | 300 | 18 | 46 | 0 | 37 | 35 | 103 | 199 | 0 | 19 | 34 | 76 | 25 | 0 | 36 | 315 | 0 | 312 | 0 | 67 | 149 | 7 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 89 | 0 | 0 | 0 | 7378 | 903 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1000.05 | 0 | 40 | 0 | 35 | 113 | 0 | 0 | 30 | 25 | 0 | 0 | 25 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 170 | 110 | 220 | 0 | 468 | 1097 | 10 | 6690.25 | 14068.25 | 103.94
02:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17.5 | 17 | 133 | 30 | 293 | 30 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 310 | 85 | 16 | 104 | 0 | 0 | 50 | 60 | 0 | 12 | 12 | 0 | 221 | 0 | 34 | 650 | 17 | 0 | 0 | 25.5 | 0 | 226 | 0 | 0 | 0 | 1160 | 0 | 51 | 138 | 0 | 397 | 300 | 18 | 45 | 0 | 37 | 64 | 103 | 200 | 0 | 19 | 0 | 72 | 0 | 0 | 36 | 305 | 0 | 312 | 0 | 67 | 142 | 7 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 89 | 0 | 0 | 0 | 7295 | 903 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 0 | 1003.63 | 0 | 40 | 0 | 0 | 113 | 0 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 170 | 110 | 220 | 0 | 301 | 1093 | 10 | 6411.63 | 13706.63 | 103.93
03:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17.5 | 17 | 105 | 30 | 175 | 15 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 310 | 15 | 16 | 73 | 0 | 0 | 50 | 60 | 0 | 12 | 12 | 0 | 220 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 51 | 80 | 0 | 397 | 300 | 29 | 46 | 0 | 37 | 69 | 104 | 200 | 0 | 19 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 312 | 0 | 67 | 145 | 7 | 0 | 78 | 30 | 0 | 0 | 161 | 17 | 49 | 48 | 89 | 0 | 0 | 0 | 6915.5 | 903 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1232 | 0 | 1023.56 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 301 | 1095 | 10 | 6219.56 | 13135.06 | 103.92
04:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17.5 | 17 | 82 | 30 | 95 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 0 | 12 | 12 | 0 | 220 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1162 | 0 | 9 | 80 | 0 | 371 | 300 | 47 | 47 | 0 | 34 | 70 | 104 | 155 | 0 | 19 | 0 | 72 | 0 | 0 | 0 | 315 | 0 | 312 | 0 | 67 | 154 | 7 | 0 | 78 | 30 | 0 | 0 | 161 | 17 | 49 | 48 | 106 | 0 | 0 | 0 | 6629.5 | 903 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1019.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 304 | 1100 | 0 | 6075.07 | 12704.57 | 103.91
05:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17.5 | 17 | 72 | 30 | 95 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 50 | 51 | 0 | 12 | 12 | 0 | 219 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1161 | 0 | 51 | 80 | 0 | 365 | 300 | 62 | 47 | 0 | 34 | 45 | 104 | 144 | 0 | 19 | 0 | 50 | 0 | 0 | 0 | 315 | 0 | 312 | 0 | 67 | 144 | 7 | 0 | 78 | 30 | 0 | 0 | 161 | 0 | 49 | 48 | 106 | 0 | 0 | 1 | 6584.5 | 903 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1231 | 0 | 1003.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 303 | 1100 | 0 | 6001.97 | 12586.47 | 103.9
06:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17.5 | 17 | 51 | 30 | 45 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 12 | 12 | 0 | 219 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1166 | 0 | 51 | 80 | 0 | 355 | 300 | 62 | 47 | 0 | 34 | 0 | 104 | 139 | 0 | 19 | 0 | 50 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 144 | 7 | 0 | 78 | 30 | 0 | 0 | 161 | 0 | 49 | 48 | 106 | 0 | 0 | 6 | 6418.5 | 904 | 376 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 0 | 1004.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 302 | 1050 | 0 | 5876.04 | 12294.54 | 103.89
07:00 | 0 | 52 | 10 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 40 | 30 | 45 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 5 | 17 | 21 | 22 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 12 | 12 | 0.49 | 219 | 0 | 27 | 650 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1169 | 0 | 44 | 80 | 0 | 340 | 300 | 80 | 47 | 0 | 34 | 0 | 103 | 180 | 0 | 19 | 0 | 42 | 0 | 13 | 0 | 320 | 0 | 312 | 0 | 67 | 155 | 6 | 0 | 78 | 30 | 0 | 0 | 161 | 0 | 48 | 48 | 96 | 0 | 6.15 | 3 | 6480.64 | 903 | 376 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1064 | 0 | 1004.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 14 | 0 | 0 | 4.65 | 169 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0.46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.5 | 2 | 0.06 | 0 | 170 | 110 | 220 | 0 | 304 | 1045 | 0 | 5839.82 | 12320.46 | 103.88
08:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 0 | 45 | 45 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 11 | 35 | 20 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 12 | 12 | 1.37 | 219 | 0 | 10 | 650 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1155 | 0 | 44 | 80 | 0 | 320 | 300 | 95 | 47 | 0 | 28 | 0 | 103 | 217 | 0 | 19 | 0 | 64 | 0 | 35 | 0 | 315 | 0 | 312 | 0 | 67 | 150 | 6 | 0 | 78 | 30 | 0 | 0 | 161 | 0 | 49 | 48 | 96 | 1 | 13.97 | 6 | 6489.34 | 903 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35 | 1009 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.61 | 28 | 0 | 0 | 19.09 | 166 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 1.56 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.8 | 19 | 0.23 | 0 | 170 | 110 | 220 | 0 | 303 | 1036 | 0 | 5827.29 | 12316.63 | 103.87
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 0 | 45 | 135 | 4 | 17 | 35 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 23 | 35 | 20 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 12 | 12 | 2.26 | 219 | 0 | 3 | 650 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1145 | 15 | 51 | 85 | 0 | 340 | 300 | 69 | 44 | 0 | 28 | 0 | 102 | 217 | 0 | 19 | 0 | 60 | 0 | 51 | 0 | 310 | 0 | 312 | 0 | 67 | 144 | 6 | 0 | 78 | 30 | 0 | 0 | 162 | 0 | 49 | 48 | 73 | 1 | 25.11 | 6 | 6624.37 | 903 | 371 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 991 | 0 | 1051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3 | 56 | 0 | 0 | 30.82 | 163 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 3.46 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.8 | 45 | 0.48 | 0 | 170 | 110 | 180 | 0 | 303 | 1028 | 0 | 5879.86 | 12504.23 | 103.86
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 17 | 0 | 45 | 260 | 55 | 17 | 72 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 23 | 52 | 20 | 22 | 0 | 330 | 0 | 0 | 38 | 0 | 0 | 0 | 43 | 0 | 12 | 12 | 2.78 | 219 | 14 | 3 | 650 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1050 | 18 | 51 | 113 | 0 | 330 | 337 | 69 | 43 | 0 | 28 | 0 | 99 | 217 | 0 | 19 | 0 | 66 | 0 | 54 | 3 | 315 | 0 | 312 | 0 | 67 | 147 | 6 | 0 | 78 | 30 | 0 | 0 | 162 | 0 | 49 | 48 | 73 | 1 | 36.01 | 6 | 6900.79 | 903 | 339 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 73.9 | 883 | 0 | 1084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.25 | 47 | 0 | 0 | 25.55 | 163 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 1.96 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 3.7 | 77 | 0.59 | 0 | 160 | 110 | 220 | 0 | 302 | 950 | 0 | 5812.95 | 12713.74 | 103.85
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 17 | 17 | 10 | 45 | 260 | 55 | 35 | 72 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 11 | 52 | 0 | 22 | 0 | 310 | 42 | 0 | 89 | 0 | 0 | 0 | 38 | 0 | 12 | 12 | 3.13 | 222 | 17 | 2 | 650 | 17 | 0 | 0 | 4 | 0 | 218 | 0 | 0 | 0 | 1160 | 17 | 51 | 113 | 0 | 390 | 345 | 73 | 42 | 0 | 31 | 0 | 99 | 216 | 0 | 19 | 60 | 68 | 8 | 50 | 20 | 320 | 0 | 312 | 0 | 67 | 156 | 6 | 0 | 78 | 30 | 0 | 0 | 162 | 14 | 49 | 48 | 66 | 1 | 43.03 | 6 | 7280.16 | 929 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 855 | 0 | 1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.14 | 110 | 0 | 0 | 23.52 | 167 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 2.38 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 3.9 | 159 | 0.62 | 0 | 160 | 110 | 220 | 0 | 303 | 982 | 0 | 5981.56 | 13261.72 | 103.84
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 17 | 17 | 118 | 45 | 260 | 55 | 35 | 72 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 13 | 52 | 20 | 22 | 0 | 310 | 91 | 0 | 89 | 0 | 3 | 0 | 38 | 0 | 12 | 12 | 3.2 | 221 | 17 | 3 | 650 | 17 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 1160 | 17 | 51 | 110 | 0 | 400 | 335 | 92 | 42 | 0 | 27 | 0 | 100 | 217 | 0 | 19 | 106 | 70 | 16 | 72 | 20 | 315 | 0 | 312 | 0 | 67 | 152 | 6 | 0 | 77 | 30 | 0 | 0 | 162 | 17 | 49 | 48 | 67 | 1 | 36.37 | 6 | 7544.57 | 930 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26.38 | 858 | 0 | 1141 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 24.5 | 108 | 0 | 0 | 64.17 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.47 | 0 | 0 | 0 | 14 | 60 | 0 | 0 | 0 | 2.1 | 95 | 0.55 | 0 | 160 | 110 | 220 | 0 | 304 | 1050 | 0 | 6149.17 | 13693.74 | 103.82
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 17 | 17 | 133 | 45 | 260 | 55 | 35 | 72 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 12 | 52 | 21 | 15 | 0 | 310 | 91 | 0 | 92 | 0 | 4 | 0 | 29 | 0 | 12 | 12 | 2.97 | 221 | 17 | 8 | 650 | 0 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1130 | 17 | 51 | 113 | 0 | 380 | 341 | 73 | 41 | 0 | 30 | 23 | 99 | 215 | 0 | 19 | 102 | 78 | 34 | 54 | 20 | 310 | 0 | 312 | 0 | 67 | 147 | 6 | 0 | 77 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 65 | 0 | 20.14 | 6 | 7488.11 | 930 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22.83 | 920 | 0 | 1148 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 27.71 | 83 | 0 | 0 | 44.61 | 183 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 4.42 | 0 | 0 | 70 | 10 | 77 | 0 | 0 | 0 | 1.9 | 86 | 0.63 | 0 | 160 | 110 | 220 | 0 | 302 | 1036 | 0 | 6200.1 | 13688.21 | 103.8
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 17 | 17 | 133 | 45 | 260 | 55 | 35 | 72 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 12 | 52 | 21 | 21 | 0 | 330 | 84 | 0 | 89 | 0 | 5 | 0 | 43 | 0 | 12 | 12 | 2.43 | 219 | 17 | 5 | 650 | 0 | 0 | 0 | 8 | 0 | 179 | 0 | 0 | 0 | 1047 | 16 | 51 | 117 | 0 | 350 | 300 | 103 | 41 | 0 | 30 | 67 | 99 | 200 | 0 | 6 | 72 | 80 | 16 | 55 | 20 | 310 | 0 | 312 | 0 | 67 | 142 | 0 | 0 | 77 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 65 | 0 | 8.68 | 6 | 7289.11 | 930 | 338 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22.05 | 932 | 0 | 1227 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 24.12 | 54 | 0 | 0 | 18.32 | 161 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 2 | 0 | 0 | 70 | 4 | 98 | 0 | 0 | 0 | 1.5 | 69 | 0.49 | 0 | 160 | 110 | 220 | 0 | 302 | 950 | 0 | 6140.48 | 13429.59 | 103.78
15:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 17 | 17 | 133 | 45 | 260 | 55 | 35 | 68 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 9 | 52 | 21 | 21 | 0 | 310 | 95 | 0 | 82 | 0 | 4 | 0 | 43 | 0 | 12 | 12 | 1.6 | 221 | 17 | 2 | 650 | 0 | 0 | 0 | 8 | 0 | 224 | 0 | 0 | 0 | 1085 | 11 | 51 | 115 | 0 | 390 | 343 | 125 | 41 | 0 | 30 | 69 | 99 | 182 | 0 | 6 | 64 | 76 | 16 | 8 | 20 | 315 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 77 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 34 | 0 | 0.28 | 6 | 7332.88 | 929 | 330 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 911 | 0 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.28 | 26 | 0 | 0 | 38.56 | 177 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 1.61 | 0 | 0 | 35 | 3 | 40 | 0 | 0 | 0 | 0.8 | 30 | 0.05 | 0 | 160 | 110 | 220 | 0 | 304 | 1020 | 0 | 5914.3 | 13247.18 | 103.76
16:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 35 | 17 | 110 | 15 | 225 | 30 | 35 | 65 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 2 | 35 | 0 | 21 | 0 | 320 | 94 | 0 | 89 | 0 | 5 | 0 | 36 | 0 | 12 | 12 | 0.15 | 221 | 21 | 3 | 650 | 0 | 0 | 0 | 15 | 0 | 220 | 0 | 0 | 0 | 1100 | 6 | 51 | 100 | 0 | 336 | 320 | 150 | 41 | 0 | 30 | 50 | 100 | 120 | 0 | 6 | 15 | 76 | 8 | 0 | 21 | 315 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 77 | 30 | 0 | 0 | 160 | 17 | 49 | 8 | 38 | 0 | 2.79 | 6 | 6975.94 | 930 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 863 | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.99 | 7 | 0 | 0 | 7.63 | 180 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0.62 | 0 | 0 | 35 | 1 | 34 | 0 | 0 | 0 | 0.3 | 16 | 0.06 | 0 | 160 | 110 | 220 | 0 | 303 | 1000 | 0 | 5788.6 | 12764.54 | 103.74
17:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 54 | 17 | 96 | 50 | 225 | 30 | 35 | 71 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 35 | 15 | 21 | 0 | 325 | 92 | 0 | 96 | 0 | 5 | 0 | 36 | 0 | 12 | 12 | 0.03 | 221 | 34 | 10 | 650 | 35 | 0 | 0 | 17 | 0 | 220 | 0 | 0 | 0 | 1095 | 0 | 51 | 100 | 0 | 335 | 320 | 187 | 44 | 0 | 33 | 51 | 103 | 119 | 0 | 8 | 15 | 78 | 8 | 0 | 21 | 320 | 0 | 312 | 0 | 67 | 156 | 8 | 0 | 51 | 30 | 0 | 0 | 160 | 17 | 49 | 45 | 40 | 0 | 0.16 | 6 | 7157.19 | 929 | 304 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 881 | 0 | 1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0.35 | 3 | 0 | 0 | 0.33 | 189 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0.04 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 160 | 110 | 220 | 0 | 303 | 1000 | 0 | 5755.73 | 12912.92 | 103.72
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 51.4 | 30 | 100 | 110 | 270 | 30 | 35 | 126 | 0 | 300 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 125 | 20 | 21 | 0 | 340 | 96 | 16 | 100 | 0 | 0 | 50 | 36 | 35 | 12 | 12 | 0 | 219 | 34 | 14 | 650 | 89 | 0 | 0 | 25.5 | 4 | 221 | 0 | 0 | 0 | 1170 | 0 | 51 | 117 | 0 | 355 | 346 | 250 | 43 | 0 | 38 | 64 | 103 | 125 | 0 | 6 | 64 | 84 | 14 | 0 | 21 | 315 | 0 | 312 | 0 | 67 | 156 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 46 | 38 | 0 | 0 | 0 | 8029.9 | 930 | 305 | 0 | 19 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1047 | 0 | 1218 | 0 | 48 | 0 | 35 | 20 | 0 | 96 | 15 | 26 | 0 | 0 | 22 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 160 | 110 | 220 | 0 | 424 | 1058 | 10 | 6619 | 14648.9 | 103.7
19:00 | 0 | 105 | 25 | 0 | 0 | 90 | 0 | 0 | 304 | 0 | 0 | 45.6 | 35 | 133 | 125 | 293 | 55 | 55 | 126 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 20 | 15 | 0 | 310 | 86 | 16 | 104 | 0 | 0 | 50 | 36 | 35 | 12 | 12 | 0 | 219 | 41 | 17 | 650 | 15 | 0 | 0 | 25.5 | 17 | 221 | 0 | 0 | 0 | 1177 | 0 | 51 | 135 | 0 | 285 | 280 | 220 | 46 | 0 | 38 | 83 | 104 | 172 | 0 | 8 | 14 | 82 | 8 | 0 | 21 | 300 | 0 | 312 | 0 | 67 | 146 | 10 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 46 | 38 | 0 | 0 | 0 | 7979.1 | 929 | 270 | 0 | 40 | 67 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1204 | 0 | 48 | 0 | 35 | 35 | 0 | 97 | 30 | 8 | 0 | 0 | 22 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 160 | 110 | 220 | 0 | 400 | 1120 | 10 | 6699 | 14678.1 | 103.68
19:30 | 0 | 105 | 25 | 0 | 0 | 130 | 0 | 0 | 304 | 0 | 0 | 45.6 | 35 | 133 | 125 | 293 | 55 | 55 | 126 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 108 | 20 | 15 | 0 | 310 | 84 | 16 | 104 | 0 | 0 | 50 | 15 | 35 | 12 | 12 | 0 | 219 | 51 | 13 | 650 | 15 | 0 | 0 | 8 | 17 | 223 | 0 | 0 | 0 | 1192 | 0 | 51 | 135 | 0 | 285 | 280 | 165 | 46 | 0 | 35 | 45 | 104 | 144 | 0 | 19 | 15 | 76 | 8 | 0 | 21 | 305 | 0 | 312 | 0 | 67 | 138 | 10 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 46 | 41 | 0 | 0 | 0 | 7849.6 | 929 | 270 | 0 | 35 | 55 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1137 | 0 | 1209 | 0 | 48 | 0 | 35 | 35 | 0 | 97 | 30 | 8 | 0 | 0 | 22 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 50 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 160 | 110 | 220 | 0 | 401 | 1090 | 10 | 6613 | 14462.6 | 103.68
20:00 | 0 | 105 | 25 | 0 | 0 | 130 | 0 | 0 | 289 | 0 | 0 | 45.1 | 35 | 134 | 124 | 293 | 55 | 55 | 126 | 0 | 300 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 108 | 20.8 | 15 | 0 | 310 | 85 | 16 | 104 | 0 | 0 | 50 | 15 | 35 | 12 | 12 | 0 | 218 | 52 | 16 | 650 | 15 | 0 | 0 | 8 | 17 | 223 | 0 | 0 | 0 | 1192 | 0 | 51 | 133 | 0 | 305 | 280 | 147 | 45 | 0 | 38 | 50 | 103 | 150 | 0 | 19 | 15 | 82 | 8 | 0 | 21 | 310 | 0 | 312 | 0 | 67 | 140 | 10 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 46 | 0 | 0 | 0 | 7869.9 | 930 | 270 | 0 | 35 | 55 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 1202 | 0 | 48 | 0 | 35 | 35 | 0 | 97 | 32 | 8 | 0 | 0 | 22 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 160 | 110 | 220 | 0 | 401 | 1093 | 10 | 6613 | 14482.9 | 103.67
21:00 | 0 | 105 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 51 | 35 | 134 | 75 | 295 | 55 | 35 | 126 | 0 | 450 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 108 | 0 | 17 | 0 | 360 | 77 | 16 | 104 | 0 | 0 | 50 | 0 | 17 | 12 | 12 | 0 | 218 | 53 | 21 | 650 | 0 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 1190 | 0 | 51 | 128 | 0 | 360 | 353 | 165 | 45 | 0 | 38 | 47 | 104 | 100 | 0 | 19 | 0 | 76 | 0 | 0 | 21 | 315 | 0 | 312 | 0 | 67 | 143 | 10 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 46 | 0 | 0 | 0 | 7460 | 930 | 286 | 0 | 0.4 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1145 | 0 | 1210 | 0 | 48 | 0 | 0 | 35 | 0 | 98 | 36 | 0 | 0 | 0 | 13 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 50 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 110 | 220 | 0 | 370 | 1084 | 10 | 6408.4 | 13868.4 | 103.67
22:00 | 0 | 70 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 133 | 45 | 125 | 55 | 35 | 90 | 0 | 450 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 20.5 | 20 | 0 | 540 | 32 | 16 | 87 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 219 | 55 | 25 | 650 | 0 | 0 | 0 | 0 | 17 | 224 | 0 | 0 | 0 | 1192 | 0 | 51 | 50 | 0 | 345 | 353 | 230 | 45 | 0 | 38 | 46 | 104 | 68 | 0 | 19 | 0 | 84 | 0 | 0 | 21 | 310 | 0 | 324 | 0 | 67 | 150 | 10 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 38 | 0 | 0 | 1 | 7213.5 | 930 | 285 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 0 | 1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 110 | 220 | 0 | 370 | 1085 | 0 | 6258 | 13471.5 | 103.65
23:00 | 0 | 69 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 17.5 | 15 | 141 | 45 | 125 | 55 | 35 | 54 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20.5 | 20 | 0 | 540 | 32 | 16 | 82 | 0 | 0 | 50 | 0 | 17 | 12 | 12 | 0 | 219 | 54 | 27 | 650 | 0 | 0 | 0 | 0 | 17 | 224 | 0 | 0 | 0 | 1160 | 0 | 51 | 50 | 0 | 285 | 352 | 154 | 42 | 0 | 37 | 49 | 104 | 65 | 0 | 20 | 0 | 84 | 0 | 0 | 21 | 315 | 0 | 324 | 0 | 67 | 157 | 10 | 0 | 78 | 30 | 0 | 0 | 162 | 17 | 49 | 48 | 67 | 0 | 0 | 6 | 7048 | 929 | 282 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 110 | 220 | 0 | 370 | 1090 | 0 | 6252 | 13300 | 103.64
Total KWH | 0 | 1353600 | 491040 | 0 | 0 | 589125 | 0 | 0 | 6372000 | 0 | 0 | 519840 | 508320 | 2307024 | 1221600 | 4791360 | 908244 | 530468 | 1589760 | 0 | 7927500 | 0 | 0 | 0 | 129364 | 5200930 | 0 | 0 | 123886 | 1282800 | 447000 | 491040 | 0 | 8312727.27 | 1488418 | 155564 | 1618560 | 0 | 24480 | 547492 | 871728 | 187149 | 296640 | 297600 | 20160 | 5239784 | 511855 | 440640 | 15723636.36 | 260945 | 0 | 0 | 199000.8 | 100364 | 5222992 | 0 | 0 | 0 | 27561815 | 112320 | 1160548 | 2534181 | 0 | 8580500 | 7942600 | 2652000 | 1043520 | 0 | 819144 | 957120 | 2430322 | 3984000 | 0 | 370820 | 652080 | 1686720 | 219331 | 396018 | 354592 | 7604500 | 0 | 7895000 | 0 | 1548797 | 3596155 | 198384 | 0 | 1848960 | 712128 | 0 | 0 | 3448700 | 308520 | 1184400 | 1087200 | 1561920 | 5500 | 190840 | 89760 | 173043031.43 | 22234909 | 8243136 | 0 | 104640 | 136064 | 912000 | 0 | 0 | 0 | 0 | 0 | 400320 | 25505460 | 0 | 26787820 | 0 | 305630 | 0 | 166752 | 622176 | 0 | 384448 | 140466 | 119515 | 232498 | 560170 | 146881 | 0 | 254240 | 4106545 | 0 | 0 | 0 | 0 | 0 | 8835345 | 0 | 23160 | 0 | 0 | 945642 | 74743 | 1412688 | 0 | 0 | 0 | 16324.44 | 623520 | 3372 | 308064 | 3971000 | 2637000 | 5343960 | 0 | 8275536 | 25940363.64 | 74400 | 149848788.08 | 322891819.51

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13693.74 | MW | 12:00 Hr. | Energy Generated |  |  | 322.8918 |  | MKWHr.
| Day Peak Demand |  |  | 13822.74 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.869 |  | MKWHr.
| Evening Peak Generation |  |  | 14678.1 | MW | 19:00 Hr. | Energy Demand |  |  | 324.7608 |  | MKWHr.
| Evening Peak Demand |  |  | 14731.1 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33.1 |  | °C
| Minimum Generation of the Day |  |  | 12294.54 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 868.18 |  | MMCFD
| Maximum Generation of the Day |  |  | 14678.1 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.6037 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.3403 | 0 | 15.6334 | 0 | 0 | 0.12389 | 0 | 0 | 45.0976 | Gas | 117.5839 | Gas | 416852338.4359
| Chattogram Zone |  |  | 5.6636 | 43.2855 | 6.5353 | 0 | 5.2398 | 0.13248 | 0 | 0.02448 | 60.8811 | Coal | 106.9778 | Coal | 676579543.032
| Cumilla Zone |  |  | 24.9995 | 0 | 8.7013 | 0 | 0 | 0.39602 | 1.6867 | 0 | 35.7835 | HFO | 38.4073 | HFO | 685569630.782
| Mymensingh Zone |  |  | 1.5619 | 0 | 2.6699 | 0 | 0 | 0.19634 | 0 | 0 | 4.4281 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8526 | Hydro | 5.2398 | Hydro | 523978.4
| Khulna Zone |  |  | 8.2431 | 25.5055 | 0.2407 | 0 | 0 | 0.40032 | 23.1469 | 0 | 57.5365 | Solar | 3.0371 | Solar | 47371796.5804
| Barishal Zone |  |  | 7.981 | 38.1869 | 0.38246 | 0 | 0 | 0.003372 | 0 | 0 | 46.5537 | Import | 51.6214 | Import | 305029297.79
| Rajshahi Zone |  |  | 12.9419 | 0 | 1.8859 | 0 | 0 | 1.0701 | 26.7878 | 0 | 42.6856 | Wind | 0.02448 | Wind | 360100.8
| Rangpur Zone |  |  | 0 | 0 | 2.3583 | 0 | 0 | 0.71459 | 0 | 0 | 3.0729
| Total |  |  | 117.5839 | 106.9778 | 38.4073 | 0 | 5.2398 | 3.0371 | 51.6214 | 0.02448 | 322.8918
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416852338.4359 |  | Hydro | 523978.4
|  |  |  | Coal | 676579543.032 |  | Solar | 47371796.5804
|  |  |  | HFO | 685569630.782 |  | Import | 305029297.79
|  |  |  | HSD | 0 |  | Wind | 360100.8
[5 empty] | Total: | 213,22,86,685 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2349 | Peak Hr Flow | 929.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49420946.25 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.7878 | Peak Hr Flow | 1204.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2408 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6867 | Peak Hr Flow | 82.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2558 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.7094 | Peak Hr Flow | 2215.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5478
|  |  |  | Chattogram |  | 15 |  | 1569
|  |  |  | Cumilla |  | 15 |  | 1419
|  |  |  | Mymensingh |  | 21 |  | 988
|  |  |  | Sylhet |  | 0 |  | 643
|  |  |  | Khulna |  | 0 |  | 1565
|  |  |  | Barishal |  | 0 |  | 456
|  |  |  | Rajshahi |  | 0 |  | 1224
|  |  |  | Rangpur |  | 0 |  | 829
|  |  |  | Total |  | 51 |  | 14171
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to Annual Maintenance.
| 08:12 | 15:27 | Ishwardi-Rooppur 132kV Ckt-1 Scheduled S/D from Ruppur 132/11kV end Due to A/M
| 08:14 | 15:23 | Ishwardi-Rooppur 132kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end Due to ANNUAL
MAINTENANCE
| 08:30 | 20:13 | Gopalganj 400/132kV S/S 400kV Rooppur Project Work S/D
| 08:40 | 15:57 | Bogura 230/132kV S/S T-03 HT Scheduled S/D Due to Annual Maintenance Work.
| 08:40 | 15:59 | Bogura 230/132kV S/S T-03 LT Scheduled S/D Due to Annual Maintenance Work.
|  | 08:42 | Feni 132/33kV S/S T-1(405T) LT is restored.
|  | 08:42 | Feni 132/33kV S/S T-1(405T) HT is restored.
| 08:54 | 14:00 | Fenchuganj-Fenchuganj 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 08:58 |  | Muktagacha 132/33kV S/S RPCL-2 Scheduled S/D Due to Dead line checking
| 09:25 | 17:01 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
Maintenance Work.
| 09:43 |  | Sathia- Baghabari 132 KV ckt Shutdown due to OPGW Stringing work.
| 09:50 | 12:20 | Joypurhat 132/33kV S/S Patnitola Ckt.-1 Project Work S/D Due to CB Spring Charging
Auxiliary Contact Change (Work done by CCCE)
|  | 09:52 | Madaripur 132/33kV S/S 33 KV BUS is restored.
| 10:10 | 12:32 | Joypurhat 132/33kV S/S Patnitola Ckt.-2 Project Work S/D Due to CB Spring Charging
Auxiliary Contact Change (Work done by CCCE)
| 10:26 | 14:45 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D Due to 132kV Tr-1 33kV side LV Bushing
oil Leakage.
| 10:27 | 14:43 | Bajitpur 132/33kV S/S Tr-1(404T) HT Scheduled S/D Due to 132kV Tr-1 33kV side LV Bushing
oil Leakage.
| 12:40 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
|  | 12:57 | Sholosohor 132/33kV S/S TRAFO-02 HT is restored.
|  | 12:58 | Sholosohor 132/33kV S/S TRAFO-02 LT is restored.
| 14:19 | 16:40 | Chowmuhani 132/33kV S/S TR3-435T LT Forced S/D Due to lakshmipur 33kv feeder isolator | [7 empty] | 35.0MW load
|  |  | maintenance | [7 empty] | interrup.
|  | 14:33 | Saidpur 132/33kV S/S TR-01 HT is restored.
| 14:40 | 16:40 | Chowmuhani 132/33kV S/S TR3-435T HT Forced S/D Due to lakshmipur 33kv feeder isolator | [7 empty] | 35.0MW load
|  |  | maintenance | [7 empty] | interrup.
|  | 14:48 | Chattak-Sylhet 132 kV Ckt-1 is restored.
| 15:25 |  | Bibiana 400/230kV S/S Bibiyana-South Forced S/D Due to maintenance at bibiayana south
| 15:26 |  | Rajshahi-Rajshahi(New) 132kV Ckt-1 Scheduled S/D from Mirsorai 230/33kV end Due to
Annual Maintenance
| 15:42 | 16:30 | Benapole-Jashore 132 kV Ckt-2 Tripped from Benapole 132/33kV end showing EF(67N) IDMT,
Dist(21L), Zone-01 relays Due to Thundering and from Jashore 132/33kV end showing OC(67),
EF(67N),Dist(21L),Zone-1,Zcom relays.
|  | 15:45 | Chauddagram-Cumilla(S) 132 kV Ckt-2 is restored.
|  | 16:42 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
|  | 16:43 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
|  | 16:43 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
|  | 16:50 | Madaripur 132/33kV S/S T3-426T HT is restored.
|  | 16:51 | Madaripur 132/33kV S/S T3-426T LT is restored.
|  | 16:53 | Lalmonirhat 132/33kV S/S T-2 (415T) LT is restored.
|  | 17:54 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
|  | 18:12 | Gopalganj 400/132kV S/S 400kV Bus-01 is restored.
| 18:36 |  | Satiya - Bera 132V ckt syn .(Bera line disconnected from Bagabari line.
|  | 18:48 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
| 18:53 |  | Ghorasal unit-4 was sync.
| 18:53 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 19:16 |  | Daudkandi-Sonargaon 132 kV Ckt-2 Forced S/D from Sonargaon 132/33kV end Due to NLDC
instruction.
| 19:25 |  | Bagabari 132 KV line charge upto tower No. 268. (Bera line disconnected from Bagabari
line.
| 20:20 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 20:32 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
| 20:40 |  | Siddhirganj 335 MW CCPP ST was shut down.
| 20:44 |  | Siddhirganj 335 MW CCPP GT was shut down.
| 21:37 |  | Evening Peak Generation: 14677 MW.
| 01:22 | 02:05 | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing Non relays Due to Shaitaganj and
Habiganj Bypass Feeder Trip
| 01:22 | 02:01 | Shahjibazar 132/33kV S/S TR-06 HT Tripped showing Over Current Relay relays Due to
Shaitaganj and Habiganj Bypass Feeder Trip
| 01:22 | 02:03 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Trip Relay relays Due to Chunarughat
Feeder Trip
| 01:22 | 02:00 | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing Lockout Relay, Over Current Earth Fault
Relay relays Due to Chunarughat Feeder Trip
| 01:22 | 02:00 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing Lockout Relay, Over current earth fault
Relay relays Due to Chunarughat Feeder Trip.
| 01:22 | 02:03 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lockout Relay relays Due to Chunarughat
Feeder Trip
| 01:52 |  | Adani Power Jharkhand Ltd. Unit-1 was forced shutdown due to a problem in the
Main Turbine MCV.
| 03:00 | 03:22 | Hatirjheel 132/33kV T-1 and T-2 transformers tripped showing over-voltage due to bad | [7 empty] | 19MW load interrup.
weather.
| 06:00 |  | Minimum Generation: 11190 MW.
| 07:04 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to 132KV Sylhet -
Chhatak ckt -1 Shutdown for Annual maintenance. and from Sylhet 132/33kV end Due to
Annual Maintenance Purpose.
| 07:11 |  | Patuakhali 132/33kV S/S 425T (T-3) HT Scheduled S/D Due to Annual Maintenance work
| 07:11 |  | Patuakhali 132/33kV S/S 425T (T-3) LT Scheduled S/D Due to Annual Maintenance work
| 07:13 |  | Barapukuria-Saidpur 132 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
saidpur end maintenance work
| 07:16 |  | Barapukuria-Rangpur 132 kV Ckt-2 Forced S/D from Saidpur 132/33kV end Due to Line LA
Replace
| 07:54 |  | Madaripur 132/33kV S/S T3-426T HT Scheduled S/D Due to Annual Maintenance
| 07:54 |  | Madaripur 132/33kV S/S T3-426T LT Scheduled S/D Due to Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 90 | 589125 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 304 | 6372000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7927500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 908244 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 5200930 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45.6 | 519840 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1221600 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 530468 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 129364 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 447000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 491040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 491040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 4791360 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2307024 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1353600 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1589760 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 123886 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 508320 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 310 | 8312727.27 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1282800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2445.6 | 45097628.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 199000.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112320 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5239784 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5222992 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 100364 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 36 | 871728 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 547492 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 296640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 440640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 104 | 1618560 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 155564 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 187149 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 41 | 511855 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 297600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 86 | 1488418 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 15 | 260945 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1177 | 27561815 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 24480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15723636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2733.5 | 60881143.16
| Ashuganj TPP Unit- 3, 4 |  | APSCL | 1*150+1*150 | 0 | 0 | 0 | Contract Expired
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7942600 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 220 | 2652000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 285 | 8580500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 819144 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1043520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1160548 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 135 | 2534181 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 354592 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2430322 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 172 | 3984000 | -
| Import (Tripura) |  | Import | 0 | 160 | 82 | 1686720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 219331 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 370820 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 14 | 652080 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 83 | 957120 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 396018 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1547 | 35783496
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 38 | 1561920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 46 | 1087200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 49 | 1184400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 190840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 89760 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 308520 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 150 | 4428140
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1548797 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3596155 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 712128 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1848960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3448700 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 198384 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7604500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 312 | 7895000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1103 | 26852624
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 929 | 22234909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 104640 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 67 | 136064 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 270 | 8243136 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 400320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1112 | 25505460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2456 | 57536529
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 400 | 8275536 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 57 | 308064 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2637000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 25940363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5343960 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 10 | 74400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 160 | 3971000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3372 | -
Barishal Area Total |  |  |  |  | 2858 | 2077 | 46553695.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 232498 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 305630 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 140466 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 4106545 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 336 | 8835345 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 146881 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 119515 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 384448 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 622176 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 166752 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23160 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1204 | 26787820 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 254240 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 560170 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1983 | 42685646
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1412688 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 16324.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 945642 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 74743 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 623520 | -
Rangpur Area Total |  |  |  |  | 950 | 183 | 3072917.44
Eastern Grid Total |  |  |  |  | 17383.855 | 7979.1 | 173043031.43
Western Grid Total |  |  |  |  | 10980.24 | 6699 | 149848788.08
National Grid Total |  |  |  |  | 28364.095 | 14678.1 | 322891819.51
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10045.78 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4073.8 | MW
i) Dhaka area |  |  | 5477.8 |  | MW | i) Khulna area |  |  |  | 1565.2 | MW
ii) Chattogram area |  |  | 1554 |  | MW | ii) Barishal area |  |  |  | 456 | MW
iii) Cumilla area |  |  | 1403.98 |  | MW | iii) Rajshahi area |  |  |  | 1223.6 | MW
iv) Mymensingh area |  |  | 967 |  | MW | iv) Rangpur area |  |  |  | 829 | MW
v) Sylhet area |  |  | 643 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14119.58 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 89 | 18:00 | 133 | Niamatpur | 70 | 00:00
2 | AKSML | 140 | 00:00 | 68 | Ishurdi | 75 | 18:00 | 134 | Noapara | 42 | 18:30
3 | Aftabnagar | 40 | 13:00 | 69 | Jaldhaka | 70 | 18:00 | 135 | PHP | 4 | 18:00
4 | Agargaon | 115 | 13:00 | 70 | Jamalpur | 113 | 11:00 | 136 | Pabna | 102 | 18:00
5 | Agrabad | 104 | 19:00 | 71 | Jashore | 130 | 13:00 | 137 | Palashbari | 100 | 18:30
6 | Amnura | 32 | 00:00 | 72 | Jhenaidah | 114 | 00:00 | 138 | Panchagarh | 50 | 18:00
7 | Ashuganj | 97 | 04:00 | 73 | Joydebpur | 159 | 18:00 | 139 | Patiya | 10.2 | 20:00
8 | BSRM | 184 | 20:00 | 74 | Joypurhat | 63 | 18:30 | 140 | Patuakhali | 69.5 | 22:00
9 | Bagerhat | 80 | 00:00 | 75 | Juldah | 17.5 | 14:00 | 141 | Payra | 34 | 21:00
10 | Bajitpur | 80 | 19:00 | 76 | KSRM | 27 | 21:00 | 142 | Postogola | 69 | 13:00
11 | Bakulia | 101 | 18:30 | 77 | Kabirpur | 264 | 18:30 | 143 | Purbachal | 22 | 00:00
12 | Banani | 53.6 | 11:00 | 78 | Kachua | 87 | 22:00 | 144 | Purbasadipur | 108 | 18:00
13 | Bangabhaban | 27 | 10:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rahanpur | 32 | 00:00
14 | Barapukuria | 59 | 18:30 | 80 | Kalurghat | 44 | 12:00 | 146 | Rahim | 44 | 22:00
15 | Barguna | 22 | 21:00 | 81 | Kamrangirchar | 79 | 19:30 | 147 | Rajbari | 80 | 18:00
16 | Barishal | 116 | 18:30 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 130 | 18:30
17 | Barishal-230 | 94 | 18:30 | 83 | Kasba | 37 | 22:00 | 149 | Rajshahi | 102 | 00:00
18 | Baroaulia | 61 | 01:00 | 84 | Kazla | 102 | 19:00 | 150 | Rajshahi-230 | 89 | 13:00
19 | Baroirhat | 69 | 18:00 | 85 | Keranigonj | 81 | 12:00 | 151 | Ramganj | 112 | 19:00
20 | Bashundhara | 196 | 11:00 | 86 | Khagrachori | 32 | 18:30 | 152 | Rampur | 46 | 00:00
21 | BashundharaCement | 2 | 23:00 | 87 | Khulna | 78 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 80 | 18:00 | 88 | Khulshi | 198 | 18:00 | 154 | Rangpur | 140 | 18:30
23 | Benapole | 58 | 19:30 | 89 | Kishoreganj | 124 | 19:00 | 155 | Ruppur | 7.6 | 16:00
24 | Bhaluka | 141 | 12:00 | 90 | Kodda | 295 | 12:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 57 | 00:00 | 91 | Kulaura | 51 | 22:00 | 157 | Saidpur | 94 | 18:00
26 | Bhangura | 36 | 18:00 | 92 | Kurigram | 58 | 18:00 | 158 | Satkhira | 125 | 00:00
27 | Bheramara(GK) | 63 | 18:00 | 93 | Kushtia | 142 | 18:00 | 159 | Satmasjid | 103 | 18:00
28 | Bhulta | 218 | 06:00 | 94 | Laksam | 31 | 00:00 | 160 | Savar | 232 | 12:00
29 | Bog-Sherpur | 58 | 18:00 | 95 | Lakshmipur | 34 | 23:00 | 161 | SevenRings | 13.28 | 03:00
30 | Bogura | 148 | 00:00 | 96 | Lalbag | 64 | 13:00 | 162 | ShahCement | 25 | 16:00
31 | Borhanuddin | 94 | 00:00 | 97 | Lalmonirhat | 54 | 18:00 | 163 | Shahjadpur | 76 | 18:00
32 | Brahmanbaria | 133 | 00:00 | 98 | MI_Cement | 16.2 | 02:00 | 164 | Shahjibazar | 132 | 21:00
33 | Cantonment | 160 | 11:00 | 99 | Madanganj | 44 | 13:00 | 165 | Shahmirpur | 58 | 00:00
34 | Chandina | 24.52 | 18:00 | 100 | Madaripur | 107 | 18:00 | 166 | Shariatpur | 85 | 22:00
35 | Chandpur | 80 | 00:00 | 101 | Madartek | 100 | 00:00 | 167 | Sherpur | 112 | 01:00
36 | Chandraghona | 36 | 18:00 | 102 | Madunaghat | 62 | 20:00 | 168 | Shikalbaha | 30 | 00:00
37 | Chapai | 64 | 00:00 | 103 | Magura | 57 | 18:00 | 169 | Shitalakhya | 87.2 | 15:00
38 | Charsaidpur | 37 | 15:00 | 104 | Mahasthangarh | 66 | 00:00 | 170 | Sholosohor | 48 | 11:00
39 | Chauddagram | 69 | 00:00 | 105 | Maijdee | 38 | 21:00 | 171 | Shyampur | 114 | 09:00
40 | Chhatak | 38 | 22:00 | 106 | Manikganj | 126 | 18:00 | 172 | Siddhirganj | 125 | 12:00
41 | Chowmuhani | 158 | 20:00 | 107 | Maniknagar | 64 | 13:00 | 173 | Sirajganj | 108 | 19:00
42 | Chuadanga | 99 | 00:00 | 108 | Matarbari | 51 | 00:00 | 174 | Sonargaon | 141 | 19:30
43 | Coxsbazar | 148 | 18:00 | 109 | Matuail | 73 | 13:00 | 175 | Sreemongol | 88 | 18:30
44 | Cumilla(N) | 139 | 19:30 | 110 | Metrorail_Motijheel | 33 | 08:00 | 176 | Sreepur | 109 | 18:00
45 | Cumilla(S) | 154 | 13:00 | 111 | Metrorail_Uttara | 20 | 11:00 | 177 | Srinagar | 46.47 | 18:30
46 | Daganbhuiyan | 20 | 22:00 | 112 | Millgate | 134 | 11:00 | 178 | Sunamganj | 58 | 00:00
47 | Daudkandi | 152 | 18:30 | 113 | Mirpur | 142 | 12:00 | 179 | Sylhet | 53 | 18:00
48 | DhakaUniversity | 94 | 13:00 | 114 | Mirsorai | 10 | 21:00 | 180 | Sylhet-132 | 134 | 18:00
49 | Dhamrai | 126 | 15:00 | 115 | Mirzapur | 41 | 14:00 | 181 | TK | 24.5 | 19:00
50 | Dhanmondi | 146 | 13:00 | 116 | Mithapukur | 52 | 18:00 | 182 | Tangail | 163 | 18:30
51 | Dohazari | 108 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 21 | 18:30
52 | Faridpur | 160 | 18:30 | 118 | Mogbazar | 103 | 13:00 | 184 | Thakurgaon | 88 | 18:00
53 | Fatullah | 112 | 12:00 | 119 | Mongla | 48 | 10:00 | 185 | Tongi | 123 | 11:00
54 | Fenchuganj | 48 | 22:00 | 120 | Motijheel | 49 | 13:00 | 186 | Ullahpara | 37 | 18:30
55 | Feni | 124 | 18:00 | 121 | Muktagacha | 29 | 17:00 | 187 | Ullon | 68 | 00:00
56 | GPH | 72 | 09:00 | 122 | Munshiganj | 109 | 00:00 | 188 | Uttara | 97 | 11:00
57 | Ghatail | 64 | 18:00 | 123 | Muradnagar | 41 | 19:30 | 189 | UttaraNew | 32 | 12:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 192 | 00:00 | 190 | Zigatola | 76 | 00:00
59 | Ghorashal-230 | 107 | 01:00 | 125 | Naogaon | 110 | 00:00
60 | Goalpara | 39 | 18:00 | 126 | Narail | 52 | 18:00
61 | Gollamari | 94 | 00:00 | 127 | Narinda | 78 | 13:00
62 | Gopalganj | 105 | 18:00 | 128 | Narshingdi | 176 | 21:00
63 | Gulshan | 132 | 11:00 | 129 | Natore | 128 | 01:00
64 | Halishahar | 80.5 | 15:00 | 130 | Nawabganj | 50 | 22:00
65 | HaripurSBU | 155 | 00:00 | 131 | Netrakona | 115 | 21:00
66 | Hasnabad | 107 | 18:00 | 132 | New | 58 | 11:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14452.25 | 132 |  | 14590.19
1:00 | 14068.25 | 127 |  | 14201.25
2:00 | 13706.63 | 110 |  | 13821.63
3:00 | 13135.06 | 63 |  | 13201.06
4:00 | 12704.57 | 45 |  | 12751.57
5:00 | 12586.47 | 33 |  | 12620.47
6:00 | 12294.54 | 34 |  | 12330.54
7:00 | 12320.46 | 79 |  | 12403.46
8:00 | 12316.63 | 102 |  | 12423.63
9:00 | 12504.23 | 85 |  | 12593.23
10:00 | 12713.74 | 30 |  | 12744.74
11:00 | 13261.72 | 96 |  | 13361.72
12:00 | 13693.74 | 123 |  | 13822.74
13:00 | 13688.21 | 83 |  | 13775.21
14:00 | 13429.59 | 22 |  | 13452.58
15:00 | 13247.18 | 53 |  | 13302.57
16:00 | 12764.54 | 37 |  | 12803.21
17:00 | 12912.92 | 55 |  | 12970.4
18:00 | 14648.9 | 50 |  | 14700.9
19:00 | 14678.1 | 51 |  | 14731.1
19:30 | 14462.6 | 36 |  | 14500.6
20:00 | 14482.9 | 46 |  | 14530.9
21:00 | 13868.4 | 174 |  | 14050.23
22:00 | 13471.5 | 123 |  | 13600.5
23:00 | 13300 | 116 |  | 13421.22
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7641 | 6811.25 | 14452.25 | DAILY GENERATION CURVE
00:30 | 7509.5 | 6750.75 | 14260.25
01:00 | 7378 | 6690.25 | 14068.25 | 29-10-2025
01:30 | 7336.5 | 6550.94 | 13887.44
02:00 | 7295 | 6411.63 | 13706.63
02:30 | 7105.25 | 6315.595 | 13420.845
03:00 | 6915.5 | 6219.56 | 13135.06
03:30 | 6772.5 | 6147.315 | 12919.815
04:00 | 6629.5 | 6075.07 | 12704.57
04:30 | 6607 | 6038.52 | 12645.52
05:00 | 6584.5 | 6001.97 | 12586.47
05:30 | 6501.5 | 5939.005 | 12440.505
06:00 | 6418.5 | 5876.04 | 12294.54
06:30 | 6449.57 | 5857.93 | 12307.5
07:00 | 6480.64 | 5839.82 | 12320.46
07:30 | 6484.99 | 5833.555 | 12318.545
08:00 | 6489.34 | 5827.29 | 12316.63
08:30 | 6556.855 | 5853.575 | 12410.43
09:00 | 6624.37 | 5879.86 | 12504.23
09:30 | 6762.58 | 5846.405 | 12608.985
10:00 | 6900.79 | 5812.95 | 12713.74
10:30 | 7090.475 | 5897.255 | 12987.73
11:00 | 7280.16 | 5981.56 | 13261.72
11:30 | 7412.365 | 6065.365 | 13477.73
12:00 | 7544.57 | 6149.17 | 13693.74
12:30 | 7516.34 | 6174.635 | 13690.975
13:00 | 7488.11 | 6200.1 | 13688.21
13:30 | 7388.61 | 6170.29 | 13558.9
14:00 | 7289.11 | 6140.48 | 13429.59
14:30 | 7310.995 | 6027.39 | 13338.385
15:00 | 7332.88 | 5914.3 | 13247.18
15:30 | 7154.41 | 5851.45 | 13005.86
16:00 | 6975.94 | 5788.6 | 12764.54
16:30 | 7066.565 | 5772.165 | 12838.73
17:00 | 7157.19 | 5755.73 | 12912.92
17:30 | 7593.545 | 6187.365 | 13780.91
18:00 | 8029.9 | 6619 | 14648.9
18:30 | 8004.5 | 6659 | 14663.5
19:00 | 7979.1 | 6699 | 14678.1
19:30 | 7849.6 | 6613 | 14462.6
20:00 | 7869.9 | 6613 | 14482.9
20:30 | 7664.95 | 6510.7 | 14175.65 |  | Executive Engineer
21:00 | 7460 | 6408.4 | 13868.4 |  | Network Operation Division
21:30 | 7336.75 | 6333.2 | 13669.95
22:00 | 7213.5 | 6258 | 13471.5
22:30 | 7130.75 | 6255 | 13385.75
23:00 | 7048 | 6252 | 13300

## En-Curve
QF-LDC-12
Date | 29-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3316 | 1589 | 903 | 38 | 84 | 1028.05 | 221 | 4834 | 0 | 411 | 2028.2 | 0 | 0 | 0 | 132 | DAILY ENERGY CURVE
00:30 | 3309.5 | 1580.5 | 903 | 38 | 80 | 1014.05 | 221 | 4804.1 | 0 | 373 | 1937.1 | 0 | 0 | 0 | 129.5 | 29-10-2025
01:00 | 3303 | 1572 | 903 | 38 | 76 | 1000.05 | 221 | 4774.2 | 0 | 335 | 1846 | 0 | 0 | 0 | 127
01:30 | 3297.5 | 1563 | 903 | 38 | 74 | 1001.84 | 221 | 4687.1 | 0 | 333 | 1769 | 0 | 0 | 0 | 118.5 | Energy Generated | 322.8918 |  | MKWHr
02:00 | 3292 | 1554 | 903 | 38 | 72 | 1003.63 | 221 | 4600 | 0 | 331 | 1692 | 0 | 0 | 0 | 110 | Energy not Served | 1.869 |  | MKWHr
02:30 | 3301 | 1556.5 | 903 | 38 | 71 | 1013.595 | 220.5 | 4604 | 0 | 278 | 1435.25 | 0 | 0 | 0 | 86.5 | Total Energy Requirement | 324.7608 |  | MKWHr
03:00 | 3310 | 1559 | 903 | 38 | 70 | 1023.56 | 220 | 4608 | 0 | 225 | 1178.5 | 0 | 0 | 0 | 63
03:30 | 3334 | 1548 | 903 | 38 | 71 | 1021.715 | 220 | 4614.1 | 0 | 208.5 | 961.5 | 0 | 0 | 0 | 54
04:00 | 3358 | 1537 | 903 | 38 | 72 | 1019.87 | 220 | 4620.2 | 0 | 192 | 744.5 | 0 | 0 | 0 | 45
04:30 | 3339 | 1553.5 | 903 | 38 | 61 | 1011.92 | 219.5 | 4617.6 | 0 | 191.5 | 710.5 | 0 | 0 | 0 | 39
05:00 | 3320 | 1570 | 903 | 38 | 50 | 1003.97 | 219 | 4615 | 0 | 191 | 676.5 | 0 | 0 | 0 | 33
05:30 | 3322 | 1572.5 | 903.5 | 38 | 50 | 1004.005 | 219 | 4571.5 | 0 | 166 | 594 | 0 | 0 | 0 | 33.5
06:00 | 3324 | 1575 | 904 | 38 | 50 | 1004.04 | 219 | 4528 | 0 | 141 | 511.5 | 0 | 0 | 0 | 34
06:30 | 3345 | 1587 | 903.5 | 38 | 46 | 1004.495 | 219 | 4465 | 33.255 | 150.5 | 515.75 | 0 | 0 | 0 | 56.5
07:00 | 3366 | 1599 | 903 | 38 | 42 | 1004.95 | 219 | 4402 | 66.51 | 160 | 520 | 0 | 0 | 0 | 79
07:30 | 3332 | 1570 | 903 | 38 | 53 | 1012.975 | 219 | 4362.5 | 131.57 | 176 | 520.5 | 0 | 0 | 0 | 90.5
08:00 | 3298 | 1541 | 903 | 38 | 64 | 1021 | 219 | 4323 | 196.63 | 192 | 521 | 0 | 0 | 0 | 102
08:30 | 3273 | 1514 | 903 | 38 | 62 | 1036 | 219 | 4305 | 276.93 | 196 | 587.5 | 0 | 0 | 0 | 93.5
09:00 | 3248 | 1487 | 903 | 38 | 60 | 1051 | 219 | 4287 | 357.23 | 200 | 654 | 0 | 0 | 0 | 85
09:30 | 3265.5 | 1520.5 | 903 | 38 | 63 | 1067.5 | 219 | 4141 | 380.985 | 210 | 800.5 | 0 | 0 | 0 | 57.5
10:00 | 3283 | 1554 | 903 | 38 | 66 | 1084 | 219 | 3995 | 404.74 | 220 | 947 | 0 | 0 | 0 | 30
10:30 | 3329.5 | 1540 | 916 | 38 | 67 | 1080.5 | 220.5 | 4052.5 | 457.73 | 226 | 1060 | 0 | 0 | 0 | 63
11:00 | 3376 | 1526 | 929 | 38 | 68 | 1077 | 222 | 4110 | 510.72 | 232 | 1173 | 0 | 0 | 0 | 96
11:30 | 3392.5 | 1531.5 | 929.5 | 38 | 69 | 1109 | 221.5 | 4146 | 495.73 | 232 | 1311.5 | 0 | 0 | 1.5 | 109.5
12:00 | 3409 | 1537 | 930 | 38 | 70 | 1141 | 221 | 4182 | 480.74 | 232 | 1450 | 0 | 0 | 3 | 123
12:30 | 3368 | 1531 | 930 | 38 | 74 | 1144.5 | 221 | 4190 | 433.975 | 227.5 | 1529.5 | 0 | 0 | 3.5 | 103
13:00 | 3327 | 1525 | 930 | 38 | 78 | 1148 | 221 | 4198 | 387.21 | 223 | 1609 | 0 | 0 | 4 | 83
13:30 | 3280.5 | 1524.5 | 930 | 38 | 79 | 1187.5 | 220 | 4119.5 | 338.4 | 230 | 1607 | 0 | 0 | 4.5 | 52.5
14:00 | 3234 | 1524 | 930 | 38 | 80 | 1227 | 219 | 4041 | 289.59 | 237 | 1605 | 0 | 0 | 5 | 22
14:30 | 3284.5 | 1525 | 929.5 | 38 | 78 | 1200 | 220 | 4085.5 | 216.885 | 228.5 | 1528 | 0 | 0 | 4.5 | 37.5
15:00 | 3335 | 1526 | 929 | 38 | 76 | 1173 | 221 | 4130 | 144.18 | 220 | 1451 | 0 | 0 | 4 | 53
15:30 | 3305.5 | 1521 | 929.5 | 38 | 76 | 1186.5 | 221 | 4103 | 100.86 | 193.5 | 1326.5 | 0 | 0 | 4.5 | 45
16:00 | 3276 | 1516 | 930 | 38 | 76 | 1200 | 221 | 4076 | 57.54 | 167 | 1202 | 0 | 0 | 5 | 37
16:30 | 3309 | 1522.5 | 929.5 | 38 | 77 | 1180.5 | 221 | 4082.5 | 31.73 | 184.5 | 1257.5 | 0 | 0 | 5 | 46
17:00 | 3342 | 1529 | 929 | 38 | 78 | 1161 | 221 | 4089 | 5.92 | 202 | 1313 | 0 | 0 | 5 | 55
17:30 | 3418 | 1550.5 | 929.5 | 38 | 81 | 1189.5 | 220 | 4299 | 2.96 | 447 | 1602.95 | 0 | 0 | 2.5 | 52.5
18:00 | 3494 | 1572 | 930 | 38 | 84 | 1218 | 219 | 4509 | 0 | 692 | 1892.9 | 0 | 0 | 0 | 50
18:30 | 3388.5 | 1546.5 | 929.5 | 38 | 83 | 1211 | 219 | 4564 | 0 | 750 | 1934 | 0 | 0 | 0 | 50.5
19:00 | 3283 | 1521 | 929 | 38 | 82 | 1204 | 219 | 4619 | 0 | 808 | 1975.1 | 0 | 0 | 0 | 51
19:30 | 3269 | 1525 | 929 | 38 | 76 | 1209 | 219 | 4630 | 0 | 736 | 1831.6 | 0 | 0 | 0 | 36
20:00 | 3266 | 1534.8 | 930 | 38 | 82 | 1202 | 218 | 4646 | 0 | 737 | 1829.1 | 0 | 0 | 0 | 46
20:30 | 3077.5 | 1631.9 | 930 | 38 | 79 | 1206 | 218 | 4622.5 | 0 | 658.2 | 1714.55 | 0 | 0 | 0 | 110
21:00 | 2889 | 1729 | 930 | 38 | 76 | 1210 | 218 | 4599 | 0 | 579.4 | 1600 | 0 | 0 | 0 | 174
21:30 | 2953.5 | 1833.75 | 930 | 38 | 80 | 1210.5 | 218.5 | 4613 | 0 | 440.2 | 1352.5 | 0 | 0 | 0 | 148.5
22:00 | 3018 | 1938.5 | 930 | 38 | 84 | 1211 | 219 | 4627 | 0 | 301 | 1105 | 0 | 0 | 0 | 123
22:30 | 2943 | 1944.5 | 929.5 | 38 | 84 | 1211.5 | 219 | 4629.5 | 0 | 300.5 | 1086.25 | 0 | 0 | 0 | 119.5
23:00 | 2868 | 1950.5 | 929 | 38 | 84 | 1212 | 219 | 4632 | 0 | 300 | 1067.5 | 0 | 0 | 0 | 116
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 06:00 | 368 | 12:00 | Payra | 409 | 06:00 | 401 | 12:00
Ashuganj | 401 | 0:00 | 376 | 12:00 | Rahanpur | 407 | 02:00 | 399 | 12:00
Bhulta | 394 | 02:00 | 369 | 12:00 | Rampal | 400 | 06:00 | 390 | 08:00
Bibiana | 385 | 06:00 | 379 | 12:00
BIPTC | 403 | 04:00 | 393 | 13:00
Bogura | 394 | 02:00 | 382 | 12:00
Gopalganj | 391 | 08:00 | 383 | 18:00
Kaliakoir | 368 | 02:00 | 360 | 12:00
Madunaghat | 391 | 03:00 | 387 | 22:00
Meghnaghat | 379 | 03:00 | 372 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 21:00 | 216 | 12:00 | Kaliakoir | 230 | 02:00 | 222 | 12:00
AKSML | 229 | 13:00 | 224 | 22:00 | Keranigonj | 222 | 05:00 | 214 | 12:00
Aminbazar | 226 | 04:00 | 218 | 12:00 | Khulna(S) | 231 | 15:00 | 222 | 00:00
Ashuganj | 226 | 06:00 | 218 | 12:00 | Madunaghat | 231 | 13:00 | 227 | 22:00
Ashuganj-400 | 226 | 06:00 | 218 | 12:00 | Madunaghat-400 | 231 | 01:00 | 228 | 22:00
Baghabari | 233 | 04:00 | 226 | 12:00 | Maniknagar | 215 | 02:00 | 210 | 12:00
Barapukuria | 222 | 00:00 | 209 | 07:00 | Meghnaghat | 224 | 04:00 | 220 | 10:00
Barapukuria-230 | 222 | 00:00 | 209 | 07:00 | Meghnaghat-400 | 220 | 02:00 | 215 | 12:00
Barishal | 231 | 06:00 | 226 | 22:00 | Mirsorai | 228 | 18:00 | 219 | 22:00
Bheramara | 231 | 06:00 | 223 | 12:00 | Rajshahi | 230 | 06:00 | 222 | 12:00
Bhulta | 225 | 02:00 | 208 | 12:00 | Rampal | 230 | 06:00 | 222 | 00:00
Bibiana | 226 | 06:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 234 | 06:00 | 224 | 12:00 | Rampura | 224 | 02:00 | 206 | 11:00
Bogura | 239 | 01:00 | 232 | 08:00 | Shikalbaha | 230 | 17:00 | 225 | 22:00
Bogura-400 | 240 | 02:00 | 232 | 08:00 | Shyampur | 220 | 05:00 | 213 | 12:00
Borhanuddin | 235 | 07:00 | 231 | 22:00 | Siddhirganj | 218 | 23:00 | 214 | 10:00
BSRM | 227 | 18:30 | 219 | 22:00 | Sirajgonj | 238 | 02:00 | 233 | 12:00
Cumilla(N) | 220 | 05:00 | 216 | 10:00 | Sreepur | 225 | 23:00 | 216 | 12:00
Faridpur | 228 | 06:00 | 223 | 22:00 | Tongi | 225 | 18:30 | 215 | 11:00
Fenchuganj | 228 | 06:00 | 225 | 00:00
Ghorashal | 230 | 00:00 | 225 | 01:00
Ghorashal-230 | 224 | 02:00 | 211 | 12:00
Gopalganj | 230 | 06:00 | 225 | 12:00
GPH | 228 | 00:00 | 226 | 01:00
Haripur | 217 | 03:00 | 214 | 00:00
Hasnabad | 222 | 21:00 | 213 | 12:00
Hathazari | 229 | 17:00 | 224 | 22:00
Ishurdi | 234 | 06:00 | 227 | 11:00
Jhenaidah | 230 | 06:00 | 221 | 12:00
Kachua | 228 | 07:00 | 216 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 02:00 | 124 | 12:00 | Lalmonirhat | 130 | 00:00 | 120 | 07:00
Agargaon | 132 | 05:00 | 125 | 12:00 | Madanganj | 129 | 08:00 | 124 | 19:00
Agrabad | 131 | 07:00 | 127 | 22:00 | Madaripur | 133 | 08:00 | 130 | 00:00
AKS | 129 | 00:00 | 127 | 20:00 | Madartek | 136 | 02:00 | 123 | 12:00
Aminbazar | 133 | 20:00 | 127 | 12:00 | Madunaghat | 134 | 13:00 | 131 | 22:00
Amnura | 136 | 00:00 | 128 | 12:00 | Magura | 136 | 15:00 | 128 | 00:00
Ashuganj | 136 | 06:00 | 133 | 00:00 | Mahasthangarh | 133 | 01:00 | 127 | 07:00
Bagerhat | 129 | 14:00 | 119 | 00:00 | Maijdee | 132 | 08:00 | 124 | 22:00
Bajitpur | 127 | 07:00 | 123 | 10:00 | Manikganj | 130 | 01:00 | 122 | 18:00
Bakulia | 132 | 02:00 | 129 | 09:00 | Maniknagar | 131 | 05:00 | 125 | 12:00
Banani | 138 | 02:00 | 124 | 12:00 | Matarbari | 120 | 08:00 | 107 | 19:30
Bangabhaban | 130 | 03:00 | 125 | 12:00 | Matuail | 128 | 02:00 | 123 | 12:00
Barapukuria | 136 | 00:00 | 125 | 07:00 | Metrorail_Motijheel | 132 | 05:00 | 125 | 12:00
Barguna | 134 | 06:00 | 131 | 00:00 | Metrorail_Uttara | 135 | 02:00 | 127 | 12:00
Barishal | 134 | 00:00 | 129 | 20:00 | Millgate | 135 | 01:00 | 127 | 12:00
Barishal-230 | 133 | 00:00 | 128 | 23:00 | Mirpur | 134 | 21:00 | 126 | 11:00
Baroaulia | 131 | 00:00 | 129 | 20:00 | Mirzapur | 130 | 21:00 | 122 | 12:00
Baroirhat | 130 | 08:00 | 125 | 22:00 | Mithapukur | 135 | 02:00 | 124 | 08:00
Bashundhara | 137 | 01:00 | 123 | 12:00 | MI_Cement | 128 | 20:00 | 124 | 00:00
BashundharaCement | 128 | 00:00 | 124 | 18:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 128 | 07:00 | 123 | 18:00 | Mogbazar | 139 | 06:00 | 125 | 11:00
Benapole | 134 | 17:00 | 123 | 00:00 | Mongla | 129 | 15:00 | 120 | 00:00
Bhaluka | 129 | 15:00 | 121 | 12:00 | Motijheel | 130 | 03:00 | 125 | 12:00
Bhandaria | 130 | 08:00 | 121 | 22:00 | Muktagacha | 131 | 15:00 | 121 | 12:00
Bhangura | 132 | 03:00 | 127 | 12:00 | Munshiganj | 128 | 21:00 | 123 | 00:00
Bheramara | 137 | 05:00 | 134 | 12:00 | Muradnagar | 125 | 03:00 | 118 | 22:00
Bheramara(GK) | 137 | 04:00 | 134 | 12:00 | Mymensingh | 133 | 15:00 | 115 | 12:00
Bhulta | 125 | 21:00 | 121 | 01:00 | Naogaon | 131 | 01:00 | 125 | 11:00
Bog-Sherpur | 134 | 01:00 | 128 | 12:00 | Narail | 137 | 06:00 | 128 | 00:00
Bogura | 135 | 01:00 | 130 | 08:00 | Narinda | 0 | 00:00 | N/A | N/A
Bogura-230 | 136 | 01:00 | 130 | 08:00 | Narshingdi | 135 | 23:00 | 118 | 00:00
Brahmanbaria | 130 | 06:00 | 126 | 00:00 | Natore | 134 | 04:00 | 129 | 12:00
Cantonment | 132 | 06:00 | 126 | 11:00 | Nawabganj | 131 | 06:00 | 126 | 11:00
Chandina | 129 | 07:00 | 125 | 22:00 | Netrakona | 122 | 15:00 | 115 | 14:00
Chandpur | 139 | 13:00 | 129 | 22:00 | New | 135 | 05:00 | 129 | 12:00
Chandraghona | 134 | 02:00 | 132 | 19:30 | Niamatpur | 138 | 03:00 | 134 | 17:00
Chapai | 137 | 02:00 | 134 | 11:00 | Noapara | 133 | 06:00 | 125 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 21:00 | 118 | 12:00 | Pabna | 135 | 06:00 | 131 | 12:00
Chauddagram | 129 | 17:00 | 124 | 22:00 | Palashbari | 132 | 02:00 | 123 | 07:00
Chhatak | 127 | 04:00 | 121 | 00:00 | Panchagarh | 141 | 02:00 | 124 | 07:00
Chowmuhani | 132 | 07:00 | 124 | 23:00 | Patiya | 130 | 02:00 | 127 | 19:30
Chuadanga | 134 | 07:00 | 124 | 00:00 | Patuakhali | 135 | 10:00 | 132 | 01:00
Coxsbazar | 117 | 10:00 | 107 | 19:30 | Payra | 136 | 02:00 | 134 | 00:00
Cumilla(N) | 128 | 01:00 | 125 | 10:00 | PHP | 130 | 08:00 | 124 | 22:00
Cumilla(S) | 132 | 05:00 | 124 | 22:00 | Postogola | 132 | 21:00 | 126 | 12:00
Daganbhuiyan | 126 | 20:00 | 124 | 22:00 | Purbachal | 137 | 01:00 | 123 | 12:00
Daudkandi | 132 | 00:00 | 115 | 19:30 | Purbasadipur | 135 | 02:00 | 120 | 07:00
DhakaUniversity | 137 | 05:00 | 125 | 11:00 | Rahanpur | 139 | 01:00 | 137 | 10:00
Dhamrai | 135 | 21:00 | 124 | 12:00 | Rahanpur-400 | 140 | 01:00 | 137 | 12:00
Dhanmondi | 137.7 | 06:00 | 122 | 12:00 | Rahim | 126 | 05:00 | 123 | 10:00
Dohazari | 126 | 09:00 | 122 | 22:00 | Rajbari | 134 | 06:00 | 129 | 00:00
Faridpur | 135 | 06:00 | 131 | 00:00 | Rajendrapur | 135 | 21:00 | 120 | 11:00
Fatullah | 134 | 02:00 | 124 | 12:00 | Rajshahi | 133 | 19:30 | 128 | 12:00
Fenchuganj | 135 | 06:00 | 132 | 00:00 | Rajshahi-230 | 133 | 06:00 | 127 | 12:00
Feni | 130 | 14:00 | 125 | 00:00 | Ramganj | 133 | 13:00 | 125 | 22:00
Ghatail | 128 | 15:00 | 118 | 12:00 | Rampur | 131 | 07:00 | 128 | 19:30
Ghorashal | 136 | 23:00 | 128 | 11:00 | Rampura | 137 | 02:00 | 124 | 11:00
Goalpara | 133 | 14:00 | 126 | 00:00 | Rangamati | 133 | 03:00 | 130 | 22:00
Gollamari | 133 | 14:00 | 127 | 00:00 | Rangpur | 134 | 00:00 | 124 | 07:00
Gopalganj | 132 | 06:00 | 128 | 01:00 | Ruppur | 137 | 05:00 | 134 | 12:00
Gopalganj-400 | 135 | 06:00 | 131 | 18:00 | Saidpur | 134 | 01:00 | 121 | 08:00
Gulshan | 140 | 12:00 | 125 | 11:00 | Satkhira | 132 | 15:00 | 120 | 00:00
Halishahar | 132 | 02:00 | 128 | 22:00 | Satmasjid | 132 | 05:00 | 125 | 12:00
Haripur | 127 | 19:30 | 124 | 10:00 | Savar | 135 | 21:00 | 125 | 12:00
HaripurSBU | 127 | 19:30 | 125 | 00:00 | SevenRings | 137 | 23:00 | 127 | 10:00
Hasnabad | 131 | 04:00 | 126 | 11:00 | ShahCement | 128 | 21:00 | 123 | 09:00
Hathazari | 134 | 00:00 | 131 | 04:00 | Shahjadpur | 136 | 04:00 | 132 | 18:00
Ishurdi | 138 | 06:00 | 134 | 12:00 | Shahjibazar | 132 | 08:00 | 126 | 00:00
Jaldhaka | 132 | 13:00 | 118 | 08:00 | Shahmirpur | 132 | 01:00 | 129 | 19:30
Jamalpur | 138 | 15:00 | 120 | 00:00 | Shariatpur | 133 | 06:00 | 128 | 22:00
Jashore | 135 | 16:00 | 124 | 12:00 | Sherpur | 137 | 15:00 | 117 | 00:00
Jhenaidah | 137 | 05:00 | 123 | 19:30 | Shikalbaha | 122 | 00:00 | 119 | 04:00
Jhenaidah-230 | 137 | 06:00 | 130 | 12:00 | Shikalbaha-230 | 133 | 02:00 | 130 | 05:00
Joydebpur | 142 | 23:00 | 125 | 09:00 | Shitalakhya | 130 | 05:00 | 124 | 00:00
Joypurhat | 128 | 20:00 | 123 | 12:00 | Sholosohor | 133 | 00:00 | 130 | 23:00
Juldah | 131 | 00:00 | 128 | 23:00 | Shyampur | 132 | 05:00 | 130 | 00:00
Kabirpur | 136 | 21:00 | 125 | 18:00 | Shyampur-230 | 134 | 02:00 | 129 | 12:00
Kachua | 135 | 07:00 | 128 | 22:00 | Siddhirganj | 128 | 20:00 | 124 | 10:00
Kaliakoir | 133 | 02:00 | 128 | 11:00 | Sirajganj | 132 | 01:00 | 127 | 10:00
Kallyanpur | 135 | 21:00 | 126 | 11:00 | Sonargaon | 126 | 21:00 | 121 | 12:00
Kalurghat | 134 | 17:00 | 131 | 22:00 | Sreemongol | 131 | 07:00 | 126 | 00:00
Kamrangirchar | 132 | 07:00 | 124 | 12:00 | Sreepur | 131 | 19:00 | 124 | 11:00
Kaptai | 135 | 1:00 | 134 | 21:00 | Srinagar | 132 | 21:00 | 126 | 12:00
Kasba | 125 | 08:00 | 117 | 22:00 | SSM | 135 | 00:00 | 132 | 22:00
Kazla | 130 | 05:00 | 125 | 12:00 | Sunamganj | 124 | 05:00 | 119 | 00:00
Keranigonj | 132 | 05:00 | 125 | 12:00 | Sylhet | 129 | 07:00 | 125 | 18:00
Khagrachori | 132 | 07:00 | 129 | 19:30 | Sylhet-132 | 129 | 06:00 | 127 | 00:00
Khulna | 132 | 15:00 | 125 | 00:00 | Tangail | 127 | 05:00 | 118 | 12:00
Khulna(S) | 134 | 15:00 | 127 | 00:00 | Taraganj | 134 | 03:00 | 121 | 11:00
Khulshi | 130 | 15:00 | 127 | 22:00 | Thakurgaon | 139 | 02:00 | 120 | 08:00
Kishoreganj | 128 | 15:00 | 122 | 10:00 | TK | 133 | 01:00 | 130 | 23:00
Kodda | 139 | 23:00 | 119 | 10:00 | Tongi | 135 | 17:00 | 131 | 11:00
KSRM | 134 | 01:00 | 129 | 22:00 | Ullahpara | 133 | 01:00 | 128 | 12:00
Kulaura | 134 | 07:00 | 130 | 18:30 | Ullon | 137 | 02:00 | 123 | 12:00
Kurigram | 133 | 03:00 | 120 | 07:00 | Uttara | 133 | 21:00 | 126 | 11:00
Kushtia | 135 | 05:00 | 131 | 12:00 | UttaraNew | 135 | 02:00 | 127 | 12:00
Laksam | 134 | 07:00 | 127 | 22:00 | Zigatola | 131 | 04:00 | 126 | 11:00
Lakshmipur | 132 | 08:00 | 124 | 23:00
Lalbag | 131 | 05:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division