## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-10-2025 | during | 01-11-2025 | during | 01-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 190 | 190 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 160 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 410 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 340 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 10 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 134 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 30 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 14 | 24.75 | 24.75 | 24.75 | 24.75 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 17 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 98 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 70 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 86 | 162 | 162 | 108 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 7 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 440 | 420 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 70 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1599 | 2389 | 5736.15 | 5796.15 | 5398.69 | 5475.69
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 13 | 0 | 13 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 219 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 90 | 90 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 46 | 70 | 70 | 70 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 24 | 29 | 35 | 35 | 35 | 35 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 97 | 102 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.27 | 0 | 3.22 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 49 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 32 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 17 | 159 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1004 | 1146 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 1 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 375 | 315 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1981.27 | 2245 | 3072.08 | 3055.86 | 2388.72 | 2514.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 347 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 310 | 301 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 305 | 320 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 33 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 45 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 101 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 81 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 64 | 80 | 160 | 160 | 88 | 88 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 31 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 72 | 0 | 72 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1336 | 1485 | 2623.56 | 2551.56 | 2342.86 | 2279.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-10-2025 | during | 01-11-2025 | during | 01-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 126 | 158 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 47 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.79 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 2 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 274.79 | 276 | 381.2 | 330 | 327.7 | 276.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 146 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 9 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 381 | 325 | 325 | 325 | 325 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1191 | 1200 | 1197 | 1197 | 1163 | 1163
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 364 | 372 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 851 | 1100 | 0 | 0 | 1100 | 1100 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2253 | 2412 | 2070 | 1982 | 2745 | 2657
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 304 | 463 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 724 | 1110 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 140 | 110 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1498.64 | 2013 | 1840 | 1839 | 1699 | 1698
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 35 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 174 | 167 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 347 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 98 | 98 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.59 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 624.57 | 752 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 69.18 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 57 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1379.34 | 1376 | 2492.59 | 2327.99 | 2318.81 | 2154.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.4 | 0 | 1.8 | 0 | 1.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 113 | 0 | 122.7 | 0 | 122.7 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 114.4 | 105 | 402.5 | 248 | 362.5 | 208
System Total |  |  |  |  | 28823.2 | 28364.095 | 11627.44 | 13501 | 19815.08 | 19327.56 | 18746.28 | 18426.76
Forecast Scenario (01-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13110 |  | 0 |  | 13110
|  |  |  | 1:00 | 12790 |  | 0 |  | 12790
|  |  |  | 2:00 | 12130 |  | 0 |  | 12130
|  |  |  | 3:00 | 11690 |  | 0 |  | 11690
|  |  |  | 4:00 | 11410 |  | 0 |  | 11410
|  |  |  | 5:00 | 11070 |  | 0 |  | 11070
|  |  |  | 6:00 | 10790 |  | 0 |  | 10790
|  |  |  | 7:00 | 10960 |  | 0 |  | 10960
|  |  |  | 8:00 | 11210 |  | 0 |  | 11210
|  |  |  | 9:00 | 10950 |  | 0 |  | 10950
|  |  |  | 10:00 | 10990 |  | 0 |  | 10990
|  |  |  | 11:00 | 11400 |  | 0 |  | 11400
|  |  |  | 12:00 | 11940 |  | 0 |  | 11940
|  |  |  | 13:00 | 12440 |  | 0 |  | 12440
|  |  |  | 14:00 | 12520 |  | 0 |  | 12520
|  |  |  | 15:00 | 12710 |  | 0 |  | 12710
|  |  |  | 16:00 | 12440 |  | 0 |  | 12440
|  |  |  | 17:00 | 12390 |  | 0 |  | 12390
|  |  |  | 18:00 | 14330 |  | 0 |  | 14330
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 14630 |  | 0 |  | 14630
|  |  |  | 19:30 | 14560 |  | 0 |  | 14560
|  |  |  | 20:00 | 14510 |  | 0 |  | 14510
|  |  |  | 21:00 | 14240 |  | 0 |  | 14240
|  |  |  | 22:00 | 14230 |  | 0 |  | 14230
|  |  |  | 23:00 | 14080 |  | 0 |  | 14080
Probable Maximum Temperature: |  |  | 31.50°C
Probable Maximum Demand at Day Peak: |  |  | 11940.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14630.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14630.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 298.96 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:37 hrs on 01-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-10-2025 | [28 empty] | Date: | 31-10-2025 | [28 empty] | Date: | 31-10-2025 | [28 empty] | Date: | 31-10-2025 | [28 empty] | Date: | 31-10-2025 | [14 empty] | Date: | 31-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [14 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 8 | 0 | 0 | 240 | 0 | 0 | 387 | 0 | 0 | 0 | 17 | 87 | 60 | 45 | 30 | 0 | 126 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 35 | 20.5 | 20 | 0 | 400 | 15 | 16 | 102 | 0 | 0 | 50 | 8 | 0 | 12 | 12 | 0 | 218 | 34 | 30 | 650 | 0 | 0 | 0 | 0 | 29 | 225 | 0 | 0 | 0 | 1150 | 0 | 51 | 50 | 0 | 345 | 320 | 260 | 46 | 0 | 37 | 31 | 105 | 48 | 0 | 19 | 0 | 84 | 8 | 0 | 29 | 310 | 0 | 371 | 0 | 68 | 156 | 10 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 49 | 49 | 99 | 0 | 0 | 6 | 7404.5 | 904 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1135 | 0 | 749 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 110 | 220 | 0 | 402 | 1090 | 10 | 5932 | 13336.5 | 103.3
01:00 | 0 | 35 | 8 | 0 | 0 | 240 | 0 | 0 | 387 | 0 | 0 | 0 | 17 | 87 | 45 | 45 | 30 | 0 | 54 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 17 | 21 | 20 | 0 | 400 | 15 | 16 | 103 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 218 | 34 | 35 | 650 | 0 | 0 | 0 | 0 | 35 | 226 | 0 | 0 | 0 | 1140 | 0 | 51 | 50 | 0 | 345 | 320 | 260 | 46 | 0 | 37 | 31 | 104 | 49 | 0 | 19 | 0 | 78 | 8 | 0 | 29 | 310 | 0 | 352 | 0 | 67 | 156 | 10 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 49 | 49 | 105 | 0 | 0 | 1 | 7253 | 904 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1137 | 0 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 110 | 220 | 0 | 350 | 1096 | 10 | 5732 | 12985 | 103.28
02:00 | 0 | 17 | 8 | 0 | 0 | 240 | 0 | 0 | 386 | 0 | 0 | 0 | 17 | 65 | 15 | 0 | 30 | 0 | 35 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 17 | 21 | 20 | 0 | 400 | 0 | 0 | 71 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0 | 218 | 34 | 35 | 650 | 0 | 0 | 0 | 0 | 51 | 225 | 0 | 0 | 0 | 1112 | 0 | 51 | 0 | 0 | 345 | 320 | 260 | 46 | 0 | 37 | 30 | 103 | 47 | 0 | 19 | 0 | 78 | 0 | 0 | 29 | 315 | 0 | 356 | 0 | 67 | 154 | 10 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 48 | 49 | 106 | 0 | 0 | 6 | 6976 | 904 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 110 | 220 | 0 | 350 | 1090 | 0 | 5562 | 12538 | 103.26
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 17 | 51 | 0 | 0 | 30 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 17 | 21 | 20 | 0 | 400 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 219 | 34 | 35 | 650 | 0 | 0 | 0 | 0 | 51 | 225 | 0 | 0 | 0 | 1097 | 0 | 51 | 0 | 0 | 360 | 320 | 260 | 46 | 0 | 37 | 21 | 103 | 47 | 0 | 19 | 0 | 78 | 0 | 0 | 29 | 305 | 0 | 378 | 0 | 67 | 154 | 10 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 49 | 49 | 106 | 0 | 0 | 6 | 6636 | 904 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 110 | 220 | 0 | 303 | 1085 | 0 | 5484 | 12120 | 103.24
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 17 | 21 | 20 | 0 | 400 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 51 | 225 | 0 | 0 | 0 | 1090 | 0 | 51 | 0 | 0 | 360 | 320 | 260 | 46 | 0 | 37 | 18 | 104 | 34 | 0 | 19 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 356 | 0 | 67 | 153 | 10 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 49 | 48 | 106 | 0 | 0 | 6 | 6485 | 904 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 979 | 0 | 749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 110 | 220 | 0 | 303 | 1000 | 0 | 5342 | 11827 | 103.22
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 15 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 17 | 21 | 20 | 0 | 400 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 17 | 225 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 0 | 360 | 320 | 260 | 46 | 0 | 37 | 0 | 104 | 0 | 0 | 19 | 0 | 76 | 0 | 0 | 0 | 305 | 0 | 390 | 0 | 67 | 156 | 6 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 49 | 48 | 106 | 0 | 0 | 6 | 6421 | 904 | 387 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 905 | 0 | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 110 | 220 | 0 | 306 | 900 | 0 | 5191 | 11612 | 103.2
06:00 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 17 | 52 | 0 | 0 | 15 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 17 | 21 | 20 | 0 | 385 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 222 | 0 | 39 | 650 | 0 | 0 | 0 | 0 | 15 | 226 | 0 | 0 | 0 | 956 | 0 | 51 | 0 | 0 | 360 | 320 | 260 | 46 | 0 | 37 | 0 | 104 | 0 | 0 | 19 | 0 | 62 | 0 | 0 | 0 | 305 | 0 | 358 | 0 | 67 | 155 | 6 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 48 | 49 | 107 | 0 | 0 | 6 | 6240 | 903 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 110 | 220 | 0 | 303 | 800 | 0 | 4970 | 11210 | 103.18
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 112 | 0 | 0 | 15 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 5 | 17 | 21 | 20 | 0 | 313 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 30 | 650 | 0 | 0 | 0 | 0 | 14 | 224 | 0 | 0 | 0 | 850 | 4 | 51 | 0 | 0 | 300 | 280 | 260 | 46 | 0 | 37 | 0 | 104 | 0 | 0 | 19 | 0 | 70 | 0 | 15 | 0 | 310 | 0 | 386 | 0 | 67 | 151 | 6 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 49 | 49 | 112 | 0 | 5.01 | 6 | 6057.01 | 903 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.32 | 765 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 6 | 0 | 0 | 2.75 | 160 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0.32 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 31 | 0.05 | 0 | 150 | 110 | 220 | 0 | 303 | 700 | 0 | 4806.84 | 10863.85 | 103.16
08:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 17 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 13 | 35 | 21 | 20 | 0 | 400 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.35 | 220 | 0 | 30 | 650 | 0 | 0 | 0 | 0 | 14 | 222 | 0 | 0 | 0 | 840 | 10 | 51 | 0 | 0 | 300 | 280 | 260 | 46 | 0 | 37 | 0 | 104 | 0 | 0 | 19 | 0 | 64 | 0 | 39 | 0 | 310 | 0 | 356 | 0 | 67 | 155 | 6 | 0 | 33 | 30 | 0 | 0 | 161 | 0 | 49 | 48 | 137 | 0 | 14.38 | 3 | 6151.73 | 902 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 763 | 0 | 673.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.77 | 21 | 0 | 0 | 10.19 | 165 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0.66 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 67 | 0.21 | 0 | 150 | 110 | 220 | 0 | 305 | 620 | 0 | 4702.46 | 10854.19 | 103.14
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 17 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 23 | 35 | 19 | 20 | 0 | 350 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.2 | 220 | 0 | 30 | 650 | 0 | 0 | 0 | 0 | 14 | 218 | 0 | 0 | 0 | 829 | 15 | 51 | 0 | 0 | 270 | 280 | 260 | 46 | 0 | 37 | 0 | 103 | 0 | 0 | 19 | 0 | 66 | 0 | 49 | 0 | 305 | 0 | 336 | 0 | 67 | 145 | 6 | 0 | 77 | 30 | 0 | 0 | 161 | 0 | 49 | 48 | 144 | 0 | 12.53 | 6 | 6025.73 | 902 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62 | 747 | 0 | 577.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.38 | 71 | 0 | 0 | 20.69 | 159 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 2.64 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 75 | 0.44 | 0 | 150 | 110 | 180 | 0 | 304 | 582 | 0 | 4645.08 | 10670.81 | 103.12
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 17 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 25 | 47 | 19 | 20 | 0 | 300 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.87 | 219 | 0 | 30 | 550 | 0 | 0 | 0 | 0 | 15 | 218 | 0 | 0 | 0 | 805 | 18 | 51 | 0 | 0 | 270 | 280 | 260 | 44 | 0 | 34 | 0 | 100 | 0 | 0 | 19 | 0 | 60 | 0 | 65 | 0 | 310 | 0 | 332 | 0 | 67 | 142 | 6 | 0 | 77 | 30 | 0 | 0 | 161 | 0 | 49 | 48 | 121 | 1 | 26.06 | 6 | 5857.93 | 902 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 757 | 0 | 549.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.36 | 104 | 0 | 0 | 54.19 | 164 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 4.45 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 56 | 0.65 | 0 | 150 | 110 | 180 | 0 | 301 | 585 | 0 | 4712.87 | 10570.8 | 103.11
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 10 | 17 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 34 | 52 | 19 | 20 | 0 | 365 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.22 | 219 | 0 | 28 | 465 | 0 | 0 | 0 | 0 | 16 | 217 | 0 | 0 | 0 | 907 | 13 | 51 | 0 | 0 | 300 | 320 | 295 | 45 | 0 | 30 | 0 | 100 | 0 | 0 | 19 | 0 | 58 | 0 | 68 | 0 | 315 | 0 | 335 | 0 | 67 | 150 | 6 | 0 | 77 | 30 | 0 | 0 | 160 | 0 | 49 | 48 | 126 | 1 | 35.95 | 6 | 6182.17 | 902 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64 | 788 | 0 | 528.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 54 | 0 | 0 | 43.95 | 169 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 4.61 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.3 | 70 | 0.29 | 0 | 149 | 110 | 220 | 0 | 304 | 600 | 0 | 4816.06 | 10998.23 | 103.1
12:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 98 | 0 | 15 | 10 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 7 | 70 | 19 | 20 | 0 | 440 | 0 | 0 | 97 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 3.27 | 219 | 0 | 24 | 375 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1004 | 18 | 51 | 0 | 0 | 305 | 335 | 310 | 44 | 0 | 36 | 0 | 100 | 0 | 0 | 19 | 0 | 64 | 0 | 72 | 0 | 315 | 0 | 387 | 0 | 67 | 146 | 6 | 0 | 80 | 30 | 0 | 0 | 160 | 2 | 49 | 48 | 126 | 2 | 41.79 | 6 | 6382.06 | 902 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98 | 851 | 0 | 624.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 57 | 0 | 0 | 69.18 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.59 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 113 | 0.64 | 0 | 140 | 110 | 220 | 0 | 304 | 724 | 0 | 5245.38 | 11627.44 | 103.1
13:00 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17.5 | 17 | 112 | 0 | 15 | 15 | 0 | 12 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 30 | 70 | 19 | 12 | 0 | 450 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.91 | 219 | 10 | 42 | 320 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1150 | 17 | 51 | 0 | 0 | 393 | 339 | 330 | 44 | 0 | 35 | 0 | 100 | 0 | 0 | 19 | 0 | 80 | 0 | 69 | 0 | 320 | 0 | 386 | 0 | 67 | 153 | 6 | 0 | 80 | 30 | 0 | 0 | 160 | 17 | 48 | 49 | 139 | 1 | 46.94 | 6 | 6722.35 | 902 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24.24 | 1029 | 0 | 753.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 26 | 0 | 0 | 35.22 | 186 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 5.43 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.3 | 73 | 0.66 | 0 | 140 | 110 | 220 | 0 | 403 | 830 | 0 | 5546.39 | 12268.74 | 103.09
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17.5 | 17 | 105 | 0 | 0 | 0 | 0 | 15 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 29 | 70 | 5 | 12 | 0 | 440 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.36 | 220 | 15 | 42 | 314 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1005 | 15 | 51 | 0 | 0 | 350 | 334 | 330 | 43 | 0 | 32 | 0 | 100 | 0 | 0 | 19 | 0 | 78 | 0 | 60 | 0 | 305 | 0 | 390 | 0 | 67 | 147 | 7 | 0 | 80 | 30 | 0 | 0 | 160 | 17 | 48 | 49 | 138 | 2 | 34.58 | 6 | 6428.44 | 903 | 359 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35.29 | 960 | 0 | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.03 | 60 | 0 | 0 | 28.53 | 165 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 4.74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.3 | 46 | 0.6 | 0 | 140 | 110 | 180 | 0 | 303 | 900 | 0 | 5329.49 | 11757.93 | 103.09
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 17.5 | 17 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 20 | 35 | 18 | 12 | 0 | 500 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.55 | 219 | 0 | 31 | 314 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1033 | 11 | 51 | 0 | 0 | 393 | 340 | 294 | 43 | 0 | 35 | 0 | 99 | 0 | 0 | 19 | 0 | 78 | 0 | 45 | 0 | 310 | 0 | 361 | 0 | 67 | 149 | 7 | 0 | 79 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 153 | 1 | 16.73 | 6 | 6389.78 | 903 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 39 | 969 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 28 | 0 | 0 | 36.55 | 173 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 3.52 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 61 | 0.09 | 0 | 140 | 110 | 190 | 0 | 303 | 915 | 0 | 5328.46 | 11718.24 | 103.08
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17.5 | 17 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 8 | 35 | 18 | 12 | 0 | 500 | 0 | 0 | 85 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0.66 | 220 | 0 | 32 | 315 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1003 | 5 | 51 | 0 | 0 | 393 | 342 | 283 | 43 | 0 | 35 | 0 | 99 | 0 | 0 | 19 | 0 | 72 | 0 | 22 | 0 | 310 | 0 | 336 | 0 | 67 | 139 | 7 | 0 | 79 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 153 | 0 | 5.79 | 6 | 6218.95 | 902 | 359 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29.52 | 974 | 0 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.93 | 20 | 0 | 0 | 3.39 | 164 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0.27 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.1 | 23 | 0.05 | 0 | 140 | 110 | 190 | 0 | 303 | 900 | 0 | 5144.26 | 11363.21 | 103.08
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17.5 | 17 | 96 | 15 | 15 | 0 | 17 | 30 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 1 | 35 | 16 | 12 | 0 | 450 | 1 | 0 | 95 | 0 | 6 | 3 | 2 | 0 | 24 | 12 | 0.03 | 220 | 0 | 33 | 315 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 985 | 0 | 51 | 7 | 0 | 355 | 345 | 283 | 43 | 0 | 32 | 1 | 100 | 8 | 0 | 7 | 0 | 70 | 0 | 1 | 0 | 315 | 0 | 313 | 0 | 67 | 145 | 7 | 0 | 82 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 154 | 0 | 0.82 | 6 | 6176.35 | 902 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.35 | 956 | 0 | 628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 1 | 0 | 0 | 0.82 | 170 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0.07 | 0 | 0 | 24 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 140 | 110 | 190 | 0 | 303 | 925 | 0 | 5124.53 | 11300.88 | 103.07
18:00 | 0 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17.5 | 28 | 106 | 45 | 145 | 29 | 35 | 118 | 0 | 370 | 0 | 0 | 0 | 17 | 7 | 130 | 0 | 0 | 142 | 16 | 18 | 0 | 450 | 23 | 0 | 88 | 0 | 5 | 50 | 40 | 0 | 24 | 12 | 0 | 220 | 24 | 34 | 315 | 16 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1150 | 0 | 51 | 48 | 0 | 325 | 346 | 301 | 45 | 0 | 35 | 38 | 100 | 69 | 0 | 19 | 17 | 74 | 0 | 0 | 10 | 315 | 0 | 338 | 0 | 67 | 147 | 9 | 0 | 64 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 155 | 0 | 0 | 6 | 7260.5 | 902 | 363 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 0 | 753 | 0 | 0 | 0 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 70 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 110 | 220 | 0 | 469 | 960 | 0 | 5829 | 13089.5 | 103.07
19:00 | 0 | 70 | 17 | 110 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 35 | 35 | 149 | 30 | 95 | 30 | 35 | 126 | 0 | 370 | 0 | 0 | 0 | 17 | 80 | 97 | 0 | 0 | 142 | 16 | 20 | 0 | 450 | 30 | 0 | 98 | 0 | 7 | 50 | 46 | 0 | 24 | 12 | 0 | 220 | 48 | 35 | 315 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1140 | 0 | 51 | 50 | 0 | 300 | 345 | 301 | 45 | 0 | 36 | 56 | 100 | 125 | 0 | 19 | 0 | 80 | 0 | 0 | 28 | 305 | 0 | 365 | 0 | 67 | 150 | 9 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 155 | 0 | 0 | 6 | 7558 | 903 | 356 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 0 | 757 | 0 | 0 | 0 | 0 | 35 | 0 | 58 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 110 | 220 | 0 | 462 | 1072 | 0 | 5853 | 13411 | 103.06
19:30 | 0 | 70 | 17 | 140 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 35 | 35 | 149 | 30 | 95 | 30 | 35 | 88 | 0 | 370 | 0 | 0 | 0 | 17 | 100 | 36 | 0 | 0 | 125 | 14 | 20 | 0 | 480 | 32 | 0 | 101 | 0 | 5 | 50 | 46 | 0 | 24 | 12 | 0 | 220 | 48 | 35 | 315 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 50 | 0 | 320 | 342 | 301 | 45 | 0 | 36 | 33 | 101 | 85 | 0 | 17 | 0 | 82 | 0 | 0 | 28 | 325 | 0 | 389 | 0 | 67 | 152 | 9 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 155 | 0 | 0 | 6 | 7532 | 902 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 0 | 759 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 110 | 220 | 0 | 462 | 1117 | 0 | 5948 | 13480
20:00 | 0 | 70 | 17 | 160 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 35 | 35 | 149 | 30 | 95 | 30 | 35 | 86 | 0 | 340 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 108 | 14 | 20 | 0 | 420 | 32 | 0 | 102 | 0 | 1 | 50 | 46 | 0 | 24 | 12 | 0 | 220 | 49 | 29 | 315 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1146 | 0 | 51 | 50 | 0 | 320 | 347 | 301 | 45 | 0 | 33 | 31 | 101 | 81 | 0 | 17 | 0 | 80 | 0 | 0 | 28 | 315 | 0 | 381 | 0 | 67 | 155 | 9 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 47 | 48 | 158 | 0 | 0 | 6 | 7595 | 902 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 752 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 110 | 220 | 0 | 463 | 1110 | 0 | 5906 | 13501 | 103.06
21:00 | 0 | 50 | 17 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 35 | 136 | 30 | 95 | 15 | 35 | 84 | 0 | 340 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 108 | 15 | 0 | 0 | 410 | 31 | 0 | 77 | 0 | 0 | 50 | 46 | 0 | 24 | 12 | 0 | 219 | 51 | 30 | 315 | 0 | 0 | 0 | 1 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 50 | 0 | 340 | 346 | 301 | 46 | 0 | 36 | 32 | 102 | 84 | 0 | 17 | 0 | 80 | 0 | 0 | 29 | 320 | 0 | 390 | 0 | 67 | 158 | 9 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 156 | 0 | 0 | 6 | 7501 | 902 | 390 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 756.2 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 110 | 220 | 0 | 461 | 1100 | 0 | 5969.2 | 13470.2 | 103.05
22:00 | 0 | 50 | 17 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 131 | 30 | 95 | 15 | 35 | 86 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 108 | 15 | 0 | 0 | 400 | 31 | 0 | 50 | 0 | 0 | 33 | 46 | 0 | 24 | 12 | 0 | 219 | 51 | 38 | 315 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 50 | 0 | 340 | 347 | 300 | 46 | 0 | 37 | 32 | 103 | 85 | 0 | 17 | 0 | 80 | 0 | 0 | 28 | 315 | 0 | 390 | 0 | 67 | 158 | 9 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 158 | 0 | 0 | 6 | 7370 | 899 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 757.66 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 110 | 220 | 0 | 462 | 1099 | 0 | 5962.66 | 13332.66 | 103.05
23:00 | 0 | 50 | 17 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 131 | 30 | 95 | 15 | 35 | 87 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 15 | 0 | 0 | 430 | 30 | 0 | 50 | 0 | 0 | 33 | 46 | 0 | 24 | 12 | 0 | 218 | 51 | 35 | 315 | 0 | 0 | 0 | 8 | 0 | 224 | 0 | 0 | 0 | 1155 | 0 | 51 | 50 | 0 | 340 | 346 | 300 | 46 | 0 | 37 | 34 | 102 | 82 | 0 | 17 | 0 | 80 | 0 | 0 | 28 | 325 | 0 | 390 | 0 | 67 | 157 | 9 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 156 | 0 | 0 | 6 | 7337 | 899 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 758.85 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 462 | 1104 | 0 | 5916.85 | 13253.85 | 103.04
Total KWH | 0 | 551098 | 233760 | 839700 | 0 | 0 | 0 | 0 | 9568800 | 0 | 0 | 259668 | 498960 | 2423088 | 313920 | 770542 | 385074 | 247311 | 784800 | 0 | 8317000 | 0 | 0 | 0 | 141394 | 1418892 | 2514000 | 0 | 189608 | 1315200 | 436200 | 381240 | 0 | 9905000 | 242127 | 10036 | 1919040 | 0 | 22080 | 402646 | 294988 | 0 | 376320 | 296640 | 20281 | 5308805 | 513525 | 814560 | 11294545.45 | 13382 | 0 | 0 | 25236 | 332872 | 5283072 | 0 | 0 | 0 | 25150907 | 115830 | 1231008 | 485091 | 0 | 8103400 | 8163600 | 6880000 | 1079040 | 0 | 866232 | 365760 | 2427065 | 806400 | 0 | 419920 | 17100 | 1733760 | 22454 | 504745 | 278048 | 7596000 | 0 | 9161000 | 0 | 1589640 | 3645081.82 | 198912 | 0 | 1876800 | 692352 | 0 | 0 | 3342270 | 358920 | 1164000 | 1159200 | 3120000 | 9250 | 251880 | 141120 | 161622196.27 | 21855272 | 8873280 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 468000 | 23120000 | 0 | 17020948 | 0 | 0 | 0 | 21120 | 305088 | 0 | 370160 | 0 | 0 | 334290 | 472042 | 174990 | 0 | 324000 | 4188091 | 0 | 0 | 0 | 0 | 0 | 8766763 | 0 | 27780 | 0 | 0 | 332780 | 38087 | 576988 | 0 | 0 | 0 | 1774.56 | 601200 | 3502 | 0 | 3120000 | 2645000 | 5287390 | 0 | 8516363 | 22653090.91 | 14400 | 131024399.47 | 292646595.74

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11627.44 | MW | 12:00 Hr. | Energy Generated |  |  | 292.6466 |  | MKWHr.
| Day Peak Demand |  |  | 11673.42 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.862 |  | MKWHr.
| Evening Peak Generation |  |  | 13501 | MW | 20:00 Hr. | Energy Demand |  |  | 293.5086 |  | MKWHr.
| Evening Peak Demand |  |  | 13501 | MW | 20:00 Hr. | Maximum Temperature |  |  | 34.5 |  | °C
| Minimum Generation of the Day |  |  | 10570.8 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 967.06 |  | MMCFD
| Maximum Generation of the Day |  |  | 13501 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 5.7724 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.3808 | 0 | 7.9248 | 0 | 0 | 0.18961 | 0 | 0 | 41.4953 | Gas | 129.6313 | Gas | 464838071.1662
| Chattogram Zone |  |  | 6.0976 | 36.4455 | 4.4268 | 0 | 5.3088 | 0.13611 | 0 | 0.02208 | 52.4369 | Coal | 93.8549 | Coal | 595951208.4147
| Cumilla Zone |  |  | 29.1703 | 0 | 1.9749 | 0 | 0 | 0.50474 | 1.7338 | 0 | 33.3836 | HFO | 18.9452 | HFO | 339954247.86
| Mymensingh Zone |  |  | 3.12 | 0 | 2.8232 | 0 | 0 | 0.26113 | 0 | 0 | 6.2044 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1021 | Hydro | 5.3088 | Hydro | 530880.5
| Khulna Zone |  |  | 8.8733 | 23.12 | 0 | 0 | 0 | 0.468 | 22.7673 | 0 | 55.2286 | Solar | 3.3623 | Solar | 51824379.8696
| Barishal Zone |  |  | 7.9324 | 34.2895 | 0.0144 | 0 | 0 | 0.003502 | 0 | 0 | 42.2397 | Import | 41.522 | Import | 235850282.8
| Rajshahi Zone |  |  | 12.9549 | 0 | 0.87136 | 0 | 0 | 1.1581 | 17.0209 | 0 | 32.0053 | Wind | 0.02208 | Wind | 324796.8
| Rangpur Zone |  |  | 0 | 0 | 0.90977 | 0 | 0 | 0.64106 | 0 | 0 | 1.5508
| Total |  |  | 129.6313 | 93.8549 | 18.9452 | 0 | 5.3088 | 3.3623 | 41.522 | 0.02208 | 292.6466
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 464838071.1662 |  | Hydro | 530880.5
|  |  |  | Coal | 595951208.4147 |  | Solar | 51824379.8696
|  |  |  | HFO | 339954247.86 |  | Import | 235850282.8
|  |  |  | HSD | 0 |  | Wind | 324796.8
[5 empty] | Total: | 168,92,73,867 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8553 | Peak Hr Flow | 902.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9962345.52 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.0209 | Peak Hr Flow | 752.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2018 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7338 | Peak Hr Flow | 80.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2255 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.61 | Peak Hr Flow | 1734.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4672
|  |  |  | Chattogram |  | 0 |  | 1441
|  |  |  | Cumilla |  | 0 |  | 1368
|  |  |  | Mymensingh |  | 0 |  | 1092
|  |  |  | Sylhet |  | 0 |  | 633
|  |  |  | Khulna |  | 0 |  | 1580
|  |  |  | Barishal |  | 0 |  | 438
|  |  |  | Rajshahi |  | 0 |  | 1162
|  |  |  | Rangpur |  | 0 |  | 551
|  |  |  | Total |  | 0 |  | 12937
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 09:30 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D
| 08:20 | 11:04 | Tangail 132/33kV S/S Kaliakair-1 Scheduled S/D Due to ROW
|  | 08:50 | Sreepur 230/132/33kV S/S 132 kV BUS-1 is restored.
|  | 08:57 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT is restored.
|  | 08:58 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT is restored.
| 09:17 |  | Sreepur 230/132/33kV S/S 230/132 kV T-2 LT Scheduled S/D Due to Red hot maintenance work.
| 09:17 |  | Sreepur 230/132/33kV S/S 230/132 kV T-2 HT Scheduled S/D Due to Red hot maintenance
works.
| 09:20 |  | Sreepur 230/132/33kV S/S 132 kV BUS-2 Scheduled S/D Due to Red hot maintenance work done.
|  | 09:40 | Shahjibazar 132/33kV S/S TR-02 LT is restored.
| 11:06 | 12:43 | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to Right of Way.
| 11:11 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:-
| 11:30 | 13:30 | Sonargaon 132/33kV S/S Bashundhara Line Forced S/D Due to Red hot maintenance | [7 empty] | 3.0MW load
interrup.
| 12:00 |  | Day Peak Generation is 11624 MW.
|  | 12:56 | Siddhirganj 132/33kV S/S T-2 LT is restored.
|  | 12:56 | Siddhirganj 132/33kV S/S T-2 HT is restored.
| 14:50 | 15:05 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing OC/ EF relays Due to OC/ EF | [7 empty] | 50.0MW load
interrup.
| 17:06 |  | Siddhirganj 335 MW CCPP GT was synchronized
| 17:16 | 19:55 | Khagrachori 132/33kV S/S TR-2 LT Forced S/D Due to 33kV Bus-2 Shutdown due to Emergency
Maintenance work khagrachari -2 33kV Feeder
| 17:51 | 18:22 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing OC/EF Relay , Lockout Relay relays Due
to LA Blast of Bisic Feeder under PBS
| 17:51 | 18:31 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing OC/EF Relay, Trip relay relays Due to
LA Blast of Bisic Feeder under PBS
| 17:51 | 18:28 | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing OC/EF Relay, Lockout Relay relays Due
to LA Blast of Bisic Feeder under PBS
| 17:51 | 18:15 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing OC/EF Relay, Lockout Relay relays Due
to LA Blast of Bisic Feeder under PBS
| 18:04 |  | Ghorashal unit-7 GT was synchronized
| 18:08 |  | Siddhirganj 2*120 MW GT-2 was shutdown
| 18:48 |  | Siddhirganj 335 MW CCPP ST was synchronized
|  | 19:05 | Madunaghat-TKCL 132kV Ckt-1 is restored.
| 19:56 |  | Siddhirganj 2*120 MW GT-1 was shutdown
|  | 20:21 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
| 21:46 | 22:11 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) LT Tripped showing REF630 relays Due to | [7 empty] | 37.5MW load
|  |  | NESCO FAULTY FEEDER TRIAL | [7 empty] | interrup.
| 21:46 | 22:12 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT Tripped showing REF630 relays Due to | [7 empty] | 37.5MW load
|  |  | NESCO faulty feeder trail | [7 empty] | interrup.
| 22:30 |  | Barisal 307 MW Shutdown
|  | 23:58 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 04:37 | 05:06 | Amnura 132/33kV S/S T-3 (426T) LT Tripped showing Gen. Trip relays Due to 33kV Amnura
feeder faults
| 07:00 |  | Minimum Generation is 10497 MW
| 07:41 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to For
the phile driving work under the drainage improvement project of Chattogram City,
implemented by the Bangladesh Army.
| 07:46 |  | Shikalbaha 230/132kV S/S Modunaghat Ckt-1 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 160 | 839700 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 410 | 9568800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 8317000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 385074 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 2514000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 1418892 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259668 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 313920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 247311 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 141394 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14 | 436200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 381240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 233760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 770542 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2423088 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 551098 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 86 | 784800 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 189608 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 498960 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 420 | 9905000 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 1315200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2389 | 41495255
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 25236 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115830 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5308805 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5283072 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 332872 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 294988 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 402646 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 376320 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 814560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 102 | 1919040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 10036 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 49 | 513525 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 296640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 32 | 242127 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 13382 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1146 | 25150907 | DCT
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 22080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 315 | 11294545.45 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2245 | 52436892.45
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 347 | 8163600 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 301 | 6880000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 320 | 8103400 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 866232 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 45 | 1079040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1231008 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 485091 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 278048 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 2427065 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 81 | 806400 | -
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1733760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 22454 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 419920 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 17100 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 31 | 365760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 504745 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1485 | 33383623
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 158 | 3120000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1159200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 1164000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 141120 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 358920 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 276 | 6204370
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1589640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3645081.82 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 692352 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1876800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3342270 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 9 | 198912 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7596000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 9161000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1200 | 28102055.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21855272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 372 | 8873280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 468000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1100 | 23120000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2412 | 55228552
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 463 | 8516363 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2645000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 22653090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5287390 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 14400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 110 | 3120000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3502 | -
Barishal Area Total |  |  |  |  | 2858 | 2013 | 42239745.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 334290 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 167 | 4188091 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 347 | 8766763 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 174990 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 370160 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 305088 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 21120 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27780 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 752 | 17020948 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 324000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 472042 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1376 | 32005272
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 576988 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 1774.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 332780 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 38087 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 601200 | -
Rangpur Area Total |  |  |  |  | 950 | 105 | 1550829.56
Eastern Grid Total |  |  |  |  | 17383.855 | 7595 | 161622196.27
Western Grid Total |  |  |  |  | 10980.24 | 5906 | 131024399.47
National Grid Total |  |  |  |  | 28364.095 | 13501 | 292646595.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-10-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9206.74 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3731 | MW
i) Dhaka area |  |  | 4672.41 |  | MW | i) Khulna area |  |  |  | 1580 | MW
ii) Chattogram area |  |  | 1441 |  | MW | ii) Barishal area |  |  |  | 438 | MW
iii) Cumilla area |  |  | 1368.33 |  | MW | iii) Rajshahi area |  |  |  | 1162 | MW
iv) Mymensingh area |  |  | 1092 |  | MW | iv) Rangpur area |  |  |  | 551 | MW
v) Sylhet area |  |  | 633 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12937.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 97 | 18:00 | 133 | Niamatpur | 50 | 18:00
2 | AKSML | 133 | 13:00 | 68 | Ishurdi | 65 | 18:00 | 134 | Noapara | 39 | 22:00
3 | Aftabnagar | 36 | 18:00 | 69 | Jaldhaka | 54 | 18:30 | 135 | PHP | 7 | 00:00
4 | Agargaon | 100 | 19:00 | 70 | Jamalpur | 115 | 18:00 | 136 | Pabna | 84 | 22:00
5 | Agrabad | 90 | 19:30 | 71 | Jashore | 124 | 18:30 | 137 | Palashbari | 88 | 18:00
6 | Amnura | 23 | 19:00 | 72 | Jhenaidah | 119 | 18:00 | 138 | Panchagarh | 42 | 18:00
7 | Ashuganj | 89 | 00:00 | 73 | Joydebpur | 130 | 19:00 | 139 | Patiya | 11.9 | 18:00
8 | BSRM | 195 | 03:00 | 74 | Joypurhat | 44 | 19:30 | 140 | Patuakhali | 75.5 | 21:00
9 | Bagerhat | 77 | 18:00 | 75 | Juldah | 7 | 19:30 | 141 | Payra | 34 | 00:00
10 | Bajitpur | 80 | 20:00 | 76 | KSRM | 27 | 00:00 | 142 | Postogola | 64 | 00:00
11 | Bakulia | 79 | 00:00 | 77 | Kabirpur | 194 | 00:00 | 143 | Purbachal | 21 | 21:00
12 | Banani | 34 | 19:30 | 78 | Kachua | 90 | 20:00 | 144 | Purbasadipur | 85 | 12:00
13 | Bangabhaban | 6 | 10:00 | 79 | Kallyanpur | 102 | 23:00 | 145 | Rahanpur | 28 | 17:00
14 | Barapukuria | 52 | 11:00 | 80 | Kalurghat | 44 | 00:00 | 146 | Rahim | 56 | 03:00
15 | Barguna | 14 | 00:00 | 81 | Kamrangirchar | 71 | 01:00 | 147 | Rajbari | 73 | 18:00
16 | Barishal | 106 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 113 | 23:00
17 | Barishal-230 | 92 | 19:30 | 83 | Kasba | 37 | 19:00 | 149 | Rajshahi | 123 | 23:00
18 | Baroaulia | 66 | 20:00 | 84 | Kazla | 95 | 00:00 | 150 | Rajshahi-230 | 81 | 13:00
19 | Baroirhat | 69 | 18:00 | 85 | Keranigonj | 73 | 00:00 | 151 | Ramganj | 104 | 22:00
20 | Bashundhara | 183 | 12:00 | 86 | Khagrachori | 30 | 20:00 | 152 | Rampur | 45 | 23:00
21 | BashundharaCement | 2 | 00:00 | 87 | Khulna | 68 | 19:30 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 80 | 18:00 | 88 | Khulshi | 171 | 19:30 | 154 | Rangpur | 106 | 12:00
23 | Benapole | 56 | 00:00 | 89 | Kishoreganj | 127 | 18:00 | 155 | Ruppur | 7 | 11:00
24 | Bhaluka | 129 | 21:00 | 90 | Kodda | 244 | 00:00 | 156 | SSM | 5 | 04:00
25 | Bhandaria | 53 | 21:00 | 91 | Kulaura | 52 | 18:30 | 157 | Saidpur | 64 | 10:00
26 | Bhangura | 34 | 20:00 | 92 | Kurigram | 44 | 18:30 | 158 | Satkhira | 116 | 18:30
27 | Bheramara(GK) | 57 | 21:00 | 93 | Kushtia | 126 | 18:00 | 159 | Satmasjid | 92 | 19:30
28 | Bhulta | 219 | 02:00 | 94 | Laksam | 31 | 01:00 | 160 | Savar | 162 | 21:00
29 | Bog-Sherpur | 60 | 18:30 | 95 | Lakshmipur | 32 | 01:00 | 161 | SevenRings | 16.55 | 07:00
30 | Bogura | 128 | 22:00 | 96 | Lalbag | 51 | 00:00 | 162 | ShahCement | 27 | 23:00
31 | Borhanuddin | 94 | 20:00 | 97 | Lalmonirhat | 42 | 18:00 | 163 | Shahjadpur | 72 | 18:00
32 | Brahmanbaria | 132 | 18:00 | 98 | MI_Cement | 8.9 | 16:00 | 164 | Shahjibazar | 135 | 19:00
33 | Cantonment | 146 | 12:00 | 99 | Madanganj | 45 | 00:00 | 165 | Shahmirpur | 49 | 00:00
34 | Chandina | 15.9 | 22:00 | 100 | Madaripur | 105 | 21:00 | 166 | Shariatpur | 88 | 22:00
35 | Chandpur | 80 | 21:00 | 101 | Madartek | 92 | 23:00 | 167 | Sherpur | 120 | 19:30
36 | Chandraghona | 51 | 18:00 | 102 | Madunaghat | 52 | 00:00 | 168 | Shikalbaha | 33 | 13:00
37 | Chapai | 57 | 18:30 | 103 | Magura | 59 | 18:30 | 169 | Shitalakhya | 62.3 | 00:00
38 | Charsaidpur | 32 | 05:00 | 104 | Mahasthangarh | 56 | 18:00 | 170 | Sholosohor | 42 | 00:00
39 | Chauddagram | 72 | 22:00 | 105 | Maijdee | 38 | 21:00 | 171 | Shyampur | 116 | 01:00
40 | Chhatak | 38 | 00:00 | 106 | Manikganj | 110 | 21:00 | 172 | Siddhirganj | 101 | 15:00
41 | Chowmuhani | 168 | 18:00 | 107 | Maniknagar | 58 | 13:00 | 173 | Sirajganj | 88 | 20:00
42 | Chuadanga | 96 | 19:00 | 108 | Matarbari | 52 | 20:00 | 174 | Sonargaon | 112 | 01:00
43 | Coxsbazar | 146 | 13:00 | 109 | Matuail | 60 | 00:00 | 175 | Sreemongol | 88 | 18:30
44 | Cumilla(N) | 135 | 18:00 | 110 | Metrorail_Motijheel | 30 | 21:00 | 176 | Sreepur | 90 | 00:00
45 | Cumilla(S) | 147 | 00:00 | 111 | Metrorail_Uttara | 7 | 18:30 | 177 | Srinagar | 48.65 | 22:00
46 | Daganbhuiyan | 0 | 03:00 | 112 | Millgate | 93 | 00:00 | 178 | Sunamganj | 62 | 21:00
47 | Daudkandi | 157 | 21:00 | 113 | Mirpur | 126 | 19:30 | 179 | Sylhet | 51 | 00:00
48 | DhakaUniversity | 40 | 00:00 | 114 | Mirsorai | 9 | 01:00 | 180 | Sylhet-132 | 116 | 18:00
49 | Dhamrai | 106 | 19:00 | 115 | Mirzapur | 42 | 19:00 | 181 | TK | 26 | 21:00
50 | Dhanmondi | 115 | 18:00 | 116 | Mithapukur | 40 | 00:00 | 182 | Tangail | 168 | 18:00
51 | Dohazari | 104 | 19:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 13 | 00:00
52 | Faridpur | 148 | 21:00 | 118 | Mogbazar | 78.2 | 13:00 | 184 | Thakurgaon | 67 | 18:00
53 | Fatullah | 88 | 00:00 | 119 | Mongla | 33 | 00:00 | 185 | Tongi | 99 | 12:00
54 | Fenchuganj | 41 | 00:00 | 120 | Motijheel | 37 | 20:00 | 186 | Ullahpara | 37 | 18:00
55 | Feni | 111 | 22:00 | 121 | Muktagacha | 35 | 18:00 | 187 | Ullon | 66 | 23:00
56 | GPH | 74 | 14:00 | 122 | Munshiganj | 112 | 23:00 | 188 | Uttara | 81 | 18:00
57 | Ghatail | 78 | 18:30 | 123 | Muradnagar | 41 | 18:00 | 189 | UttaraNew | 33 | 23:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 193 | 18:30 | 190 | Zigatola | 70 | 13:00
59 | Ghorashal-230 | 97 | 00:00 | 125 | Naogaon | 90 | 19:30
60 | Goalpara | 36 | 22:00 | 126 | Narail | 55 | 18:00
61 | Gollamari | 86 | 00:00 | 127 | Narinda | 48 | 00:00
62 | Gopalganj | 102 | 18:00 | 128 | Narshingdi | 176 | 23:00
63 | Gulshan | 90 | 15:00 | 129 | Natore | 120 | 20:00
64 | Halishahar | 48 | 12:00 | 130 | Nawabganj | 46.2 | 22:00
65 | HaripurSBU | 130 | 01:00 | 131 | Netrakona | 139 | 18:00
66 | Hasnabad | 88 | 00:00 | 132 | New | 47 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13336.5 | 32 |  | 13369.94
1:00 | 12985 | 33 |  | 13019
2:00 | 12538 | 31 |  | 12570
3:00 | 12120 | 29 |  | 12150
4:00 | 11827 | 22 |  | 11850
5:00 | 11612 | 0 |  | 11612
6:00 | 11210 | 0 |  | 11210
7:00 | 10863.85 | 94 |  | 10961.85
8:00 | 10854.19 | 95 |  | 10953.47
9:00 | 10670.81 | 98 |  | 10773.22
10:00 | 10570.8 | 88 |  | 10662.76
11:00 | 10998.23 | 53 |  | 11053.62
12:00 | 11627.44 | 44 |  | 11673.42
13:00 | 12268.74 | 73 |  | 12344.74
14:00 | 11757.93 | 63 |  | 11823.93
15:00 | 11718.24 | 81 |  | 11803.24
16:00 | 11363.21 | 0 |  | 11363.21
17:00 | 11300.88 | 0 |  | 11300.88
18:00 | 13089.5 | 0 |  | 13089.5
19:00 | 13411 | 0 |  | 13411
19:30 | 13480 | 0 |  | 13480
20:00 | 13501 | 0 |  | 13501
21:00 | 13470.2 | 0 |  | 13470.2
22:00 | 13332.66 | 0 |  | 13332.66
23:00 | 13253.85 | 26 |  | 13281.02
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7404.5 | 5932 | 13336.5 | DAILY GENERATION CURVE
00:30 | 7328.75 | 5832 | 13160.75
01:00 | 7253 | 5732 | 12985 | 31-10-2025
01:30 | 7114.5 | 5647 | 12761.5
02:00 | 6976 | 5562 | 12538
02:30 | 6806 | 5523 | 12329
03:00 | 6636 | 5484 | 12120
03:30 | 6560.5 | 5413 | 11973.5
04:00 | 6485 | 5342 | 11827
04:30 | 6453 | 5266.5 | 11719.5
05:00 | 6421 | 5191 | 11612
05:30 | 6330.5 | 5080.5 | 11411
06:00 | 6240 | 4970 | 11210
06:30 | 6148.505 | 4888.42 | 11036.925
07:00 | 6057.01 | 4806.84 | 10863.85
07:30 | 6104.37 | 4754.65 | 10859.02
08:00 | 6151.73 | 4702.46 | 10854.19
08:30 | 6088.73 | 4673.77 | 10762.5
09:00 | 6025.73 | 4645.08 | 10670.81
09:30 | 5941.83 | 4678.975 | 10620.805
10:00 | 5857.93 | 4712.87 | 10570.8
10:30 | 6020.05 | 4764.465 | 10784.515
11:00 | 6182.17 | 4816.06 | 10998.23
11:30 | 6282.115 | 5030.72 | 11312.835
12:00 | 6382.06 | 5245.38 | 11627.44
12:30 | 6552.205 | 5395.885 | 11948.09
13:00 | 6722.35 | 5546.39 | 12268.74
13:30 | 6575.395 | 5437.94 | 12013.335
14:00 | 6428.44 | 5329.49 | 11757.93
14:30 | 6409.11 | 5328.975 | 11738.085
15:00 | 6389.78 | 5328.46 | 11718.24
15:30 | 6304.365 | 5236.36 | 11540.725
16:00 | 6218.95 | 5144.26 | 11363.21
16:30 | 6197.65 | 5134.395 | 11332.045
17:00 | 6176.35 | 5124.53 | 11300.88
17:30 | 6718.425 | 5476.765 | 12195.19
18:00 | 7260.5 | 5829 | 13089.5
18:30 | 7409.25 | 5841 | 13250.25
19:00 | 7558 | 5853 | 13411
19:30 | 7532 | 5948 | 13480
20:00 | 7595 | 5906 | 13501
20:30 | 7548 | 5937.6 | 13485.6 |  | Executive Engineer
21:00 | 7501 | 5969.2 | 13470.2 |  | Network Operation Division
21:30 | 7435.5 | 5965.93 | 13401.43
22:00 | 7370 | 5962.66 | 13332.66
22:30 | 7353.5 | 5939.755 | 13293.255
23:00 | 7337 | 5916.85 | 13253.85

## En-Curve
QF-LDC-12
Date | 31-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3826 | 1713.5 | 904 | 38 | 84 | 749 | 218 | 4577 | 0 | 265 | 962 | 0 | 0 | 0 | 32 | DAILY ENERGY CURVE
00:30 | 3813.5 | 1716.25 | 904 | 38 | 81 | 748.5 | 218 | 4550 | 0 | 224.5 | 867 | 0 | 0 | 0 | 32.5 | 31-10-2025
01:00 | 3801 | 1719 | 904 | 38 | 78 | 748 | 218 | 4523 | 0 | 184 | 772 | 0 | 0 | 0 | 33
01:30 | 3797.5 | 1720.5 | 904 | 38 | 78 | 743.5 | 218 | 4462.5 | 0 | 151.5 | 648 | 0 | 0 | 0 | 32 | Energy Generated | 292.6466 |  | MKWHr
02:00 | 3794 | 1722 | 904 | 38 | 78 | 739 | 218 | 4402 | 0 | 119 | 524 | 0 | 0 | 0 | 31 | Energy not Served | 0.862 |  | MKWHr
02:30 | 3677.5 | 1717 | 904 | 38 | 78 | 743 | 218.5 | 4366.5 | 0 | 95 | 491.5 | 0 | 0 | 0 | 30 | Total Energy Requirement | 293.5086 |  | MKWHr
03:00 | 3561 | 1712 | 904 | 38 | 78 | 747 | 219 | 4331 | 0 | 71 | 459 | 0 | 0 | 0 | 29
03:30 | 3554.5 | 1715 | 904 | 38 | 74 | 748 | 219 | 4251.5 | 0 | 44 | 425.5 | 0 | 0 | 0 | 25.5
04:00 | 3548 | 1718 | 904 | 38 | 70 | 749 | 219 | 4172 | 0 | 17 | 392 | 0 | 0 | 0 | 22
04:30 | 3568.5 | 1715 | 904 | 38 | 73 | 757.5 | 219.5 | 4094 | 0 | 17 | 333 | 0 | 0 | 0 | 11
05:00 | 3589 | 1712 | 904 | 38 | 76 | 766 | 220 | 4016 | 0 | 17 | 274 | 0 | 0 | 0 | 0
05:30 | 3553 | 1705 | 903.5 | 38 | 69 | 764.5 | 221 | 3856.5 | 0 | 19 | 281.5 | 0 | 0 | 0 | 0
06:00 | 3517 | 1698 | 903 | 38 | 62 | 763 | 222 | 3697 | 0 | 21 | 289 | 0 | 0 | 0 | 0
06:30 | 3462 | 1633 | 903 | 38 | 66 | 763.5 | 221 | 3557.5 | 42.925 | 23 | 327 | 0 | 0 | 0 | 47
07:00 | 3407 | 1568 | 903 | 38 | 70 | 764 | 220 | 3418 | 85.85 | 25 | 365 | 0 | 0 | 0 | 94
07:30 | 3389.5 | 1589.5 | 902.5 | 38 | 67 | 718.815 | 220 | 3373 | 161.205 | 34 | 365.5 | 0 | 0 | 0 | 94.5
08:00 | 3372 | 1611 | 902 | 38 | 64 | 673.63 | 220 | 3328 | 236.56 | 43 | 366 | 0 | 0 | 0 | 95
08:30 | 3324 | 1579.5 | 902 | 38 | 65 | 625.78 | 220 | 3295 | 310.22 | 43 | 360 | 0 | 0 | 0 | 96.5
09:00 | 3276 | 1548 | 902 | 38 | 66 | 577.93 | 220 | 3262 | 383.88 | 43 | 354 | 0 | 0 | 0 | 98
09:30 | 3277 | 1523 | 902 | 38 | 63 | 563.575 | 219.5 | 3205 | 426.23 | 49 | 354.5 | 0 | 0 | 0 | 93
10:00 | 3278 | 1498 | 902 | 38 | 60 | 549.22 | 219 | 3148 | 468.58 | 55 | 355 | 0 | 0 | 0 | 88
10:30 | 3395 | 1576.5 | 902 | 38 | 59 | 539.065 | 219 | 3180.5 | 458.95 | 57.5 | 359 | 0 | 0 | 0 | 70.5
11:00 | 3512 | 1655 | 902 | 38 | 58 | 528.91 | 219 | 3213 | 449.32 | 60 | 363 | 0 | 0 | 0 | 53
11:30 | 3592 | 1689.5 | 902 | 38 | 61 | 576.74 | 219 | 3305.5 | 486.595 | 69 | 373 | 0 | 0 | 0.5 | 48.5
12:00 | 3672 | 1724 | 902 | 38 | 64 | 624.57 | 219 | 3398 | 523.87 | 78 | 383 | 0 | 0 | 1 | 44
12:30 | 3720.5 | 1740 | 902 | 38 | 72 | 689.055 | 219 | 3635 | 441.285 | 80 | 410.75 | 0 | 0 | 0.5 | 58.5
13:00 | 3769 | 1756 | 902 | 38 | 80 | 753.54 | 219 | 3872 | 358.7 | 82 | 438.5 | 0 | 0 | 0 | 73
13:30 | 3736.5 | 1713.5 | 902.5 | 38 | 79 | 704.77 | 219.5 | 3747 | 365.565 | 88.5 | 418.5 | 0 | 0 | 0 | 68
14:00 | 3704 | 1671 | 903 | 38 | 78 | 656 | 220 | 3622 | 372.43 | 95 | 398.5 | 0 | 0 | 0 | 63
14:30 | 3687 | 1710 | 903 | 38 | 78 | 662 | 219.5 | 3648 | 338.585 | 77.5 | 376.5 | 0 | 0 | 0 | 72
15:00 | 3670 | 1749 | 903 | 38 | 78 | 668 | 219 | 3674 | 304.74 | 60 | 354.5 | 0 | 0 | 0 | 81
15:30 | 3621.5 | 1744.5 | 902.5 | 38 | 75 | 645.5 | 219.5 | 3654.5 | 222.225 | 60 | 356.5 | 0 | 0 | 1 | 40.5
16:00 | 3573 | 1740 | 902 | 38 | 72 | 623 | 220 | 3635 | 139.71 | 60 | 358.5 | 0 | 0 | 2 | 0
16:30 | 3547.5 | 1715.5 | 902 | 38 | 71 | 625.5 | 220 | 3629.5 | 75.545 | 70 | 433.5 | 0 | 0 | 4 | 0
17:00 | 3522 | 1691 | 902 | 38 | 70 | 628 | 220 | 3624 | 11.38 | 80 | 508.5 | 0 | 0 | 6 | 0
17:30 | 3585.5 | 1724.5 | 902 | 38 | 72 | 690.5 | 220 | 3852.5 | 5.69 | 283.5 | 815.5 | 0 | 0 | 5.5 | 0
18:00 | 3649 | 1758 | 902 | 38 | 74 | 753 | 220 | 4081 | 0 | 487 | 1122.5 | 0 | 0 | 5 | 0
18:30 | 3699 | 1765.5 | 902.5 | 38 | 77 | 755 | 220 | 4130 | 0 | 476.5 | 1180.75 | 0 | 0 | 6 | 0
19:00 | 3749 | 1773 | 903 | 38 | 80 | 757 | 220 | 4179 | 0 | 466 | 1239 | 0 | 0 | 7 | 0
19:30 | 3826 | 1821 | 902 | 38 | 82 | 759 | 220 | 4258 | 0 | 441 | 1128 | 0 | 0 | 5 | 0
20:00 | 3983 | 1718 | 902 | 38 | 80 | 752 | 220 | 4244 | 0 | 424 | 1139 | 0 | 0 | 1 | 0
20:30 | 4025 | 1708.5 | 902 | 38 | 80 | 754.1 | 219.5 | 4228.5 | 0 | 414.5 | 1115 | 0 | 0 | 0.5 | 0
21:00 | 4067 | 1699 | 902 | 38 | 80 | 756.2 | 219 | 4213 | 0 | 405 | 1091 | 0 | 0 | 0 | 0
21:30 | 4075 | 1695.5 | 900.5 | 38 | 80 | 756.93 | 219 | 4204.5 | 0 | 396 | 1036 | 0 | 0 | 0 | 0
22:00 | 4083 | 1692 | 899 | 38 | 80 | 757.66 | 219 | 4196 | 0 | 387 | 981 | 0 | 0 | 0 | 0
22:30 | 4086.5 | 1710 | 899 | 38 | 80 | 758.255 | 218.5 | 4172 | 0 | 350.5 | 980.5 | 0 | 0 | 0 | 13
23:00 | 4090 | 1728 | 899 | 38 | 80 | 758.85 | 218 | 4148 | 0 | 314 | 980 | 0 | 0 | 0 | 26
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 08:00 | 373 | 00:00 | Payra | 413 | 08:00 | 406 | 00:00
Ashuganj | 403 | 10:00 | 392 | 01:00 | Rahanpur | 412 | 09:00 | 404 | 02:00
Bhulta | 403 | 17:00 | 387 | 00:00 | Rampal | 408 | 09:00 | 393 | 00:00
Bibiana | 389 | 08:00 | 381 | 03:00
BIPTC | 405 | 05:00 | 394 | 18:00
Bogura | 403 | 10:00 | 392 | 01:00
Gopalganj | 400 | 08:00 | 388 | 00:00
Kaliakoir | 374 | 07:00 | 366 | 00:00
Madunaghat | 396 | 09:00 | 387 | 00:00
Meghnaghat | 388 | 08:00 | 376 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 08:00 | 223 | 00:00 | Kaliakoir | 235 | 18:00 | 227 | 00:00
AKSML | 230 | 08:00 | 224 | 02:00 | Keranigonj | 227 | 08:00 | 219 | 00:00
Aminbazar | 231 | 08:00 | 223 | 00:00 | Khulna(S) | 237 | 10:00 | 226 | 00:00
Ashuganj | 235 | 17:00 | 225 | 00:00 | Madunaghat | 232 | 07:00 | 227 | 00:00
Ashuganj-400 | 235 | 17:00 | 225 | 00:00 | Madunaghat-400 | 234 | 09:00 | 228 | 00:00
Baghabari | 239 | 11:00 | 231 | 01:00 | Maniknagar | 222 | 08:00 | 215 | 00:00
Barapukuria | 232 | 00:00 | 217 | 11:00 | Meghnaghat | 229 | 08:00 | 223 | 00:00
Barapukuria-230 | 232 | 00:00 | 217 | 11:00 | Meghnaghat-400 | 225 | 08:00 | 218 | 00:00
Barishal | 235 | 08:00 | 227 | 23:00 | Mirsorai | 228 | 17:00 | 218 | 00:00
Bheramara | 234 | 09:00 | 226 | 00:00 | Rajshahi | 234 | 10:00 | 225 | 00:00
Bhulta | 230 | 17:00 | 215 | 23:00 | Rampal | 234 | 06:00 | 224 | 00:00
Bibiana | 233 | 00:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 10:00 | 227 | 00:00 | Rampura | 228 | 18:30 | 218 | 00:00
Bogura | 245 | 10:00 | 238 | 01:00 | Shikalbaha | 231 | 08:00 | 226 | 00:00
Bogura-400 | 244 | 10:00 | 237 | 13:00 | Shyampur | 225 | 08:00 | 217 | 00:00
Borhanuddin | 237 | 07:00 | 231 | 00:00 | Siddhirganj | 224 | 07:00 | 216 | 00:00
BSRM | 228 | 17:00 | 218 | 00:00 | Sirajgonj | 244 | 17:00 | 236 | 03:00
Cumilla(N) | 225 | 09:00 | 216 | 00:00 | Sreepur | 234 | 10:00 | 222 | 00:00
Faridpur | 233 | 09:00 | 224 | 23:00 | Tongi | 231 | 07:00 | 221 | 01:00
Fenchuganj | 232 | 17:00 | 223 | 02:00
Ghorashal | 235 | 18:00 | 230 | 00:00
Ghorashal-230 | 230 | 18:30 | 219 | 03:00
Gopalganj | 234 | 07:00 | 227 | 00:00
GPH | 229 | 17:00 | 224 | 02:00
Haripur | 223 | 08:00 | 216 | 00:00
Hasnabad | 226 | 08:00 | 218 | 00:00
Hathazari | 231 | 18:00 | 221 | 00:00
Ishurdi | 239 | 10:00 | 230 | 00:00
Jhenaidah | 235 | 10:00 | 223 | 00:00
Kachua | 226 | 18:00 | 216 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 23:00 | 130 | 12:00 | Lalmonirhat | 135 | 22:00 | 125 | 13:00
Agargaon | 135 | 08:00 | 130 | 00:00 | Madanganj | 130 | 18:00 | 125 | 00:00
Agrabad | 133 | 07:00 | 128 | 00:00 | Madaripur | 136 | 04:00 | 131 | 00:00
AKS | 130 | 06:00 | 127 | 00:00 | Madartek | 135 | 10:00 | 131 | 00:00
Aminbazar | 136 | 07:00 | 132 | 00:00 | Madunaghat | 135 | 10:00 | 131 | 00:00
Amnura | 141 | 10:00 | 130 | 13:00 | Magura | 136 | 06:00 | 127 | 00:00
Ashuganj | 142 | 17:00 | 135 | 00:00 | Mahasthangarh | 137 | 10:00 | 132 | 01:00
Bagerhat | 139 | 07:00 | 121 | 00:00 | Maijdee | 129 | 08:00 | 122 | 00:00
Bajitpur | 132 | 07:00 | 127 | 00:00 | Manikganj | 134 | 08:00 | 129 | 00:00
Bakulia | 134 | 08:00 | 130 | 00:00 | Maniknagar | 134 | 08:00 | 129 | 00:00
Banani | 136 | 10:00 | 131 | 13:00 | Matarbari | 118 | 17:00 | 107 | 00:00
Bangabhaban | 134 | 08:00 | 130 | 00:00 | Matuail | 130 | 08:00 | 126 | 01:00
Barapukuria | 142 | 00:00 | 131 | 11:00 | Metrorail_Motijheel | 134 | 08:00 | 129 | 00:00
Barguna | 137 | 08:00 | 132 | 00:00 | Metrorail_Uttara | 138 | 10:00 | 132 | 00:00
Barishal | 135 | 07:00 | 129 | 00:00 | Millgate | 139 | 06:00 | 132 | 00:00
Barishal-230 | 135 | 08:00 | 129 | 00:00 | Mirpur | 135 | 07:00 | 130 | 00:00
Baroaulia | 134 | 07:00 | 129 | 13:00 | Mirzapur | 131 | 07:00 | 127 | 00:00
Baroirhat | 131 | 10:00 | 124 | 00:00 | Mithapukur | 137 | 18:00 | 130 | 13:00
Bashundhara | 137 | 08:00 | 131 | 00:00 | MI_Cement | 133 | 09:00 | 127 | 00:00
BashundharaCement | 130 | 18:00 | 125 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Beanibazar | 129 | 08:00 | 123 | 00:00 | Mogbazar | 137 | 10:00 | 133 | 00:00
Benapole | 136 | 10:00 | 123 | 22:00 | Mongla | 134 | 09:00 | 123 | 00:00
Bhaluka | 134 | 18:30 | 125 | 00:00 | Motijheel | 134 | 08:00 | 130 | 00:00
Bhandaria | 132 | 08:00 | 123 | 00:00 | Muktagacha | 131 | 08:00 | 123 | 18:00
Bhangura | 136 | 09:00 | 132 | 00:00 | Munshiganj | 129 | 18:00 | 124 | 00:00
Bheramara | 139 | 07:00 | 136 | 00:00 | Muradnagar | 128 | 19:00 | 121 | 00:00
Bheramara(GK) | 140 | 10:00 | 135 | 00:00 | Mymensingh | 132 | 15:00 | 120 | 00:00
Bhulta | 127 | 06:00 | 123 | 00:00 | Naogaon | 134 | 10:00 | 129 | 13:00
Bog-Sherpur | 138 | 10:00 | 133 | 13:00 | Narail | 136 | 10:00 | 124 | 03:00
Bogura | 137 | 05:00 | 134 | 01:00 | Narinda | 134 | 08:00 | 129 | 00:00
Bogura-230 | 138 | 09:00 | 134 | 02:00 | Narshingdi | 135 | 17:00 | 118 | 00:00
Brahmanbaria | 135 | 10:00 | 127 | 00:00 | Natore | 136 | 06:00 | 131 | 13:00
Cantonment | 134 | 06:00 | 130 | 00:00 | Nawabganj | 135 | 09:00 | 129 | 00:00
Chandina | 131 | 08:00 | 125 | 00:00 | Netrakona | 124 | 07:00 | 119 | 00:00
Chandpur | 135 | 18:00 | 126 | 00:00 | New | 138 | 08:00 | 133 | 00:00
Chandraghona | 134 | 07:00 | 131 | 00:00 | Niamatpur | 141 | 10:00 | 138 | 00:00
Chapai | 140 | 16:00 | 7 | 10:00 | Noapara | 136 | 09:00 | 126 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:00 | 124 | 23:00 | Pabna | 138 | 10:00 | 134 | 00:00
Chauddagram | 130 | 08:00 | 124 | 00:00 | Palashbari | 134 | 18:00 | 128 | 13:00
Chhatak | 128 | 05:00 | 121 | 00:00 | Panchagarh | 139 | 18:00 | 1 | 05:00
Chowmuhani | 130 | 08:00 | 123 | 00:00 | Patiya | 132 | 08:00 | 127 | 00:00
Chuadanga | 136 | 17:00 | 125 | 23:00 | Patuakhali | 137 | 08:00 | 133 | 00:00
Coxsbazar | 116 | 09:00 | 107 | 23:00 | Payra | 138 | 09:00 | 134 | 22:00
Cumilla(N) | 131 | 18:00 | 124 | 00:00 | PHP | 130 | 09:00 | 124 | 00:00
Cumilla(S) | 130 | 04:00 | 124 | 00:00 | Postogola | 134 | 07:00 | 128 | 00:00
Daganbhuiyan | 130 | 08:00 | 125 | 03:00 | Purbachal | 136 | 10:00 | 131 | 12:00
Daudkandi | 126 | 19:00 | 117 | 00:00 | Purbasadipur | 136 | 18:00 | 129 | 13:00
DhakaUniversity | 137 | 10:00 | 132 | 12:00 | Rahanpur | 142 | 04:00 | 139 | 00:00
Dhamrai | 133 | 07:00 | 130 | 01:00 | Rahanpur-400 | 142 | 09:00 | 139 | 01:00
Dhanmondi | 137 | 10:00 | 132 | 00:00 | Rahim | 130 | 08:00 | 126 | 00:00
Dohazari | 128 | 10:00 | 122 | 00:00 | Rajbari | 137 | 08:00 | 130 | 00:00
Faridpur | 137 | 06:00 | 133 | 00:00 | Rajendrapur | 135 | 06:00 | 124 | 12:00
Fatullah | 137 | 07:00 | 128 | 00:00 | Rajshahi | 135 | 06:00 | 130 | 13:00
Fenchuganj | 136 | 00:00 | 133 | 22:00 | Rajshahi-230 | 135 | 06:00 | 130 | 00:00
Feni | 129 | 08:00 | 125 | 00:00 | Ramganj | 130 | 18:00 | 122 | 00:00
Ghatail | 129 | 05:00 | 124 | 12:00 | Rampur | 133 | 10:00 | 127 | 00:00
Ghorashal | 138 | 18:00 | 132 | 02:00 | Rampura | 136 | 18:30 | 131 | 00:00
Goalpara | 137 | 09:00 | 128 | 00:00 | Rangamati | 134 | 07:00 | 130 | 00:00
Gollamari | 137 | 09:00 | 129 | 00:00 | Rangpur | 138 | 18:00 | 131 | 13:00
Gopalganj | 136 | 08:00 | 129 | 00:00 | Ruppur | 140 | 09:00 | 135 | 00:00
Gopalganj-400 | 138 | 08:00 | 133 | 00:00 | Saidpur | 137 | 18:00 | 128 | 13:00
Gulshan | 136 | 04:00 | 132 | 00:00 | Satkhira | 134 | 09:00 | 124 | 00:00
Halishahar | 133 | 08:00 | 129 | 00:00 | Satmasjid | 135 | 08:00 | 129 | 13:00
Haripur | 130 | 07:00 | 126 | 22:00 | Savar | 136 | 18:00 | 129 | 12:00
HaripurSBU | 130 | 07:00 | 126 | 01:00 | SevenRings | 138 | 10:00 | 132 | 02:00
Hasnabad | 134 | 09:00 | 130 | 00:00 | ShahCement | 130 | 18:00 | 124 | 23:00
Hathazari | 134 | 11:00 | 131 | 00:00 | Shahjadpur | 138 | 11:00 | 132 | 22:00
Ishurdi | 141 | 08:00 | 136 | 00:00 | Shahjibazar | 136 | 17:00 | 126 | 00:00
Jaldhaka | 137 | 13:00 | 129 | 08:00 | Shahmirpur | 134 | 09:00 | 130 | 00:00
Jamalpur | 132 | 09:00 | 118 | 18:00 | Shariatpur | 136 | 07:00 | 129 | 23:00
Jashore | 136 | 09:00 | 124 | 21:00 | Sherpur | 130 | 06:00 | 115 | 18:00
Jhenaidah | 139 | 09:00 | 128 | 21:00 | Shikalbaha | 124 | 09:00 | 119 | 00:00
Jhenaidah-230 | 139 | 09:00 | 131 | 00:00 | Shikalbaha-230 | 135 | 08:00 | 131 | 00:00
Joydebpur | 139 | 06:00 | 128 | 12:00 | Shitalakhya | 133 | 18:00 | 127 | 00:00
Joypurhat | 134 | 10:00 | 128 | 13:00 | Sholosohor | 134 | 07:00 | 131 | 00:00
Juldah | 134 | 08:00 | 130 | 00:00 | Shyampur | 136 | 18:00 | 130 | 12:00
Kabirpur | 136 | 09:00 | 128 | 12:00 | Shyampur-230 | 138 | 08:00 | 132 | 00:00
Kachua | 134 | 18:00 | 126 | 00:00 | Siddhirganj | 131 | 08:00 | 125 | 23:00
Kaliakoir | 136 | 17:00 | 131 | 01:00 | Sirajganj | 137 | 10:00 | 132 | 00:00
Kallyanpur | 137 | 18:00 | 131 | 12:00 | Sonargaon | 128 | 09:00 | 124 | 00:00
Kalurghat | 135 | 08:00 | 131 | 00:00 | Sreemongol | 135 | 07:00 | 126 | 00:00
Kamrangirchar | 135 | 09:00 | 129 | 00:00 | Sreepur | 135 | 10:00 | 128 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 135 | 08:00 | 129 | 00:00
Kasba | 127 | 19:00 | 120 | 00:00 | SSM | 134 | 05:00 | 132 | 00:00
Kazla | 134 | 09:00 | 130 | 00:00 | Sunamganj | 127 | 08:00 | 119 | 00:00
Keranigonj | 135 | 08:00 | 129 | 00:00 | Sylhet | 130 | 07:00 | 126 | 00:00
Khagrachori | 133 | 19:00 | 129 | 00:00 | Sylhet-132 | 130 | 07:00 | 127 | 00:00
Khulna | 136 | 09:00 | 127 | 22:00 | Tangail | 128 | 03:00 | 123 | 12:00
Khulna(S) | 137 | 09:00 | 129 | 00:00 | Taraganj | 137 | 21:00 | 130 | 13:00
Khulshi | 132 | 09:00 | 127 | 00:00 | Thakurgaon | 138 | 18:00 | 125 | 13:00
Kishoreganj | 132 | 17:00 | 124 | 23:00 | TK | 133 | 01:00 | 132 | 00:00
Kodda | 137 | 23:00 | 126 | 11:00 | Tongi | 140 | 07:00 | 134 | 01:00
KSRM | 134 | 09:00 | 128 | 00:00 | Ullahpara | 137 | 09:00 | 133 | 00:00
Kulaura | 135 | 08:00 | 130 | 00:00 | Ullon | 136 | 10:00 | 132 | 00:00
Kurigram | 134 | 23:00 | 126 | 13:00 | Uttara | 136 | 18:00 | 129 | 13:00
Kushtia | 138 | 10:00 | 132 | 21:00 | UttaraNew | 138 | 10:00 | 132 | 00:00
Laksam | 133 | 18:00 | 125 | 00:00 | Zigatola | 135 | 08:00 | 129 | 01:00
Lakshmipur | 130 | 09:00 | 122 | 00:00
Lalbag | 135 | 08:00 | 129 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division