## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-11-2025 | [28 empty] | Date: | 01-11-2025 | [28 empty] | Date: | 01-11-2025 | [28 empty] | Date: | 01-11-2025 | [28 empty] | Date: | 01-11-2025 | [14 empty] | Date: | 01-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 8 | 160 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 17 | 132 | 30 | 95 | 15 | 35 | 89 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 15 | 0 | 0 | 400 | 32 | 0 | 50 | 0 | 0 | 33 | 44 | 0 | 12 | 12 | 0 | 218 | 51 | 39 | 315 | 0 | 0 | 0 | 8 | 3 | 224 | 0 | 0 | 0 | 1149 | 0 | 51 | 50 | 0 | 360 | 352 | 300 | 46 | 0 | 37 | 31 | 104 | 81 | 0 | 17 | 0 | 84 | 0 | 0 | 28 | 320 | 0 | 363 | 0 | 67 | 158 | 9 | 0 | 83 | 30 | 0 | 0 | 162 | 17 | 48 | 48 | 158 | 0 | 0 | 6 | 7292 | 900 | 396 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 768.43 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 461 | 1104 | 0 | 5914.43 | 13206.43 | 103.04
01:00 | 0 | 50 | 8 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 125 | 0 | 45 | 15 | 0 | 35 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15 | 12 | 0 | 400 | 0 | 0 | 50 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0 | 218 | 50 | 39 | 315 | 0 | 0 | 0 | 8 | 51 | 224 | 0 | 0 | 0 | 1160 | 0 | 51 | 40 | 0 | 393 | 353 | 300 | 46 | 0 | 37 | 30 | 104 | 80 | 0 | 17 | 0 | 82 | 0 | 0 | 28 | 305 | 0 | 384 | 0 | 67 | 152 | 9 | 0 | 83 | 0 | 0 | 0 | 162 | 17 | 48 | 48 | 159 | 0 | 0 | 6 | 7082 | 900 | 378 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 761.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 463 | 1090 | 0 | 5616.16 | 12698.16 | 103.03
02:00 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 15 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15 | 20 | 0 | 400 | 0 | 0 | 50 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0 | 218 | 17 | 39 | 315 | 0 | 0 | 0 | 0 | 51 | 224 | 0 | 0 | 0 | 1151 | 0 | 51 | 0 | 0 | 393 | 354 | 300 | 46 | 0 | 34 | 0 | 104 | 51 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 364 | 0 | 0 | 154 | 8 | 0 | 83 | 0 | 0 | 0 | 162 | 17 | 48 | 48 | 159 | 0 | 0 | 0 | 6599 | 899 | 383 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 766.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 403 | 1094 | 0 | 5536.27 | 12135.27 | 103.02
03:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15 | 20 | 0 | 400 | 0 | 0 | 48 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0 | 221 | 0 | 39 | 315 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1037 | 0 | 51 | 0 | 0 | 393 | 353 | 300 | 47 | 0 | 34 | 0 | 104 | 0 | 0 | 17 | 0 | 76 | 0 | 0 | 0 | 315 | 0 | 384 | 0 | 0 | 155 | 8 | 0 | 84 | 0 | 0 | 0 | 162 | 17 | 24 | 18 | 160 | 0 | 0 | 0 | 6299 | 899 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 771.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 386 | 1050 | 0 | 5418.19 | 11717.19 | 103.01
04:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15 | 20 | 0 | 400 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 221 | 0 | 39 | 315 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 978 | 0 | 51 | 0 | 0 | 393 | 355 | 300 | 46 | 0 | 34 | 0 | 104 | 0 | 0 | 17 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 384 | 0 | 0 | 155 | 8 | 0 | 84 | 0 | 0 | 0 | 162 | 17 | 16 | 0 | 159 | 0 | 0 | 0 | 6136 | 899 | 383 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 0 | 716.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 352 | 980 | 0 | 5205.11 | 11341.11 | 103
05:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15 | 20 | 0 | 400 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 222 | 0 | 39 | 315 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 915 | 0 | 51 | 0 | 0 | 393 | 353 | 300 | 47 | 0 | 34 | 0 | 104 | 0 | 0 | 17 | 0 | 66 | 0 | 0 | 0 | 310 | 0 | 376 | 0 | 0 | 154 | 8 | 0 | 84 | 0 | 0 | 0 | 162 | 17 | 16 | 0 | 160 | 0 | 0 | 0 | 6053 | 876 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 0 | 683.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 302 | 940 | 0 | 5007.84 | 11060.84 | 102.99
06:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 17 | 15 | 20 | 0 | 400 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 222 | 0 | 42 | 315 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 860 | 0 | 43 | 0 | 0 | 393 | 356 | 300 | 46 | 0 | 31 | 0 | 104 | 0 | 0 | 17 | 0 | 60 | 0 | 0 | 0 | 305 | 0 | 336 | 0 | 0 | 152 | 6 | 0 | 84 | 0 | 0 | 0 | 162 | 17 | 16 | 0 | 162 | 0 | 0 | 0 | 5931 | 876 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 839 | 0 | 682.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 303 | 900 | 0 | 4861.96 | 10792.96 | 102.98
07:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 17 | 15 | 20 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.5 | 222 | 0 | 37 | 315 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 783 | 2 | 43 | 0 | 0 | 350 | 351 | 300 | 47 | 0 | 34 | 0 | 104 | 0 | 0 | 17 | 0 | 64 | 0 | 17 | 0 | 315 | 0 | 336 | 0 | 0 | 151 | 6 | 0 | 84 | 0 | 0 | 0 | 162 | 0 | 16 | 0 | 159 | 0 | 0 | 0 | 5775.5 | 876 | 390 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 865 | 0 | 475.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 3 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2 | 0.07 | 0 | 0 | 110 | 220 | 0 | 303 | 840 | 0 | 4722.87 | 10498.37 | 102.97
08:00 | 0 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 4 | 17 | 15 | 20 | 0 | 400 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.38 | 220 | 0 | 5 | 315 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 690 | 6 | 43 | 0 | 0 | 393 | 355 | 300 | 47 | 0 | 34 | 0 | 103 | 4 | 0 | 17 | 0 | 60 | 0 | 24 | 0 | 320 | 0 | 386 | 0 | 0 | 158 | 6 | 0 | 81 | 0 | 0 | 0 | 162 | 0 | 22 | 0 | 160 | 0 | 0 | 0 | 5796.38 | 876 | 395 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 916 | 0 | 475.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 4 | 0 | 0 | 0.53 | 211 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 7 | 0.19 | 0 | 0 | 110 | 220 | 0 | 304 | 906 | 0 | 4867.04 | 10663.42 | 102.95
09:00 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 12 | 40 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 4 | 0 | 21 | 0 | 0 | 400 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.99 | 220 | 0 | 2 | 420 | 0 | 0 | 0 | 0 | 17 | 221 | 0 | 0 | 0 | 712 | 7 | 43 | 0 | 0 | 350 | 300 | 300 | 47 | 0 | 34 | 7 | 102 | 17 | 0 | 12 | 0 | 58 | 0 | 46 | 0 | 305 | 0 | 331 | 0 | 0 | 145 | 6 | 0 | 81 | 0 | 0 | 0 | 161 | 0 | 49 | 0 | 160 | 0 | 0.38 | 0 | 5869.37 | 876 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59 | 915 | 0 | 472.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.11 | 16 | 0 | 0 | 1.12 | 224 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0.19 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1.3 | 10 | 0 | 0 | 0 | 100 | 180 | 0 | 304 | 981 | 0 | 4959.84 | 10829.21 | 102.93
10:00 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 5 | 0 | 21 | 20 | 0 | 430 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.67 | 218 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 716 | 14 | 43 | 0 | 0 | 350 | 300 | 300 | 47 | 0 | 31 | 0 | 102 | 0 | 0 | 12 | 0 | 56 | 0 | 61 | 0 | 310 | 0 | 335 | 0 | 0 | 142 | 6 | 0 | 78 | 0 | 0 | 0 | 161 | 0 | 25 | 0 | 160 | 0 | 2.76 | 0 | 5920.43 | 876 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70.78 | 826 | 0 | 480.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.04 | 18 | 0 | 0 | 1.66 | 225 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.9 | 34 | 0.46 | 0 | 0 | 100 | 180 | 0 | 303 | 960 | 0 | 4931.34 | 10851.77 | 102.91
11:00 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 35 | 0 | 19.5 | 21 | 0 | 400 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.8 | 219 | 0 | 4 | 650 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 720 | 12 | 43 | 0 | 0 | 354 | 355 | 330 | 47 | 0 | 31 | 0 | 100 | 0 | 0 | 15 | 0 | 62 | 0 | 42 | 0 | 315 | 0 | 373 | 0 | 0 | 156 | 6 | 0 | 81 | 0 | 0 | 0 | 161 | 0 | 8 | 0 | 159 | 0 | 12.05 | 0 | 6238.35 | 877 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 813 | 0 | 476.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.56 | 28 | 0 | 0 | 2.21 | 224 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.2 | 42 | 0.58 | 0 | 0 | 100 | 180 | 0 | 304 | 898 | 0 | 4861.03 | 11099.38 | 102.89
12:00 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 17 | 33 | 0 | 50 | 4 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 7 | 0 | 19.5 | 21 | 0 | 400 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.73 | 219 | 0 | 3 | 650 | 0 | 0 | 0 | 0 | 3 | 219 | 0 | 0 | 0 | 612 | 6 | 43 | 1 | 0 | 389 | 345 | 330 | 47 | 0 | 31 | 4 | 101 | 6 | 0 | 5 | 0 | 70 | 0 | 53 | 0 | 310 | 0 | 353 | 0 | 0 | 157 | 0 | 0 | 81 | 0 | 0 | 0 | 161 | 0 | 47 | 5 | 150 | 0 | 4.31 | 0 | 6275.54 | 876 | 386 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 87 | 896 | 0 | 678.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 110 | 0 | 0 | 5.7 | 226 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0.25 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1.7 | 8 | 0.69 | 0 | 0 | 110 | 220 | 0 | 304 | 972 | 0 | 5322.82 | 11598.36 | 102.87
13:00 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17.5 | 17 | 50 | 0 | 60 | 15 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 12 | 0 | 19.5 | 21 | 0 | 380 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.29 | 219 | 0 | 9 | 650 | 0 | 0 | 0 | 0 | 40 | 218 | 0 | 0 | 0 | 575 | 5 | 43 | 45 | 0 | 385 | 345 | 280 | 46 | 0 | 37 | 38 | 100 | 84 | 0 | 5 | 0 | 76 | 0 | 55 | 0 | 310 | 0 | 310 | 0 | 0 | 146 | 6 | 0 | 81 | 0 | 0 | 0 | 161 | 0 | 47 | 35 | 131 | 0 | 13.54 | 0 | 6395.83 | 876 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82.23 | 973 | 0 | 759.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 43 | 0 | 0 | 11.59 | 222 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 1.38 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2.1 | 14 | 0.64 | 0 | 0 | 110 | 220 | 0 | 303 | 1094 | 0 | 5533.59 | 11929.42 | 102.85
14:00 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 17 | 50 | 0 | 60 | 15 | 17 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 4 | 0 | 19.5 | 21 | 0 | 380 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1 | 219 | 0 | 4 | 655 | 0 | 0 | 0 | 0 | 34 | 218 | 0 | 0 | 0 | 580 | 4 | 43 | 60 | 0 | 350 | 347 | 330 | 46 | 0 | 34 | 47 | 100 | 77 | 0 | 17 | 0 | 70 | 0 | 25 | 0 | 305 | 0 | 334 | 0 | 0 | 148 | 6 | 0 | 78 | 0 | 0 | 0 | 161 | 0 | 47 | 35 | 131 | 1 | 0.65 | 0 | 6426.65 | 876 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 1040 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 62 | 0 | 0 | 22.87 | 221 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 1.61 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.7 | 9 | 0.3 | 0 | 0 | 110 | 180 | 0 | 350 | 1092 | 0 | 5501.88 | 11928.53 | 102.83
15:00 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17.5 | 17 | 50 | 0 | 60 | 15 | 21 | 27 | 0 | 330 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 3 | 0 | 19.5 | 21 | 0 | 380 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.91 | 219 | 0 | 3 | 655 | 0 | 0 | 0 | 0 | 32 | 217 | 0 | 0 | 0 | 575 | 7 | 43 | 60 | 0 | 350 | 348 | 330 | 45 | 0 | 34 | 48 | 100 | 78 | 0 | 17 | 0 | 70 | 0 | 35 | 0 | 310 | 0 | 372 | 0 | 0 | 143 | 6 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 49 | 35 | 131 | 0 | 0.9 | 0 | 6469.81 | 876 | 380 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 1093 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.73 | 12 | 0 | 0 | 4.26 | 205 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0.37 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 0.34 | 0 | 0 | 110 | 180 | 0 | 351 | 1090 | 0 | 5467.7 | 11937.51 | 102.82
16:00 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17.5 | 17 | 50 | 0 | 60 | 15 | 35 | 28 | 0 | 330 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 1 | 0 | 19.5 | 0 | 0 | 380 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.71 | 219 | 0 | 2 | 655 | 0 | 0 | 0 | 0 | 34 | 218 | 0 | 0 | 0 | 582 | 3 | 51 | 60 | 0 | 350 | 348 | 330 | 46 | 0 | 34 | 34 | 100 | 51 | 0 | 17 | 0 | 70 | 0 | 18 | 0 | 300 | 0 | 388 | 0 | 0 | 141 | 6 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 48 | 16 | 131 | 0 | 0.45 | 0 | 6310.16 | 881 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33.32 | 1079 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.96 | 14 | 0 | 0 | 1.44 | 186 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0.16 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 3 | 0.16 | 0 | 0 | 110 | 180 | 0 | 353 | 1080 | 0 | 5456.44 | 11766.6 | 102.81
17:00 | 0 | 10 | 16 | 160 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17.5 | 17 | 50 | 15 | 100 | 15 | 35 | 54 | 0 | 330 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 1 | 17 | 0 | 21 | 0 | 380 | 0 | 0 | 74 | 0 | 0 | 0 | 2 | 0 | 24 | 12 | 0.03 | 220 | 0 | 6 | 655 | 0 | 0 | 0 | 0 | 31 | 218 | 0 | 0 | 0 | 587 | 0 | 51 | 65 | 0 | 350 | 300 | 300 | 47 | 0 | 34 | 32 | 101 | 46 | 0 | 17 | 0 | 70 | 4 | 2 | 0 | 305 | 0 | 388 | 0 | 0 | 144 | 6 | 0 | 83 | 0 | 0 | 0 | 160 | 0 | 48 | 26 | 131 | 0 | 0 | 0 | 6458.53 | 881 | 371 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.19 | 1087 | 0 | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 3 | 4 | 0 | 0 | 0.1 | 180 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.1 | 0 | 0.01 | 0 | 0 | 110 | 180 | 0 | 431 | 1080 | 0 | 5542.4 | 12000.93 | 102.8
18:00 | 0 | 50 | 16 | 160 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 35 | 17 | 65 | 60 | 195 | 19 | 35 | 90 | 0 | 330 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 90 | 21 | 21 | 0 | 320 | 12 | 16 | 75 | 0 | 0 | 50 | 63 | 8 | 24 | 12 | 0 | 220 | 18 | 11 | 655 | 0 | 0 | 0 | 0 | 47 | 220 | 0 | 0 | 0 | 567 | 0 | 51 | 95 | 0 | 350 | 356 | 305 | 47 | 0 | 34 | 52 | 101 | 73 | 0 | 18 | 0 | 80 | 8 | 0 | 0 | 310 | 0 | 333 | 0 | 0 | 147 | 6 | 0 | 84 | 0 | 0 | 0 | 160 | 0 | 48 | 47 | 133 | 0 | 0 | 1 | 7042 | 880 | 372 | 0 | 33 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1099 | 0 | 767 | 0 | 35 | 0 | 25 | 18 | 0 | 99 | 13 | 0 | 0 | 0 | 20 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 95 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 110 | 180 | 0 | 503 | 1090 | 0 | 5982 | 13024 | 102.79
19:00 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 35 | 0 | 83 | 0 | 145 | 0 | 35 | 108 | 0 | 330 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 380 | 15 | 16 | 73 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 220 | 50 | 7 | 655 | 0 | 0 | 0 | 0 | 63 | 220 | 0 | 0 | 0 | 574 | 0 | 51 | 80 | 0 | 393 | 356 | 330 | 47 | 0 | 37 | 34 | 102 | 109 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 366 | 0 | 0 | 142 | 6 | 0 | 84 | 0 | 0 | 0 | 160 | 0 | 48 | 47 | 122 | 0 | 0 | 0 | 6947 | 882 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 504 | 1085 | 5 | 5839 | 12786 | 102.78
19:30 | 0 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 0 | 70 | 0 | 45 | 0 | 35 | 108 | 0 | 330 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 400 | 0 | 0 | 75 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 218 | 49 | 6 | 657 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 0 | 0 | 582 | 0 | 51 | 50 | 0 | 393 | 351 | 330 | 47 | 0 | 34 | 34 | 103 | 49 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 325 | 0 | 388 | 0 | 0 | 149 | 6 | 0 | 84 | 0 | 0 | 0 | 160 | 0 | 48 | 47 | 122 | 0 | 0 | 0 | 6819 | 881 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 501 | 1080 | 10 | 5849 | 12668
20:00 | 0 | 0 | 16 | 161 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 35 | 0 | 69 | 0 | 45 | 0 | 35 | 108 | 0 | 330 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 380 | 0 | 0 | 74 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 218 | 34 | 6 | 655 | 0 | 0 | 0 | 0 | 66 | 220 | 0 | 0 | 0 | 580 | 0 | 43 | 50 | 0 | 393 | 356 | 330 | 47 | 0 | 37 | 32 | 103 | 51 | 0 | 12 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 388 | 0 | 0 | 157 | 0 | 0 | 84 | 0 | 0 | 0 | 160 | 0 | 49 | 46 | 124 | 0 | 0 | 0 | 6756 | 881 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 501 | 1090 | 10 | 5821 | 12577 | 102.77
21:00 | 0 | 0 | 16 | 230 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 35 | 0 | 54 | 0 | 45 | 0 | 35 | 72 | 0 | 330 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 392 | 0 | 0 | 75 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 218 | 33 | 15 | 590 | 0 | 0 | 0 | 0 | 65 | 220 | 0 | 0 | 0 | 582 | 0 | 43 | 50 | 0 | 355 | 351 | 330 | 47 | 0 | 37 | 34 | 104 | 51 | 0 | 12 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 388 | 0 | 0 | 159 | 0 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 48 | 46 | 129 | 0 | 0 | 0 | 6708 | 881 | 380 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 0 | 767.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 1100 | 10 | 5857.44 | 12565.44 | 102.76
22:00 | 0 | 0 | 17 | 230 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 52 | 0 | 15 | 0 | 0 | 72 | 0 | 330 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 35 | 13 | 21 | 0 | 370 | 0 | 0 | 75 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 218 | 33 | 15 | 655 | 0 | 0 | 0 | 0 | 66 | 220 | 0 | 0 | 0 | 590 | 0 | 43 | 10 | 0 | 300 | 349 | 330 | 47 | 0 | 35 | 34 | 104 | 49 | 0 | 12 | 0 | 78 | 0 | 0 | 0 | 320 | 0 | 395 | 0 | 0 | 159 | 6 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 48 | 48 | 128 | 0 | 0 | 0 | 6571 | 881 | 401 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 0 | 773.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 501 | 1100 | 10 | 5886.41 | 12457.41 | 102.75
23:00 | 0 | 0 | 17 | 230 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 52 | 0 | 15 | 0 | 0 | 72 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 14 | 21 | 0 | 372 | 0 | 0 | 74 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 216 | 33 | 10 | 655 | 0 | 0 | 0 | 0 | 67 | 220 | 0 | 0 | 0 | 585 | 0 | 43 | 10 | 0 | 285 | 351 | 330 | 47 | 0 | 37 | 33 | 105 | 50 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 320 | 0 | 398 | 0 | 0 | 159 | 6 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 48 | 48 | 128 | 0 | 0 | 0 | 6537 | 886 | 403 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 0 | 765.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 1100 | 10 | 5868.72 | 12405.72 | 102.74
Total KWH | 0 | 131462 | 318811 | 4010400 | 0 | 0 | 0 | 0 | 8740800 | 0 | 0 | 259452 | 221400 | 1179504 | 71520 | 1019444 | 147227 | 265110 | 809280 | 0 | 8013000 | 0 | 0 | 0 | 134300 | 7598994 | 0 | 0 | 61346 | 512400 | 349800 | 429120 | 0 | 9171363.64 | 72136 | 32367 | 1401576 | 0 | 1920 | 436073 | 89690 | 28089 | 387840 | 295680 | 18242 | 5269896 | 378871 | 447840 | 12334545.46 | 0 | 0 | 0 | 8661.6 | 8405448 | 5154574 | 0 | 0 | 0 | 17509089 | 61830 | 1095396 | 761091 | 0 | 8870100 | 8663600 | 7550000 | 1114080 | 0 | 834336 | 553920 | 2426165 | 1041120 | 0 | 319090 | 0 | 1676160 | 15134 | 404173 | 57920 | 7573000 | 0 | 9146000 | 0 | 140520 | 3645081.82 | 146760 | 0 | 1914240 | 0 | 0 | 0 | 4349340 | 113760 | 939600 | 619200 | 3386880 | 2300 | 32590 | 18000 | 163188658.52 | 21370909 | 9335520 | 0 | 18240 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 492480 | 24363640 | 0 | 16508216 | 0 | 32193 | 0 | 221760 | 108384 | 0 | 160800 | 18715 | 0 | 101850 | 346310 | 51896 | 0 | 75008 | 4725455 | 0 | 0 | 0 | 0 | 0 | 8947418 | 0 | 4800 | 0 | 0 | 349499 | 27745 | 634281 | 0 | 0 | 0 | 9687.6 | 141840 | 3546 | 41472 | 0 | 2624000 | 5276110 | 0 | 9344520 | 25440000 | 54000 | 131742294.6 | 294930953.12

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-11-2025 | during | 02-11-2025 | during | 02-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 160 | 160 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 359 | 334 | 400.75 | 400.75 | 367 | 367 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 330 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 4 | 19 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 60 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 21 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 50 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 33 | 65 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 90 | 162 | 162 | 108 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 7 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 320 | 584 | 584 | 525.6 | 525.6 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 90 | 70 | 142 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1769.5 | 2205 | 5743.4 | 5785.4 | 3565.96 | 3642.96
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 220 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 3 | 47 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 63 | 40 | 70 | 70 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 11 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 73 | 75 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.73 | 0 | 3.27 | 0 | 3.27 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 8 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 18 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 12 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 145 | 145 | 17 | 159 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 567 | 612 | 612 | 582 | 582 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 655 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1812.73 | 1998 | 3011.13 | 3032.86 | 2342.77 | 2476.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 345 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 305 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 389 | 350 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 34 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 47 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 95 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 101 | 101 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 6 | 73 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 80 | 160 | 160 | 84 | 84 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 18 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 4 | 52 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 53 | 0 | 72 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1425 | 1570 | 2623.56 | 2551.56 | 2334.86 | 2275.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-11-2025 | during | 02-11-2025 | during | 02-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 150 | 133 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 5 | 47 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 48 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 4.31 | 0 | 29 | 0 | 29 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 1 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 206.31 | 229 | 360.9 | 330 | 307.4 | 276.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 161 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 6 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 353 | 333 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1062 | 1040 | 1208 | 1208 | 1110 | 1110
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 876 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 386 | 372 | 410 | 410 | 370 | 370 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 896 | 1099 | 0 | 0 | 1100 | 1100 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2283 | 2422 | 2402 | 2312 | 2707 | 2617
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 304 | 503 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 15 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 972 | 1090 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1606.69 | 1898 | 1840 | 1839 | 1699 | 1698
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 13 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 226 | 179 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 337 | 339 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 99 | 98 | 98 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 18 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 25 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.25 | 0 | 0 | 0 | 0 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 678.48 | 767 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 5.7 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1421.43 | 1495 | 2488.99 | 2327.99 | 2315.21 | 2154.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 72 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.7 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 2 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 8 | 0 | 116.43 | 0 | 116.43 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 11.7 | 167 | 414.23 | 262 | 360.23 | 208
System Total |  |  |  |  | 28823.2 | 28364.095 | 11598.36 | 13024 | 20092.21 | 19648.81 | 16742.43 | 16459.03
Forecast Scenario (02-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12200 |  | 0 |  | 12200
|  |  |  | 1:00 | 11890 |  | 0 |  | 11890
|  |  |  | 2:00 | 11540 |  | 0 |  | 11540
|  |  |  | 3:00 | 11460 |  | 0 |  | 11460
|  |  |  | 4:00 | 11120 |  | 0 |  | 11120
|  |  |  | 5:00 | 10700 |  | 0 |  | 10700
|  |  |  | 6:00 | 10540 |  | 0 |  | 10540
|  |  |  | 7:00 | 10780 |  | 0 |  | 10780
|  |  |  | 8:00 | 11010 |  | 0 |  | 11010
|  |  |  | 9:00 | 11120 |  | 0 |  | 11120
|  |  |  | 10:00 | 11210 |  | 0 |  | 11210
|  |  |  | 11:00 | 11790 |  | 0 |  | 11790
|  |  |  | 12:00 | 12260 |  | 0 |  | 12260
|  |  |  | 13:00 | 12800 |  | 0 |  | 12800
|  |  |  | 14:00 | 12640 |  | 0 |  | 12640
|  |  |  | 15:00 | 12640 |  | 0 |  | 12640
|  |  |  | 16:00 | 12760 |  | 0 |  | 12760
|  |  |  | 17:00 | 12680 |  | 0 |  | 12680
|  |  |  | 18:00 | 14190 |  | 0 |  | 14190
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 14240 |  | 0 |  | 14240
|  |  |  | 19:30 | 14000 |  | 0 |  | 14000
|  |  |  | 20:00 | 13980 |  | 0 |  | 13980
|  |  |  | 21:00 | 13890 |  | 0 |  | 13890
|  |  |  | 22:00 | 13620 |  | 0 |  | 13620
|  |  |  | 23:00 | 13480 |  | 0 |  | 13480
Probable Maximum Temperature: |  |  | 30.80°C
Probable Maximum Demand at Day Peak: |  |  | 12260.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14240.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14240.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 294.54 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:33 hrs on 02-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11598.36 | MW | 12:00 Hr. | Energy Generated |  |  | 294.931 |  | MKWHr.
| Day Peak Demand |  |  | 11633.89 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.247 |  | MKWHr.
| Evening Peak Generation |  |  | 13024 | MW | 18:00 Hr. | Energy Demand |  |  | 295.178 |  | MKWHr.
| Evening Peak Demand |  |  | 13024 | MW | 18:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 10498.37 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 973.51 |  | MMCFD
| Maximum Generation of the Day |  |  | 13206.43 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.7197 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.3135 | 0 | 5.0699 | 0 | 0 | 0.061346 | 0 | 0 | 43.4447 | Gas | 135.999 | Gas | 478742935.735
| Chattogram Zone |  |  | 5.6024 | 29.8436 | 11.5364 | 0 | 5.2699 | 0.080072 | 0 | 0.00192 | 52.3344 | Coal | 88.9918 | Coal | 567708714.1462
| Cumilla Zone |  |  | 30.8728 | 0 | 2.4292 | 0 | 0 | 0.40417 | 1.6762 | 0 | 35.3823 | HFO | 22.4173 | HFO | 383775947.244
| Mymensingh Zone |  |  | 3.3869 | 0 | 1.6906 | 0 | 0 | 0.03489 | 0 | 0 | 5.1123 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9149 | Hydro | 5.2699 | Hydro | 526989.6
| Khulna Zone |  |  | 9.3355 | 24.3636 | 0.01824 | 0 | 0 | 0.49248 | 22.2829 | 0 | 56.4928 | Solar | 1.7837 | Solar | 26463045.726
| Barishal Zone |  |  | 7.9001 | 34.7845 | 0.095472 | 0 | 0 | 0.003546 | 0 | 0 | 42.7836 | Import | 40.4673 | Import | 229661839.55
| Rajshahi Zone |  |  | 13.6729 | 0 | 0.59375 | 0 | 0 | 0.52797 | 16.5082 | 0 | 31.3028 | Wind | 0.00192 | Wind | 28243.2
| Rangpur Zone |  |  | 0 | 0 | 0.98378 | 0 | 0 | 0.17927 | 0 | 0 | 1.1631
| Total |  |  | 135.999 | 88.9918 | 22.4173 | 0 | 5.2699 | 1.7837 | 40.4673 | 0.00192 | 294.931
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 478742935.735 |  | Hydro | 526989.6
|  |  |  | Coal | 567708714.1462 |  | Solar | 26463045.726
|  |  |  | HFO | 383775947.244 |  | Import | 229661839.55
|  |  |  | HSD | 0 |  | Wind | 28243.2
[5 empty] | Total: | 168,69,07,715 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3709 | Peak Hr Flow | 880.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49104363.7 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.5082 | Peak Hr Flow | 767.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2220 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6762 | Peak Hr Flow | 80.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2498 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.5553 | Peak Hr Flow | 1727.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4699
|  |  |  | Chattogram |  | 0 |  | 1595
|  |  |  | Cumilla |  | 0 |  | 1380
|  |  |  | Mymensingh |  | 0 |  | 894
|  |  |  | Sylhet |  | 0 |  | 571
|  |  |  | Khulna |  | 0 |  | 1531
|  |  |  | Barishal |  | 0 |  | 453
|  |  |  | Rajshahi |  | 0 |  | 1061
|  |  |  | Rangpur |  | 0 |  | 674
|  |  |  | Total |  | 0 |  | 12858
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:04 | 15:23 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to For the
phile driving work under the drainage improvement project of Chattogram city, implemented
by the Bangladesh Army.
| 08:14 | 16:17 | Naogaon 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance.
| 08:14 | 16:15 | Naogaon 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenace.
| 08:23 | 10:22 | Bhulta 132/33kV S/S GT2 HT Scheduled S/D Due to GT-2 HT & LT bushing maintenance | [7 empty] | 90.0MW load
interrup.
| 08:26 | 17:16 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Scheduled S/D from BIPTC end Due to Annual
maintenance and from Jhenaidah 230/132kV end Due to Annual maintenance
| 09:29 | 09:47 | Jaldhaka 132/33kV S/S 406T-1 LT Tripped showing U/F realy relays Due to Due to RPBS | [7 empty] | 19.0MW load
|  |  | Khaprikhal 33 kv feeder triped. | [7 empty] | interrup.
| 09:29 | 09:47 | Jaldhaka 132/33kV S/S 416T-2 LT Tripped showing E/F realy relays Due to Due to RPBS | [7 empty] | 19.0MW load
|  |  | Khaprikhal 33 kv feeder triped | [7 empty] | interrup.
| 09:31 | 15:26 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
For Annual maintenance
| 09:40 | 16:02 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to
annual maintenance
| 09:55 |  | Bagabari-71-----Bera 132 KV ckt S/D. (upto tower No. 268).
| 10:05 | 10:28 | Ghatail 132/33kV S/S T-1 LT Tripped showing REC 650, ABB relays Due to Due to 33 kV | [7 empty] | 18.0MW load
|  |  | Dhanbari Feeder (MPBS-1) CT ) Brust. | [7 empty] | interrup.
| 10:05 | 10:29 | Ghatail 132/33kV S/S T-2 LT Tripped showing REC 650, ABB relays Due to Due to 33 kV | [7 empty] | 18.0MW load
|  |  | Dhanbari Feeder (MPBS-1) CT ) Brust. | [7 empty] | interrup.
| 10:12 | 18:10 | Baghabari-Bangura 132 kV Ckt-1 Project Work S/D from Bhangura 132/33kV end Due to OFCl | [7 empty] | 12.0MW load
|  |  | project shutdown from Bhagabari | [7 empty] | interrup. Bhangura
132/33kV end
| 10:47 | 16:07 | Chattak-Sunamganj 132 kV Ckt-1 Scheduled S/D from Sunamganj 132/33kV end Due to Due to
Annual Maintenance
| 10:48 | 16:04 | Chhatak 132/33kV S/S Sunamganj 1 Scheduled S/D Due to Annual Maintenance
| 11:09 | 17:31 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kv bus of T-2 shutdown taken by | [7 empty] | 65.0MW load
|  |  | Dpbs-1,due to after HDD boring, Cable connection & remove | [7 empty] | interrup.
| 11:09 | 17:31 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to After HDD boring work,Cable | [7 empty] | 65.0MW load
|  |  | connect& remove | [7 empty] | interrup.
| 11:20 | 13:12 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to 33kv bus radhot maintanas. | [7 empty] | 30.0MW load
interrup.
| 11:20 | 13:12 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to 33kv busbar radhot maintans. | [7 empty] | 30.0MW load
interrup.
| 11:23 |  | SS Power Shutdown with remarks:- unit-2
| 11:23 |  | SS Power Shutdown
| 11:23 |  | Bashkhali SS Power Unit-2 was shutdown due to annual maintenance purposes.
| 11:28 |  | SS Power Synchronized with remarks:- unit-1 (False )
| 11:28 |  | SS Power Synchronized with remarks:- unit-1 (False )
| 11:39 | 14:29 | Lakshmipur 132/33kV S/S Transformer-2 HT Forced S/D Due to Red Hot remove. | [7 empty] | 10.0MW load
interrup.
| 11:44 | 12:37 | BIPTC S/S 10CF13 Tripped showing Tripped by 87 stage 2 (L1L2L3) relays.
| 12:00 |  | Day Peak Generation: 11594 MW.
| 12:28 | 12:30 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to protection test.
| 12:28 | 12:30 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to protection test.
| 12:32 | 13:59 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to maintenance work on 33kv bus loop at | [7 empty] | 10.0MW load
|  |  | kachuadanga feeder. | [7 empty] | interrup.
| 12:32 | 14:00 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to maintenance work on 33kv bus loop at | [7 empty] | 10.0MW load
|  |  | kachuadanga feeder. | [7 empty] | interrup.
|  | 15:21 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
| 15:50 | 16:21 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lockout Relay, OC/EF Relay relays Due
to Earth fault in Bisic Feeder and Line to Line fault in Jamuna Feeder
| 15:50 | 16:23 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Trip Relay relays Due to Earth fault in
Bisic Feeder and Line to Line fault in Jamuna Feeder
| 15:50 | 16:12 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing Lockout relay, 132 kv OC/EF Relay
relays Due to Earth fault in Bisic Feeder and Line to Line fault in Jamuna Feeder
| 15:50 | 16:12 | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing Lockout Relay, OC/EF Relay relays Due
to Earth fault in Bisic Feeder and Line to Line fault in Jamuna Feeder
| 17:23 | 17:41 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB Initiation, Master Trip Relay
Operated. relays Due to Raining & Thundering.
| 17:25 | 17:43 | Keraniganj-Nawabganj 132kV Ckt-1 Tripped from Nawabganj 132/33kV end showing Distance | [7 empty] | and 11.0MW load
|  |  | protection, Overcurrent protection, l Lockout relay. relays Due to Overcurrent and from | [7 empty] | interrup.
|  |  | Keranigonj 230/132/33kV end showing 86.1 relays Due to 50/67N EF , Zone-01,distance | [7 empty] | Keranigonj
|  |  | 11.6km, R phase IL1=5.46 | [7 empty] | 230/132/33kV end
| 17:31 | 18:36 | Aminbazar-Kallyanpur 132kV Ckt-2 Tripped from Kallyanpur 132/33kV end showing 87L
operated, Phase C, General Trip relays. and from Aminbazar 400/230/132kV end showing
Siprotec relays Due to Earth Fault
| 17:42 |  | Madaripur 132/33kV S/S Capacitor Bank Scheduled S/D Due to Annual maintenance
| 18:00 |  | Evening Peak Generation is 13024 MW.
| 19:17 | 19:59 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to Red hot 33 kv side
| 19:20 | 19:57 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to Red hot 33 kv side
|  | 19:57 | Bhangura 132/33kV S/S Tr-1(403T) HT is restored.
|  | 19:59 | Bhangura 132/33kV S/S Tr-1(403T) LT is restored.
| 06:44 |  | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Tripped showing Differential over current | [7 empty] | 25.0MW load
|  |  | relays Due to 33kV Nawabganj-1 feeder trip | [7 empty] | interrup.
| 07:04 |  | Chattak-Sunamganj 132 kV Ckt-1 Scheduled S/D from Sunamganj 132/33kV end Due to Due to
Annual Maintenance
| 07:05 |  | Chhatak 132/33kV S/S Sunamganj 1 Scheduled S/D Due to Annual Maintanance
| 07:10 |  | Barishal 132/33kV S/S Bus B Scheduled S/D Due to Annual maintenance
| 07:12 |  | GPH 230/33kV S/S Transformer -2 (D07) HT Scheduled S/D Due to Maintenance Works
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 160 | 4010400 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 334 | 8740800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 8013000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 19 | 147227 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7598994 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259452 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 60 | 71520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265110 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 134300 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 349800 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 429120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 318811 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1019444 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 65 | 1179504 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 131462 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 809280 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 61346 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 221400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 9171363.64 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 512400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2205 | 43444733.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 8661.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 61830 | 33kV grid Low Voltage & Low Irradiation
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5269896 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5154574 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 47 | 8405448 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 63 | 89690 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 436073 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 387840 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 447840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 75 | 1401576 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 32367 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 8 | 28089 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 18 | 378871 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 295680 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 12 | 72136 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 567 | 17509089 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 1920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 655 | 12334545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 1998 | 52334368.06
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8663600 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 305 | 7550000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 350 | 8870100 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 834336 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1114080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1095396 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 95 | 761091 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 57920 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 2426165 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 73 | 1041120 | -
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1676160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 15134 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 319090 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 52 | 553920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 404173 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1570 | 35382285
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 133 | 3386880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 2300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 619200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 939600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 32590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 1 | 18000 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 113760 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 229 | 5112330
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 140520 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3645081.82 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1914240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 4349340 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 146760 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7573000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 333 | 9146000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1040 | 26914941.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 21370909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 18240 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 372 | 9335520 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 492480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1099 | 24363640 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2422 | 56492789
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 9344520 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 15 | 41472 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2624000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 25440000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5276110 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 54000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3546 | -
Barishal Area Total |  |  |  |  | 2858 | 1898 | 42783648
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 101850 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 32193 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 13 | 18715 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 179 | 4725455 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 339 | 8947418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 51896 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 160800 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 18 | 108384 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 25 | 221760 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 4800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 767 | 16508216 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 75008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 346310 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1495 | 31302805
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 72 | 634281 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 9687.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 349499 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 27745 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 141840 | -
Rangpur Area Total |  |  |  |  | 950 | 167 | 1163052.6
Eastern Grid Total |  |  |  |  | 17383.855 | 7042 | 163188658.52
Western Grid Total |  |  |  |  | 10980.24 | 5982 | 131742294.6
National Grid Total |  |  |  |  | 28364.095 | 13024 | 294930953.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9138.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3718.6 | MW
i) Dhaka area |  |  | 4699.1 |  | MW | i) Khulna area |  |  |  | 1531 | MW
ii) Chattogram area |  |  | 1595 |  | MW | ii) Barishal area |  |  |  | 453 | MW
iii) Cumilla area |  |  | 1379.82 |  | MW | iii) Rajshahi area |  |  |  | 1060.6 | MW
iv) Mymensingh area |  |  | 894 |  | MW | iv) Rangpur area |  |  |  | 674 | MW
v) Sylhet area |  |  | 571 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12857.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 90 | 18:00 | 133 | Niamatpur | 41 | 19:30
2 | AKSML | 134 | 00:00 | 68 | Ishurdi | 70 | 18:00 | 134 | Noapara | 44 | 21:00
3 | Aftabnagar | 36 | 00:00 | 69 | Jaldhaka | 54 | 18:00 | 135 | PHP | 5 | 18:30
4 | Agargaon | 117 | 19:30 | 70 | Jamalpur | 97 | 00:00 | 136 | Pabna | 97 | 18:00
5 | Agrabad | 100 | 18:30 | 71 | Jashore | 134 | 18:30 | 137 | Palashbari | 76 | 18:00
6 | Amnura | 17 | 20:00 | 72 | Jhenaidah | 125 | 18:00 | 138 | Panchagarh | 40 | 18:00
7 | Ashuganj | 86 | 00:00 | 73 | Joydebpur | 133 | 19:00 | 139 | Patiya | 100 | 19:30
8 | BSRM | 208 | 18:00 | 74 | Joypurhat | 40 | 18:00 | 140 | Patuakhali | 80 | 21:00
9 | Bagerhat | 80 | 18:00 | 75 | Juldah | 8 | 19:00 | 141 | Payra | 34 | 00:00
10 | Bajitpur | 88 | 18:00 | 76 | KSRM | 15 | 07:00 | 142 | Postogola | 65 | 13:00
11 | Bakulia | 88 | 18:00 | 77 | Kabirpur | 219 | 08:00 | 143 | Purbachal | 35 | 13:00
12 | Banani | 40.6 | 14:00 | 78 | Kachua | 89 | 18:00 | 144 | Purbasadipur | 85 | 12:00
13 | Bangabhaban | 10 | 10:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rahanpur | 24 | 19:00
14 | Barapukuria | 43 | 18:00 | 80 | Kalurghat | 52 | 18:00 | 146 | Rahim | 45 | 11:00
15 | Barguna | 16 | 01:00 | 81 | Kamrangirchar | 76 | 16:00 | 147 | Rajbari | 76 | 18:00
16 | Barishal | 120 | 18:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 115 | 19:00
17 | Barishal-230 | 96 | 19:00 | 83 | Kasba | 34 | 00:00 | 149 | Rajshahi | 119 | 00:00
18 | Baroaulia | 64 | 00:00 | 84 | Kazla | 99 | 18:00 | 150 | Rajshahi-230 | 29 | 13:00
19 | Baroirhat | 72 | 18:00 | 85 | Keranigonj | 80 | 13:00 | 151 | Ramganj | 112 | 21:00
20 | Bashundhara | 180 | 13:00 | 86 | Khagrachori | 32 | 18:00 | 152 | Rampur | 44 | 00:00
21 | BashundharaCement | 8 | 11:00 | 87 | Khulna | 73 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 74 | 18:00 | 88 | Khulshi | 193 | 18:00 | 154 | Rangpur | 106 | 18:00
23 | Benapole | 58 | 18:00 | 89 | Kishoreganj | 119 | 00:00 | 155 | Ruppur | 5 | 13:00
24 | Bhaluka | 118 | 09:00 | 90 | Kodda | 298 | 09:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 53 | 14:00 | 91 | Kulaura | 46 | 00:00 | 157 | Saidpur | 78 | 18:00
26 | Bhangura | 42 | 19:00 | 92 | Kurigram | 43 | 17:00 | 158 | Satkhira | 108 | 00:00
27 | Bheramara(GK) | 56 | 18:30 | 93 | Kushtia | 146 | 18:00 | 159 | Satmasjid | 100 | 13:00
28 | Bhulta | 206 | 07:00 | 94 | Laksam | 34 | 22:00 | 160 | Savar | 214 | 15:00
29 | Bog-Sherpur | 52 | 00:00 | 95 | Lakshmipur | 33 | 20:00 | 161 | SevenRings | 13.19 | 12:00
30 | Bogura | 125 | 18:30 | 96 | Lalbag | 58 | 12:00 | 162 | ShahCement | 28 | 00:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 35 | 19:00 | 163 | Shahjadpur | 65 | 00:00
32 | Brahmanbaria | 130 | 00:00 | 98 | MI_Cement | 7.5 | 02:00 | 164 | Shahjibazar | 124 | 00:00
33 | Cantonment | 158 | 13:00 | 99 | Madanganj | 40 | 00:00 | 165 | Shahmirpur | 52 | 18:00
34 | Chandina | 15.85 | 20:00 | 100 | Madaripur | 99 | 00:00 | 166 | Shariatpur | 83 | 00:00
35 | Chandpur | 78 | 00:00 | 101 | Madartek | 94 | 00:00 | 167 | Sherpur | 106 | 18:00
36 | Chandraghona | 38 | 18:00 | 102 | Madunaghat | 54 | 18:30 | 168 | Shikalbaha | 41 | 14:00
37 | Chapai | 54 | 18:00 | 103 | Magura | 63 | 18:00 | 169 | Shitalakhya | 82.3 | 16:00
38 | Charsaidpur | 37 | 15:00 | 104 | Mahasthangarh | 54 | 18:00 | 170 | Sholosohor | 48 | 14:00
39 | Chauddagram | 70 | 22:00 | 105 | Maijdee | 38 | 19:30 | 171 | Shyampur | 136 | 12:00
40 | Chhatak | 38 | 00:00 | 106 | Manikganj | 111 | 11:00 | 172 | Siddhirganj | 122 | 12:00
41 | Chowmuhani | 169 | 18:00 | 107 | Maniknagar | 62 | 13:00 | 173 | Sirajganj | 82 | 00:00
42 | Chuadanga | 104 | 18:00 | 108 | Matarbari | 53 | 18:00 | 174 | Sonargaon | 128 | 16:00
43 | Coxsbazar | 144 | 20:00 | 109 | Matuail | 68 | 12:00 | 175 | Sreemongol | 81 | 00:00
44 | Cumilla(N) | 144 | 19:30 | 110 | Metrorail_Motijheel | 26 | 09:00 | 176 | Sreepur | 117 | 18:00
45 | Cumilla(S) | 152 | 18:00 | 111 | Metrorail_Uttara | 9 | 19:00 | 177 | Srinagar | 45.3 | 00:00
46 | Daganbhuiyan | 0 | 03:00 | 112 | Millgate | 125 | 12:00 | 178 | Sunamganj | 60 | 00:00
47 | Daudkandi | 145 | 00:00 | 113 | Mirpur | 133 | 12:00 | 179 | Sylhet | 48 | 00:00
48 | DhakaUniversity | 66 | 13:00 | 114 | Mirsorai | 9 | 15:00 | 180 | Sylhet-132 | 125 | 18:00
49 | Dhamrai | 120 | 09:00 | 115 | Mirzapur | 46 | 18:30 | 181 | TK | 24.5 | 18:00
50 | Dhanmondi | 131 | 13:00 | 116 | Mithapukur | 40 | 18:00 | 182 | Tangail | 156 | 00:00
51 | Dohazari | 105 | 19:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 17 | 18:00
52 | Faridpur | 142 | 00:00 | 118 | Mogbazar | 88.6 | 13:00 | 184 | Thakurgaon | 68 | 18:00
53 | Fatullah | 116 | 16:00 | 119 | Mongla | 32 | 18:00 | 185 | Tongi | 113 | 13:00
54 | Fenchuganj | 40 | 00:00 | 120 | Motijheel | 43 | 12:00 | 186 | Ullahpara | 32 | 00:00
55 | Feni | 116 | 18:00 | 121 | Muktagacha | 33 | 00:00 | 187 | Ullon | 62 | 00:00
56 | GPH | 80 | 08:00 | 122 | Munshiganj | 112 | 00:00 | 188 | Uttara | 85 | 13:00
57 | Ghatail | 68 | 00:00 | 123 | Muradnagar | 41 | 18:00 | 189 | UttaraNew | 33 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 187 | 00:00 | 190 | Zigatola | 74 | 13:00
59 | Ghorashal-230 | 89 | 00:00 | 125 | Naogaon | 88 | 19:30
60 | Goalpara | 36 | 00:00 | 126 | Narail | 55 | 18:00
61 | Gollamari | 80 | 00:00 | 127 | Narinda | 70 | 13:00
62 | Gopalganj | 93 | 00:00 | 128 | Narshingdi | 170 | 00:00
63 | Gulshan | 110 | 13:00 | 129 | Natore | 104 | 18:00
64 | Halishahar | 75 | 09:00 | 130 | Nawabganj | 42.6 | 20:00
65 | HaripurSBU | 136 | 16:00 | 131 | Netrakona | 108 | 18:00
66 | Hasnabad | 90 | 13:00 | 132 | New | 56 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13206.43 | 18 |  | 13225.24
1:00 | 12698.16 | 16 |  | 12715.16
2:00 | 12135.27 | 0 |  | 12135.27
3:00 | 11717.19 | 0 |  | 11717.19
4:00 | 11341.11 | 0 |  | 11341.11
5:00 | 11060.84 | 0 |  | 11060.84
6:00 | 10792.96 | 0 |  | 10792.96
7:00 | 10498.37 | 0 |  | 10498.37
8:00 | 10663.42 | 37 |  | 10702.09
9:00 | 10829.21 | 0 |  | 10829.21
10:00 | 10851.77 | 0 |  | 10851.77
11:00 | 11099.38 | 0 |  | 11099.38
12:00 | 11598.36 | 34 |  | 11633.89
13:00 | 11929.42 | 53 |  | 11984.81
14:00 | 11928.53 | 44 |  | 11974.51
15:00 | 11937.51 | 45 |  | 11984.54
16:00 | 11766.6 | 0 |  | 11766.6
17:00 | 12000.93 | 0 |  | 12000.93
18:00 | 13024 | 0 |  | 13024
19:00 | 12786 | 0 |  | 12786
19:30 | 12668 | 0 |  | 12668
20:00 | 12577 | 0 |  | 12577
21:00 | 12565.44 | 0 |  | 12565.44
22:00 | 12457.41 | 0 |  | 12457.41
23:00 | 12405.72 | 0 |  | 12405.72
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7292 | 5914.43 | 13206.43 | DAILY GENERATION CURVE
00:30 | 7187 | 5765.295 | 12952.295
01:00 | 7082 | 5616.16 | 12698.16 | 01-11-2025
01:30 | 6840.5 | 5576.215 | 12416.715
02:00 | 6599 | 5536.27 | 12135.27
02:30 | 6449 | 5477.23 | 11926.23
03:00 | 6299 | 5418.19 | 11717.19
03:30 | 6217.5 | 5311.65 | 11529.15
04:00 | 6136 | 5205.11 | 11341.11
04:30 | 6094.5 | 5106.475 | 11200.975
05:00 | 6053 | 5007.84 | 11060.84
05:30 | 5992 | 4934.9 | 10926.9
06:00 | 5931 | 4861.96 | 10792.96
06:30 | 5853.25 | 4792.415 | 10645.665
07:00 | 5775.5 | 4722.87 | 10498.37
07:30 | 5785.94 | 4794.955 | 10580.895
08:00 | 5796.38 | 4867.04 | 10663.42
08:30 | 5832.875 | 4913.44 | 10746.315
09:00 | 5869.37 | 4959.84 | 10829.21
09:30 | 5894.9 | 4945.59 | 10840.49
10:00 | 5920.43 | 4931.34 | 10851.77
10:30 | 6079.39 | 4896.185 | 10975.575
11:00 | 6238.35 | 4861.03 | 11099.38
11:30 | 6256.945 | 5091.925 | 11348.87
12:00 | 6275.54 | 5322.82 | 11598.36
12:30 | 6335.685 | 5428.205 | 11763.89
13:00 | 6395.83 | 5533.59 | 11929.42
13:30 | 6411.24 | 5517.735 | 11928.975
14:00 | 6426.65 | 5501.88 | 11928.53
14:30 | 6448.23 | 5484.79 | 11933.02
15:00 | 6469.81 | 5467.7 | 11937.51
15:30 | 6389.985 | 5462.07 | 11852.055
16:00 | 6310.16 | 5456.44 | 11766.6
16:30 | 6384.345 | 5499.42 | 11883.765
17:00 | 6458.53 | 5542.4 | 12000.93
17:30 | 6750.265 | 5762.2 | 12512.465
18:00 | 7042 | 5982 | 13024
18:30 | 6994.5 | 5910.5 | 12905
19:00 | 6947 | 5839 | 12786
19:30 | 6819 | 5849 | 12668
20:00 | 6756 | 5821 | 12577
20:30 | 6732 | 5839.22 | 12571.22 |  | Executive Engineer
21:00 | 6708 | 5857.44 | 12565.44 |  | Network Operation Division
21:30 | 6639.5 | 5871.925 | 12511.425
22:00 | 6571 | 5886.41 | 12457.41
22:30 | 6554 | 5877.565 | 12431.565
23:00 | 6537 | 5868.72 | 12405.72

## En-Curve
QF-LDC-12
Date | 01-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4084 | 1698 | 900 | 38 | 84 | 768.43 | 218 | 4141 | 0 | 303 | 972 | 0 | 0 | 0 | 18 | DAILY ENERGY CURVE
00:30 | 4063.5 | 1693.5 | 900 | 38 | 83 | 764.795 | 218 | 4128.5 | 0 | 219.5 | 843.5 | 0 | 0 | 0 | 17 | 01-11-2025
01:00 | 4043 | 1689 | 900 | 38 | 82 | 761.16 | 218 | 4116 | 0 | 136 | 715 | 0 | 0 | 0 | 16
01:30 | 3994 | 1696 | 899.5 | 38 | 81 | 763.715 | 218 | 4087 | 0 | 97 | 542.5 | 0 | 0 | 0 | 8 | Energy Generated | 294.931 |  | MKWHr
02:00 | 3945 | 1703 | 899 | 38 | 80 | 766.27 | 218 | 4058 | 0 | 58 | 370 | 0 | 0 | 0 | 0 | Energy not Served | 0.247 |  | MKWHr
02:30 | 3957 | 1707 | 899 | 38 | 78 | 768.73 | 219.5 | 3938 | 0 | 54 | 267 | 0 | 0 | 0 | 0 | Total Energy Requirement | 295.178 |  | MKWHr
03:00 | 3969 | 1711 | 899 | 38 | 76 | 771.19 | 221 | 3818 | 0 | 50 | 164 | 0 | 0 | 0 | 0
03:30 | 3970 | 1705.5 | 899 | 38 | 72 | 743.65 | 221 | 3709 | 0 | 33.5 | 137.5 | 0 | 0 | 0 | 0
04:00 | 3971 | 1700 | 899 | 38 | 68 | 716.11 | 221 | 3600 | 0 | 17 | 111 | 0 | 0 | 0 | 0
04:30 | 3971.5 | 1702.5 | 887.5 | 38 | 67 | 699.975 | 221.5 | 3492.5 | 0 | 17 | 103.5 | 0 | 0 | 0 | 0
05:00 | 3972 | 1705 | 876 | 38 | 66 | 683.84 | 222 | 3385 | 0 | 17 | 96 | 0 | 0 | 0 | 0
05:30 | 3933 | 1697.5 | 876 | 38 | 63 | 683.4 | 222 | 3301 | 0 | 17 | 96 | 0 | 0 | 0 | 0
06:00 | 3894 | 1690 | 876 | 38 | 60 | 682.96 | 222 | 3217 | 0 | 17 | 96 | 0 | 0 | 0 | 0
06:30 | 3916.5 | 1680 | 876 | 38 | 62 | 579.105 | 222 | 3161.5 | 18.06 | 17 | 75.5 | 0 | 0 | 0 | 0
07:00 | 3939 | 1670 | 876 | 38 | 64 | 475.25 | 222 | 3106 | 36.12 | 17 | 55 | 0 | 0 | 0 | 0
07:30 | 3984 | 1651 | 876 | 38 | 62 | 475.13 | 221 | 3118.5 | 60.265 | 18 | 77 | 0 | 0 | 0 | 18.5
08:00 | 4029 | 1632 | 876 | 38 | 60 | 475.01 | 220 | 3131 | 84.41 | 19 | 99 | 0 | 0 | 0 | 37
08:30 | 3944.5 | 1587 | 876 | 38 | 59 | 473.565 | 220 | 3231.5 | 120.75 | 22 | 174 | 0 | 0 | 0 | 18.5
09:00 | 3860 | 1542 | 876 | 38 | 58 | 472.12 | 220 | 3332 | 157.09 | 25 | 249 | 0 | 0 | 0 | 0
09:30 | 3855.5 | 1566.5 | 876 | 38 | 57 | 476.31 | 219 | 3318.5 | 197.18 | 25 | 211.5 | 0 | 0 | 0 | 0
10:00 | 3851 | 1591 | 876 | 38 | 56 | 480.5 | 218 | 3305 | 237.27 | 25 | 174 | 0 | 0 | 0 | 0
10:30 | 3936.5 | 1589.25 | 876.5 | 38 | 59 | 478.49 | 218.5 | 3345 | 250.835 | 20.5 | 163 | 0 | 0 | 0 | 0
11:00 | 4022 | 1587.5 | 877 | 38 | 62 | 476.48 | 219 | 3385 | 264.4 | 16 | 152 | 0 | 0 | 0 | 0
11:30 | 4005.5 | 1597 | 876.5 | 38 | 66 | 577.48 | 219 | 3409.5 | 308.89 | 16 | 235 | 0 | 0 | 0 | 17
12:00 | 3989 | 1606.5 | 876 | 38 | 70 | 678.48 | 219 | 3434 | 353.38 | 16 | 318 | 0 | 0 | 0 | 34
12:30 | 3932.5 | 1621.5 | 876 | 38 | 73 | 719.065 | 219 | 3514.5 | 305.075 | 16 | 449.25 | 0 | 0 | 0 | 43.5
13:00 | 3876 | 1636.5 | 876 | 38 | 76 | 759.65 | 219 | 3595 | 256.77 | 16 | 580.5 | 0 | 0 | 0 | 53
13:30 | 3875 | 1617 | 876 | 38 | 73 | 760.825 | 219 | 3656 | 212.65 | 16 | 585.5 | 0 | 0 | 0 | 48.5
14:00 | 3874 | 1597.5 | 876 | 38 | 70 | 762 | 219 | 3717 | 168.53 | 16 | 590.5 | 0 | 0 | 0 | 44
14:30 | 3898.5 | 1588 | 876 | 38 | 70 | 764.5 | 219 | 3740.5 | 126.52 | 16 | 596 | 0 | 0 | 0 | 44.5
15:00 | 3923 | 1578.5 | 876 | 38 | 70 | 767 | 219 | 3764 | 84.51 | 16 | 601.5 | 0 | 0 | 0 | 45
15:30 | 3913.5 | 1525.5 | 878.5 | 38 | 70 | 768.5 | 219 | 3756.5 | 85.555 | 16 | 581 | 0 | 0 | 0 | 22.5
16:00 | 3904 | 1472.5 | 881 | 38 | 70 | 770 | 219 | 3749 | 86.6 | 16 | 560.5 | 0 | 0 | 0 | 0
16:30 | 3859.5 | 1521.25 | 881 | 38 | 70 | 771 | 219.5 | 3794.5 | 49.515 | 68 | 611.5 | 0 | 0 | 0 | 0
17:00 | 3815 | 1570 | 881 | 38 | 70 | 772 | 220 | 3840 | 12.43 | 120 | 662.5 | 0 | 0 | 0 | 0
17:30 | 3815.5 | 1558 | 880.5 | 38 | 75 | 769.5 | 220 | 3877 | 6.215 | 324.5 | 948.25 | 0 | 0 | 0 | 0
18:00 | 3816 | 1546 | 880 | 38 | 80 | 767 | 220 | 3914 | 0 | 529 | 1234 | 0 | 0 | 0 | 0
18:30 | 3868.5 | 1578 | 881 | 38 | 80 | 763.5 | 220 | 3942.5 | 0 | 335.5 | 1198 | 0 | 0 | 0 | 0
19:00 | 3921 | 1610 | 882 | 38 | 80 | 760 | 220 | 3971 | 0 | 142 | 1162 | 0 | 0 | 0 | 0
19:30 | 4040 | 1656 | 881 | 38 | 80 | 769 | 218 | 3972 | 0 | 118 | 896 | 0 | 0 | 0 | 0
20:00 | 4027 | 1610 | 881 | 38 | 82 | 764 | 218 | 3977 | 0 | 118 | 862 | 0 | 0 | 0 | 0
20:30 | 4059.5 | 1622.5 | 881 | 38 | 80 | 765.72 | 218 | 3952 | 0 | 118 | 836.5 | 0 | 0 | 0 | 0
21:00 | 4092 | 1635 | 881 | 38 | 78 | 767.44 | 218 | 3927 | 0 | 118 | 811 | 0 | 0 | 0 | 0
21:30 | 4076.5 | 1636 | 881 | 38 | 78 | 770.425 | 218 | 3963 | 0 | 110 | 740.5 | 0 | 0 | 0 | 0
22:00 | 4061 | 1637 | 881 | 38 | 78 | 773.41 | 218 | 3999 | 0 | 102 | 670 | 0 | 0 | 0 | 0
22:30 | 4051.5 | 1635.5 | 883.5 | 38 | 77 | 769.565 | 217 | 3996 | 0 | 102 | 661.5 | 0 | 0 | 0 | 0
23:00 | 4042 | 1634 | 886 | 38 | 76 | 765.72 | 216 | 3993 | 0 | 102 | 653 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 06:00 | 375 | 12:00 | Payra | 410 | 06:00 | 405 | 18:00
Ashuganj | 414 | 6:00 | 383 | 11:00 | Rahanpur | 415 | 08:00 | 401 | 12:00
Bhulta | 407 | 06:00 | 375 | 11:00 | Rampal | 406 | 06:00 | 395 | 13:00
Bibiana | 390 | 06:00 | 382 | 11:00
BIPTC | 405 | 05:00 | 393 | 18:00
Bogura | 407 | 07:00 | 391 | 13:00
Gopalganj | 399 | 06:00 | 388 | 23:00
Kaliakoir | 375 | 18:00 | 365 | 12:00
Madunaghat | 396 | 09:00 | 386 | 15:00
Meghnaghat | 386 | 06:00 | 376 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 18:30 | 221 | 11:00 | Kaliakoir | 236 | 18:00 | 226 | 11:00
AKSML | 231 | 08:00 | 223 | 00:00 | Keranigonj | 228 | 06:00 | 218 | 13:00
Aminbazar | 231 | 05:00 | 221 | 12:00 | Khulna(S) | 235 | 06:00 | 225 | 14:00
Ashuganj | 235 | 06:00 | 222 | 11:00 | Madunaghat | 232 | 09:00 | 227 | 14:00
Ashuganj-400 | 235 | 06:00 | 222 | 11:00 | Madunaghat-400 | 234 | 09:00 | 228 | 15:00
Baghabari | 240 | 06:00 | 227 | 12:00 | Maniknagar | 220 | 19:00 | 214 | 12:00
Barapukuria | 232 | 00:00 | 211 | 12:00 | Meghnaghat | 228 | 05:00 | 221 | 13:00
Barapukuria-230 | 232 | 00:00 | 211 | 12:00 | Meghnaghat-400 | 224 | 06:00 | 218 | 15:00
Barishal | 234 | 06:00 | 228 | 00:00 | Mirsorai | 227 | 06:00 | 219 | 23:00
Bheramara | 236 | 06:00 | 221 | 12:00 | Rajshahi | 237 | 06:00 | 220 | 13:00
Bhulta | 233 | 06:00 | 214 | 02:00 | Rampal | 234 | 06:00 | 225 | 15:00
Bibiana | 228 | 06:00 | 224 | 23:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 240 | 06:00 | 223 | 12:00 | Rampura | 232 | 06:00 | 213 | 11:00
Bogura | 247 | 06:00 | 226 | 13:00 | Shikalbaha | 231 | 09:00 | 225 | 16:00
Bogura-400 | 246 | 06:00 | 225 | 13:00 | Shyampur | 225 | 06:00 | 217 | 13:00
Borhanuddin | 237 | 06:00 | 232 | 00:00 | Siddhirganj | 221 | 05:00 | 216 | 14:00
BSRM | 226 | 06:00 | 219 | 16:00 | Sirajgonj | 245 | 06:00 | 232 | 13:00
Cumilla(N) | 224 | 06:00 | 218 | 23:00 | Sreepur | 233 | 06:00 | 221 | 11:00
Faridpur | 232 | 06:00 | 225 | 00:00 | Tongi | 232 | 18:30 | 217 | 11:00
Fenchuganj | 231 | 06:00 | 227 | 00:00
Ghorashal | 235 | 00:00 | 230 | 01:00
Ghorashal-230 | 232 | 06:00 | 217 | 11:00
Gopalganj | 234 | 06:00 | 227 | 22:00
GPH | 229 | 07:00 | 223 | 16:00
Haripur | 221 | 06:00 | 215 | 15:00
Hasnabad | 226 | 05:00 | 216 | 11:00
Hathazari | 231 | 08:00 | 222 | 15:00
Ishurdi | 240 | 06:00 | 225 | 13:00
Jhenaidah | 234 | 06:00 | 220 | 13:00
Kachua | 226 | 09:00 | 214 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 125 | 13:00 | Lalmonirhat | 136 | 00:00 | 125 | 08:00
Agargaon | 135 | 07:00 | 128 | 13:00 | Madanganj | 133 | 19:00 | 126 | 00:00
Agrabad | 131 | 08:00 | 126 | 16:00 | Madaripur | 135 | 07:00 | 131 | 19:30
AKS | 130 | 02:00 | 126 | 13:00 | Madartek | 138 | 06:00 | 121 | 13:00
Aminbazar | 136 | 04:00 | 128 | 12:00 | Madunaghat | 134 | 08:00 | 130 | 14:00
Amnura | 141 | 07:00 | 127 | 12:00 | Magura | 136 | 06:00 | 127 | 12:00
Ashuganj | 141 | 06:00 | 137 | 00:00 | Mahasthangarh | 139 | 06:00 | 127 | 12:00
Bagerhat | 133 | 20:00 | 124 | 00:00 | Maijdee | 130 | 09:00 | 123 | 22:00
Bajitpur | 133 | 06:00 | 128 | 09:00 | Manikganj | 133 | 01:00 | 128 | 11:00
Bakulia | 132 | 07:00 | 128 | 16:00 | Maniknagar | 133 | 05:00 | 128 | 12:00
Banani | 139 | 06:00 | 123 | 11:00 | Matarbari | 122 | 09:00 | 107 | 19:30
Bangabhaban | 133 | 04:00 | 128 | 13:00 | Matuail | 129.6 | 19:30 | 124.6 | 16:00
Barapukuria | 142 | 00:00 | 128 | 12:00 | Metrorail_Motijheel | 133 | 05:00 | 128 | 12:00
Barguna | 136 | 09:00 | 132 | 00:00 | Metrorail_Uttara | 138 | 03:00 | 130 | 11:00
Barishal | 135 | 06:00 | 130 | 00:00 | Millgate | 139 | 06:00 | 131 | 10:00
Barishal-230 | 135 | 06:00 | 129 | 19:30 | Mirpur | 135 | 05:00 | 127 | 11:00
Baroaulia | 132 | 03:00 | 129 | 15:00 | Mirzapur | 134 | 10:00 | 126 | 22:00
Baroirhat | 131 | 09:00 | 126 | 00:00 | Mithapukur | 139 | 06:00 | 127 | 12:00
Bashundhara | 139 | 06:00 | 122 | 11:00 | MI_Cement | 133 | 06:00 | 125 | 11:00
BashundharaCement | 133 | 19:00 | 126 | 00:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 130 | 08:00 | 125 | 00:00 | Mogbazar | 138 | 04:00 | 124 | 11:00
Benapole | 134 | 06:00 | 123 | 14:00 | Mongla | 132 | 06:00 | 124 | 00:00
Bhaluka | 132 | 06:00 | 125 | 09:00 | Motijheel | 133 | 04:00 | 128 | 13:00
Bhandaria | 132 | 08:00 | 123 | 21:00 | Muktagacha | 135 | 09:00 | 128 | 00:00
Bhangura | 140 | 06:00 | 131 | 19:30 | Munshiganj | 130 | 19:00 | 122 | 11:00
Bheramara | 140 | 06:00 | 130 | 12:00 | Muradnagar | 128 | 20:00 | 122 | 02:00
Bheramara(GK) | 140 | 05:00 | 130 | 13:00 | Mymensingh | 136 | 09:00 | 121 | 00:00
Bhulta | 128 | 17:00 | 124 | 00:00 | Naogaon | 138 | 06:00 | 126 | 12:00
Bog-Sherpur | 140 | 06:00 | 128 | 13:00 | Narail | 136 | 06:00 | 126 | 14:00
Bogura | 140 | 05:00 | 128 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
Bogura-230 | 140 | 05:00 | 128 | 13:00 | Narshingdi | 134 | 08:00 | 119 | 23:00
Brahmanbaria | 135 | 06:00 | 129 | 11:00 | Natore | 139 | 06:00 | 127 | 13:00
Cantonment | 135 | 06:00 | 128 | 13:00 | Nawabganj | 135 | 06:00 | 128 | 13:00
Chandina | 130 | 06:00 | 126 | 23:00 | Netrakona | 128 | 10:00 | 121 | 01:00
Chandpur | 133 | 09:00 | 125 | 03:00 | New | 139 | 17:00 | 132 | 11:00
Chandraghona | 134 | 07:00 | 131 | 16:00 | Niamatpur | 143 | 08:00 | 137 | 13:00
Chapai | 142 | 07:00 | 136 | 13:00 | Noapara | 135 | 06:00 | 127 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:30 | 123 | 11:00 | Pabna | 139 | 06:00 | 129 | 13:00
Chauddagram | 130 | 08:00 | 125 | 23:00 | Palashbari | 136 | 04:00 | 125 | 13:00
Chhatak | 130 | 08:00 | 122 | 00:00 | Panchagarh | 140 | 18:00 | 124 | 08:00
Chowmuhani | 130 | 09:00 | 124 | 22:00 | Patiya | 132 | 09:00 | 126 | 16:00
Chuadanga | 135 | 06:00 | 123 | 13:00 | Patuakhali | 136 | 06:00 | 133 | 00:00
Coxsbazar | 122 | 09:00 | 108 | 00:00 | Payra | 136 | 04:00 | 134 | 00:00
Cumilla(N) | 130 | 08:00 | 126 | 03:00 | PHP | 130 | 09:00 | 125 | 23:00
Cumilla(S) | 131 | 03:00 | 126 | 23:00 | Postogola | 134 | 04:00 | 128 | 11:00
Daganbhuiyan | 130 | 09:00 | 125 | 03:00 | Purbachal | 139 | 05:00 | 123 | 11:00
Daudkandi | 127 | 20:00 | 118 | 16:00 | Purbasadipur | 136 | 00:00 | 122 | 08:00
DhakaUniversity | 139 | 06:00 | 123 | 11:00 | Rahanpur | 142 | 04:00 | 138 | 12:00
Dhamrai | 134 | 04:00 | 128 | 11:00 | Rahanpur-400 | 143 | 07:00 | 138 | 12:00
Dhanmondi | 140 | 06:00 | 123.6 | 11:00 | Rahim | 129 | 18:00 | 125 | 00:00
Dohazari | 131 | 04:00 | 122 | 00:00 | Rajbari | 136 | 06:00 | 131 | 00:00
Faridpur | 137 | 05:00 | 132 | 23:00 | Rajendrapur | 133 | 20:00 | 125 | 09:00
Fatullah | 137 | 06:00 | 126 | 12:00 | Rajshahi | 138 | 06:00 | 127 | 13:00
Fenchuganj | 136 | 06:00 | 133 | 00:00 | Rajshahi-230 | 137 | 05:00 | 127 | 11:00
Feni | 130 | 09:00 | 124 | 22:00 | Ramganj | 131 | 09:00 | 123 | 02:00
Ghatail | 135 | 08:00 | 125 | 16:00 | Rampur | 133 | 09:00 | 126 | 16:00
Ghorashal | 139 | 01:00 | 131 | 10:00 | Rampura | 139 | 06:00 | 123 | 11:00
Goalpara | 137 | 06:00 | 129 | 00:00 | Rangamati | 133 | 07:00 | 130 | 16:00
Gollamari | 136 | 06:00 | 130 | 00:00 | Rangpur | 139 | 00:00 | 128 | 13:00
Gopalganj | 135 | 06:00 | 130 | 00:00 | Ruppur | 141 | 06:00 | 131 | 13:00
Gopalganj-400 | 138 | 06:00 | 133 | 21:00 | Saidpur | 137 | 00:00 | 126 | 08:00
Gulshan | 138 | 04:00 | 123 | 11:00 | Satkhira | 133 | 06:00 | 125 | 00:00
Halishahar | 133 | 08:00 | 127 | 16:00 | Satmasjid | 135 | 06:00 | 127 | 13:00
Haripur | 130 | 18:30 | 125 | 11:00 | Savar | 136 | 19:00 | 126 | 11:00
HaripurSBU | 130 | 18:30 | 125 | 13:00 | SevenRings | 140 | 18:00 | 130 | 11:00
Hasnabad | 134 | 05:00 | 127 | 13:00 | ShahCement | 130 | 18:30 | 123 | 11:00
Hathazari | 135 | 08:00 | 129 | 11:00 | Shahjadpur | 140 | 06:00 | 133 | 12:00
Ishurdi | 141 | 06:00 | 132 | 11:00 | Shahjibazar | 135 | 06:00 | 130 | 00:00
Jaldhaka | 136 | 00:00 | 123 | 08:00 | Shahmirpur | 133 | 09:00 | 29 | 15:00
Jamalpur | 134 | 12:00 | 122 | 00:00 | Shariatpur | 135 | 06:00 | 129 | 23:00
Jashore | 135 | 04:00 | 124 | 18:00 | Sherpur | 133 | 07:00 | 120 | 02:00
Jhenaidah | 138 | 05:00 | 124 | 13:00 | Shikalbaha | 122 | 05:00 | 111 | 16:00
Jhenaidah-230 | 139 | 06:00 | 129 | 14:00 | Shikalbaha-230 | 135 | 09:00 | 130 | 16:00
Joydebpur | 138 | 01:00 | 125 | 11:00 | Shitalakhya | 133 | 06:00 | 125 | 11:00
Joypurhat | 137 | 05:00 | 125 | 13:00 | Sholosohor | 134 | 06:00 | 130 | 16:00
Juldah | 133 | 09:00 | 128 | 15:00 | Shyampur | 133 | 03:00 | 130 | 16:00
Kabirpur | 137 | 06:00 | 127 | 21:00 | Shyampur-230 | 137 | 06:00 | 132 | 13:00
Kachua | 134 | 09:00 | 126 | 04:00 | Siddhirganj | 130 | 18:30 | 125 | 11:00
Kaliakoir | 136 | 06:00 | 130 | 11:00 | Sirajganj | 138 | 06:00 | 128 | 13:00
Kallyanpur | 136 | 19:00 | 128 | 12:00 | Sonargaon | 127 | 00:00 | 122 | 16:00
Kalurghat | 134 | 09:00 | 130 | 16:00 | Sreemongol | 134 | 08:00 | 129 | 00:00
Kamrangirchar | 134 | 19:00 | 128 | 12:00 | Sreepur | 134 | 05:00 | 127 | 11:00
Kaptai | 136 | 9:00 | 134 | 13:00 | Srinagar | 134 | 05:00 | 128 | 12:00
Kasba | 128 | 20:00 | 121 | 00:00 | SSM | 132 | 00:00 | 132 | 00:00
Kazla | 133 | 06:00 | 127 | 13:00 | Sunamganj | 128 | 08:00 | 120 | 00:00
Keranigonj | 135 | 06:00 | 128 | 13:00 | Sylhet | 131 | 08:00 | 126 | 00:00
Khagrachori | 133 | 06:00 | 129 | 16:00 | Sylhet-132 | 130 | 03:00 | 127 | 00:00
Khulna | 135 | 05:00 | 128 | 00:00 | Tangail | 134 | 08:00 | 124 | 22:00
Khulna(S) | 136 | 06:00 | 130 | 00:00 | Taraganj | 138 | 00:00 | 125 | 13:00
Khulshi | 131 | 09:00 | 126 | 15:00 | Thakurgaon | 139 | 18:00 | 122 | 08:00
Kishoreganj | 131 | 16:00 | 125 | 00:00 | TK | 135 | 00:00 | 131 | 17:00
Kodda | 137 | 00:00 | 124 | 11:00 | Tongi | 140 | 04:00 | 132 | 11:00
KSRM | 133 | 08:00 | 130 | 03:00 | Ullahpara | 140 | 05:00 | 130 | 12:00
Kulaura | 135 | 10:00 | 132 | 00:00 | Ullon | 139 | 06:00 | 123 | 11:00
Kurigram | 136 | 00:00 | 122 | 12:00 | Uttara | 135 | 03:00 | 127 | 12:00
Kushtia | 138 | 06:00 | 127 | 12:00 | UttaraNew | 138 | 03:00 | 130 | 11:00
Laksam | 131 | 07:00 | 127 | 22:00 | Zigatola | 135 | 06:00 | 128 | 12:00
Lakshmipur | 129 | 09:00 | 122 | 22:00
Lalbag | 136 | 01:00 | 127 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division