## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12276.05 | 0 |  | 12276.05
1:00 | 11959.93 | 0 |  | 11959.93
2:00 | 11534.28 | 0 |  | 11534.28
3:00 | 11226.57 | 0 |  | 11226.57
4:00 | 10908.55 | 0 |  | 10908.55
5:00 | 10776.22 | 0 |  | 10776.22
6:00 | 10559.48 | 0 |  | 10559.48
7:00 | 10901.85 | 0 |  | 10901.85
8:00 | 11113.92 | 0 |  | 11113.92
9:00 | 11130.95 | 0 |  | 11130.95
10:00 | 11272.53 | 0 |  | 11272.53
11:00 | 11494.3 | 0 |  | 11494.3
12:00 | 12204.77 | 0 |  | 12204.77
13:00 | 12228.55 | 0 |  | 12228.55
14:00 | 11982.49 | 0 |  | 11982.49
15:00 | 12034.97 | 0 |  | 12034.97
16:00 | 11764.4 | 0 |  | 11764.4
17:00 | 11971.71 | 0 |  | 11971.71
18:00 | 13365.5 | 0 |  | 13365.5
19:00 | 13297.09 | 0 |  | 13297.09
19:30 | 12997.95 | 0 |  | 12997.95
20:00 | 12970.14 | 0 |  | 12970.14
21:00 | 12780.5 | 0 |  | 12780.5
22:00 | 12693 | 0 |  | 12693
23:00 | 12286.6 | 0 |  | 12286.6
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 02-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4007 | 1636 | 886 | 38 | 46 | 773.05 | 215 | 3981 | 0 | 84 | 610 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 4010.5 | 1639.5 | 886 | 38 | 47 | 768.99 | 215.5 | 3948 | 0 | 75.5 | 489 | 0 | 0 | 0 | 0 | 02-11-2025
01:00 | 4014 | 1643 | 886 | 38 | 48 | 764.93 | 216 | 3915 | 0 | 67 | 368 | 0 | 0 | 0 | 0
01:30 | 3978 | 1636.5 | 886 | 38 | 51 | 763.105 | 216.5 | 3848 | 0 | 58.5 | 271.5 | 0 | 0 | 0 | 0 | Energy Generated | 287.5041 |  | MKWHr
02:00 | 3942 | 1630 | 886 | 38 | 54 | 761.28 | 217 | 3781 | 0 | 50 | 175 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3929.5 | 1627 | 886 | 38 | 52 | 713.925 | 217.5 | 3733.5 | 0 | 50 | 133 | 0 | 0 | 0 | 0 | Total Energy Requirement | 287.5041 |  | MKWHr
03:00 | 3917 | 1624 | 886 | 38 | 50 | 666.57 | 218 | 3686 | 0 | 50 | 91 | 0 | 0 | 0 | 0
03:30 | 3892.5 | 1622 | 886.5 | 38 | 51 | 622.06 | 218 | 3635 | 0 | 25 | 77.5 | 0 | 0 | 0 | 0
04:00 | 3868 | 1620 | 887 | 38 | 52 | 577.55 | 218 | 3584 | 0 | 0 | 64 | 0 | 0 | 0 | 0
04:30 | 3885.5 | 1628 | 886.5 | 38 | 49 | 577.885 | 218.5 | 3499 | 0 | 0 | 60 | 0 | 0 | 0 | 0
05:00 | 3903 | 1636 | 886 | 38 | 46 | 578.22 | 219 | 3414 | 0 | 0 | 56 | 0 | 0 | 0 | 0
05:30 | 3896.5 | 1623 | 886 | 38 | 47 | 553.35 | 219.5 | 3348.5 | 0 | 0 | 56 | 0 | 0 | 0 | 0
06:00 | 3890 | 1610 | 886 | 38 | 48 | 528.48 | 220 | 3283 | 0 | 0 | 56 | 0 | 0 | 0 | 0
06:30 | 3943.5 | 1614.5 | 886 | 38 | 48 | 529.16 | 220 | 3336 | 17.505 | 12.5 | 85.5 | 0 | 0 | 0 | 0
07:00 | 3997 | 1619 | 886 | 38 | 48 | 529.84 | 220 | 3389 | 35.01 | 25 | 115 | 0 | 0 | 0 | 0
07:30 | 3977 | 1611 | 886 | 38 | 43 | 581.335 | 219.5 | 3395 | 91.55 | 29 | 136.5 | 0 | 0 | 0 | 0
08:00 | 3957 | 1603 | 886 | 38 | 38 | 632.83 | 219 | 3401 | 148.09 | 33 | 158 | 0 | 0 | 0 | 0
08:30 | 3917 | 1604 | 886.5 | 38 | 40 | 600.355 | 219 | 3386 | 194.08 | 33 | 204.5 | 0 | 0 | 0 | 0
09:00 | 3877 | 1605 | 887 | 38 | 42 | 567.88 | 219 | 3371 | 240.07 | 33 | 251 | 0 | 0 | 0 | 0
09:30 | 3874 | 1612.5 | 886.5 | 38 | 51 | 567.165 | 218.5 | 3392.5 | 269.325 | 33 | 259.25 | 0 | 0 | 0 | 0
10:00 | 3871 | 1620 | 886 | 38 | 60 | 566.45 | 218 | 3414 | 298.58 | 33 | 267.5 | 0 | 0 | 0 | 0
10:30 | 3855 | 1622.5 | 886 | 38 | 62 | 600.42 | 218 | 3498 | 278.495 | 33.5 | 291.5 | 0 | 0 | 0 | 0
11:00 | 3839 | 1625 | 886 | 38 | 64 | 634.39 | 218 | 3582 | 258.41 | 34 | 315.5 | 0 | 0 | 0 | 0
11:30 | 3777.5 | 1729.5 | 886 | 38 | 65 | 682.745 | 218 | 3677 | 307.79 | 48.5 | 419.5 | 0 | 0 | 0 | 0
12:00 | 3716 | 1834 | 886 | 38 | 66 | 731.1 | 218 | 3772 | 357.17 | 63 | 523.5 | 0 | 0 | 0 | 0
12:30 | 3546.5 | 1775.5 | 886 | 38 | 71 | 744.665 | 218 | 3742.5 | 324.495 | 81 | 787.5 | 0 | 0 | 1.5 | 0
13:00 | 3377 | 1717 | 886 | 38 | 76 | 758.23 | 218 | 3713 | 291.82 | 99 | 1051.5 | 0 | 0 | 3 | 0
13:30 | 3354 | 1680.2 | 886.5 | 38 | 77 | 756.83 | 218.5 | 3712 | 251.49 | 91 | 1038.5 | 0 | 0 | 1.5 | 0
14:00 | 3331 | 1643.4 | 887 | 38 | 78 | 755.43 | 219 | 3711 | 211.16 | 83 | 1025.5 | 0 | 0 | 0 | 0
14:30 | 3371.5 | 1637.2 | 886.5 | 38 | 77 | 755.66 | 218.5 | 3715 | 196.87 | 85.5 | 1026 | 0 | 0 | 1 | 0
15:00 | 3412 | 1631 | 886 | 38 | 76 | 755.89 | 218 | 3719 | 182.58 | 88 | 1026.5 | 0 | 0 | 2 | 0
15:30 | 3375 | 1643.75 | 886 | 38 | 70 | 752.445 | 218 | 3698.5 | 127.74 | 89 | 999.75 | 0 | 0 | 1.5 | 0
16:00 | 3338 | 1656.5 | 886 | 38 | 64 | 749 | 218 | 3678 | 72.9 | 90 | 973 | 0 | 0 | 1 | 0
16:30 | 3477 | 1623.5 | 886.5 | 38 | 66 | 748.5 | 218.5 | 3611 | 38.555 | 149.5 | 1010.5 | 0 | 0 | 0.5 | 0
17:00 | 3616 | 1590.5 | 887 | 38 | 68 | 748 | 219 | 3544 | 4.21 | 209 | 1048 | 0 | 0 | 0 | 0
17:30 | 3689 | 1617 | 886.5 | 38 | 74 | 749.35 | 219 | 3649.5 | 2.105 | 384.5 | 1359.65 | 0 | 0 | 0 | 0
18:00 | 3762 | 1643.5 | 886 | 38 | 80 | 750.7 | 219 | 3755 | 0 | 560 | 1671.3 | 0 | 0 | 0 | 0
18:30 | 3738 | 1635.5 | 886 | 38 | 74 | 747.395 | 219 | 3765 | 0 | 557 | 1671.4 | 0 | 0 | 0 | 0
19:00 | 3714 | 1627.5 | 886 | 38 | 68 | 744.09 | 219 | 3775 | 0 | 554 | 1671.5 | 0 | 0 | 0 | 0
19:30 | 3721 | 1642 | 886 | 38 | 74 | 739.45 | 219 | 3788 | 0 | 493 | 1397.5 | 0 | 0 | 0 | 0
20:00 | 3692 | 1634 | 886 | 38 | 76 | 740.64 | 220 | 3790 | 0 | 486 | 1407.5 | 0 | 0 | 0 | 0
20:30 | 3704 | 1635 | 886 | 38 | 74 | 736.32 | 220 | 3785.5 | 0 | 432 | 1364.5 | 0 | 0 | 0 | 0
21:00 | 3716 | 1636 | 886 | 38 | 72 | 732 | 220 | 3781 | 0 | 378 | 1321.5 | 0 | 0 | 0 | 0
21:30 | 3690 | 1662 | 886 | 38 | 73 | 727 | 219 | 3784.5 | 0 | 356 | 1301.25 | 0 | 0 | 0 | 0
22:00 | 3664 | 1688 | 886 | 38 | 74 | 722 | 218 | 3788 | 0 | 334 | 1281 | 0 | 0 | 0 | 0
22:30 | 3686 | 1690 | 886 | 38 | 75 | 720.5 | 218 | 3787 | 0 | 265.5 | 1123.8 | 0 | 0 | 0 | 0
23:00 | 3708 | 1692 | 886 | 38 | 76 | 719 | 218 | 3786 | 0 | 197 | 966.6 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6480 | 5796.05 | 12276.05 | DAILY GENERATION CURVE
00:30 | 6400.5 | 5717.49 | 12117.99
01:00 | 6321 | 5638.93 | 11959.93 | 02-11-2025
01:30 | 6197.5 | 5549.605 | 11747.105
02:00 | 6074 | 5460.28 | 11534.28
02:30 | 6014 | 5366.425 | 11380.425
03:00 | 5954 | 5272.57 | 11226.57
03:30 | 5896.5 | 5171.06 | 11067.56
04:00 | 5839 | 5069.55 | 10908.55
04:30 | 5845.5 | 4996.885 | 10842.385
05:00 | 5852 | 4924.22 | 10776.22
05:30 | 5800 | 4867.85 | 10667.85
06:00 | 5748 | 4811.48 | 10559.48
06:30 | 5878.28 | 4852.385 | 10730.665
07:00 | 6008.56 | 4893.29 | 10901.85
07:30 | 6002.01 | 5005.875 | 11007.885
08:00 | 5995.46 | 5118.46 | 11113.92
08:30 | 6057.76 | 5064.675 | 11122.435
09:00 | 6120.06 | 5010.89 | 11130.95
09:30 | 6114.32 | 5087.42 | 11201.74
10:00 | 6108.58 | 5163.95 | 11272.53
10:30 | 6056.99 | 5326.425 | 11383.415
11:00 | 6005.4 | 5488.9 | 11494.3
11:30 | 6201.535 | 5648 | 11849.535
12:00 | 6397.67 | 5807.1 | 12204.77
12:30 | 6526.125 | 5690.535 | 12216.66
13:00 | 6654.58 | 5573.97 | 12228.55
13:30 | 6528.325 | 5577.195 | 12105.52
14:00 | 6402.07 | 5580.42 | 11982.49
14:30 | 6458.04 | 5550.69 | 12008.73
15:00 | 6514.01 | 5520.96 | 12034.97
15:30 | 6443.705 | 5455.98 | 11899.685
16:00 | 6373.4 | 5391 | 11764.4
16:30 | 6495.655 | 5372.4 | 11868.055
17:00 | 6617.91 | 5353.8 | 11971.71
17:30 | 6978.355 | 5690.25 | 12668.605
18:00 | 7338.8 | 6026.7 | 13365.5
18:30 | 7265.9 | 6065.395 | 13331.295
19:00 | 7193 | 6104.09 | 13297.09
19:30 | 7123.5 | 5874.45 | 12997.95
20:00 | 7124.5 | 5845.64 | 12970.14
20:30 | 7062 | 5813.32 | 12875.32 |  | Executive Engineer
21:00 | 6999.5 | 5781 | 12780.5 |  | Network Operation Division
21:30 | 6973.75 | 5763 | 12736.75
22:00 | 6948 | 5745 | 12693
22:30 | 6800.8 | 5689 | 12489.8
23:00 | 6653.6 | 5633 | 12286.6

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12204.77 | MW | 12:00 Hr. | Energy Generated |  |  | 287.5041 |  | MKWHr.
| Day Peak Demand |  |  | 12204.77 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13365.5 | MW | 18:00 Hr. | Energy Demand |  |  | 287.5041 |  | MKWHr.
| Evening Peak Demand |  |  | 13365.5 | MW | 18:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 10559.48 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 924.49 |  | MMCFD
| Maximum Generation of the Day |  |  | 13365.5 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.7126 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.0554 | 0 | 8.3083 | 0 | 0 | 0.10695 | 0 | 0 | 45.4706 | Gas | 131.1609 | Gas | 459975099.5412
| Chattogram Zone |  |  | 5.6129 | 29.1436 | 3.4635 | 0 | 5.2299 | 0.11629 | 0 | 0.00768 | 43.5739 | Coal | 87.9829 | Coal | 561184091.4673
| Cumilla Zone |  |  | 30.1122 | 0 | 4.0922 | 0 | 0 | 0.31677 | 1.4813 | 0 | 36.0024 | HFO | 20.8857 | HFO | 362199506.38
| Mymensingh Zone |  |  | 2.8723 | 0 | 2.1304 | 0 | 0 | 0.12124 | 0 | 0 | 5.1239 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.0202 | Hydro | 5.2299 | Hydro | 522992.5
| Khulna Zone |  |  | 9.3828 | 24.6109 | 0.075072 | 0 | 0 | 0.47376 | 22.3775 | 0 | 56.9199 | Solar | 1.9774 | Solar | 30869103.406
| Barishal Zone |  |  | 8.0019 | 34.2283 | 0.11093 | 0 | 0 | 0.003262 | 0 | 0 | 42.3444 | Import | 40.2596 | Import | 227521583.05
| Rajshahi Zone |  |  | 13.1033 | 0 | 1.2612 | 0 | 0 | 0.48333 | 16.4009 | 0 | 31.2487 | Wind | 0.00768 | Wind | 112972.8
| Rangpur Zone |  |  | 0 | 0 | 1.4442 | 0 | 0 | 0.3558 | 0 | 0 | 1.8
| Total |  |  | 131.1609 | 87.9829 | 20.8857 | 0 | 5.2299 | 1.9774 | 40.2596 | 0.00768 | 287.5041
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 459975099.5412 |  | Hydro | 522992.5
|  |  |  | Coal | 561184091.4673 |  | Solar | 30869103.406
|  |  |  | HFO | 362199506.38 |  | Import | 227521583.05
|  |  |  | HSD | 0 |  | Wind | 112972.8
[5 empty] | Total: | 164,23,85,349 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4655 | Peak Hr Flow | 886.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41745541.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.4009 | Peak Hr Flow | 750.70 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2288 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4813 | Peak Hr Flow | 80.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2749 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.3476 | Peak Hr Flow | 1716.70 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5056
|  |  |  | Chattogram |  | 0 |  | 1508
|  |  |  | Cumilla |  | 0 |  | 1369
|  |  |  | Mymensingh |  | 0 |  | 1002
|  |  |  | Sylhet |  | 0 |  | 571
|  |  |  | Khulna |  | 0 |  | 1484
|  |  |  | Barishal |  | 0 |  | 417
|  |  |  | Rajshahi |  | 0 |  | 1050
|  |  |  | Rangpur |  | 0 |  | 701
|  |  |  | Total |  | 0 |  | 13158
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:06 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT is restored.
| 08:09 | 16:44 | Naogaon 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance
| 08:09 | 16:42 | Naogaon 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintennce
| 08:27 | 17:43 | Jaldhaka-Saidpur 132kV Ckt-1 Scheduled S/D from Jaldhaka 132/33kV end Due to Annual
Maintenance and from Saidpur 132/33kV end Due to Annual maintenance
| 08:28 | 17:01 | Gopalganj 400/132kV S/S ATR-01 LT Scheduled S/D Due to Annual Maintenance
| 08:30 | 17:25 | BSRM-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Annual
Maintenance work
| 08:33 | 16:59 | Gopalganj 400/132kV S/S ATR-01 HT Scheduled S/D Due to Annual Maintenance
| 08:33 | 16:59 | Gopalganj 400/132kV S/S ATR-01 HT Scheduled S/D Due to Annual Maintenance
| 08:33 | 16:59 | Gopalganj 400/132kV S/S ATR-01 HT Scheduled S/D Due to Annual Maintenance
| 08:46 | 08:56 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR -1 ( A) Annual maintenance
| 08:47 | 08:56 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR -1 ( A) Annual maintenance
| 08:52 | 15:57 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Annual maintenance
| 09:03 | 16:01 | Bheramara P/S-Ishurdi 132 kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to annual
maintenance and from Bheramara 230/132kV end Due to Annual maintenance
| 09:05 | 16:10 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance work
| 09:05 | 16:55 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Scheduled S/D Due to Annual
Maintenance
| 09:06 | 16:51 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Scheduled S/D Due to Annual
Maintenance
| 09:08 | 19:20 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to Annual Maintenance.
| 09:31 | 16:48 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end Due to
Annual Maintenance
| 09:43 | 15:42 | Goalpara 132/33kV S/S Bus 1 Scheduled S/D Due to Annual maintanance shutdown
| 09:48 | 16:48 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Scheduled S/D from BIPTC end Due to Shutdown id
taken from Jhenaidah S/S end for annual maintenance work
| 09:52 | 18:43 | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual maintenance
| 09:53 | 14:29 | Mithapukur 132/33kV S/S TR-1(404T) LT Scheduled S/D Due to Yearly Maintenance
| 09:54 | 14:29 | Mithapukur 132/33kV S/S TR-1(404T) HT Scheduled S/D Due to Yearly Maintenance
| 09:57 | 16:28 | Barapukuria 230/132/33kV S/S 132 KV Bus B Scheduled S/D Due to Annual Maintenance
| 10:04 | 16:01 | Bheramara P/S-Ishurdi 132 kV Ckt-2 Forced S/D from Ishurdi 132/33kV end.
| 10:18 | 17:10 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to Annual maintenance work
| 10:18 | 17:10 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to Annual maintenance work
| 10:18 |  | Ghorashal unit-7 was shutdown due to gas shortage.
| 11:03 | 15:02 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Forced S/D Due to Transformer Oli leakage
Maintenance work.
| 11:04 | 15:01 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Forced S/D Due to Transformer Oli leakage
Maintenance work.
| 11:18 |  | Baghabari-----Sathia Ckt shut down[ to tower no. 268 , operation perfomed only by
baghabari power station]
| 11:21 | 17:15 | Baghabari-Bangura 132 kV Ckt-1 Forced S/D from Bhangura 132/33kV end Due to Optical Fiber | [7 empty] | 15.0MW load
|  |  | Installation from Baghabari to Sathia Grid Substation | [7 empty] | interrup. Bhangura
132/33kV end
| 11:21 |  | Baghabari-----Bhangura Ckt--1 shut down[ Baghabari power station(CB open, DS Open, ES | [7 empty] | 16MW load interrup.
closed)--Bhangura End(DS open, ES closed)] Baghabari-----Bhangura Ckt--2[ Baghabari
power station(CB previously opened, DS previously Open, ES closed)--Bhangura End(No any
bay )]
| 12:00 |  | Day peak generation: 12205 MW
| 12:57 | 14:50 | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to MULTIPLICATION METER
INSTALATION
| 12:57 | 14:50 | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to MULTIPLICATION METER
INSTALATION
|  | 15:14 | Chhatak 132/33kV S/S Sunamganj 1 is restored.
|  | 15:15 | Chattak-Sunamganj 132 kV Ckt-1 is restored.
| 15:32 | 17:19 | Bogura 132/33kV S/S Transformer-4 LT Scheduled S/D Due to Multi function Meter
installation to T-4 33 kv control penal
| 15:32 | 17:19 | Bogura 132/33kV S/S Transformer-4 HT Scheduled S/D Due to Multi function Meter
installation to T-4 123 kv control penal
|  | 15:40 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 is restored.
|  | 16:00 | Barishal 132/33kV S/S 132 kV Bus-coupler is restored.
| 16:27 | 16:43 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR -1 ( A) Annual maintenance
| 16:27 | 16:44 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR -1 ( A) Annual maintenance
| 17:18 |  | Bagabari 132 KV line charge upto tower No. 268. (Bera line disconnected from Bagabari
line.
| 18:00 |  | Evening Peak Generation is 13364 MW.
| 22:47 | 01:37 | Kabirpur 132/33kV S/S XFR, T-2 LT Forced S/D Due to Tr-2 33 kv bus ds redhot maintenance. | [7 empty] | 65.0MW load
interrup.
| 22:48 | 01:37 | Kabirpur 132/33kV S/S XFR, T-2 HT Forced S/D Due to T-2, 33 kv BUS DS Redhot maintenance | [7 empty] | 65.0MW load
interrup.
| 06:00 |  | Min. Gen. 10149 MW
| 06:30 | 07:02 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Tripped showing O/C relays Due to PBS 33 Kv | [7 empty] | 12.0MW load
|  |  | Three Feeder(Baowkomerjani,Square,Vadgram) Trip at a time | [7 empty] | interrup.
| 06:55 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Scheduled S/D Due to Annual | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 06:56 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Scheduled S/D Due to Annual | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:08 |  | Sylhet-Sylhet (South) 132KV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Annual
Maintenance
| 07:42 |  | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Scheduled S/D from Meghnaghat 230/132kV end Due to
Annual maintenance work. and from Cumilla(N) 230/132/33kV end Due to Annual maintenance.
| 07:43 |  | Hasnabad 132/33kV S/S 132/33kV 424 T-5 HT Scheduled S/D Due to Annual Maintenance
| 07:43 |  | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Scheduled S/D Due to Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 2351300 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 364 | 8449200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8480000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 237526 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7500303 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48.3 | 519120 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 45 | 115680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 534902 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 139216 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.5 | 418800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 497160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 299040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 2273989 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 73 | 1197216 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 480960 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 140 | 1591200 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 106952 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 257040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 410 | 9358636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 662400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2326.8 | 45470640.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 40806 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 97470 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 120960 | “Fuel transfer halted: terminal–plant road work.
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5229925 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5210189 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 75 | 868145 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 80304 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 518916 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 378240 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 6 | 402720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 43 | 647040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18820 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 22582 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 15 | 27876 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 45 | 381380 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 286080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 16 | 37636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 50 | 53527 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 550 | 13434544 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 7680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15709090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2028 | 43573930.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 348 | 8556100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7664000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 380 | 8234500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 30 | 834192 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 18 | 736320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1237608 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 132 | 1224436 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 27 | 229968 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2437673 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 106 | 1775520 | -
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1481280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 18998 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 411770 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 14 | 33060 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 56 | 810240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 316773 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1702 | 36002438
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 105 | 2872320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 859200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 49 | 1006800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 118090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 50160 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 214200 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 225 | 5123920
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3614973 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 214560 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1902720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3331650 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 142752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7606500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 310 | 8207000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1057 | 25020155
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 886 | 21465455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 58560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 3 | 16512 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 398 | 9382752 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 473760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1088 | 24610910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2446 | 56919949
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 400 | 8477044 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 11 | 25728 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2640000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1067 | 25751272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5361880 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 10 | 85200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3262 | -
Barishal Area Total |  |  |  |  | 2858 | 1818 | 42344386.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 119048 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 44 | 215999 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 13 | 121572 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 181 | 4353273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8750036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 142179 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 13939 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 596048 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 38 | 112320 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 59136 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 11040 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 750.7 | 16400880 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 136496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 216741 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1610.7 | 31248707
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 57 | 868147 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 19212.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 576023 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 62272 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 274320 | -
Rangpur Area Total |  |  |  |  | 950 | 152 | 1799974.6
Eastern Grid Total |  |  |  |  | 17383.855 | 7338.8 | 155191084.27
Western Grid Total |  |  |  |  | 10980.24 | 6026.7 | 132313017.33
National Grid Total |  |  |  |  | 28364.095 | 13365.5 | 287504101.6
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-11-2025 | during | 03-11-2025 | during | 03-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 313 | 364 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 320 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 48.3 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 45 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21.5 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 30 | 293 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 73 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 140 | 162 | 162 | 108 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 2 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 410 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 108 | 160 | 160 | 55 | 55 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1889.5 | 2326.8 | 5835.4 | 5803.4 | 4387.11 | 4462.11
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 13 | 0 | 13 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 50 | 50 | 50 | 50 | “Fuel transfer halted: terminal–plant road work.
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 219 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 219 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 14 | 75 | 105 | 105 | 105 | 105 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 48 | 56 | 48 | 56 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 6 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 41 | 43 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.33 | 0 | 3.25 | 0 | 3.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 15 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 11 | 45 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 16 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 50 | 145 | 145 | 17 | 159 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 565 | 550 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 3 | 4 | 3 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1768.33 | 2028 | 3023.11 | 3019.86 | 2364.75 | 2503.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 350 | 348 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 370 | 380 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 30 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 37 | 18 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 15 | 132 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 13 | 27 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 102 | 103 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 50 | 106 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 80 | 160 | 160 | 84 | 84 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 14 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 56 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 72 | 0 | 72 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1507 | 1702 | 2623.56 | 2551.56 | 2085.86 | 2022.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-11-2025 | during | 03-11-2025 | during | 03-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 105 | 105 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 31 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 49 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 29.84 | 0 | 33 | 0 | 33 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 219.84 | 225 | 364.9 | 330 | 311.4 | 276.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 153 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 81 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 5 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 287 | 310 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1013 | 1057 | 1180 | 1180 | 1113 | 1113
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 886 | 886 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 3 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 397 | 398 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 93 | 3 | 93 | 3 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1092 | 1088 | 0 | 0 | 1140 | 1140 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2502 | 2446 | 2405 | 2315 | 2790 | 2700
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 405 | 400 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 11 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1060 | 1067 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 10 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.68 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1795.68 | 1818 | 1840 | 1840 | 1699 | 1699
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 2.86 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 44 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 13 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 200 | 181 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 406 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 38 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.64 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 731.1 | 750.7 | 1209 | 1435.88 | 1600 | 1600 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 16.62 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 55 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1413.22 | 1610.7 | 2955.44 | 3016.87 | 3173.66 | 3008.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 57 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.2 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 47 | 0 | 116.43 | 0 | 116.43 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 96.2 | 152 | 400.23 | 248 | 360.23 | 208
System Total |  |  |  |  | 28823.2 | 28364.095 | 12204.77 | 13365.5 | 20627.64 | 20304.69 | 18285.01 | 17993.18
Forecast Scenario (03-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12270 |  | 0 |  | 12270
|  |  |  | 1:00 | 11960 |  | 0 |  | 11960
|  |  |  | 2:00 | 11530 |  | 0 |  | 11530
|  |  |  | 3:00 | 11220 |  | 0 |  | 11220
|  |  |  | 4:00 | 10900 |  | 0 |  | 10900
|  |  |  | 5:00 | 10770 |  | 0 |  | 10770
|  |  |  | 6:00 | 10550 |  | 0 |  | 10550
|  |  |  | 7:00 | 10900 |  | 0 |  | 10900
|  |  |  | 8:00 | 12910 |  | 0 |  | 12910
|  |  |  | 9:00 | 11030 |  | 0 |  | 11030
|  |  |  | 10:00 | 11270 |  | 0 |  | 11270
|  |  |  | 11:00 | 11090 |  | 0 |  | 11090
|  |  |  | 12:00 | 11800 |  | 0 |  | 11800
|  |  |  | 13:00 | 11820 |  | 0 |  | 11820
|  |  |  | 14:00 | 11580 |  | 0 |  | 11580
|  |  |  | 15:00 | 11630 |  | 0 |  | 11630
|  |  |  | 16:00 | 11360 |  | 0 |  | 11360
|  |  |  | 17:00 | 11570 |  | 0 |  | 11570
|  |  |  | 18:00 | 12960 |  | 0 |  | 12960
|  |  |  | 18:30 | 12920 |  | 0 |  | 12920
|  |  |  | 19:00 | 12890 |  | 0 |  | 12890
|  |  |  | 19:30 | 12590 |  | 0 |  | 12590
|  |  |  | 20:00 | 12570 |  | 0 |  | 12570
|  |  |  | 21:00 | 12380 |  | 0 |  | 12380
|  |  |  | 22:00 | 12290 |  | 0 |  | 12290
|  |  |  | 23:00 | 12000 |  | 0 |  | 12000
Probable Maximum Temperature: |  |  | 31.50°C
Probable Maximum Demand at Day Peak: |  |  | 11800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12960.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12960.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 281.25 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:00 hrs on 03-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9505.09 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3652 | MW
i) Dhaka area |  |  | 5055.53 |  | MW | i) Khulna area |  |  |  | 1484 | MW
ii) Chattogram area |  |  | 1507.6 |  | MW | ii) Barishal area |  |  |  | 417 | MW
iii) Cumilla area |  |  | 1368.96 |  | MW | iii) Rajshahi area |  |  |  | 1050 | MW
iv) Mymensingh area |  |  | 1002 |  | MW | iv) Rangpur area |  |  |  | 701 | MW
v) Sylhet area |  |  | 571 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13157.09 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 88 | 18:00 | 133 | Niamatpur | 42 | 21:00
2 | AKSML | 146 | 03:00 | 68 | Ishurdi | 64 | 18:00 | 134 | Noapara | 41 | 18:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jaldhaka | 56 | 18:00 | 135 | PHP | 4 | 04:00
4 | Agargaon | 106 | 13:00 | 70 | Jamalpur | 96 | 19:30 | 136 | Pabna | 81 | 17:00
5 | Agrabad | 102 | 18:00 | 71 | Jashore | 115 | 18:30 | 137 | Palashbari | 82 | 18:30
6 | Amnura | 18 | 18:00 | 72 | Jhenaidah | 111 | 18:30 | 138 | Panchagarh | 42 | 19:00
7 | Ashuganj | 89 | 01:00 | 73 | Joydebpur | 141 | 12:00 | 139 | Patiya | 10 | 00:00
8 | BSRM | 198 | 05:00 | 74 | Joypurhat | 43 | 18:30 | 140 | Patuakhali | 70 | 01:00
9 | Bagerhat | 74 | 18:00 | 75 | Juldah | 8 | 05:00 | 141 | Payra | 32 | 00:00
10 | Bajitpur | 80 | 00:00 | 76 | KSRM | 11.5 | 02:00 | 142 | Postogola | 62 | 13:00
11 | Bakulia | 90 | 18:00 | 77 | Kabirpur | 232 | 15:00 | 143 | Purbachal | 34 | 13:00
12 | Banani | 46.6 | 13:00 | 78 | Kachua | 83 | 18:00 | 144 | Purbasadipur | 86 | 08:00
13 | Bangabhaban | 25 | 10:00 | 79 | Kallyanpur | 93 | 12:00 | 145 | Rahanpur | 22 | 18:30
14 | Barapukuria | 48 | 18:30 | 80 | Kalurghat | 54 | 16:00 | 146 | Rahim | 46 | 10:00
15 | Barguna | 14 | 02:00 | 81 | Kamrangirchar | 72 | 13:00 | 147 | Rajbari | 68 | 18:00
16 | Barishal | 112 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 119 | 18:00
17 | Barishal-230 | 80 | 00:00 | 83 | Kasba | 34 | 19:00 | 149 | Rajshahi | 112 | 13:00
18 | Baroaulia | 69 | 17:00 | 84 | Kazla | 86 | 01:00 | 150 | Rajshahi-230 | 38 | 20:00
19 | Baroirhat | 70 | 18:00 | 85 | Keranigonj | 68 | 18:00 | 151 | Ramganj | 98 | 18:00
20 | Bashundhara | 184 | 18:00 | 86 | Khagrachori | 28 | 18:00 | 152 | Rampur | 43 | 00:00
21 | BashundharaCement | 14 | 15:00 | 87 | Khulna | 71 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 70 | 18:00 | 88 | Khulshi | 163 | 23:00 | 154 | Rangpur | 112 | 18:00
23 | Benapole | 54 | 00:00 | 89 | Kishoreganj | 113 | 18:30 | 155 | Ruppur | 4 | 00:00
24 | Bhaluka | 124 | 18:00 | 90 | Kodda | 289 | 08:00 | 156 | SSM | 1 | 23:00
25 | Bhandaria | 48 | 00:00 | 91 | Kulaura | 43 | 00:00 | 157 | Saidpur | 81 | 18:00
26 | Bhangura | 34 | 18:00 | 92 | Kurigram | 44 | 18:30 | 158 | Satkhira | 103 | 00:00
27 | Bheramara(GK) | 49 | 18:00 | 93 | Kushtia | 127 | 18:00 | 159 | Satmasjid | 95 | 14:00
28 | Bhulta | 210 | 15:00 | 94 | Laksam | 33 | 00:00 | 160 | Savar | 196 | 12:00
29 | Bog-Sherpur | 50 | 18:00 | 95 | Lakshmipur | 30 | 18:30 | 161 | SevenRings | 14.24 | 17:00
30 | Bogura | 121 | 18:00 | 96 | Lalbag | 58 | 17:00 | 162 | ShahCement | 27 | 07:00
31 | Borhanuddin | 89 | 19:30 | 97 | Lalmonirhat | 41 | 18:00 | 163 | Shahjadpur | 66 | 18:00
32 | Brahmanbaria | 124 | 19:00 | 98 | MI_Cement | 14.4 | 15:00 | 164 | Shahjibazar | 118 | 18:30
33 | Cantonment | 144 | 13:00 | 99 | Madanganj | 40 | 19:30 | 165 | Shahmirpur | 50 | 18:30
34 | Chandina | 12.35 | 00:00 | 100 | Madaripur | 86 | 00:00 | 166 | Shariatpur | 73 | 00:00
35 | Chandpur | 72 | 18:30 | 101 | Madartek | 81 | 00:00 | 167 | Sherpur | 108 | 18:30
36 | Chandraghona | 36 | 18:00 | 102 | Madunaghat | 56 | 18:00 | 168 | Shikalbaha | 40 | 15:00
37 | Chapai | 52 | 18:00 | 103 | Magura | 51 | 18:00 | 169 | Shitalakhya | 73.4 | 18:00
38 | Charsaidpur | 31 | 00:00 | 104 | Mahasthangarh | 52 | 18:00 | 170 | Sholosohor | 47 | 15:00
39 | Chauddagram | 69 | 18:00 | 105 | Maijdee | 35 | 00:00 | 171 | Shyampur | 126 | 09:00
40 | Chhatak | 34 | 18:30 | 106 | Manikganj | 101 | 22:00 | 172 | Siddhirganj | 114 | 15:00
41 | Chowmuhani | 167 | 18:00 | 107 | Maniknagar | 60 | 13:00 | 173 | Sirajganj | 87 | 19:30
42 | Chuadanga | 92 | 00:00 | 108 | Matarbari | 51 | 18:00 | 174 | Sonargaon | 127 | 07:00
43 | Coxsbazar | 142 | 12:00 | 109 | Matuail | 65 | 16:00 | 175 | Sreemongol | 83 | 18:30
44 | Cumilla(N) | 136 | 02:00 | 110 | Metrorail_Motijheel | 26 | 18:00 | 176 | Sreepur | 101 | 18:30
45 | Cumilla(S) | 150 | 18:00 | 111 | Metrorail_Uttara | 13 | 18:00 | 177 | Srinagar | 40.7 | 22:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 121 | 15:00 | 178 | Sunamganj | 57 | 22:00
47 | Daudkandi | 139 | 18:30 | 113 | Mirpur | 127 | 12:00 | 179 | Sylhet | 46 | 19:30
48 | DhakaUniversity | 82 | 13:00 | 114 | Mirsorai | 8 | 09:00 | 180 | Sylhet-132 | 120 | 20:00
49 | Dhamrai | 112 | 18:00 | 115 | Mirzapur | 43 | 19:30 | 181 | TK | 24 | 18:00
50 | Dhanmondi | 127.7 | 13:00 | 116 | Mithapukur | 42 | 18:00 | 182 | Tangail | 146 | 18:00
51 | Dohazari | 102 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 16 | 18:00
52 | Faridpur | 136 | 00:00 | 118 | Mogbazar | 90.9 | 13:00 | 184 | Thakurgaon | 74 | 18:00
53 | Fatullah | 109 | 10:00 | 119 | Mongla | 30 | 12:00 | 185 | Tongi | 115 | 10:00
54 | Fenchuganj | 37 | 00:00 | 120 | Motijheel | 43 | 13:00 | 186 | Ullahpara | 28 | 18:00
55 | Feni | 114 | 18:00 | 121 | Muktagacha | 28 | 18:00 | 187 | Ullon | 59 | 18:30
56 | GPH | 10 | 11:00 | 122 | Munshiganj | 95 | 19:00 | 188 | Uttara | 80 | 13:00
57 | Ghatail | 52 | 18:00 | 123 | Muradnagar | 39 | 01:00 | 189 | UttaraNew | 54 | 04:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 178 | 18:00 | 190 | Zigatola | 66 | 18:00
59 | Ghorashal-230 | 93 | 18:30 | 125 | Naogaon | 79 | 19:00
60 | Goalpara | 33 | 00:00 | 126 | Narail | 50 | 18:00
61 | Gollamari | 78 | 21:00 | 127 | Narinda | 72 | 13:00
62 | Gopalganj | 90 | 18:00 | 128 | Narshingdi | 168 | 19:30
63 | Gulshan | 116 | 13:00 | 129 | Natore | 101 | 18:30
64 | Halishahar | 73 | 15:00 | 130 | Nawabganj | 43.4 | 14:00
65 | HaripurSBU | 160 | 15:00 | 131 | Netrakona | 121 | 18:00
66 | Hasnabad | 94 | 19:30 | 132 | New | 54 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 06:00 | 372 | 11:00 | Payra | 410 | 06:00 | 405 | 00:00
Ashuganj | 403 | 17:00 | 395 | 00:00 | Rahanpur | 411 | 10:00 | 405 | 00:00
Bhulta | 408 | 06:00 | 382 | 11:00 | Rampal | 405 | 04:00 | 396 | 11:00
Bibiana | 389 | 07:00 | 381 | 12:00
BIPTC | 403 | 17:00 | 395 | 00:00
Bogura | 405 | 05:00 | 398 | 00:00
Gopalganj | 397 | 06:00 | 36 | 08:00
Kaliakoir | 377 | 20:00 | 362 | 11:00
Madunaghat | 392 | 18:00 | 386 | 00:00
Meghnaghat | 384 | 06:00 | 375 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 22:00 | 220 | 11:00 | Kaliakoir | 236 | 20:00 | 224 | 11:00
AKSML | 232 | 18:00 | 223 | 02:00 | Keranigonj | 226 | 06:00 | 218 | 11:00
Aminbazar | 230 | 05:00 | 222 | 11:00 | Khulna(S) | 235 | 06:00 | 228 | 00:00
Ashuganj | 235 | 19:00 | 224 | 11:00 | Madunaghat | 231 | 17:00 | 226 | 11:00
Ashuganj-400 | 235 | 19:00 | 224 | 11:00 | Madunaghat-400 | 232 | 18:00 | 227 | 00:00
Baghabari | 238 | 18:30 | 230 | 12:00 | Maniknagar | 220 | 05:00 | 212 | 12:00
Barapukuria | 228 | 10:00 | 209 | 07:00 | Meghnaghat | 227 | 21:00 | 221 | 00:00
Barapukuria-230 | 228 | 10:00 | 209 | 07:00 | Meghnaghat-400 | 223 | 06:00 | 217 | 11:00
Barishal | 234 | 06:00 | 228 | 00:00 | Mirsorai | 229 | 18:00 | 219 | 03:00
Bheramara | 235 | 05:00 | 228 | 00:00 | Rajshahi | 233 | 06:00 | 223 | 23:00
Bhulta | 234 | 07:00 | 209 | 11:00 | Rampal | 233 | 05:00 | 226 | 00:00
Bibiana | 229 | 07:00 | 225 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 05:00 | 229 | 00:00 | Rampura | 234 | 06:00 | 215 | 11:00
Bogura | 235 | 04:00 | 231 | 00:00 | Shikalbaha | 230 | 17:00 | 224 | 02:00
Bogura-400 | 264 | 06:00 | 229 | 08:00 | Shyampur | 224 | 06:00 | 217 | 11:00
Borhanuddin | 236 | 08:00 | 232 | 00:00 | Siddhirganj | 221 | 06:00 | 215 | 11:00
BSRM | 227 | 08:00 | 219 | 01:00 | Sirajgonj | 240 | 04:00 | 235 | 11:00
Cumilla(N) | 225 | 08:00 | 219 | 00:00 | Sreepur | 230 | 06:00 | 222 | 11:00
Faridpur | 231 | 06:00 | 225 | 00:00 | Tongi | 233 | 20:00 | 218 | 12:00
Fenchuganj | 231 | 08:00 | 227 | 00:00
Ghorashal | 238 | 00:00 | 230 | 01:00
Ghorashal-230 | 232 | 06:00 | 217 | 11:00
Gopalganj | 233 | 06:00 | 227 | 00:00
GPH | 230 | 18:00 | 224 | 00:00
Haripur | 221 | 22:00 | 214 | 12:00
Hasnabad | 225 | 04:00 | 218 | 12:00
Hathazari | 229 | 19:00 | 222 | 00:00
Ishurdi | 237 | 05:00 | 231 | 00:00
Jhenaidah | 234 | 09:00 | 225 | 00:00
Kachua | 228 | 17:00 | 214 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 123 | 11:00 | Lalmonirhat | 132 | 18:00 | 122 | 07:00
Agargaon | 135 | 06:00 | 128 | 11:00 | Madanganj | 130 | 02:00 | 126 | 14:00
Agrabad | 132 | 22:00 | 127 | 00:00 | Madaripur | 134 | 07:00 | 131 | 00:00
AKS | 129 | 06:00 | 126 | 00:00 | Madartek | 136 | 06:00 | 123 | 11:00
Aminbazar | 137 | 19:30 | 130 | 10:00 | Madunaghat | 134 | 17:00 | 131 | 00:00
Amnura | 140 | 10:00 | 131 | 00:00 | Magura | 137 | 06:00 | 129 | 00:00
Ashuganj | 142 | 06:00 | 138 | 00:00 | Mahasthangarh | 134 | 18:30 | 129 | 13:00
Bagerhat | 131 | 06:00 | 124 | 01:00 | Maijdee | 131 | 13:00 | 123 | 01:00
Bajitpur | 133 | 06:00 | 126 | 11:00 | Manikganj | 134 | 06:00 | 126 | 12:00
Bakulia | 135 | 19:30 | 128 | 02:00 | Maniknagar | 133 | 08:00 | 127 | 12:00
Banani | 137 | 06:00 | 124 | 11:00 | Matarbari | 114 | 09:00 | 108 | 00:00
Bangabhaban | 133 | 04:00 | 127 | 11:00 | Matuail | 128.4 | 20:00 | 124 | 11:00
Barapukuria | 138 | 18:30 | 126 | 07:00 | Metrorail_Motijheel | 133 | 08:00 | 127 | 12:00
Barguna | 135 | 06:00 | 133 | 00:00 | Metrorail_Uttara | 139 | 06:00 | 130 | 11:00
Barishal | 134 | 05:00 | 130 | 00:00 | Millgate | 139 | 21:00 | 130 | 11:00
Barishal-230 | 134 | 06:00 | 130 | 00:00 | Mirpur | 136 | 20:00 | 129 | 11:00
Baroaulia | 133 | 08:00 | 129 | 00:00 | Mirzapur | 131 | 20:00 | 125 | 11:00
Baroirhat | 130 | 13:00 | 125 | 01:00 | Mithapukur | 135 | 18:00 | 127 | 07:00
Bashundhara | 137 | 01:00 | 123 | 11:00 | MI_Cement | 132 | 04:00 | 125 | 11:00
BashundharaCement | 130 | 02:00 | 120 | 20:00 | Modern | 0 | 00:00 | 0 | 00:00
Beanibazar | 130 | 06:00 | 126 | 18:30 | Mogbazar | 138 | 05:00 | 125 | 11:00
Benapole | 135 | 09:00 | 125 | 00:00 | Mongla | 132 | 06:00 | 126 | 01:00
Bhaluka | 132 | 07:00 | 125 | 12:00 | Motijheel | 133 | 03:00 | 127 | 11:00
Bhandaria | 130 | 06:00 | 125 | 00:00 | Muktagacha | 131 | 00:00 | 128 | 11:00
Bhangura | 135 | 01:00 | 131 | 00:00 | Munshiganj | 128 | 17:00 | 123 | 12:00
Bheramara | 139 | 09:00 | 136 | 00:00 | Muradnagar | 127 | 17:00 | 122 | 01:00
Bheramara(GK) | 139 | 10:00 | 136 | 00:00 | Mymensingh | 131 | 03:00 | 122 | 11:00
Bhulta | 126 | 04:00 | 121 | 12:00 | Naogaon | 132 | 18:00 | 128 | 12:00
Bog-Sherpur | 134 | 04:00 | 131 | 12:00 | Narail | 136 | 09:00 | 127 | 00:00
Bogura | 135 | 18:00 | 130 | 08:00 | Narinda | 133 | 08:00 | 127 | 12:00
Bogura-230 | 135 | 18:30 | 131 | 08:00 | Narshingdi | 134 | 08:00 | 117 | 15:00
Brahmanbaria | 136 | 08:00 | 130 | 11:00 | Natore | 134 | 03:00 | 131 | 00:00
Cantonment | 135 | 05:00 | 128 | 11:00 | Nawabganj | 134 | 06:00 | 129 | 11:00
Chandina | 131 | 17:00 | 126 | 01:00 | Netrakona | 126 | 19:00 | 120 | 11:00
Chandpur | 137 | 18:00 | 126 | 03:00 | New | 140 | 20:00 | 131 | 11:00
Chandraghona | 134 | 17:00 | 131 | 11:00 | Niamatpur | 141 | 03:00 | 139 | 07:00
Chapai | 140 | 05:00 | 138 | 00:00 | Noapara | 134 | 06:00 | 129 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 17:00 | 124 | 11:00 | Pabna | 137 | 05:00 | 133 | 12:00
Chauddagram | 130 | 13:00 | 125 | 00:00 | Palashbari | 132 | 18:00 | 126 | 07:00
Chhatak | 129 | 05:00 | 123 | 19:30 | Panchagarh | 141 | 19:00 | 127 | 13:00
Chowmuhani | 130 | 22:00 | 124 | 01:00 | Patiya | 130 | 22:00 | 126 | 04:00
Chuadanga | 136 | 06:00 | 128 | 00:00 | Patuakhali | 136 | 17:00 | 133 | 11:00
Coxsbazar | 114 | 09:00 | 108 | 00:00 | Payra | 136 | 04:00 | 135 | 00:00
Cumilla(N) | 131 | 17:00 | 126 | 00:00 | PHP | 130 | 17:00 | 125 | 00:00
Cumilla(S) | 133 | 02:00 | 126 | 00:00 | Postogola | 134 | 05:00 | 127 | 11:00
Daganbhuiyan | 131 | 13:00 | 125 | 00:00 | Purbachal | 136 | 05:00 | 123 | 11:00
Daudkandi | 126 | 17:00 | 119 | 00:00 | Purbasadipur | 136 | 18:30 | 124 | 12:00
DhakaUniversity | 137 | 05:00 | 125 | 11:00 | Rahanpur | 141 | 04:00 | 139 | 00:00
Dhamrai | 134 | 05:00 | 128 | 11:00 | Rahanpur-400 | 141 | 04:00 | 139 | 21:00
Dhanmondi | 137 | 05:00 | 124 | 11:00 | Rahim | 128 | 05:00 | 124 | 11:00
Dohazari | 126 | 17:00 | 122 | 00:00 | Rajbari | 136 | 07:00 | 131 | 00:00
Faridpur | 136 | 07:00 | 132 | 00:00 | Rajendrapur | 132 | 06:00 | 125 | 11:00
Fatullah | 137 | 22:00 | 126 | 11:00 | Rajshahi | 134 | 04:00 | 130 | 00:00
Fenchuganj | 136 | 06:00 | 134 | 00:00 | Rajshahi-230 | 134 | 05:00 | 131 | 00:00
Feni | 129 | 17:00 | 124 | 01:00 | Ramganj | 132 | 13:00 | 123 | 02:00
Ghatail | 130 | 03:00 | 125 | 00:00 | Rampur | 130 | 18:30 | 127 | 11:00
Ghorashal | 139 | 06:00 | 133 | 14:00 | Rampura | 136 | 04:00 | 124 | 11:00
Goalpara | 136 | 05:00 | 130 | 00:00 | Rangamati | 133 | 08:00 | 130 | 00:00
Gollamari | 135 | 06:00 | 131 | 00:00 | Rangpur | 136 | 18:30 | 126 | 08:00
Gopalganj | 134 | 05:00 | 130 | 00:00 | Ruppur | 139 | 06:00 | 135 | 02:00
Gopalganj-400 | 136 | 05:00 | 133 | 00:00 | Saidpur | 135 | 18:30 | 124 | 08:00
Gulshan | 136 | 06:00 | 124 | 11:00 | Satkhira | 132 | 17:00 | 125 | 01:00
Halishahar | 132 | 22:00 | 128 | 00:00 | Satmasjid | 135 | 05:00 | 128 | 12:00
Haripur | 129 | 20:00 | 124 | 12:00 | Savar | 137 | 20:00 | 129 | 10:00
HaripurSBU | 128 | 04:00 | 125 | 15:00 | SevenRings | 140 | 08:00 | 131 | 11:00
Hasnabad | 135 | 23:00 | 128 | 12:00 | ShahCement | 128 | 17:00 | 124 | 11:00
Hathazari | 135 | 19:00 | 130 | 00:00 | Shahjadpur | 138 | 04:00 | 135 | 10:00
Ishurdi | 139 | 04:00 | 136 | 00:00 | Shahjibazar | 137 | 08:00 | 131 | 00:00
Jaldhaka | 133 | 19:00 | 122 | 13:00 | Shahmirpur | 132 | 22:00 | 129 | 02:00
Jamalpur | 131 | 01:00 | 120 | 06:00 | Shariatpur | 134 | 06:00 | 129 | 00:00
Jashore | 136 | 09:00 | 127 | 00:00 | Sherpur | 128 | 09:00 | 117 | 06:00
Jhenaidah | 139 | 07:00 | 129 | 00:00 | Shikalbaha | 122 | 18:30 | 118 | 11:00
Jhenaidah-230 | 139 | 09:00 | 132 | 00:00 | Shikalbaha-230 | 133 | 17:00 | 130 | 01:00
Joydebpur | 140 | 18:30 | 125 | 11:00 | Shitalakhya | 132 | 04:00 | 125 | 11:00
Joypurhat | 132 | 18:00 | 128 | 00:00 | Sholosohor | 133 | 18:30 | 130 | 02:00
Juldah | 133 | 22:00 | 128 | 11:00 | Shyampur | 133 | 05:00 | 132 | 00:00
Kabirpur | 137 | 07:00 | 125 | 11:00 | Shyampur-230 | 136 | 05:00 | 131 | 11:00
Kachua | 135 | 17:00 | 127 | 01:00 | Siddhirganj | 129 | 19:30 | 124 | 11:00
Kaliakoir | 136 | 05:00 | 129 | 11:00 | Sirajganj | 133 | 06:00 | 129 | 12:00
Kallyanpur | 137 | 18:30 | 129 | 11:00 | Sonargaon | 128 | 19:00 | 122 | 11:00
Kalurghat | 133 | 07:00 | 130 | 02:00 | Sreemongol | 135 | 06:00 | 130 | 00:00
Kamrangirchar | 135 | 05:00 | 128 | 11:00 | Sreepur | 134 | 19:00 | 128 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 134 | 06:00 | 128 | 11:00
Kasba | 128 | 17:00 | 121 | 01:00 | SSM | 138 | 20:00 | 132 | 00:00
Kazla | 132 | 04:00 | 127 | 12:00 | Sunamganj | 127 | 04:00 | 121 | 12:00
Keranigonj | 135 | 06:00 | 129 | 11:00 | Sylhet | 131 | 08:00 | 127 | 23:00
Khagrachori | 132 | 08:00 | 129 | 01:00 | Sylhet-132 | 130 | 01:00 | 128 | 12:00
Khulna | 134 | 05:00 | 130 | 01:00 | Tangail | 128 | 20:00 | 124 | 11:00
Khulna(S) | 136 | 06:00 | 131 | 00:00 | Taraganj | 135 | 19:00 | 124 | 13:00
Khulshi | 130 | 22:00 | 126 | 11:00 | Thakurgaon | 140 | 19:00 | 124 | 13:00
Kishoreganj | 131 | 09:00 | 125 | 11:00 | TK | 133 | 01:00 | 130 | 11:00
Kodda | 135 | 22:00 | 122 | 11:00 | Tongi | 141 | 19:30 | 131 | 15:00
KSRM | 132 | 05:00 | 129 | 04:00 | Ullahpara | 136 | 06:00 | 132 | 12:00
Kulaura | 136 | 08:00 | 133 | 00:00 | Ullon | 136 | 06:00 | 124 | 11:00
Kurigram | 133 | 19:00 | 122 | 08:00 | Uttara | 136 | 20:00 | 129 | 11:00
Kushtia | 137 | 10:00 | 132 | 00:00 | UttaraNew | 140 | 22:00 | 130 | 11:00
Laksam | 134 | 13:00 | 126 | 02:00 | Zigatola | 134 | 04:00 | 129 | 11:00
Lakshmipur | 131 | 13:00 | 124 | 01:00
Lalbag | 134 | 05:00 | 128 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-11-2025 | [28 empty] | Date: | 02-11-2025 | [28 empty] | Date: | 02-11-2025 | [28 empty] | Date: | 02-11-2025 | [28 empty] | Date: | 02-11-2025 | [14 empty] | Date: | 02-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 17 | 230 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 0 | 72 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 14 | 21 | 0 | 350 | 0 | 0 | 76 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 215 | 30 | 33 | 655 | 0 | 0 | 0 | 0 | 65 | 220 | 0 | 0 | 0 | 580 | 0 | 51 | 10 | 0 | 310 | 356 | 330 | 47 | 0 | 37 | 34 | 104 | 49 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 315 | 0 | 387 | 0 | 0 | 157 | 0 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 48 | 48 | 128 | 0 | 0 | 0 | 6480 | 886 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 773.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 35 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 1096 | 10 | 5796.05 | 12276.05 | 102.73
01:00 | 0 | 0 | 17 | 230 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 35 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 350 | 0 | 0 | 53 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 216 | 0 | 33 | 655 | 0 | 0 | 0 | 0 | 34 | 223 | 0 | 0 | 0 | 578 | 0 | 51 | 10 | 0 | 310 | 357 | 330 | 47 | 0 | 37 | 0 | 104 | 48 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 315 | 0 | 386 | 0 | 0 | 158 | 0 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 49 | 48 | 160 | 0 | 0 | 0 | 6321 | 886 | 397 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 764.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 450 | 1108 | 0 | 5638.93 | 11959.93 | 102.72
02:00 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 350 | 0 | 0 | 27 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 217 | 0 | 33 | 655 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 576 | 0 | 51 | 0 | 0 | 310 | 356 | 330 | 47 | 0 | 37 | 0 | 104 | 34 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 310 | 0 | 342 | 0 | 0 | 145 | 5 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 35 | 16 | 152 | 0 | 0 | 0 | 6074 | 886 | 390 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 0 | 761.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 362 | 1101 | 0 | 5460.28 | 11534.28 | 102.71
03:00 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 33 | 655 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 0 | 305 | 356 | 330 | 47 | 0 | 37 | 0 | 105 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 310 | 0 | 315 | 0 | 0 | 145 | 5 | 0 | 81 | 0 | 0 | 0 | 160 | 0 | 35 | 16 | 153 | 0 | 0 | 0 | 5954 | 886 | 389 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 0 | 666.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 305 | 1102 | 0 | 5272.57 | 11226.57 | 102.7
04:00 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 33 | 655 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 578 | 0 | 51 | 0 | 0 | 295 | 357 | 300 | 47 | 0 | 37 | 0 | 104 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 310 | 0 | 320 | 0 | 0 | 144 | 5 | 0 | 78 | 0 | 0 | 0 | 160 | 0 | 16 | 8 | 153 | 0 | 0 | 0 | 5839 | 887 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 0 | 577.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 305 | 1050 | 0 | 5069.55 | 10908.55 | 102.69
05:00 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 33 | 655 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 581 | 0 | 51 | 0 | 0 | 300 | 357 | 280 | 47 | 0 | 37 | 0 | 104 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 320 | 0 | 336 | 0 | 0 | 149 | 5 | 0 | 79 | 0 | 0 | 0 | 160 | 0 | 8 | 8 | 153 | 0 | 0 | 0 | 5852 | 886 | 395 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 0 | 578.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 305 | 960 | 0 | 4924.22 | 10776.22 | 102.68
06:00 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 30 | 655 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 505 | 0 | 51 | 0 | 0 | 300 | 355 | 280 | 47 | 0 | 34 | 0 | 104 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 310 | 0 | 334 | 0 | 0 | 150 | 5 | 0 | 79 | 0 | 0 | 0 | 160 | 0 | 8 | 8 | 153 | 0 | 0 | 0 | 5748 | 886 | 396 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 528.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 303 | 910 | 0 | 4811.48 | 10559.48 | 102.67
07:00 | 0 | 17 | 8 | 230 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 5 | 0 | 20 | 21 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.24 | 220 | 0 | 30 | 655 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 562 | 3 | 51 | 0 | 0 | 300 | 352 | 330 | 47 | 0 | 34 | 0 | 104 | 0 | 0 | 17 | 0 | 48 | 0 | 1 | 0 | 315 | 0 | 351 | 0 | 0 | 154 | 5 | 0 | 79 | 0 | 0 | 0 | 160 | 0 | 47 | 25 | 142 | 0 | 1.32 | 0 | 6008.56 | 886 | 404 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 930 | 0 | 529.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.32 | 4 | 0 | 0 | 1.99 | 178 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0.1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 8 | 0.04 | 0 | 0 | 110 | 180 | 0 | 306 | 936 | 0 | 4893.29 | 10901.85 | 102.66
08:00 | 0 | 17 | 16 | 230 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 16 | 0 | 14 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.19 | 219 | 0 | 6 | 655 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 550 | 6 | 51 | 0 | 0 | 300 | 356 | 310 | 47 | 0 | 35 | 0 | 105 | 0 | 0 | 17 | 0 | 38 | 0 | 8 | 0 | 315 | 0 | 374 | 0 | 0 | 148 | 5 | 0 | 79 | 0 | 0 | 0 | 160 | 0 | 47 | 25 | 142 | 0 | 9.27 | 0 | 5995.46 | 886 | 396 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 940 | 0 | 632.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.06 | 22 | 0 | 0 | 7.88 | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0.88 | 0 | 0 | 0 | 5 | 13 | 0 | 0 | 0 | 0.7 | 26 | 0.11 | 0 | 0 | 110 | 220 | 0 | 306 | 950 | 0 | 5118.46 | 11113.92 | 102.65
09:00 | 0 | 17 | 16 | 230 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 26 | 0 | 14 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.26 | 219 | 0 | 2 | 655 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 552 | 9 | 51 | 0 | 0 | 350 | 354 | 310 | 47 | 0 | 35 | 0 | 103 | 0 | 0 | 17 | 0 | 42 | 0 | 39 | 0 | 320 | 0 | 386 | 0 | 0 | 149 | 5 | 0 | 79 | 0 | 0 | 0 | 160 | 0 | 49 | 25 | 133 | 0 | 6.8 | 0 | 6120.06 | 887 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 913 | 0 | 567.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.03 | 32 | 0 | 0 | 22.5 | 177 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 1.8 | 0 | 0 | 35 | 7 | 34 | 0 | 0 | 0 | 1.4 | 30 | 0.28 | 0 | 0 | 110 | 220 | 0 | 306 | 945 | 0 | 5010.89 | 11130.95 | 102.64
10:00 | 0 | 17 | 16 | 110 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17.5 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 17 | 0 | 20 | 21 | 0 | 350 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.01 | 218 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 580 | 8 | 51 | 0 | 0 | 395 | 353 | 330 | 44 | 0 | 34 | 0 | 104 | 0 | 0 | 17 | 0 | 60 | 0 | 64 | 0 | 325 | 0 | 344 | 0 | 0 | 157 | 5 | 0 | 78 | 0 | 0 | 0 | 160 | 0 | 49 | 25 | 119 | 0 | 9.07 | 0 | 6108.58 | 886 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 852 | 0 | 566.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.68 | 33 | 0 | 0 | 42.25 | 194 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 1.09 | 0 | 0 | 35 | 6 | 34 | 0 | 0 | 0 | 2.8 | 29 | 0.68 | 0 | 0 | 110 | 220 | 0 | 350 | 982 | 0 | 5163.95 | 11272.53 | 102.63
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17.5 | 0 | 50 | 0 | 0 | 0 | 35 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 16 | 0 | 20 | 21 | 0 | 360 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.93 | 218 | 0 | 3 | 650 | 0 | 0 | 5 | 0 | 0 | 217 | 0 | 0 | 0 | 590 | 12 | 51 | 0 | 0 | 395 | 345 | 330 | 43 | 0 | 37 | 0 | 102 | 0 | 0 | 17 | 0 | 64 | 0 | 13 | 1 | 315 | 0 | 344 | 0 | 0 | 157 | 5 | 0 | 83 | 0 | 0 | 0 | 160 | 0 | 49 | 25 | 106 | 1 | 16.97 | 1 | 6005.4 | 886 | 381 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 939 | 0 | 634.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.73 | 24 | 0 | 0 | 15.12 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.18 | 0 | 0 | 35 | 11 | 34 | 0 | 0 | 0 | 4.2 | 41 | 0.28 | 0 | 0 | 110 | 220 | 0 | 355 | 1048 | 0 | 5488.9 | 11494.3 | 102.62
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 17.5 | 2 | 51 | 0 | 30 | 0 | 35 | 90 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 8 | 17 | 20 | 21 | 0 | 480 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.33 | 218 | 11 | 2 | 650 | 0 | 0 | 6 | 0 | 14 | 217 | 0 | 0 | 0 | 565 | 17 | 51 | 15 | 0 | 370 | 350 | 330 | 37 | 0 | 34 | 1 | 102 | 50 | 0 | 17 | 0 | 66 | 0 | 71 | 13 | 320 | 0 | 287 | 0 | 0 | 158 | 5 | 0 | 83 | 0 | 0 | 0 | 160 | 0 | 48 | 31 | 105 | 0 | 29.84 | 6 | 6397.67 | 886 | 397 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 89 | 1092 | 0 | 731.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 55 | 0 | 0 | 16.62 | 200 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 1.64 | 0 | 0 | 0 | 11 | 34 | 0 | 0 | 0 | 4.2 | 47 | 0.68 | 0 | 0 | 110 | 220 | 0 | 405 | 1060 | 0 | 5807.1 | 12204.77 | 102.61
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 17.5 | 17 | 85 | 0 | 145 | 12 | 35 | 138 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 13 | 52 | 18 | 21 | 0 | 460 | 0 | 0 | 44 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 3.27 | 218 | 30 | 6 | 650 | 0 | 0 | 6 | 0 | 51 | 217 | 0 | 0 | 0 | 528 | 18 | 51 | 78 | 0 | 350 | 316 | 290 | 10 | 0 | 33 | 38 | 102 | 162 | 0 | 17 | 0 | 76 | 0 | 67 | 14 | 305 | 0 | 277 | 0 | 0 | 141 | 5 | 0 | 83 | 0 | 0 | 0 | 160 | 17 | 49 | 46 | 105 | 0 | 14.81 | 6 | 6654.58 | 886 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 1075 | 0 | 758.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.04 | 35 | 0 | 0 | 15.27 | 169 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 1.59 | 0 | 0 | 0 | 4 | 34 | 0 | 0 | 0 | 2.2 | 22 | 0.64 | 0 | 0 | 110 | 180 | 0 | 360 | 1100 | 0 | 5573.97 | 12228.55 | 102.6
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 17.5 | 17 | 65 | 0 | 115 | 30 | 35 | 126 | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 9 | 35 | 21.4 | 21 | 0 | 415 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.16 | 219 | 32 | 4 | 650 | 0 | 0 | 6 | 0 | 49 | 216 | 0 | 0 | 0 | 557 | 14 | 51 | 113 | 0 | 300 | 280 | 280 | 10 | 0 | 36 | 52 | 100 | 147 | 0 | 17 | 0 | 78 | 0 | 16 | 15 | 305 | 0 | 318 | 0 | 0 | 151 | 5 | 0 | 83 | 0 | 0 | 0 | 160 | 17 | 49 | 48 | 105 | 0 | 14.01 | 6 | 6402.07 | 887 | 380 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 1101 | 0 | 755.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.67 | 26 | 0 | 0 | 10.18 | 170 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0.56 | 0 | 0 | 0 | 7 | 34 | 0 | 0 | 0 | 4.2 | 28 | 0.38 | 0 | 0 | 110 | 180 | 0 | 303 | 1100 | 0 | 5580.42 | 11982.49 | 102.59
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17.5 | 17 | 51 | 0 | 115 | 30 | 35 | 126 | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 35 | 15 | 21 | 0 | 400 | 0 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 1.84 | 218 | 33 | 3 | 650 | 0 | 0 | 6 | 0 | 47 | 214 | 0 | 0 | 0 | 552 | 12 | 51 | 125 | 0 | 305 | 280 | 280 | 10 | 0 | 33 | 51 | 102 | 151 | 0 | 17 | 0 | 76 | 0 | 49 | 20 | 315 | 0 | 318 | 0 | 0 | 154 | 6 | 0 | 79 | 0 | 0 | 0 | 160 | 17 | 49 | 48 | 105 | 0 | 7.67 | 6 | 6514.01 | 886 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 1115 | 0 | 755.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8 | 9 | 0 | 0 | 7.47 | 176 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0.83 | 0 | 0 | 0 | 4 | 34 | 0 | 0 | 0 | 0.8 | 20 | 0.17 | 0 | 0 | 110 | 180 | 0 | 302 | 1100 | 0 | 5520.96 | 12034.97 | 102.56
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 17 | 51 | 0 | 115 | 30 | 35 | 90 | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 35 | 20.5 | 21 | 0 | 400 | 0 | 0 | 44 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 0.62 | 218 | 34 | 3 | 650 | 0 | 0 | 6 | 0 | 46 | 218 | 0 | 0 | 0 | 541 | 6 | 51 | 123 | 0 | 305 | 280 | 280 | 10 | 0 | 33 | 50 | 102 | 100 | 0 | 17 | 0 | 64 | 0 | 16 | 22 | 305 | 0 | 287 | 0 | 0 | 143 | 6 | 0 | 80 | 0 | 0 | 0 | 160 | 17 | 49 | 48 | 105 | 0 | 4.28 | 6 | 6373.4 | 886 | 320 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1084 | 0 | 749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.92 | 4 | 0 | 0 | 5.95 | 167 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0.45 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 0 | 0.6 | 17 | 0.08 | 0 | 0 | 110 | 220 | 0 | 303 | 1100 | 0 | 5391 | 11764.4 | 102.51
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 18 | 51 | 15 | 115 | 30 | 35 | 86 | 0 | 320 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 40 | 21.5 | 21 | 0 | 400 | 5 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 0.02 | 219 | 33 | 9 | 650 | 6 | 0 | 6 | 1 | 47 | 220 | 0 | 0 | 0 | 552 | 0 | 51 | 125 | 0 | 393 | 349 | 330 | 10 | 0 | 31 | 52 | 102 | 95 | 0 | 19 | 14 | 68 | 5 | 2 | 27 | 310 | 0 | 310 | 0 | 0 | 148 | 6 | 0 | 55 | 20 | 0 | 0 | 160 | 17 | 49 | 48 | 105 | 0 | 0.39 | 6 | 6617.91 | 887 | 320 | 0 | 6 | 3 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 990 | 0 | 748 | 0 | 0 | 0 | 0 | 1 | 0 | 85 | 0 | 3 | 0.24 | 0 | 0 | 0 | 0.5 | 171 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0.04 | 0 | 0 | 30 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 110 | 220 | 0 | 302 | 1050 | 2 | 5353.8 | 11971.71 | 102.52
18:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 48.3 | 35 | 73 | 45 | 293 | 30 | 35 | 140 | 0 | 320 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 108 | 21.5 | 21 | 0 | 410 | 16 | 16 | 43 | 0 | 0 | 50 | 24 | 15 | 24 | 12 | 0 | 219 | 45 | 6 | 650 | 50 | 0 | 6 | 8 | 75 | 219 | 0 | 0 | 0 | 550 | 0 | 51 | 132 | 0 | 380 | 348 | 330 | 18 | 0 | 30 | 56 | 103 | 106 | 0 | 19 | 14 | 80 | 8 | 0 | 27 | 315 | 0 | 310 | 0 | 0 | 153 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 105 | 0 | 0 | 6 | 7338.8 | 886 | 398 | 0 | 33 | 3 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 750.7 | 0 | 44 | 0 | 35 | 38 | 0 | 100 | 13 | 8 | 0 | 0 | 27 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 95 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 110 | 220 | 0 | 400 | 1067 | 10 | 6026.7 | 13365.5 | 102.5
19:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 46.5 | 35 | 96 | 30 | 293 | 15 | 55 | 151 | 0 | 320 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 90 | 21.5 | 21 | 0 | 400 | 0 | 0 | 45 | 0 | 0 | 50 | 24 | 0 | 24 | 12 | 0 | 219 | 28 | 4 | 650 | 15 | 0 | 6 | 8 | 80 | 220 | 0 | 0 | 0 | 542 | 0 | 51 | 137 | 0 | 380 | 356 | 330 | 20 | 0 | 31 | 82 | 103 | 140 | 0 | 19 | 0 | 68 | 0 | 0 | 27 | 310 | 0 | 286 | 0 | 0 | 152 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 104 | 0 | 0 | 0 | 7193 | 886 | 388 | 0 | 40 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 0 | 744.09 | 0 | 48 | 0 | 0 | 35 | 0 | 100 | 28 | 0 | 0 | 0 | 26 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 401 | 1095 | 10 | 6104.09 | 13297.09 | 102.48
19:30 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 46.5 | 17 | 65 | 30 | 293 | 15 | 55 | 150 | 0 | 320 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 90 | 21 | 21 | 0 | 410 | 0 | 0 | 44 | 0 | 0 | 50 | 24 | 0 | 24 | 12 | 0 | 219 | 16 | 11 | 650 | 0 | 0 | 6 | 8 | 77 | 220 | 0 | 0 | 0 | 552 | 0 | 51 | 60 | 0 | 380 | 352 | 330 | 20 | 0 | 34 | 88 | 104 | 140 | 0 | 19 | 0 | 74 | 0 | 0 | 27 | 315 | 0 | 313 | 0 | 0 | 145 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 105 | 0 | 0 | 0 | 7123.5 | 886 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 739.45 | 0 | 48 | 0 | 0 | 0 | 0 | 100 | 32 | 0 | 0 | 0 | 26 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 400 | 1095 | 10 | 5874.45 | 12997.95
20:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 46.5 | 17 | 69 | 30 | 293 | 15 | 55 | 148 | 0 | 320 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 90 | 21 | 21 | 0 | 400 | 0 | 0 | 44 | 0 | 0 | 50 | 24 | 0 | 24 | 12 | 0 | 220 | 17 | 18 | 650 | 0 | 0 | 6 | 8 | 78 | 221 | 0 | 0 | 0 | 550 | 0 | 51 | 60 | 0 | 393 | 357 | 330 | 20 | 0 | 34 | 85 | 103 | 149 | 0 | 19 | 0 | 76 | 0 | 0 | 27 | 310 | 0 | 300 | 0 | 0 | 145 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 104 | 0 | 0 | 0 | 7124.5 | 886 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 740.64 | 0 | 48 | 0 | 0 | 0 | 0 | 100 | 32 | 0 | 0 | 0 | 19 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 400 | 1095 | 10 | 5845.64 | 12970.14 | 102.46
21:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 46.5 | 17 | 60 | 0 | 293 | 15 | 35 | 147 | 0 | 320 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 52 | 21 | 21 | 0 | 400 | 0 | 0 | 44 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 220 | 14 | 25 | 650 | 0 | 0 | 6 | 8 | 77 | 221 | 0 | 0 | 0 | 551 | 0 | 51 | 60 | 0 | 393 | 356 | 330 | 20 | 0 | 34 | 85 | 104 | 153 | 0 | 19 | 0 | 72 | 0 | 0 | 27 | 305 | 0 | 314 | 0 | 0 | 145 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 104 | 0 | 0 | 0 | 6999.5 | 886 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 732 | 0 | 48 | 0 | 0 | 0 | 0 | 100 | 32 | 0 | 0 | 0 | 19 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 400 | 1095 | 10 | 5781 | 12780.5 | 102.44
22:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 46 | 17 | 60 | 0 | 293 | 0 | 35 | 130 | 0 | 370 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 35 | 19 | 21 | 0 | 400 | 0 | 0 | 44 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 218 | 14 | 27 | 650 | 0 | 0 | 9 | 0 | 79 | 222 | 0 | 0 | 0 | 558 | 0 | 51 | 60 | 0 | 393 | 356 | 330 | 20 | 0 | 34 | 84 | 104 | 149 | 0 | 19 | 0 | 74 | 0 | 0 | 0 | 305 | 0 | 291 | 0 | 0 | 147 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 104 | 0 | 0 | 0 | 6948 | 886 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 0 | 722 | 0 | 48 | 0 | 0 | 0 | 0 | 100 | 32 | 0 | 0 | 0 | 19 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 401 | 1095 | 10 | 5745 | 12693 | 102.42
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 45.6 | 17 | 60 | 0 | 95 | 0 | 35 | 72 | 0 | 370 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 35 | 18 | 21 | 0 | 400 | 0 | 0 | 24 | 0 | 0 | 50 | 0 | 0 | 24 | 12 | 0 | 218 | 14 | 26 | 650 | 0 | 0 | 15 | 0 | 77 | 222 | 0 | 0 | 0 | 555 | 0 | 51 | 60 | 0 | 385 | 355 | 330 | 20 | 0 | 31 | 86 | 104 | 105 | 0 | 19 | 0 | 76 | 0 | 0 | 0 | 305 | 0 | 310 | 0 | 0 | 153 | 8 | 0 | 81 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 114 | 0 | 0 | 0 | 6653.6 | 886 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 0 | 719 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 402 | 1095 | 10 | 5633 | 12286.6 | 102.4
Total KWH | 0 | 480960 | 299040 | 2351300 | 0 | 0 | 0 | 0 | 8449200 | 0 | 0 | 519120 | 257040 | 1197216 | 115680 | 2273989 | 237526 | 534902 | 1591200 | 0 | 8480000 | 0 | 0 | 0 | 139216 | 7500303 | 0 | 0 | 106952 | 662400 | 418800 | 497160 | 0 | 9358636.36 | 37636 | 22582 | 647040 | 0 | 7680 | 518916 | 80304 | 27876 | 378240 | 286080 | 18820 | 5229925 | 381380 | 402720 | 15709090.91 | 53527 | 0 | 120960 | 40806 | 868145 | 5210189 | 0 | 0 | 0 | 13434544 | 97470 | 1237608 | 1224436 | 0 | 8234500 | 8556100 | 7664000 | 736320 | 0 | 834192 | 810240 | 2437673 | 1775520 | 0 | 411770 | 33060 | 1481280 | 18998 | 316773 | 229968 | 7606500 | 0 | 8207000 | 0 | 0 | 3614973 | 142752 | 0 | 1902720 | 214560 | 0 | 0 | 3331650 | 214200 | 1006800 | 859200 | 2872320 | 3150 | 118090 | 50160 | 155191084.27 | 21465455 | 9382752 | 0 | 58560 | 16512 | 912000 | 0 | 0 | 0 | 0 | 0 | 473760 | 24610910 | 0 | 16400880 | 0 | 215999 | 0 | 59136 | 112320 | 0 | 596048 | 121572 | 13939 | 119048 | 216741 | 142179 | 0 | 136496 | 4353273 | 0 | 0 | 0 | 0 | 0 | 8750036 | 0 | 11040 | 0 | 0 | 576023 | 62272 | 868147 | 0 | 0 | 0 | 19212.6 | 274320 | 3262 | 25728 | 0 | 2640000 | 5361880 | 0 | 8477044 | 25751272.73 | 85200 | 132313017.33 | 287504101.6