## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-01-22 | Tuesday
|  | Date (day): | 2019-01-22 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10222 | MW |  |  | (b) At Evening Peak Hour : |  | 11669 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-01-21 | 2019-01-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 263 | 263 | 263 |  |  | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 240 | 240 | 240 |  | 365 | Under maint.
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 35 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 108 | 0 | 0 | 0 |  |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 374 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 13 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 365 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 430 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 7 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 80 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 50 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 98 | 0 | 0 | 0 |  |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 180 | 226 | 120 | 225
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 64 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 47 | 37 | 47 | 47
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 38 | 38 | 46 | 46 |  | 62 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 50 | 50 | 50 |  | 30 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 8 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 34 | 42 | 43 | 43 |  | 9 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 105 | 300 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 70 | 89 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2181 | 2681 | 3983 | 4288 | 338 | 706
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 26 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 12.43 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 40 | 46 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 39 | 70 | 105 |  | 125 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  |  | Under S/D
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 51 | 51 | 51
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 64 | 70 | 70
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 85 | 85
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 58 | 74 | 68 | 68 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 50 | 50 | 90 | 90 |  | 10 | Engine problem
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 30 | 15 | 20
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 87 | 93 | 80 | 93 |  | 15 | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 501.43 | 683 | 766 | 799 | 240 | 372
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 150 | 150
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 188 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | S/D from (06/01/19 to 21/01/2019)
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 272 | 0 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 36 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 16 | 182 | 182 | 13 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 45 | 51 | 51
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 10 | 85 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 40 | 108 | 150 | 180
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 80 | 108 | 91 | 116
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 11 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 20 | 23 | 23
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1117 | 1339 | 1606 | 2171 | 111 | 365
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 136 | 111 | 115 | 120
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 87 | 86 | 95 | 95
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.1 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 70 | 150 | 100 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 316.1 | 369 | 334 | 437 | 0 | 0
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 57 | 57
79 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 62 | 61 | 62 | 62
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 25 | 163 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 50 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 44 | 44
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 61 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 84 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 49 | 48 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 135 | 0 | 0 | 0 |  |  | Under Maint.
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 20 | 15 | 20 | 20
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 23 | 23 | 23 | 25 |  | 27 | Engine problem
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 25 | 25 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 320 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 821 | 951 | 1009 | 1011 | 0 | 357
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 538 | 684 | 545 | 693
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 115 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 43
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 72 | 20 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 380 | 410 | 410
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 1092 | 1440 | 1335 | 1632 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 9 | 14 | 20 | 26 |  | 7 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 190 | 188 | 194 | 194
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 294 | 347 | 419 | 455 | 0 | 7
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Gas shortage.
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 42 | 0 | 42
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 40 | 50 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 177 | 194 | 230 | 230
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Gas shortage.
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 26 | 40
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 13 | 15 | 15
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 51 | 52 | 52
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 102 | 100 | 100
| Paramount Baghabari |  | HSD | IPP | 200 MW | 0 | 0 | 0 | 2 | 0 | 0 |  |  | on test
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 350 | 614 | 586 | 692 | 353 | 110
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 293 | 149 | 149 | 125 |  | Coal shortage
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 17 | 16 | 17 | 17
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 19 | 15 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 211 | 324 | 184 | 184 | 125 | 170
| Total |  |  |  |  | 17685 | 17142 | 6883.53 | 8748 | 10222 | 11669 | 1167 | 2087
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6511.341 | 8275 | 9669.3016 | 11038.063
A. |  | 2019-01-21 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 8748 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5363 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8748 | MW
3 | Day peak Generation : |  |  | 6883.53 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8275 | MW
4 | Evening peak Generation : |  |  | 8748 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 163.7874 | MKWHr | By Solar | 0.14193 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 118.632 | MKWHr |  | By Oil: | 25.4488 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 5.0996 | MKWHr |  | By Hydro: | 0.861 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1167 | MW | Dhaka | 2969 | 2969 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2087 | MW | Chittagong | 878 | 878 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3254 | MW | Khulna | 1013 | 1013 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 966.14 | MMCFD |  |  | Rajshahi | 956 | 956 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 82995158.22 | ii) Oil : | Taka | 181451430.66 | Comilla | 695 | 695 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19684456 | Total | Taka | 284131044.88 | Mymensingh | 673 | 673 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.178 | MKWHr. | Sylhet | 320 | 320 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -250 | MW (E to W) at | 19:00 | hrs | Barisal | 220 | 220 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -540 | MW at | 7:00 | hrs | Rangpur | 551 | 551 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.4° C |  |  | Total | 8275 | 8275 |  | 0
B. |  | 2019-01-22 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 27.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11669 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7000 | MW
4 | Reserve(Generation end) |  |  |  | 2869 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 164.761 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5282 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.5891 | MKWHr. | ii) HVDC Flow at Peak Time |  | 684 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.015 | MKWHr. | iii) Maximum HVDC Flow : |  | 685 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.09 |  | (b) Today: | 96.99 |  | (c) Rule Curve: |  | 99
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-01-21
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 361 | 368 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 230 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 25 | 0 | 39 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 19 | 22 | 40 | 0 | 150 | 135 | 0 | 276 | 185 | 16 | 101 | 33 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 11 | 24 | 22 | 78 | 152 | 28 | 22 | 0 | 30 | 62 | 51 | 50 | 70 | 0 | 62 | 40 | 49 | 98 | 20 | 23 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 50 | 85 | 0 | 0 |  | 259 | 0 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 166 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 183 | 0 | 0 | 21 | 0 |  | 4484 | 1434 | 5918 | 3231 | 259 | 1786 | 376 | 149 | 39 | 0 | 78 | 0 | 0 | 97.1
2:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 362 | 341 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 230 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 38 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 150 | 135 | 0 | 276 | 193 | 16 | 102 | 33 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 8 | 24 | 22 | 74 | 150 | 7 | 22 | 0 | 28 | 62 | 51 | 50 | 109 | 0 | 65 | 40 | 49 | 80 | 20 | 23 | 0 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 0 | 0 | 0 |  | 259 | 0 | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 190 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 181 | 0 | 0 | 0 | 0 |  | 4268 | 1350 | 5618 | 3245 | 259 | 1743 | 110 | 149 | 38 | 0 | 74 | 0 | 0 | 97.1
3:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 350 | 340 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 230 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 38 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 150 | 135 | 0 | 276 | 185 | 16 | 95 | 33 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 8 | 24 | 22 | 74 | 153 | 0 | 22 | 0 | 28 | 62 | 51 | 50 | 109 | 0 | 55 | 40 | 49 | 80 | 20 | 23 | 0 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 0 | 0 | 0 |  | 259 | 0 | 448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 176 | 0 | 0 | 0 | 0 |  | 4171 | 1330 | 5501 | 3177 | 259 | 1743 | 61 | 149 | 38 | 0 | 74 | 0 | 0 | 97.1
4:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 350 | 320 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 230 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 38 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 150 | 135 | 0 | 287 | 194 | 16 | 100 | 33 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 8 | 25 | 22 | 70 | 153 | 0 | 22 | 0 | 30 | 62 | 51 | 50 | 10 | 0 | 56 | 40 | 49 | 80 | 20 | 23 | 0 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 0 | 0 | 0 |  | 259 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 179 | 0 | 0 | 0 | 0 |  | 4077 | 1291 | 5368 | 3164 | 259 | 1627 | 61 | 149 | 38 | 0 | 70 | 0 | 0 | 97.09
5:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 350 | 320 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 230 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 38 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 150 | 135 | 0 | 276 | 198 | 16 | 102 | 33 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 8 | 24 | 22 | 72 | 152 | 0 | 22 | 0 | 27 | 62 | 51 | 50 | 10 | 0 | 56 | 40 | 49 | 80 | 20 | 23 | 0 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 0 | 0 | 0 |  | 252 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 179 | 0 | 0 | 0 | 0 |  | 4080 | 1283 | 5363 | 3155 | 252 | 1636 | 61 | 149 | 38 | 0 | 72 | 0 | 0 | 97.09
6:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 375 | 367 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 225 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 6 | 0 | 38 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 150 | 135 | 0 | 276 | 207 | 16 | 100 | 33 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 8 | 24 | 22 | 74 | 166 | 6 | 22 | 0 | 28 | 62 | 51 | 50 | 20 | 0 | 69 | 40 | 49 | 118 | 20 | 23 | 0 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 40 | 0 | 0 | 0 |  | 248 | 0 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 190 | 0 | 0 | 0 | 0 |  | 4316 | 1370 | 5686 | 3309 | 248 | 1748 | 120 | 149 | 38 | 0 | 74 | 0 | 0 | 97.09
7:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 390 | 367 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 225 | 0 | 72 | 0 | 0 | 4 | 0 | 0 | 38 | 0 | 0 | 54 | 18 | 0 | 19 | 25 | 25 | 33 | 33 | 34 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 20 | 0 | 12 | 22 | 36 | 0 | 150 | 135 | 0 | 272 | 206 | 16 | 100 | 33 | 5 | 5 | 45 | 10 | 0 | 0 | 16 | 8 | 25 | 22 | 70 | 166 | 30 | 22 | 0 | 29 | 62 | 51 | 50 | 20 | 0 | 69 | 40 | 49 | 120 | 20 | 23 | 0 | 330 | 24 | 3 | 0 | 0 | 0 | 0 | 7 | 0 | 26 | 1 | 50 | 32 | 0 | 0 |  | 247 | 0 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 171 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 193 | 0 | 0 | 70 | 0 |  | 4622 | 1515 | 6137 | 3296 | 247 | 1783 | 551 | 149 | 40 | 0 | 70 | 1 | 0 | 99.08
8:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 380 | 320 | 18 | 0 | 450 | 0 | 3 | 2 | 15 | 230 | 0 | 70 | 0 | 0 | 24 | 0 | 0 | 38 | 0 | 18 | 54 | 54 | 0 | 19 | 25 | 25 | 33 | 33 | 34 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 55 | 57 | 36 | 22 | 21 | 0 | 150 | 135 | 0 | 253 | 184 | 16 | 100 | 30 | 5 | 5 | 35 | 30 | 0 | 0 | 16 | 8 | 25 | 22 | 76 | 136 | 50 | 22 | 0 | 30 | 62 | 51 | 47 | 20 | 0 | 40 | 10 | 48 | 118 | 20 | 23 | 0 | 290 | 24 | 8 | 0 | 5 | 0 | 0 | 12 | 0 | 47 | 5.4 | 50 | 52 | 0 | 0 |  | 539 | 0 | 390 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 0 | 0 | 95 | 0 | 194 | 0 | 0 | 105 | 0 |  | 4699.4 | 1913 | 6612.4 | 3154 | 539 | 1655 | 975 | 149 | 40 | 19 | 76 | 5.4 | 0 | 99.08
9:00 | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 345 | 320 | 13 | 0 | 450 | 0 | 50 | 15 | 30 | 180 | 0 | 98 | 0 | 0 | 24 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 25 | 33 | 33 | 34 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 58 | 87 | 40 | 22 | 7 | 0 | 150 | 135 | 0 | 250 | 184 | 16 | 100 | 33 | 5 | 5 | 35 | 10 | 0 | 0 | 16 | 11 | 25 | 22 | 80 | 136 | 87 | 22 | 1.1 | 30 | 62 | 51 | 47 | 25 | 0 | 50 | 10 | 49 | 135 | 20 | 23 | 0 | 285 | 23 | 11 | 0 | 45 | 0 | 0 | 70 | 0 | 70 | 12.43 | 50 | 40 | 0 | 0 |  | 538 | 0 | 360 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 175 | 17 | 19 | 0 | 0 | 0 | 0 | 95 | 0 | 177 | 0 | 0 | 105 | 0 |  | 4936.53 | 1947 | 6883.53 | 3082 | 538 | 1621 | 1298 | 175 | 40 | 36 | 80 | 13.53 | 0 | 0
10:00 | 35 | 0 | 0 | 0 | 0 | 42 | 20 | 350 | 321 | 0 | 0 | 450 | 0 | 15 | 15 | 30 | 180 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 38 | 0 | 47 | 54 | 56 | 0 | 19 | 25 | 25 | 33 | 33 | 34 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 47 | 40 | 22 | 4 | 0 | 150 | 135 | 0 | 257 | 203 | 16 | 100 | 36 | 5 | 5 | 40 | 10 | 0 | 0 | 19 | 11 | 25 | 22 | 84 | 124 | 87 | 22 | 1 | 30 | 62 | 45 | 50 | 100 | 0 | 52 | 10 | 48 | 0 | 20 | 23 | 10 | 290 | 24 | 11 | 0 | 28 | 0 | 0 | 70 | 0 | 70 | 16 | 50 | 18 | 0 | 0 |  | 536 | 0 | 360 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 52 | 0 | 22 | 15 | 3 | 0 | 0 | 230 | 17 | 19 | 0 | 0 | 0 | 0 | 66 | 0 | 182 | 0 | 0 | 105 | 10 |  | 4686 | 1995 | 6681 | 2980 | 536 | 1601 | 1157 | 230 | 40 | 36 | 84 | 17 | 0 | 0
11:00 | 35 | 0 | 0 | 0 | 40 | 12 | 0 | 355 | 323 | 0 | 0 | 450 | 0 | 7 | 30 | 30 | 180 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 38 | 0 | 47 | 54 | 56 | 0 | 19 | 25 | 25 | 33 | 0 | 34 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 44 | 47 | 41 | 22 | 4 | 0 | 150 | 135 | 0 | 268 | 198 | 16 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 11 | 25 | 22 | 86 | 123 | 87 | 22 | 2 | 30 | 62 | 48 | 50 | 100 | 0 | 40 | 10 | 48 | 0 | 20 | 23 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 70 | 0 | 70 | 19.42 | 50 | 17 | 0 | 0 |  | 537 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 188 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 52 | 0 | 22 | 15 | 5 | 0 | 0 | 278 | 17 | 18 | 0 | 0 | 0 | 0 | 65 | 0 | 187 | 0 | 0 | 105 | 46 |  | 4665.42 | 2068 | 6733.42 | 2990 | 537 | 1572 | 1174 | 278 | 40 | 35 | 86 | 21.42 | 0 | 0
12:00 | 35 | 0 | 0 | 0 | 40 | 12 | 0 | 365 | 340 | 0 | 0 | 450 | 0 | 7 | 15 | 30 | 180 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 24 | 33 | 0 | 34 | 0 | 39 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 40 | 42 | 22 | 5 | 0 | 150 | 135 | 0 | 272 | 224 | 16 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 11 | 25 | 22 | 88 | 121 | 86 | 22 | 2 | 30 | 62 | 48 | 50 | 130 | 0 | 64 | 10 | 48 | 0 | 19 | 23 | 10 | 305 | 24 | 11 | 0 | 15 | 0 | 0 | 32 | 0 | 70 | 20 | 50 | 17 | 0 | 0 |  | 537 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 188 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 52 | 0 | 22 | 15 | 5 | 0 | 0 | 296 | 17 | 18 | 0 | 0 | 0 | 0 | 66 | 0 | 190 | 0 | 0 | 105 | 45 |  | 4725 | 2048 | 6773 | 3053 | 537 | 1627 | 1076 | 296 | 39 | 35 | 88 | 22 | 0 | 0
13:00 | 35 | 0 | 0 | 0 | 50 | 12 | 0 | 375 | 356 | 0 | 0 | 450 | 0 | 7 | 15 | 30 | 235 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 24 | 33 | 0 | 34 | 0 | 39 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 46 | 40 | 22 | 11 | 0 | 150 | 135 | 0 | 272 | 190 | 16 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 11 | 25 | 20 | 90 | 111 | 87 | 22 | 2 | 30 | 62 | 51 | 50 | 163 | 0 | 63 | 10 | 48 | 0 | 15 | 23 | 10 | 310 | 24 | 11 | 0 | 15 | 0 | 0 | 32 | 0 | 70 | 20 | 50 | 17 | 0 | 0 |  | 537 | 0 | 423 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 187 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 3 | 0 | 0 | 296 | 17 | 18 | 0 | 0 | 0 | 0 | 65 | 0 | 199 | 0 | 0 | 105 | 48 |  | 4819 | 2119 | 6938 | 3146 | 537 | 1689 | 1084 | 296 | 39 | 35 | 90 | 22 | 0 | 0
14:00 | 35 | 0 | 0 | 0 | 90 | 0 | 0 | 350 | 308 | 0 | 0 | 450 | 0 | 7 | 15 | 30 | 215 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 21 | 33 | 0 | 34 | 0 | 39 | 0 | 120 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 46 | 46 | 22 | 7 | 0 | 150 | 135 | 0 | 272 | 186 | 16 | 100 | 36 | 0 | 5 | 45 | 10 | 0 | 0 | 19 | 11 | 25 | 20 | 88 | 110 | 87 | 22 | 1.7 | 30 | 61 | 51 | 50 | 100 | 0 | 58 | 10 | 48 | 0 | 15 | 23 | 10 | 280 | 24 | 11 | 0 | 12 | 0 | 0 | 32 | 0 | 36 | 15.9 | 50 | 17 | 0 | 0 |  | 537 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 187 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 3 | 0 | 0 | 292 | 17 | 18 | 0 | 0 | 0 | 0 | 65 | 0 | 206 | 0 | 0 | 105 | 44 |  | 4511.6 | 2025 | 6536.6 | 2941 | 537 | 1527 | 1060 | 292 | 39 | 35 | 88 | 17.6 | 0 | 0
15:00 | 35 | 90 | 0 | 0 | 135 | 0 | 0 | 360 | 336 | 0 | 0 | 450 | 0 | 7 | 15 | 30 | 218 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 0 | 16 | 25 | 24 | 33 | 0 | 34 | 0 | 39 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 46 | 46 | 22 | 5 | 0 | 150 | 135 | 0 | 272 | 202 | 16 | 100 | 36 | 0 | 5 | 45 | 10 | 0 | 0 | 19 | 11 | 25 | 18 | 88 | 109 | 86 | 22 | 1.1 | 30 | 62 | 50 | 50 | 100 | 0 | 63 | 10 | 48 | 0 | 15 | 22 | 10 | 300 | 23 | 8 | 0 | 12 | 0 | 0 | 32 | 0 | 31 | 12.1 | 50 | 17 | 0 | 0 |  | 536 | 0 | 330 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 40 | 186 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 3 | 0 | 0 | 293 | 16 | 18 | 0 | 0 | 0 | 0 | 65 | 0 | 187 | 0 | 0 | 70 | 36 |  | 4707.2 | 1952 | 6659.2 | 3084 | 536 | 1570 | 1002 | 293 | 39 | 34 | 88 | 13.2 | 0 | 0
16:00 | 35 | 250 | 0 | 0 | 195 | 0 | 0 | 350 | 336 | 0 | 0 | 450 | 0 | 7 | 15 | 30 | 190 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 25 | 33 | 0 | 36 | 0 | 37 | 0 | 120 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 46 | 47 | 22 | 7 | 0 | 150 | 135 | 0 | 272 | 186 | 16 | 100 | 36 | 5 | 5 | 45 | 10 | 0 | 0 | 19 | 11 | 25 | 20 | 88 | 110 | 86 | 22 | 0.5 | 30 | 62 | 50 | 50 | 100 | 0 | 58 | 10 | 48 | 0 | 15 | 22 | 10 | 300 | 23 | 8 | 0 | 15 | 0 | 0 | 32 | 0 | 30 | 6.7 | 50 | 17 | 0 | 0 |  | 537 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 3 | 0 | 0 | 293 | 16 | 18 | 0 | 0 | 0 | 0 | 67 | 0 | 180 | 0 | 0 | 70 | 0 |  | 4880.2 | 1910 | 6790.2 | 3242 | 537 | 1579 | 964 | 293 | 37 | 43 | 88 | 7.2 | 0 | 0
17:00 | 35 | 263 | 0 | 0 | 230 | 0 | 0 | 354 | 311 | 0 | 0 | 370 | 0 | 9 | 15 | 30 | 150 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 38 | 0 | 18 | 54 | 55 | 17 | 0 | 25 | 25 | 33 | 0 | 41 | 0 | 39 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 68 | 60 | 47 | 22 | 14 | 0 | 150 | 135 | 0 | 272 | 186 | 16 | 95 | 36 | 5 | 5 | 45 | 10 | 0 | 2 | 19 | 11 | 25 | 20 | 88 | 111 | 86 | 22 | 0 | 28 | 61 | 50 | 50 | 100 | 0 | 43 | 10 | 48 | 0 | 15 | 23 | 10 | 280 | 23 | 8 | 0 | 12 | 0 | 0 | 32 | 0 | 30 | 1.1 | 50 | 17 | 0 | 0 |  | 627 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 38 | 25 | 40 | 185 | 12 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 0 | 0 | 0 | 293 | 16 | 18 | 0 | 0 | 0 | 0 | 66 | 0 | 183 | 0 | 0 | 70 | 11 |  | 4763.1 | 2076 | 6839.1 | 3215 | 627 | 1461 | 1008 | 293 | 39 | 107 | 88 | 1.1 | 0 | 0
18:00 | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 350 | 331 | 0 | 0 | 350 | 0 | 7 | 30 | 30 | 150 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 38 | 0 | 32 | 54 | 56 | 17 | 19 | 25 | 25 | 33 | 0 | 42 | 0 | 39 | 0 | 120 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 51 | 62 | 68 | 68 | 93 | 46 | 22 | 16 | 0 | 150 | 135 | 0 | 272 | 190 | 16 | 95 | 36 | 5 | 5 | 45 | 85 | 8 | 11 | 19 | 11 | 25 | 20 | 106 | 111 | 86 | 22 | 0 | 30 | 62 | 51 | 50 | 100 | 0 | 63 | 84 | 48 | 0 | 15 | 23 | 10 | 270 | 23 | 10 | 0 | 35 | 0 | 0 | 100 | 0 | 33 | 0 | 50 | 56 | 0 | 0 |  | 684 | 0 | 300 | 0 | 105 | 0 | 0 | 0 | 44 | 78 | 40 | 187 | 12 | 48 | 0 | 0 | 0 | 50 | 42 | 102 | 40 | 24 | 0 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 292 | 16 | 18 | 0 | 0 | 0 | 0 | 96 | 0 | 179 | 0 | 0 | 105 | 21 |  | 5360 | 2618 | 7978 | 3248 | 684 | 1633 | 1452 | 292 | 39 | 524 | 106 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2
19:00 | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 374 | 365 | 0 | 0 | 430 | 0 | 7 | 80 | 50 | 226 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 38 | 0 | 37 | 54 | 55 | 17 | 19 | 25 | 25 | 33 | 8 | 42 | 0 | 39 | 0 | 120 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 51 | 64 | 68 | 74 | 93 | 46 | 22 | 30 | 0 | 150 | 135 | 0 | 272 | 188 | 16 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 11 | 19 | 11 | 25 | 20 | 108 | 111 | 86 | 22 | 0 | 30 | 61 | 50 | 50 | 163 | 0 | 61 | 84 | 48 | 0 | 15 | 23 | 10 | 320 | 25 | 11 | 0 | 105 | 0 | 0 | 150 | 0 | 89 | 0 | 50 | 108 | 0 | 0 |  | 684 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 44 | 72 | 40 | 188 | 14 | 48 | 0 | 0 | 0 | 50 | 42 | 102 | 40 | 50 | 0 | 51 | 37 | 22 | 13 | 11 | 0 | 0 | 293 | 16 | 15 | 0 | 0 | 0 | 0 | 97 | 0 | 194 | 0 | 0 | 105 | 2 |  | 6023 | 2725 | 8748 | 3455 | 684 | 1875 | 1784 | 293 | 39 | 510 | 108 | 0 | 0 | 97.2
19:30 | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 375 | 361 | 0 | 0 | 430 | 0 | 7 | 80 | 50 | 226 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 17 | 19 | 25 | 25 | 33 | 8 | 42 | 0 | 39 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 64 | 68 | 74 | 93 | 39 | 22 | 34 | 0 | 150 | 135 | 0 | 272 | 204 | 16 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 16 | 19 | 11 | 25 | 20 | 110 | 111 | 86 | 22 | 0 | 30 | 62 | 48 | 50 | 163 | 0 | 66 | 84 | 48 | 0 | 15 | 23 | 10 | 335 | 25 | 11 | 0 | 102 | 0 | 0 | 150 | 0 | 96 | 0 | 50 | 108 | 0 | 0 |  | 684 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 44 | 66 | 40 | 188 | 14 | 48 | 0 | 0 | 0 | 50 | 41 | 102 | 40 | 50 | 0 | 51 | 36 | 22 | 13 | 11 | 0 | 0 | 253 | 16 | 16 | 0 | 0 | 0 | 0 | 96 | 0 | 185 | 0 | 0 | 105 | 2 |  | 6071 | 2668 | 8739 | 3469 | 684 | 1887 | 1794 | 253 | 39 | 503 | 110 | 0 | 0 | 97.2
20:00 | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 360 | 363 | 0 | 0 | 430 | 0 | 7 | 80 | 55 | 226 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 38 | 0 | 47 | 54 | 56 | 17 | 0 | 25 | 25 | 33 | 8 | 42 | 0 | 39 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 64 | 68 | 74 | 93 | 39 | 22 | 36 | 0 | 150 | 135 | 0 | 272 | 193 | 16 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 16 | 19 | 11 | 25 | 22 | 108 | 110 | 87 | 22 | 0 | 29 | 62 | 48 | 50 | 163 | 0 | 60 | 84 | 48 | 0 | 15 | 23 | 10 | 320 | 25 | 11 | 0 | 103 | 0 | 0 | 150 | 0 | 96 | 0 | 50 | 107 | 0 | 0 |  | 684 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 44 | 60 | 40 | 188 | 14 | 48 | 0 | 0 | 0 | 50 | 41 | 102 | 40 | 50 | 0 | 51 | 36 | 22 | 13 | 11 | 0 | 0 | 217 | 17 | 16 | 0 | 0 | 0 | 0 | 96 | 0 | 188 | 0 | 0 | 105 | 2 |  | 6015 | 2630 | 8645 | 3421 | 684 | 1876 | 1802 | 217 | 39 | 498 | 108 | 0 | 0 | 97.2
21:00 | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 355 | 330 | 0 | 0 | 400 | 0 | 7 | 80 | 55 | 226 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 17 | 0 | 25 | 25 | 33 | 16 | 42 | 0 | 39 | 0 | 120 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 68 | 74 | 93 | 39 | 22 | 36 | 0 | 150 | 135 | 0 | 272 | 205 | 16 | 101 | 36 | 5 | 5 | 45 | 85 | 0 | 16 | 19 | 11 | 25 | 20 | 104 | 110 | 86 | 22 | 0 | 28 | 62 | 51 | 50 | 130 | 0 | 66 | 84 | 48 | 0 | 15 | 23 | 10 | 300 | 25 | 11 | 0 | 103 | 0 | 0 | 150 | 0 | 96 | 0 | 50 | 107 | 0 | 0 |  | 684 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 44 | 30 | 40 | 189 | 14 | 48 | 0 | 0 | 0 | 0 | 13 | 102 | 40 | 50 | 0 | 51 | 29 | 22 | 13 | 11 | 0 | 0 | 150 | 17 | 17 | 0 | 0 | 0 | 0 | 95 | 0 | 183 | 0 | 0 | 105 | 2 |  | 5852 | 2444 | 8296 | 3436 | 684 | 1762 | 1801 | 150 | 39 | 320 | 104 | 0 | 0 | 97.2
22:00 | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 350 | 332 | 0 | 0 | 400 | 0 | 0 | 0 | 55 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 54 | 55 | 0 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 74 | 66 | 41 | 22 | 40 | 0 | 150 | 135 | 0 | 272 | 187 | 16 | 95 | 33 | 5 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 25 | 20 | 96 | 109 | 87 | 22 | 0 | 28 | 62 | 51 | 50 | 130 | 0 | 63 | 84 | 48 | 0 | 15 | 23 | 10 | 305 | 25 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 39 | 0 | 50 | 107 | 0 | 0 |  | 684 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 44 | 0 | 40 | 176 | 13 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 0 | 0 | 51 | 29 | 22 | 13 | 11 | 0 | 0 | 150 | 17 | 18 | 0 | 0 | 0 | 0 | 95 | 0 | 184 | 0 | 0 | 105 | 0 |  | 5421 | 2337 | 7758 | 3428 | 684 | 1772 | 1378 | 150 | 40 | 210 | 96 | 0 | 0 | 99.03
23:00 | 35 | 262 | 0 | 0 | 240 | 0 | 0 | 350 | 310 | 0 | 0 | 350 | 0 | 0 | 0 | 15 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 47 | 54 | 56 | 0 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 38 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 39 | 22 | 42 | 0 | 150 | 135 | 0 | 272 | 186 | 16 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 25 | 20 | 88 | 112 | 87 | 22 | 0 | 30 | 62 | 51 | 50 | 130 | 0 | 64 | 84 | 49 | 0 | 15 | 23 | 10 | 270 | 25 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 50 | 50 | 0 | 0 |  | 685 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 51 | 29 | 22 | 13 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 180 | 0 | 0 | 105 | 0 |  | 5019 | 1986 | 7005 | 3382 | 685 | 1671 | 920 | 149 | 38 | 72 | 88 | 0 | 0 | 99.03
24:00 | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 350 | 312 | 0 | 0 | 350 | 0 | 0 | 0 | 15 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 47 | 54 | 56 | 0 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 38 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 40 | 22 | 40 | 0 | 150 | 135 | 0 | 272 | 187 | 16 | 95 | 36 | 5 | 5 | 32 | 85 | 0 | 0 | 19 | 11 | 25 | 22 | 78 | 113 | 87 | 22 | 0 | 30 | 62 | 51 | 50 | 130 | 0 | 62 | 84 | 49 | 0 | 15 | 23 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 35 | 0 | 0 |  | 247 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 188 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 29 | 22 | 13 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 181 | 0 | 0 | 105 | 0 |  | 4893 | 1531 | 6424 | 3383 | 247 | 1674 | 826 | 149 | 38 | 29 | 78 | 0 | 0 | 99.02
KWH | 696000 | 2381700 | 0 | 0 | 2257463 | 1093545 | 390432 | 8779890 | 8006000 | 31000 | 0 | 9952500 | 0 | 187200 | 495288 | 582204 | 5156602 | 0 | 1170000 | 0 | 0 | 359712 | 0 | 0 | 635520 | 0 | 746640 | 993600 | 916896 | 89000 | 392256 | 600000 | 569520 | 813100 | 444000 | 738516 | 0 | 861000 | 0 | 2900000 | 0 | 460260 | 0 | 0 | 0 | 0 | 0 | 1042080 | 194008 | 262320 | 902640 | 1022400 | 760320 | 531504 | 596160 | 0 | 3532519 | 3245832 | 0 | 6557000 | 4705000 | 418182 | 2364910 | 769032 | 123360 | 120000 | 980415 | 768184 | 6704 | 72677 | 438264 | 239040 | 596300 | 526810 | 2015040 | 2994840 | 1513920 | 526824 | 11250 | 692000 | 1475000 | 1201200 | 1194000 | 2383510 | 0 | 1475000 | 1031040 | 1140840 | 848420 | 421000 | 546980 | 175320 | 7745750 | 578688 | 247632 | 0 | 617240 | 0 | 0 | 1521600 | 0 | 961920 | 130680 | 1104000 | 1049280 | 0 | 0 |  | 11589091 | 0 | 9488160 | 0 | 873600 | 0 | 0 | 0 | 238560 | 246272 | 778125 | 4521873 | 278609 | 237120 | 0 | 0 | 0 | 165704 | 159388 | 571856 | 673820 | 381498 | 0 | 979200 | 241882 | 510240 | 333144 | 143460 | 0 | 0 | 5099600 | 239000 | 277000 | 0 | 0 | 0 | 0 | 1907905 | 0 | 4655000 | 0 | 0 | 1847040 | 271818 |  | 117078479 | 46708965 | 163787444 | 77734639 | 11589091 | 40897316 | 22846134 | 5099600 | 861000 | 2602694 | 2015040 | 141930 | 0
Fuel Cost | 598560 | 2048262 | 0 | 0 | 1444776.32 | 885771.45 | 367006.08 | 5355732.9 | 4883660 | 297910 | 0 | 6668175 | 0 | 1175616 | 3308523.84 | 3557266.44 | 3351791.3 | 0 | 1298700 | 0 | 0 | 2370502.08 | 0 | 0 | 3806764.8 | 0 | 4980088.8 | 7084368 | 5730600 | 558030 | 294192 | 450000 | 0 | 0 | 0 | 6986361.36 | 0 | 0 | 0 | 3190000 | 0 | 4358662.2 | 0 | 0 | 0 | 0 | 0 | 9159883.2 | 2089466.16 | 2552373.6 | 5587341.6 | 6604704 | 4972492.8 | 451778.4 | 0 | 0 | 3214592.29 | 2953707.12 | 0 | 4524330 | 3293500 | 288545.58 | 2270313.6 | 515251.44 | 106089.6 | 110400 | 803940.3 | 729774.8 | 72671.36 | 539263.34 | 337463.28 | 179280 | 459151 | 395107.5 | 13782873.6 | 2246130 | 13912924.8 | 405654.48 | 0 | 719680 | 1534000 | 1153152 | 1074600 | 1859137.8 | 0 | 1681500 | 1103212.8 | 1254924 | 967198.8 | 538880 | 508691.4 | 163047.6 | 4957280 | 434016 | 188200.32 | 0 | 4481162.4 | 0 | 0 | 10879440 | 0 | 0 | 0 | 0 | 9800275.2 | 0 | 0 |  | 59104364.1 | 0 | 6357067.2 | 0 | 7242144 | 0 | 0 | 0 | 2686185.6 | 2901084.16 | 6131625 | 3120092.37 | 275822.91 | 1754688 | 0 | 0 | 0 | 1897310.8 | 1708639.36 | 5123829.76 | 5828543 | 3395332.2 | 0 | 9713664 | 2846951.14 | 561264 | 313155.36 | 108599.22 | 0 | 0 | 19684456 | 7702970 | 7415290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236481.66 |  | 200908722.74 | 156109559.84 | 357018282.58 | 54927507.54 | 59104364.1 | 28067650.68 | 144454658.72 | 19684456 | 0 | 36996771.94 | 13782873.6 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 0 | 108 | 35 | 345 | 320 | 13 | 0 | 450 | 0 | 50 | 15 | 30 | 180 | 0 | 98 | 0 | 0 | 24 | 0 | 0 | 38 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 25 | 33 | 33 | 34 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 58 | 87 | 40 | 22 | 7 | 0 | 150 | 135 | 0 | 250 | 184 | 16 | 100 | 33 | 5 | 5 | 35 | 10 | 0 | 0 | 16 | 11 | 25 | 22 | 80 | 136 | 87 | 22 | 1.1 | 30 | 62 | 51 | 47 | 25 | 0 | 50 | 10 | 49 | 135 | 20 | 23 | 0 | 285 | 23 | 11 | 0 | 45 | 0 | 0 | 70 | 0 | 70 | 12.43 | 50 | 40 | 0 | 0 |  | 538 | 0 | 360 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 52 | 0 | 22 | 14 | 5 | 0 | 0 | 175 | 17 | 19 | 0 | 0 | 0 | 0 | 95 | 0 | 177 | 0 | 0 | 105 | 0 |  | 6883.53 | DayPeak
Yesterday Evening Peak | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 374 | 365 | 0 | 0 | 430 | 0 | 7 | 80 | 50 | 226 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 38 | 0 | 37 | 54 | 55 | 17 | 19 | 25 | 25 | 33 | 8 | 42 | 0 | 39 | 0 | 120 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 51 | 64 | 68 | 74 | 93 | 46 | 22 | 30 | 0 | 150 | 135 | 0 | 272 | 188 | 16 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 11 | 19 | 11 | 25 | 20 | 108 | 111 | 86 | 22 | 0 | 30 | 61 | 50 | 50 | 163 | 0 | 61 | 84 | 48 | 0 | 15 | 23 | 10 | 320 | 25 | 11 | 0 | 105 | 0 | 0 | 150 | 0 | 89 | 0 | 50 | 108 | 0 | 0 |  | 684 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 44 | 72 | 40 | 188 | 14 | 48 | 0 | 0 | 0 | 50 | 42 | 102 | 40 | 50 | 0 | 51 | 37 | 22 | 13 | 11 | 0 | 0 | 293 | 16 | 15 | 0 | 0 | 0 | 0 | 97 | 0 | 194 | 0 | 0 | 105 | 2 |  | 8748 | EvPeak
Forecast for Evening | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 225 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 46 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 75 | 30 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 70 | 85 | 68 | 93 | 50 | 22 | 20 | 0 | 150 | 135 | 0 | 360 | 221 | 182 | 100 | 40 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 11 | 33 | 23 | 116 | 120 | 95 | 22 | 0 | 57 | 62 | 51 | 44 | 163 | 0 | 66 | 86 | 50 | 0 | 20 | 25 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 180 | 150 | 0 |  | 693 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 43 | 80 | 40 | 194 | 26 | 110 | 30 | 0 | 0 | 50 | 42 | 100 | 40 | 50 | 40 | 52 | 40 | 22 | 15 | 11 | 0 | 0 | 149 | 17 | 18 | 0 | 0 | 0 | 0 | 95 | 100 | 230 | 0 | 0 | 105 | 0
Forecast for Day | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 120 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 46 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 43 | 0 | 40 | 30 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 70 | 85 | 68 | 80 | 50 | 22 | 15 | 0 | 150 | 135 | 0 | 0 | 221 | 182 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 23 | 91 | 115 | 95 | 22 | 2 | 57 | 62 | 51 | 44 | 163 | 0 | 66 | 86 | 50 | 0 | 20 | 23 | 10 | 341 | 25 | 11 | 100 | 300 | 300 | 0 | 100 | 0 | 149 | 20 | 90 | 150 | 150 | 0 |  | 545 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 20 | 40 | 194 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 50 | 40 | 52 | 26 | 22 | 15 | 11 | 0 | 0 | 149 | 17 | 18 | 0 | 0 | 0 | 0 | 95 | 100 | 230 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 263 | 0 | 0 | 240 | 0 | 0 | 375 | 373 | 0 | 0 | 400 | 0 | 0 | 0 | 41 | 120 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 38 | 0 | 47 | 55 | 54 | 0 | 0 | 25 | 25 | 33 | 33 | 43 | 0 | 37 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 48 | 46 | 68 | 70 | 40 | 22 | 20 | 0 | 150 | 135 | 0 | 0 | 184 | 16 | 95 | 36 | 5 | 5 | 32 | 85 | 0 | 0 | 19 | 8 | 25 | 21 | 82 | 112 | 81 | 22 | 0.7 | 30 | 62 | 48 | 50 | 130 | 0 | 69 | 84 | 49 | 0 | 0 | 23 | 10 | 290 | 24 | 11 | 0 | 2 | 0 | 0 | 19 | 0 | 2 | 7.3 | 50 | 75 | 0 | 0 | 0 | 537 | 0 | 400 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 40 | 93 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 0 | 52 | 0 | 22 | 15 | 11 | 0 | 0 | 149 | 17 | 18 | 0 | 0 | 0 | 0 | 95 | 0 | 192 | 0 | 0 | 105 | 0 | 0
199
| Minimum Generation |  | 5363 | 5:00
| Highest Generation |  | 8748 | 19:00
| Day Peak Generation |  | 6883.53 | 9:00
| Evening Peak Generation |  | 8748 | 19:00
| HVDC Max Flow |  | 685 | 23:00
| HVDC EvPeak Flow |  | 684 | 19:00
| Load factor L.F |  | 78.01%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-01-22
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-01-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6883.53 | MW Hour : | 9:00 | Min. Gen. at | 5:00 | 5282 | MW
Evening Peak Generation : |  | 8748 | MW Hour : | 19:00 | Available Max Generation : |  | 11669 | MW
E.P. Demand (at gen end) : |  | 8748 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8800 | MW
Maximum Generation : |  | 8748 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2869 | MW
Total Gen. (MKWH) : |  | 163.7874 | System Load Factor : | 78.01% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -540 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-01-22
Actual : | 96.99 | Ft.(MSL) , | Rule curve : | 99 | Ft.( MSL )
Gas Consumed : | Total = | 966.14 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 82995158.22
|  | Coal : | 19684456 | Oil : | 181451430.66 | Total : | 284131044.88
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3111.4231 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1051.9913 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 941.4686 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 850.3126 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 768.6268 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 620.2393 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 354.6118 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 159.9015 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 478.322 |  |  | 0 | 0%
Total | 0 |  | 8336.897 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Sirajganj Unit-1,2,4
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Ashuganj #3
|  |  |  | 3) Ghorasal Unit-1,3,4,5 |  | 11) Raozan # 02
|  |  |  | 4) Tongi GT |  | 12) Sikalbaha 225 MW
5) Haripur GT-1,2
6) Siddhirganj ST 210 MW
7) Bhagabari 71 MW,100 MW
8) Sikalbaha 150MW Peaking
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Sylhet 150 MW was shut down at 08:59 for enabling FGMO.
b) Ghorasal Unit-7 GT & ST were synchronized at 10:28 & 13:50 respectively.
c) Kushiara CCPP ST was synchronized at 09:50.
d) Bashundhara 132/33 kV T3 transformer was shut down at 11:02 for replacing relay at 132 kV side.
e) Madunaghat 132/33 kV T3 transformer was under shut down from 08:15 to 13:24 for A/M.
f) Tongi(New) 132 kV bus section-2 was under shut down from 08:55 to 13:11 for A/M.
g) Comilla(N)-Daudkandi 132 kV Ckt-2 was under shut down from 09:25 to 16:21 for A/M.
h) Haripur 230/132 kV T3 transformer was under shut down from 09:52 to for A/M.
i) Shahjibazar-Srimongal 132 kV Ckt-2 was under shut down from 09:04 to 14:30 for A/M.
j) Aminbazar-Kaliakoir 230 kV Ckt-2 was under shut down from 09:13 to 20:10 for A/M.
k) Kaliakoir-Bibiyana 400 kV Ckt-1 was under shut down from 08:48 to 20:27 for A/M.
l) Hathazari-Baroaihat 132 kV Ckt-1 was under shut down from 12:13 to 16:56 for D/W.
m) Chandraghona-Kaptai 132 kV Ckt-1 was under shut down from 08:36 to 09:45 for red hot maintenance at
Chandraghona end.
n) Barapukuria 230/132 kV T2 & T6 transformers were under shut down from 08:48 to 17:57 for reconductoring. |  |  |  | About 40MW Power interruption occurred under Rangpur zone
from 08:48 to 17:57.
o) Barisal-Patuakhali 132 kV Ckt was under shut down from 10:10 to 17:03 for C/M. |  |  |  | About 15MW Power interruption occurred under Patuakhali S/S area
from 10:10 to 17:03.
p) Ruppur 132/11 kV T2 transformer was under shut down from 09:52 to 13:21 for D/W.
q) Ruppur 132/11 kV T1 transformer was under shut down from 13:21 to 20:31 for D/W.
r) Netrokona 132/33 kV T2 transformer was under shut down from 13:45 to 14:05 for D/W.
s) Siddhirganj GT-1 was shut down at 13:09 due to gas shortage.
t) After maintenance Hasnabad-Aminbazar 230 kV Ckt-1 was switched on at 21:15 and tripped at 22:11 from both
ends showing Dist RST at Aminbazar end & Dist Z1 3-phase at Hasnabad end due to Y-phase LA burst at
Aminbazar end and was switched on at 00:48(22/01/2019).
u) Siddhirganj 335 MW GT tripped at 04:33 (22/01/2019) due to exhaust temperature high and was
synchronized at 06:13.
v) Ashuganj(S) 450 MW CCPP was shut down at 04:34(22/01/2019) due to differential pressure high.
w) Bhola 225 MW CCPP GT-1 tripped at 05:27(22/01/2019) due to high vibration.
x) Ashuganj-Kishoreganj 132 kV Ckt-1 was shut down at 07:35 (22/01/2019) for D/W.
y) Comilla(N)-BSRM 230 kV Ckt-2 was shut down at 07:34 (22/01/2019) for A/M.
z) Mirpur-Uttara 132 kV Ckt was shut down at 06:01(22/01/2019) for D/W.
aa) Mirpur-Uttara 3rd phase 132 kV Ckt was shut down at 06:05 (22/01/2019) for D/W.
ab) Rampura-Bhulta 230 kV Ckt-2 was shut down at 06:53(22/01/2019) for D/W.
ac) Palashbari 33 kV bus associated 132/33 kV T1 transformer were under shut down from 06:30 to 08:05 . |  |  |  | About 30MW Power interruption occurred under Palashbari S/S area
(22/01/2019) for D/W |  |  |  | from 06:30 to 08:05(22/0/2019).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-01-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 696000 | #1 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 263 | 2381700 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 240 | 2257463
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 390432 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 1093545 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 374 | 8779890 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 31000 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 365 | 8006000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 430 | 9952500 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 7 | 187200 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 80 | 495288 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 50 | 582204
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 392256 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 1170000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 226 | 5156602
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 64 | 359712 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 37 | 746640 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 993600
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 916896
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 17 | 89000 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 38 | 635520 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1169520 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 813100
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 8 | 444000
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 42 | 738516 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 105 | 617240 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 89 | 961920 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2681 | 50057744
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2900000
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 26 | 460260
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 130680
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 46 | 760320 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 39 | 861000 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Test run.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 1042080
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 64 | 194008
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 262320 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 74 | 902640
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 50 | 1104000 | Low demand
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 531504
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 596160
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 93 | 1022400 | Engine problem
| Chattogram area Total |  |  |  | 1681 | 683 | 10767372
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 150 | 3532519
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 135 | 3245832 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 188 | 4705000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 272 | 6557000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 36 | 769032 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 123360 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 16 | 418182 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 980415 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 768184
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 6704 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2364910
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 108 | 1049280 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 438264
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239040
** | Tripura |  | Imported power | 0 | 160 | 108 | 2015040
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 596300 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 11 | 72677 | Low demand
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 526810
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1339 | 28528549
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 111 | 2994840 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 526824
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 86 | 1513920 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 11250
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 150 | 1521600 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 369 | 6568434
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 30 | 692000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 61 | 1475000
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 2383510
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 1201200
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1194000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 247632
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 61 | 1475000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 84 | 1031040
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 48 | 1140840
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 848420 | under maint.
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 15 | 421000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 23 | 546980
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 578688
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 320 | 7745750 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 175320
| Sylhet Area Total |  |  |  | 1549 | 951 | 21156380
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 684 | 11589091
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 873600
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 44 | 238560
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 72 | 246272
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 380 | 9488160
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 778125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1847040
| Khulna Area Total |  |  |  | 2209 | 1440 | 25060848
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 48 | 237120 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 14 | 278609 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 188 | 4521873 | FGMO
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1907905
| Barisal Area Total |  |  |  | 462 | 347 | 6945507
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 165704
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 42 | 159388
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 673820 | Engine problem
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 381498
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 194 | 4655000
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 37 | 241882
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 510240
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 13 | 333144
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 143460
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 51 | 979200
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 571856
| Paramount Baghabari |  | IPP | 200 MW | 0 | 2 | 271818
| Rajshahi Area Total |  |  |  | 1546 | 614 | 9087010
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 293 | 5099600
122 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 239000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 15 | 277000
| Rangpur Area Total |  |  |  | 484 | 324 | 5615600
| Total |  |  |  | 17142 | 8748 | 163787444
| Eastern Grid Total |  |  |  | 12441 | 6023 | 117078479
| Western Grid Total |  |  |  | 4701 | 2725 | 46708965
| National Grid Total |  |  |  | 17142 | 8748 | 163787444
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-01-21 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5535 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2740 | MW
i) Dhaka area |  |  | 2969 | MW | i) Khulna area |  |  | 1013 | MW
ii) Chittagong area |  |  | 878 | MW | ii) Rajshahi area |  |  | 956 | MW
iii) Comilla area |  |  | 695 | MW | iii) Barisal area |  |  | 220 | MW
iv) Mymensingh area |  |  | 673 | MW | iv) Rangpur area |  |  | 551 | MW
v) Sylhet area |  |  | 320 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8275 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 94 | 1900 | Netrokona | 86 | 2100 | Goalpara | 20 | 2100
Munsiganj | 66 | 1900 | Jamalpur | 100 | 1830 | Central s/s | 66 | 1830
Sonargaon | 40 | 1800 | Sherpur | 82 | 1930 | Noapara | 76 | 1830
Shyampur | 148 | 900 | Srimongal | 24 | 1800 | Jessore | 116 | 1830
Bhulta | 142 | 2100 | Shahjibazar | 86 | 1830 | Jhenida | 82 | 1830
Madanganj | 51 | 100 | Fenchuganj | 29 | 1830 | Bottail | 92 | 1830
Shitalakhya | 100 | 1100 | Kulawara | 27 | 1830 | G.K Project | 33 | 1830
Rahim steel | 6 | 1000 | Sylhet | 87 | 1830 | Faridpur | 124 | 1830
Matuail | 78 | 1000 | Chatak | 18 | 1800 | Madaripur | 89 | 2000
Ghorasal | 68 | 1930 | Sunamganj | 25 | 1930 | Gopalganj | 63 | 1830
Narsingdi | 95 | 1830 | Biani Bazar | 28 | 1830 | Bagerhat | 71 | 1830
Haripur (SBU) | 94 | 1100 | Comilla (S) | 110 | 1830 | Mongla | 36 | 1000
Ullon | 60 | 1800 | Comilla(N) | 93 | 1930 | Satkhira | 67 | 1830
Hasnabad | 147 | 1830 | Chandpur | 74 | 2000 | Gallamari | 36 | 1300
Magbazar | 96 | 1800 | Feni | 88 | 2000 | Magura | 36 | 1830
Maniknagar | 80 | 1200 | Chowmuhani | 114 | 1800 | Chuadanga | 58 | 1900
Bangabhaban | 18 | 1300 | Ashuganj | 40 | 2100 | Barisal | 88 | 1900
Narinda | 70 | 1400 | Daudkandi | 80 | 1800 | Patuakhali | 63 | 1900
Dhanmondi | 73 | 1300 | B.Baria | 92 | 1830 | Bhandaria | 40 | 1930
Lalbag | 63 | 1300 | Ramganj | 24 | 1800 | Ishurdi | 40 | 1830
Madartek | 33 | 2000 | Madunaghat | 46.5 | 2200 | Ruppur Paromanobik | 1 | 100
Mirpur | 75 | 1900 | Hathazari | 69 | 1900 | Natore | 88 | 1930
Kalyanpur | 63 | 1900 | Khulshi | 134 | 1500 | Bogra | 191 | 1830
Gulshan | 88 | 1830 | Halishahar | 97 | 1830 | Noagaon | 105 | 2000
Uttara | 36 | 1830 | Baraulia | 134 | 2200 | Rajshahi | 102 | 2000
Uttara(New) | 6 | 1830 | Sikalbaha | 31 | 1800 | C.Nawabganj | 68 | 1830
Kamrangirchar | 58 | 1900 | Dohazari | 64 | 1930 | Amnura | 33 | 2000
Savar | 96 | 1830 | Cox'sbazar | 67 | 1830 | Pabna | 77 | 1830
Bhasantec | 98 | 1830 | Chandraghona | 22 | 1800 | Shahjadpur | 71 | 1830
Agargaon | 37 | 1830 | Kaptai | 3.8 | 1800 | Serajganj | 76 | 1900
Satmosjid | 59 | 1900 | A. Khaer Stl. | 20 | 1700 | Niyamatpur | 94 | 1800
Tongi | 125 | 1100 | Bakulia | 72 | 1800 | Joypurhat | 37 | 1830
Kabirpur | 142 | 1200 | Julda | 18 | 1500 | Rangpur | 95 | 1900
Basundhara | 68 | 1800 | TK chemical | 4.8 | 1200 | Lalmonirhat | 79 | 2000
Manikganj | 64 | 1930 | Modern Steel | 14 | 200 | Saidpur | 91 | 1900
Joydevpur | 185 | 1830 | Shahmirpur | 21 | 1830 | Purbasadipur | 83 | 1930
New Tongi | 87 | 1800 | Khagrachhari | 15 | 1800 | Thakurgaon | 53 | 1830
Korda | 206 | 1900 | Matarbari | 20 | 1800 | Palashbari | 87 | 800
Dhamrai | 36 | 800 | Baroiar Hat | 20 | 1800 | Barapukuria | 45 | 1930
Tangail | 139 | 1830 | Rangamati | 8 | 1800 | Panchagar | 34 | 1900
Mymensing | 212 | 1800 | Abul Khair 230 | 150 | 400 | Joldhaka | 16 | 1800
Kishorganj | 78 | 1800 | BSRM | 98 | 700
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-01-21
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 411 | 1:00 | 399 | 12:00 | Kaliakoir | 398 | 1:00 | 378 | 12:00
Bheramara | 405 | 3:00 | 394 | 19:00 | Bhulta | 402 | 24:00 | 389 | 16:00
Ashuganj(N) | 400 | 3:00 | 389 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 1:00 | 232 | 10:00 | Hathazari | 225 | 19:00 | 212 | 12:00
Ishurdi | 237 | 1:00 | 233 | 8:00 | Megnaghat | 236 | 3:00 | 228 | 16:00
Ashuganj | 240 | 1:00 | 235 | 13:00 | Fenchuganj | 242 | 2:00 | 238 | 15:00
Serajganj | 232 | 5:00 | 225 | 8:00 | Siddhirganj | 233 | 6:00 | 226 | 12:00
Baghabari | 231 | 4:00 | 220 | 9:00 | Maniknagar | 231 | 4:00 | 223 | 15:00
Barapukuria | 230 | 3:00 | 221 | 19:30 | Old Airport | 233 | 1:00 | 224 | 12:00
Bogra | 230 | 5:00 | 219 | 19:30 | Barisal | 237 | 1:00 | 232 | 13:00
Khulna South | 242 | 22:00 | 231 | 7:00 | AKSML | 226 | 20:00 | 216 | 15:00
Rampura | 229 | 1:00 | 223 | 15:00 | BSRM | 230 | 1:00 | 217 | 11:00
Haripur | 230 | 1:00 | 224 | 12:00 | Bibiyana | 243 | 1:00 | 235 | 19:00
Hasnabad | 234 | 24:00 | 225 | 10:00 | Bhulta | 232 | 3:00 | 225 | 12:00
Aminbazar | 234 | 4:00 | 225 | 12:00 | Ashuganj (S) | 240 | 1:00 | 235 | 12:00
Tongi | 230 | 24:00 | 220 | 10:00 | Kaliakoir | 236 | 2:00 | 226 | 12:00
Comilla (N) | 241 | 8:00 | 235 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 800 | 131 | 1200 | Ramganj | 136 | 700 | 132 | 1600
Munsiganj | 137 | 700 | 132 | 1600 | Madanhat | 138 | 2100 | 130 | 1300
Megnaghat | 135 | 700 | 131 | 1200 | Hathazari | 136 | 1900 | 130 | 600
Shyampur | 132 | 700 | 126 | 1100 | Khulshi | 135 | 2100 | 125 | 1100
Bhulta | 131 | 700 | 125 | 100 | Halishahar | 138 | 1900 | 129 | 1100
Madanganj | 141 | 2100 | 132 | 1000 | Baraulia | 136 | 1900 | 127 | 1200
Shitalakhya | 141 | 300 | 133 | 1200 | Sikalbaha | 137 | 1930 | 129 | 1200
Rahim steal | 136 | 500 | 131 | 1200 | Dohazari | 138 | 800 | 130 | 600
Matuail | 135 | 400 | 129 | 1200 | Cox'sbazar | 131 | 900 | 123 | 1700
Ghorasal | 142 | 100 | 140 | 800 | Chandraghona | 137 | 800 | 130 | 1000
Narsinghdi | 136 | 2300 | 132 | 1200 | Kaptai | 137 | 1830 | 130 | 1000
Haripur (SBU) | 136 | 300 | 131 | 1200 | A. Khaer Stl. | 135 | 900 | 129 | 600
Ullon | 133 | 500 | 127 | 1200 | Bakulia | 135 | 800 | 126 | 1100
Hasnabad | 140 | 700 | 132 | 1200 | Julda | 137 | 2000 | 128 | 1100
Magbazar | 134 | 500 | 127 | 1200 | TK Chemical | 142 | 2100 | 129 | 900
Maniknagar | 135 | 500 | 130 | 1300 | Modern Steel | 136 | 800 | 126 | 1300
Bangabhaban | 140 | 400 | 131 | 1200 | Shahmirpur | 138 | 2100 | 127 | 1000
Narinda | 133 | 500 | 127 | 1200 | Khagrachhari | 136 | 700 | 128 | 1100
Dhanmondi | 133 | 500 | 127 | 1200 | Matarbari | 132 | 800 | 125 | 400
Lalbag | 140 | 400 | 131 | 1200 | Baroiar Hat | 136 | 100 | 133 | 400
Madartek | 133 | 500 | 127 | 1200 | Rangamati | 136 | 800 | 128 | 1100
Mirpur | 136 | 600 | 128 | 1100 | Goalpara | 139 | 2200 | 130 | 600
Kalyanpur | 135 | 200 | 130 | 1200 | Central s/s | 137 | 2200 | 125 | 500
Gulshan | 132 | 300 | 126 | 1200 | Noapara | 135 | 2200 | 124 | 600
Uttara | 134 | 200 | 127 | 1200 | Jessore | 130 | 100 | 123 | 700
Uttara(New) | 133 | 300 | 127 | 1200 | Jhenida | 129 | 100 | 119 | 700
Kamrangirchar | 139 | 300 | 132 | 1200 | Bottail | 140 | 300 | 134 | 1830
Savar | 132 | 200 | 127 | 1200 | G.K.Project | 142 | 600 | 140 | 700
Bhasantec | 136 | 300 | 128 | 1200 | Faridpur | 137 | 1700 | 132 | 1300
Agargaon | 135 | 200 | 129 | 1200 | Madaripur | 136 | 1700 | 132 | 900
Satmosjid | 135 | 300 | 129 | 1200 | Gopalganj | 140 | 1800 | 131 | 800
Tongi | 136 | 2400 | 129 | 1000 | Bagerhat | 136 | 2200 | 131 | 600
Kabirpur | 135 | 2400 | 128 | 1200 | Mongla | 135 | 2200 | 129 | 300
Basundhara | 131 | 100 | 120 | 1300 | Satkhira | 136 | 2200 | 129 | 1830
Manikganj | 140 | 2400 | 134 | 1000 | Gallamari | 139 | 2200 | 131 | 600
Joydevpur | 142 | 2000 | 138 | 1830 | Magura | 136 | 200 | 125 | 1930
New Tongi | 136 | 300 | 128 | 1000 | Chuadanga | 135 | 400 | 122 | 1900
Kodda | 144 | 1600 | 136 | 1500 | Barisal | 137 | 1930 | 134 | 1200
Dhamrai | 136 | 600 | 128 | 1200 | Patuakhali | 139 | 900 | 130 | 1800
Tangail | 138 | 200 | 128 | 700 | Bhandaria | 137 | 1700 | 132 | 1830
Mymensing | 134 | 2300 | 120 | 800 | Ishurdi | 140 | 200 | 136 | 1000
Kishorganj | 132 | 400 | 130 | 1000 | Ruppur Paromanobik | 140 | 100 | 137 | 800
Netrokona | 132 | 2300 | 123 | 800 | Natore | 137 | 1800 | 132 | 800
Jamalpur | 137 | 2300 | 120 | 700 | Bogra | 135 | 400 | 127 | 1000
Sherpur | 137 | 2300 | 116 | 700 | Noagaon | 131 | 500 | 121 | 1000
Srimongal | 140 | 100 | 138 | 900 | Rajshahi | 135 | 1800 | 129 | 1200
Shahjibazar | 140 | 2300 | 135 | 1700 | C.Nawabganj | 134 | 1800 | 124 | 1400
Fenchuganj | 138 | 200 | 135 | 1700 | Amnura | 138 | 1800 | 124 | 700
Khulawara | 137 | 100 | 135 | 1300 | Pabna | 135 | 100 | 130 | 700
Sylhet | 137 | 100 | 133 | 1200 | Shahjadpur | 142 | 100 | 138 | 1100
Chatak | 138 | 100 | 133 | 1200 | Serajganj | 135 | 100 | 129 | 1000
Sunamganj | 136 | 100 | 132 | 1200 | Niyamatpur | 126 | 400 | 114 | 800
Biani Bazar | 137 | 100 | 133 | 1800 | Joypurhat | 131 | 100 | 121 | 800
Cumilla(s) | 131 | 1500 | 126 | 800 | Rangpur | 129 | 500 | 114 | 1900
Cumilla(n) | 143 | 800 | 140 | 1100 | Lalmonirhat | 122 | 900 | 101 | 1200
Chandpur | 143 | 600 | 139 | 1700 | Saidpur | 127 | 500 | 115 | 1900
Feni | 138 | 900 | 133 | 700 | Purbasadipur | 130 | 1800 | 112 | 2000
Chowmuhani | 136 | 2200 | 131 | 1600 | Thakurgaon | 124 | 900 | 102 | 1900
Ashuganj | 140 | 100 | 137 | 1500 | Palashbari | 128 | 200 | 115 | 1200
Daudkandi | 137 | 700 | 131 | 1200 | Barapukuria | 130 | 300 | 121 | 1930
B.Baria | 140 | 2300 | 135 | 1400 | Panchagar | 122 | 900 | 101 | 1930
[5 empty] | Joldhaka | 124 | 1800 | 117 | 1700

## L-Curve
Date | 2019-01-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 440 | 4893 | 1531 | 6424 |  |  |  | QF-LDC-12
0:30 | 440 | 4688.5 | 1482.5 | 6171 | Date: | 2019-01-21
1:00 | 440 | 4484 | 1434 | 5918
1:30 | 432 | 4376 | 1392 | 5768
2:00 | 424 | 4268 | 1350 | 5618
2:30 | 422 | 4219.5 | 1340 | 5559.5 | [5 empty] | Gen. at Eve. Peak | 8748 | 8748 MW (19:00 )
3:00 | 420 | 4171 | 1330 | 5501 | [6 empty] | 19:00
3:30 | 420 | 4124 | 1310.5 | 5434.5 | [5 empty] | Gen. at Day Peak | 6883.53 | 6883.53 MW (09:00 )
4:00 | 420 | 4077 | 1291 | 5368 | [6 empty] | 9:00
4:30 | 405 | 4078.5 | 1287 | 5365.5 | [5 empty] | Highest Generation | 8748
5:00 | 390 | 4080 | 1283 | 5363 | [6 empty] | 19:00
5:30 | 415 | 4198 | 1326.5 | 5524.5
6:00 | 440 | 4316 | 1370 | 5686
6:30 | 490 | 4469 | 1442.5 | 5911.5
7:00 | 540 | 4622 | 1515 | 6137
7:30 | 490 | 4660.7 | 1714 | 6374.7
8:00 | 440 | 4699.4 | 1913 | 6612.4
8:30 | 350 | 4817.965 | 1930 | 6747.965
9:00 | 260 | 4936.53 | 1947 | 6883.53
9:30 | 200 | 4811.265 | 1971 | 6782.265
10:00 | 140 | 4686 | 1995 | 6681
10:30 | 120 | 4675.71 | 2031.5 | 6707.21
11:00 | 100 | 4665.42 | 2068 | 6733.42
11:30 | 125 | 4695.21 | 2058 | 6753.21
12:00 | 150 | 4725 | 2048 | 6773
12:30 | 125 | 4772 | 2083.5 | 6855.5
13:00 | 100 | 4819 | 2119 | 6938
13:30 | 120 | 4665.3 | 2072 | 6737.3
14:00 | 140 | 4511.6 | 2025 | 6536.6
14:30 | 160 | 4609.4 | 1988.5 | 6597.9
15:00 | 180 | 4707.2 | 1952 | 6659.2
15:30 | 215 | 4793.7 | 1931 | 6724.7
16:00 | 250 | 4880.2 | 1910 | 6790.2
16:30 | 162.5 | 4821.65 | 1993 | 6814.65
17:00 | 75 | 4763.1 | 2076 | 6839.1
17:30 | 112.5 | 5061.55 | 2347 | 7408.55
18:00 | 150 | 5360 | 2618 | 7978
18:30 | 200 | 5691.5 | 2671.5 | 8363
19:00 | 250 | 6023 | 2725 | 8748
19:30 | 300 | 6071 | 2668 | 8739
20:00 | 310 | 6015 | 2630 | 8645 |  |  |  | Executive Engineer
20:30 | 320 | 5933.5 | 2537 | 8470.5 |  |  |  | Network Operation Division
21:00 | 330 | 5852 | 2444 | 8296
21:30 | 195 | 5636.5 | 2390.5 | 8027
22:00 | 60 | 5421 | 2337 | 7758 |  |  |  |  | Page 6 of 7
22:30 | 35 | 5220 | 2161.5 | 7381.5
23:00 | 10 | 5019 | 1986 | 7005
23:30 | 225 | 4956 | 1758.5 | 6714.5
24:00 | 440 | 4893 | 1531 | 6424
8748 MW (19:00 )
6883.53 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-01-21 |  | Energy | 163787444
[10 empty] | 2019-01-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3383 | 247 | 1674 | 826 | 149 | 38 | 29 | 0 | 78
0:30 | 3307 | 253 | 1730 | 601 | 149 | 38.5 | 14.5 | 0 | 78 | Date: | 2019-01-21
1:00 | 3231 | 259 | 1786 | 376 | 149 | 39 | 0 | 0 | 78
1:30 | 3238 | 259 | 1764.5 | 243 | 149 | 38.5 | 0 | 0 | 76 | [7 empty] | Total Energy | 163.7874 | Total Energy Gen 163.787 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 163.787 MKWHr
2:00 | 3245 | 259 | 1743 | 110 | 149 | 38 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3211 | 259 | 1743 | 85.5 | 149 | 38 | 0 | 0 | 74 | [7 empty] | Energy Requirement | 163.7874
3:00 | 3177 | 259 | 1743 | 61 | 149 | 38 | 0 | 0 | 74
3:30 | 3170.5 | 259 | 1685 | 61 | 149 | 38 | 0 | 0 | 72 | [6 empty] | Shortage
4:00 | 3164 | 259 | 1627 | 61 | 149 | 38 | 0 | 0 | 70
4:30 | 3159.5 | 255.5 | 1631.5 | 61 | 149 | 38 | 0 | 0 | 71
5:00 | 3155 | 252 | 1636 | 61 | 149 | 38 | 0 | 0 | 72
5:30 | 3232 | 250 | 1692 | 90.5 | 149 | 38 | 0 | 0 | 73
6:00 | 3309 | 248 | 1748 | 120 | 149 | 38 | 0 | 0 | 74
6:30 | 3302.5 | 247.5 | 1765.5 | 335.5 | 149 | 39 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 3296 | 247 | 1783 | 551 | 149 | 40 | 0 | 0 | 70
7:30 | 3225 | 393 | 1719 | 763 | 149 | 40 | 9.5 | 0 | 73 |  |  |  | Oil |  |  |  | ,
8:00 | 3154 | 539 | 1655 | 975 | 149 | 40 | 19 | 0 | 76
8:30 | 3118 | 538.5 | 1638 | 1136.5 | 162 | 40 | 27.5 | 0 | 78
9:00 | 3082 | 538 | 1621 | 1298 | 175 | 40 | 36 | 0 | 80
9:30 | 3031 | 537 | 1611 | 1227.5 | 202.5 | 40 | 36 | 0 | 82
10:00 | 2980 | 536 | 1601 | 1157 | 230 | 40 | 36 | 0 | 84
10:30 | 2985 | 536.5 | 1586.5 | 1165.5 | 254 | 40 | 35.5 | 0 | 85
11:00 | 2990 | 537 | 1572 | 1174 | 278 | 40 | 35 | 0 | 86
11:30 | 3021.5 | 537 | 1599.5 | 1125 | 287 | 39.5 | 35 | 0 | 87
12:00 | 3053 | 537 | 1627 | 1076 | 296 | 39 | 35 | 0 | 88
12:30 | 3099.5 | 537 | 1658 | 1080 | 296 | 39 | 35 | 0 | 89
13:00 | 3146 | 537 | 1689 | 1084 | 296 | 39 | 35 | 0 | 90
13:30 | 3146 | 537 | 1689 | 1084 | 296 | 39 | 35 | 0 | 90
14:00 | 3146 | 537 | 1689 | 1084 | 296 | 39 | 35 | 0 | 90
14:30 | 3115 | 536.5 | 1629.5 | 1043 | 294.5 | 39 | 34.5 | 0 | 89
15:00 | 3084 | 536 | 1570 | 1002 | 293 | 39 | 34 | 0 | 88
15:30 | 3163 | 536.5 | 1574.5 | 983 | 293 | 38 | 38.5 | 0 | 88
16:00 | 3242 | 537 | 1579 | 964 | 293 | 37 | 43 | 0 | 88
16:30 | 3228.5 | 582 | 1520 | 986 | 293 | 38 | 75 | 0 | 88
17:00 | 3215 | 627 | 1461 | 1008 | 293 | 39 | 107 | 0 | 88
17:30 | 3231.5 | 655.5 | 1547 | 1230 | 292.5 | 39 | 315.5 | 0 | 97
18:00 | 3248 | 684 | 1633 | 1452 | 292 | 39 | 524 | 0 | 106
18:30 | 3351.5 | 684 | 1754 | 1618 | 292.5 | 39 | 517 | 0 | 107
19:00 | 3455 | 684 | 1875 | 1784 | 293 | 39 | 510 | 0 | 108
19:30 | 3469 | 684 | 1887 | 1794 | 253 | 39 | 503 | 0 | 110
20:00 | 3421 | 684 | 1876 | 1802 | 217 | 39 | 498 | 0 | 108
20:30 | 3428.5 | 684 | 1819 | 1801.5 | 183.5 | 39 | 409 | 0 | 106
21:00 | 3436 | 684 | 1762 | 1801 | 150 | 39 | 320 | 0 | 104
21:30 | 3432 | 684 | 1767 | 1589.5 | 150 | 39.5 | 265 | 0 | 100
22:00 | 3428 | 684 | 1772 | 1378 | 150 | 40 | 210 | 0 | 96
22:30 | 3405 | 684.5 | 1721.5 | 1149 | 149.5 | 39 | 141 | 0 | 92
23:00 | 3382 | 685 | 1671 | 920 | 149 | 38 | 72 | 0 | 88
23:30 | 3382.5 | 466 | 1672.5 | 873 | 149 | 38 | 50.5 | 0 | 83 | Max Temp. in Dhaka |  | 28.4° C
24:00 | 3383 | 247 | 1674 | 826 | 149 | 38 | 29 | 0 | 78
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 163.787 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 163.787 MKWHr
Note on W13: Author:

## Generation
2019-01-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 39 | 38 | 38 | 38 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 37 | 39 | 39 |  | 39 | 39 | 39 | 39 | 40 | 38 | 38 | 861000
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 8 | 0 |  |  |  | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 25 | 26 | 25 | 17 |  | 26 | 25 | 25 | 26 | 25 | 25 | 25 | 460260
| Teknaf Solartech 20MW | [6 empty] | 1 | 5.4 | 12.43 | 16 | 19.42 | 20 | 20 | 15.9 | 12.1 | 6.7 | 1.1 | 0 | [8 empty] | 130680
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 68 |  | 68 | 68 | 68 | 68 | 0 |  |  | 262320
12 | Hathazari peaking | [17 empty] | 62 |  | 64 | 64 | 64 | 0 |  |  |  | 194008
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 6704
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 92 | 97 | 67 | 67 | 67 | 72 | 72 | 70 | 98 | 100 | 100 | 100 | 100 | 0 | 0 | [11 empty] | 1170000
17 | Siddhirganj CCPP-335 MW | 230 | 230 | 230 | 230 | 230 | 225 | 225 | 230 | 180 | 180 | 180 | 180 | 235 | 215 | 218 | 190 | 150 | 150 |  | 226 | 226 | 226 | 226 | 230 | 225 | 200 | 5156602
18 | Summit Gazipur -2 | [7 empty] | 5 | 45 | 28 | 15 | 15 | 15 | 12 | 12 | 15 | 12 | 35 |  | 105 | 102 | 103 | 103 | 0 |  |  | 617240
19 | Ashuganj 195MW Modular | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 418182
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 696000
21 | Ghorasal GT: Unit-3 | [14 empty] | 90 | 250 | 263 | 263 |  | 263 | 263 | 263 | 263 | 263 | 262 | 263 | 2381700
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | [10 empty] | 40 | 40 | 50 | 90 | 135 | 195 | 230 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 2257463
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3532519
30 | Ashuganj ST: Unit- 5 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3245832
32 | Ashuganj Engines TSK | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 33 | 36 | 36 | 769032
33 | Ashuganj CCPP 225 MW | 185 | 193 | 185 | 194 | 198 | 207 | 206 | 184 | 184 | 203 | 198 | 224 | 190 | 186 | 202 | 186 | 186 | 190 |  | 188 | 204 | 193 | 205 | 187 | 186 | 187 | 4705000
34 | Ashuganj CCPP(South) | 276 | 276 | 276 | 287 | 276 | 276 | 272 | 253 | 250 | 257 | 268 | 272 | 272 | 272 | 272 | 272 | 272 | 272 |  | 272 | 272 | 272 | 272 | 272 | 272 | 272 | 6557000
Ashuganj CCPP(North)
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 |  | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 123360
36 | Chandpur CCPP | 101 | 102 | 95 | 100 | 102 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 |  | 100 | 100 | 100 | 101 | 95 | 100 | 95 | 2364910
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 361 | 362 | 350 | 350 | 350 | 375 | 390 | 380 | 345 | 350 | 355 | 365 | 375 | 350 | 360 | 350 | 354 | 350 |  | 374 | 375 | 360 | 355 | 350 | 350 | 350 | 8779890
40 | Meghnaghat CCPP 450MW | 400 | 400 | 400 | 400 | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 370 | 350 |  | 430 | 430 | 430 | 400 | 400 | 350 | 350 | 9952500
41 | Haripur Power CCPP 360MW | 368 | 341 | 340 | 320 | 320 | 367 | 367 | 320 | 320 | 321 | 323 | 340 | 356 | 308 | 336 | 336 | 311 | 331 |  | 365 | 361 | 363 | 330 | 332 | 310 | 312 | 8006000
42 | Mymensingh RPCL 210MW | 152 | 150 | 153 | 153 | 152 | 166 | 166 | 136 | 136 | 124 | 123 | 121 | 111 | 110 | 109 | 110 | 111 | 111 |  | 111 | 111 | 110 | 110 | 109 | 112 | 113 | 2994840
43 | Haripur NEPC 110MW | [7 empty] | 18 | 13 | 0 | 0 | [15 empty] | 31000
44 | Fenchugonj CCPP-1 | 30 | 28 | 28 | 30 | 27 | 28 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 30 |  | 30 | 30 | 29 | 28 | 28 | 30 | 30 | 692000
45 | Fenchugonj CCPP-2 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 62 | 62 | 61 | 62 |  | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 1475000
46 | Shajibazar 330 MW
47 | Shahjibazar GT: Unit- 8, 9 | 62 | 65 | 55 | 56 | 56 | 69 | 69 | 40 | 50 | 52 | 40 | 64 | 63 | 58 | 63 | 58 | 43 | 63 |  | 61 | 66 | 60 | 66 | 63 | 64 | 62 | 1475000
48 | Shahjibazar 86MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1031040
49 | Shahjibazar (EPL) 50MW | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 49 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 1140840
50 | Sylhet GT 150 MW | 98 | 80 | 80 | 80 | 80 | 118 | 120 | 118 | 135 | 0 | [16 empty] | 848420
51 | Sylhet GT 20 MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 421000
52 | Sylhet (EPL) 50MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 546980
53 | Sylhet (Desh) 10MW | 10 | 0 | [6 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 175320
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 3 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 10 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 247632
55 | Fenchugonj (Barakatullah) 51MW | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 45 | 48 | 48 | 51 | 51 | 50 | 50 | 50 | 51 |  | 50 | 48 | 48 | 51 | 51 | 51 | 51 | 1201200
56 | Shahjahanulla 25 MW | 24 | 24 | 23 | 23 | 24 | 24 | 24 | 24 | 23 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 |  | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 578688
57 | Summit Bibiana- 2 | 320 | 310 | 310 | 310 | 320 | 320 | 330 | 290 | 285 | 290 | 300 | 305 | 310 | 280 | 300 | 300 | 280 | 270 |  | 320 | 335 | 320 | 300 | 305 | 270 | 290 | 7745750
58 | Southern 55MW | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 89000
59 | Sikalbaha (Energis) | 50 | 32 | 24 | 24 | 24 | 25 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 51 |  | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 1042080
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531504
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 19 | 0 | 19 |  | 19 | 19 | 0 | 0 | 19 | 19 | 19 | 392256
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 526824
63 | Tripura | 78 | 74 | 74 | 70 | 72 | 74 | 70 | 76 | 80 | 84 | 86 | 88 | 90 | 88 | 88 | 88 | 88 | 106 |  | 108 | 110 | 108 | 104 | 96 | 88 | 78 | 2015040
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 42 | 42 | 42 | 42 | 36 | 21 | 7 | 4 | 4 | 5 | 11 | 7 | 5 | 7 | 14 | 16 |  | 30 | 34 | 36 | 36 | 40 | 42 | 40 | 596160
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 438264
66 | Feni, Mohipal (Doreen) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239040
67 | Jangalia (Summit) 33MW | 24 | 24 | 24 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 596300
68 | Summit Cumilla 25MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 18 | 20 | 20 | 20 |  | 20 | 20 | 22 | 20 | 20 | 20 | 22 | 526810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 21 | 24 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 569520
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 813100
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | [8 empty] | 8 | 8 | 8 | 16 | 33 | 33 | 33 | 444000
73 | Ghorashal (Regent) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 42 | 12 | 12 | 12 | 0 | [12 empty] | 1093545
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | 25 | 0 |  |  | 0 | 6 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 41 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 738516
79 | Kodda 149MW
80 | Jamalpur 95MW | 28 | 7 | 0 |  | 0 | 6 | 30 | 50 | 87 | 87 | 87 | 86 | 87 | 87 | 86 | 86 | 86 | 86 |  | 86 | 86 | 87 | 86 | 87 | 87 | 87 | 1513920
81 | Lakdhanvi 52 MW | [16 empty] | 2 | 11 |  | 11 | 16 | 16 | 16 | 0 |  |  | 72677
82 | Madanganj 102MW | [7 empty] | 2 | 15 | 15 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 30 |  | 80 | 80 | 80 | 80 | 0 |  |  | 495288
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 768184
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [7 empty] | 3 | 50 | 15 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 7 |  | 7 | 7 | 7 | 7 | 0 |  |  | 187200
88 | Ghorashal 78MW (MAX) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 0 | [15 empty] | 390432
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [6 empty] | 20 | 55 | 58 | 40 | 44 | 50 | 50 | 50 | 50 | 50 | 68 | 68 |  | 74 | 74 | 74 | 74 | 74 | 0 |  | 902640
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1194000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 35 | 35 | 40 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 32 | 980415
94 | Gagnagar (Orion) | [6 empty] | 4 | 24 | 24 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 15 | 65 |  | 64 | 64 | 65 | 65 | 0 |  |  | 359712
95 | Patenga 50MW | 19 | 0 |  |  |  | 0 | 12 | 36 | 40 | 40 | 41 | 42 | 40 | 46 | 46 | 47 | 47 | 46 |  | 46 | 39 | 39 | 39 | 41 | 39 | 40 | 760320
96 | Chattogram ECPV 108 MW | [7 empty] | 57 | 87 | 47 | 47 | 40 | 46 | 46 | 46 | 46 | 60 | 93 |  | 93 | 93 | 93 | 93 | 66 | 0 |  | 1022400
97 | Katpotti 51 MW | [6 empty] | 0 | 18 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 18 | 32 |  | 37 | 47 | 47 | 47 | 46 | 47 | 47 | 746640
98 | Bosila 108MW |  |  |  |  | 0 | 6 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 19 | 38 | 635520
99 | Madanganj-55 MW | [6 empty] | 0 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 50 | 50 | 55 | 55 | 55 | 15 | 15 | 582204
100 | Northern 55 MW | [5 empty] | 0 | 18 | 54 | 55 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 56 |  | 55 | 55 | 56 | 55 | 55 | 56 | 56 | 916896
101 | Kushiara 163 MW CCPP GT | 70 | 109 | 109 | 10 | 10 | 20 | 20 | 20 | 25 | 100 | 100 | 130 | 163 | 100 | 100 | 100 | 100 | 100 |  | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 2383510
102 | Sarishabari (Solar) | [8 empty] | 1.1 | 1 | 2 | 2 | 2 | 1.7 | 1.1 | 0.5 | 0 | [9 empty] | 11250
103 | Banco Energy 54MW | 18 | 18 | 0 |  |  | 0 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 993600
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 12 | 70 | 70 | 70 | 32 | 32 | 32 | 32 | 32 | 32 | 100 |  | 150 | 150 | 150 | 150 | 150 | 150 | 50 | 1521600
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [5 empty] | 0 | 26 | 47 | 70 | 70 | 70 | 70 | 70 | 36 | 31 | 30 | 30 | 33 |  | 89 | 96 | 96 | 96 | 39 | 0 |  | 961920
115 | Juldah 100 MW Unit-3 | 50 | 30 | 30 | 30 | 30 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1104000
116 | Chandpur Desh 200MW | 85 | 0 |  |  |  | 0 | 32 | 52 | 40 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 56 |  | 108 | 108 | 107 | 107 | 107 | 50 | 35 | 1049280
117 | Midland 150MW
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4484 | 4268 | 4171 | 4077 | 4080 | 4316 | 4622 | 4699.4 | 4936.53 | 4686 | 4665.42 | 4725 | 4819 | 4511.6 | 4707.2 | 4880.2 | 4763.1 | 5360 |  | 6023 | 6071 | 6015 | 5852 | 5421 | 5019 | 4893 | 117078479
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [7 empty] | 49 | 49 | 49 | 32 | 32 | 32 | 32 | 24 | 16 | 16 | 105 |  | 115 | 115 | 115 | 115 | 115 | 0 |  | 873600
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [16 empty] | 38 | 44 |  | 44 | 44 | 44 | 44 | 44 | 0 |  | 238560
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 21 | 0 |  |  |  | 0 | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 70 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1847040
130
131
132
133
| Summit Barisal 110 MW | 0 | [15 empty] | 0 | 48 |  | 48 | 48 | 48 | 48 | 48 | 0 |  | 237120
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 94 | 61 | 59 | 62 | 61 | 65 | 96 | 95 | 95 | 66 | 65 | 66 | 65 | 65 | 65 | 67 | 66 | 96 |  | 97 | 96 | 96 | 95 | 95 | 96 | 96 | 1907905
| Bhola CCPP 194MW | 166 | 190 | 188 | 191 | 191 | 191 | 171 | 190 | 190 | 190 | 188 | 188 | 187 | 187 | 186 | 183 | 185 | 187 |  | 188 | 188 | 188 | 189 | 176 | 190 | 188 | 4521873
140 | Bhola (Venture) 33MW | 11 | 11 | 10 | 10 | 10 | 11 | 11 | 10 | 9 | 9 | 11 | 12 | 13 | 13 | 12 | 12 | 12 | 12 |  | 14 | 14 | 14 | 14 | 13 | 15 | 11 | 278609
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | 40 | 8 | 0 |  |  | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 778125
143 | Gopalganj Peaking | [16 empty] | 25 | 78 |  | 72 | 66 | 60 | 30 | 0 |  |  | 246272
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 259 | 259 | 259 | 259 | 252 | 248 | 247 | 539 | 538 | 536 | 537 | 537 | 537 | 537 | 536 | 537 | 627 | 684 |  | 684 | 684 | 684 | 684 | 684 | 685 | 247 | 11589091
147 | Bheramara 360 MW | 445 | 444 | 448 | 400 | 400 | 445 | 446 | 390 | 360 | 360 | 360 | 360 | 423 | 330 | 330 | 330 | 330 | 300 |  | 380 | 380 | 380 | 380 | 380 | 320 | 350 | 9488160
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 175 | 230 | 278 | 296 | 296 | 292 | 293 | 293 | 293 | 292 |  | 293 | 253 | 217 | 150 | 150 | 149 | 149 | 5099600
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 50 |  | 50 | 50 | 50 | 0 |  |  |  | 165704
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 183 | 181 | 176 | 179 | 179 | 190 | 193 | 194 | 177 | 182 | 187 | 190 | 199 | 206 | 187 | 180 | 183 | 179 |  | 194 | 185 | 188 | 183 | 184 | 180 | 181 | 4655000
| Sirajgonj Unit-3 225 MW(Oil) | [15 empty] | 0
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [15 empty] | 9 | 10 | 42 |  | 42 | 41 | 41 | 13 | 0 |  |  | 159388
162 | Bogra (GBB) | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510240
163 | Bogra (EPL) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 14 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 333144
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 5 | 5 | 3 | 3 | 3 | 3 | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 143460
165 | Amnura 50MW | [6 empty] | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 673820
166 | Katakhali (Northern) | [8 empty] | 40 | 50 | 50 | 8 | 8 | 8 | 8 | 8 | 8 | 24 |  | 50 | 50 | 50 | 50 | 0 |  |  | 381498
167 | Katakhali Peaking
168 | Santahar Peaking | [17 empty] | 36 |  | 37 | 36 | 36 | 29 | 29 | 29 | 29 | 241882
169 | Rajlanka 52 MW | 25 | 8 | 0 |  | 0 | 30 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 979200
170 | Chapainawabganj-100 MW | [17 empty] | 102 |  | 102 | 102 | 102 | 102 | 102 | 43 | 0 | 571856
171 | Paramount Baghabari | [9 empty] | 10 | 46 | 45 | 48 | 44 | 36 | 0 | 11 | 21 |  | 2 | 2 | 2 | 2 |  |  |  | 271818
172
173 | Rangpur GT | [7 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 |  | 16 | 16 | 17 | 17 | 17 | 0 |  | 239000
175 | Saidpur GT | [6 empty] | 0 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 15 | 16 | 16 | 17 | 18 | 0 |  | 277000
176
177
178
178 | Western Zone Total | 1434 | 1350 | 1330 | 1291 | 1283 | 1370 | 1515 | 1913 | 1947 | 1995 | 2068 | 2048 | 2119 | 2025 | 1952 | 1910 | 2076 | 2618 |  | 2725 | 2668 | 2630 | 2444 | 2337 | 1986 | 1531 | 46708965