## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-11-2025 | [28 empty] | Date: | 04-11-2025 | [28 empty] | Date: | 04-11-2025 | [28 empty] | Date: | 04-11-2025 | [28 empty] | Date: | 04-11-2025 | [14 empty] | Date: | 04-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 47.8 | 0 | 33 | 15 | 45 | 0 | 35 | 152 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 70 | 22 | 21 | 0 | 300 | 0 | 0 | 19 | 0 | 20 | 50 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 28 | 650 | 0 | 0 | 26 | 0 | 65 | 223 | 0 | 0 | 0 | 583 | 0 | 51 | 50 | 0 | 305 | 280 | 280 | 5 | 0 | 10 | 48 | 103 | 96 | 0 | 17 | 0 | 66 | 0 | 0 | 0 | 315 | 0 | 372 | 0 | 0 | 158 | 8 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 48 | 48 | 73 | 0 | 0 | 0 | 6112.8 | 903 | 338 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1086 | 0 | 1327.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 501 | 795 | 0 | 5906.89 | 12019.69 | 102.05
01:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 45.4 | 0 | 33 | 0 | 0 | 0 | 17 | 149 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 300 | 0 | 0 | 10 | 0 | 33 | 0 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 28 | 650 | 0 | 0 | 18 | 0 | 30 | 223 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 0 | 300 | 280 | 280 | 5 | 0 | 10 | 25 | 104 | 51 | 0 | 19 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 302 | 0 | 0 | 150 | 8 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 49 | 49 | 73 | 0 | 0 | 0 | 5614.4 | 904 | 334 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 1319.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 500 | 602 | 0 | 5623.16 | 11237.56 | 102.04
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 90 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20.5 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 12 | 12 | 0 | 216 | 0 | 28 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 572 | 0 | 51 | 0 | 0 | 300 | 280 | 280 | 5 | 0 | 10 | 0 | 104 | 0 | 0 | 19 | 0 | 62 | 0 | 0 | 0 | 310 | 0 | 306 | 0 | 0 | 140 | 8 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 49 | 24 | 74 | 0 | 0 | 0 | 5308.5 | 904 | 330 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1077 | 0 | 1219.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 418 | 605 | 0 | 5447.88 | 10756.38 | 102.03
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 570 | 0 | 51 | 0 | 0 | 300 | 280 | 280 | 5 | 0 | 10 | 0 | 104 | 0 | 0 | 19 | 0 | 64 | 0 | 0 | 0 | 310 | 0 | 310 | 0 | 0 | 141 | 6 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 16 | 8 | 74 | 0 | 0 | 0 | 5151 | 904 | 330 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 0 | 1080.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 379 | 605 | 0 | 5258.5 | 10409.5 | 102.02
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 38 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 560 | 0 | 51 | 0 | 0 | 300 | 280 | 280 | 5 | 0 | 10 | 0 | 104 | 0 | 0 | 19 | 0 | 64 | 0 | 0 | 0 | 310 | 0 | 308 | 0 | 0 | 143 | 6 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 16 | 8 | 74 | 0 | 0 | 0 | 5139 | 904 | 324 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1029 | 0 | 934.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 305 | 602 | 0 | 4981.06 | 10120.06 | 102.01
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 503 | 0 | 51 | 0 | 0 | 300 | 280 | 280 | 5 | 0 | 10 | 0 | 104 | 0 | 0 | 19 | 0 | 62 | 0 | 0 | 0 | 305 | 0 | 331 | 0 | 0 | 144 | 6 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 16 | 8 | 74 | 0 | 0 | 0 | 5094 | 878 | 325 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 841 | 0 | 850.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 304 | 604 | 0 | 4662.21 | 9756.21 | 102
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 325 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 515 | 0 | 51 | 0 | 0 | 300 | 330 | 280 | 5 | 0 | 10 | 0 | 104 | 0 | 0 | 19 | 0 | 52 | 0 | 0 | 0 | 315 | 0 | 324 | 0 | 0 | 153 | 6 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 16 | 8 | 74 | 0 | 0 | 0 | 5157 | 878 | 325 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 841.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 303 | 606 | 0 | 4663.31 | 9820.31 | 101.99
07:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 5 | 0 | 21 | 21 | 0 | 280 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.2 | 216 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 590 | 3 | 51 | 0 | 0 | 300 | 330 | 320 | 8 | 0 | 38 | 0 | 104 | 0 | 0 | 19 | 0 | 50 | 0 | 9 | 0 | 320 | 0 | 353 | 0 | 0 | 155 | 6 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 22 | 12 | 73 | 0 | 3.56 | 0 | 5307.76 | 878 | 325 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 965 | 0 | 965.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.21 | 5 | 0 | 0 | 7 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.7 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.6 | 17 | 0.07 | 0 | 0 | 110 | 220 | 0 | 306 | 606 | 0 | 5056.27 | 10364.03 | 101.98
08:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 7.5 | 0 | 13 | 0 | 0 | 0 | 0 | 32 | 0 | 280 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 13 | 0 | 0 | 21 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0.36 | 219 | 0 | 8 | 650 | 0 | 0 | 0 | 0 | 8 | 189 | 0 | 0 | 0 | 575 | 6 | 51 | 15 | 0 | 300 | 280 | 280 | 20 | 0 | 38 | 7 | 103 | 19 | 0 | 19 | 0 | 54 | 0 | 33 | 0 | 310 | 0 | 321 | 0 | 0 | 148 | 6 | 0 | 79 | 30 | 0 | 0 | 161 | 0 | 46 | 47 | 73 | 1 | 18.92 | 0 | 5327.78 | 878 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1004 | 0 | 1118.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.91 | 35 | 0 | 0 | 30.81 | 179 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 2.74 | 0 | 0 | 0 | 13 | 10 | 0 | 0 | 0 | 2.5 | 82 | 0.22 | 0 | 0 | 110 | 180 | 0 | 305 | 500 | 0 | 5119.64 | 10447.42 | 101.97
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 17.5 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 0 | 280 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 1.13 | 176 | 0 | 4 | 650 | 0 | 0 | 0 | 0 | 16 | 188 | 0 | 0 | 0 | 578 | 3 | 43 | 0 | 0 | 290 | 280 | 260 | 20 | 0 | 39 | 16 | 103 | 31 | 0 | 19 | 0 | 56 | 0 | 26 | 0 | 305 | 0 | 300 | 0 | 0 | 145 | 6 | 0 | 76 | 30 | 0 | 0 | 160 | 0 | 49 | 24 | 33 | 2 | 33.68 | 0 | 5187.31 | 878 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 1009 | 0 | 1110.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.71 | 61 | 0 | 0 | 48.13 | 172 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 4.17 | 0 | 0 | 0 | 25 | 34 | 0 | 0 | 0 | 4.4 | 132 | 0.38 | 0 | 0 | 110 | 180 | 0 | 303 | 495 | 0 | 5270.02 | 10457.33 | 101.96
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 17.5 | 0 | 32 | 0 | 0 | 0 | 10 | 33 | 0 | 280 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 25 | 0 | 20 | 21 | 0 | 280 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.85 | 176 | 0 | 4 | 650 | 0 | 0 | 0 | 0 | 16 | 220 | 0 | 0 | 0 | 596 | 6 | 43 | 0 | 0 | 275 | 280 | 260 | 20 | 0 | 36 | 17 | 100 | 31 | 0 | 19 | 0 | 60 | 0 | 31 | 0 | 310 | 0 | 361 | 0 | 0 | 148 | 6 | 0 | 75 | 30 | 0 | 0 | 160 | 0 | 48 | 24 | 33 | 2 | 44.01 | 0 | 5348.36 | 878 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 1010 | 0 | 950.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.99 | 88 | 0 | 0 | 55.35 | 173 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 5.03 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5.6 | 168 | 0.45 | 0 | 0 | 110 | 180 | 0 | 304 | 500 | 0 | 5245.8 | 10594.16 | 101.95
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 17.5 | 0 | 49 | 0 | 95 | 4 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 31 | 17 | 20 | 21 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 12 | 12 | 3.48 | 176 | 7 | 2 | 650 | 0 | 0 | 4 | 0 | 40 | 220 | 0 | 0 | 0 | 607 | 8 | 43 | 38 | 0 | 280 | 280 | 260 | 20 | 0 | 35 | 35 | 100 | 66 | 0 | 19 | 0 | 60 | 0 | 43 | 0 | 315 | 0 | 332 | 0 | 0 | 159 | 6 | 0 | 77 | 30 | 0 | 0 | 161 | 0 | 48 | 24 | 33 | 2 | 38.18 | 0 | 5732.16 | 878 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 73 | 964 | 0 | 921.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.59 | 84 | 0 | 0 | 66.14 | 188 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 5.6 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 6.4 | 188 | 0.52 | 0 | 0 | 110 | 180 | 0 | 305 | 500 | 0 | 5240.18 | 10972.34 | 101.94
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 17.5 | 2 | 104 | 30 | 270 | 35 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 32 | 70 | 19 | 21 | 0 | 280 | 10 | 15 | 0 | 0 | 2 | 0 | 8 | 7 | 24 | 12 | 3.03 | 126 | 39 | 6 | 650 | 0 | 0 | 23 | 0 | 88 | 217 | 0 | 0 | 0 | 582 | 16 | 43 | 107 | 0 | 280 | 280 | 260 | 20 | 0 | 29 | 48 | 100 | 117 | 0 | 19 | 0 | 68 | 5 | 63 | 4 | 310 | 0 | 334 | 0 | 0 | 156 | 6 | 0 | 78 | 30 | 0 | 0 | 161 | 0 | 48 | 28 | 33 | 2 | 46.94 | 0 | 6375.47 | 897 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75 | 953 | 0 | 926.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.03 | 95 | 0 | 0 | 64.79 | 178 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 5.1 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 6.4 | 190 | 0.66 | 0 | 0 | 110 | 220 | 0 | 407 | 539 | 0 | 5439.35 | 11814.82 | 101.93
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 17.5 | 17 | 131 | 30 | 277 | 40 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 31 | 70 | 12 | 21 | 0 | 280 | 17 | 15 | 0 | 0 | 2 | 0 | 10 | 17 | 24 | 12 | 1.71 | 126 | 50 | 10 | 650 | 0 | 0 | 37 | 0 | 103 | 217 | 0 | 0 | 0 | 580 | 4 | 43 | 115 | 0 | 280 | 280 | 260 | 13 | 0 | 31 | 51 | 99 | 117 | 0 | 19 | 26 | 60 | 16 | 44 | 15 | 320 | 0 | 374 | 0 | 0 | 157 | 6 | 0 | 78 | 30 | 0 | 0 | 161 | 6 | 48 | 28 | 33 | 2 | 37.13 | 0 | 6478.34 | 898 | 278 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 1063 | 0 | 1018.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 74 | 0 | 0 | 49.48 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 6.1 | 180 | 0.32 | 0 | 0 | 110 | 220 | 0 | 506 | 552 | 0 | 5742.56 | 12220.9 | 101.92
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17.5 | 17 | 145 | 30 | 277 | 55 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 24 | 52 | 15 | 21 | 0 | 280 | 15 | 15 | 0 | 0 | 2 | 0 | 31 | 17 | 24 | 12 | 1.32 | 126 | 45 | 6 | 650 | 0 | 0 | 39 | 0 | 91 | 217 | 0 | 0 | 0 | 573 | 3 | 43 | 110 | 0 | 275 | 280 | 260 | 5 | 0 | 34 | 45 | 99 | 109 | 0 | 19 | 25 | 76 | 16 | 52 | 15 | 300 | 0 | 389 | 0 | 0 | 147 | 6 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 33 | 2 | 27.32 | 0 | 6513.14 | 905 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59 | 1086 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.09 | 79 | 0 | 0 | 40.44 | 181 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 3.06 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 5.1 | 153 | 0.26 | 0 | 0 | 100 | 180 | 0 | 502 | 537 | 0 | 5637.95 | 12151.09 | 101.91
15:00 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17.5 | 17 | 112 | 45 | 277 | 55 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 11 | 52 | 19 | 21 | 0 | 280 | 15 | 15 | 0 | 0 | 0 | 0 | 31 | 17 | 24 | 12 | 0.9 | 126 | 34 | 3 | 650 | 0 | 0 | 39 | 0 | 102 | 217 | 0 | 0 | 0 | 581 | 1 | 43 | 108 | 0 | 250 | 280 | 260 | 5 | 0 | 36 | 50 | 99 | 114 | 0 | 19 | 17 | 70 | 16 | 22 | 15 | 310 | 0 | 386 | 0 | 20 | 155 | 6 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 33 | 1 | 23.92 | 0 | 6479.32 | 906 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 1116 | 0 | 1039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.97 | 55 | 0 | 0 | 37.12 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.21 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3.6 | 108 | 0 | 0 | 0 | 100 | 220 | 0 | 501 | 550 | 0 | 5641.9 | 12121.22 | 101.9
16:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17.5 | 17 | 112 | 60 | 277 | 55 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 5 | 52 | 20 | 21 | 0 | 330 | 16 | 15 | 7 | 0 | 6 | 0 | 31 | 0 | 12 | 12 | 0.23 | 80 | 33 | 2 | 650 | 0 | 0 | 13 | 0 | 100 | 217 | 0 | 0 | 0 | 584 | 1 | 43 | 117 | 0 | 250 | 280 | 260 | 5 | 0 | 37 | 51 | 100 | 116 | 0 | 19 | 16 | 64 | 16 | 7 | 28 | 310 | 0 | 386 | 0 | 20 | 156 | 6 | 0 | 78 | 30 | 0 | 0 | 160 | 0 | 48 | 28 | 34 | 0 | 12.69 | 0 | 6426.42 | 906 | 255 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.61 | 1094 | 0 | 1088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.11 | 28 | 0 | 0 | 13.59 | 180 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 1.1 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.7 | 30 | 0.11 | 5 | 0 | 110 | 220 | 0 | 504 | 550 | 0 | 5447.22 | 11873.64 | 101.89
17:00 | 0 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 33 | 17 | 113 | 85 | 277 | 55 | 35 | 108 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 70 | 19 | 21 | 0 | 310 | 22 | 48 | 40 | 0 | 6 | 15 | 31 | 0 | 24 | 12 | 0.01 | 80 | 38 | 2 | 650 | 30 | 0 | 39 | 0 | 102 | 183 | 0 | 0 | 0 | 575 | 0 | 43 | 117 | 0 | 250 | 280 | 230 | 5 | 0 | 37 | 51 | 100 | 120 | 0 | 19 | 17 | 64 | 16 | 1 | 28 | 310 | 0 | 388 | 0 | 20 | 156 | 6 | 0 | 78 | 30 | 0 | 0 | 160 | 5 | 48 | 28 | 34 | 0 | 1.15 | 0 | 6558.16 | 906 | 252 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1070 | 0 | 1170 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.7 | 3 | 0 | 0 | 1.7 | 183 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0.14 | 0 | 0 | 30 | 1 | 34 | 0 | 0 | 0 | 0.2 | 8 | 0.01 | 22 | 0 | 110 | 220 | 0 | 504 | 545 | 2 | 5466.75 | 12024.91 | 101.88
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 44 | 35 | 121 | 122 | 277 | 55 | 35 | 108 | 0 | 200 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 330 | 65 | 83 | 55 | 0 | 8 | 65 | 67 | 0 | 24 | 12 | 0 | 126 | 91 | 14 | 650 | 126 | 0 | 50 | 15 | 103 | 218 | 0 | 0 | 0 | 582 | 0 | 51 | 123 | 0 | 270 | 280 | 230 | 5 | 0 | 38 | 65 | 100 | 133 | 0 | 8 | 102 | 72 | 34 | 0 | 28 | 315 | 0 | 386 | 0 | 40 | 155 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 7394 | 905 | 243 | 0 | 33 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 1455 | 0 | 0 | 0 | 15 | 63 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 95 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 110 | 220 | 0 | 503 | 550 | 17 | 6263 | 13657 | 101.87
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 52 | 35 | 149 | 122 | 277 | 55 | 35 | 108 | 0 | 200 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 142 | 25 | 0 | 0 | 350 | 95 | 83 | 60 | 0 | 0 | 65 | 67 | 0 | 24 | 12 | 0 | 126 | 102 | 17 | 650 | 100 | 0 | 35 | 25 | 100 | 218 | 0 | 0 | 0 | 572 | 0 | 51 | 125 | 0 | 265 | 280 | 230 | 5 | 0 | 38 | 90 | 100 | 181 | 0 | 19 | 70 | 70 | 52.2 | 0 | 29 | 310 | 0 | 386 | 0 | 40 | 156 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 7511.2 | 906 | 233 | 0 | 40 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 1421 | 0 | 0 | 0 | 0 | 70 | 0 | 42 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 70 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 503 | 590 | 17 | 6237 | 13748.2 | 101.86
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 51 | 17 | 142 | 108 | 277 | 55 | 35 | 90 | 0 | 200 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 125 | 25 | 7 | 0 | 350 | 92 | 48 | 42 | 0 | 0 | 65 | 67 | 0 | 24 | 12 | 0 | 126 | 100 | 22 | 650 | 65 | 0 | 32 | 25 | 96 | 218 | 0 | 0 | 0 | 580 | 0 | 51 | 123 | 0 | 260 | 280 | 230 | 5 | 0 | 38 | 90 | 100 | 180 | 0 | 20 | 30 | 78 | 25 | 0 | 29 | 315 | 0 | 390 | 0 | 57 | 154 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 7349 | 906 | 234 | 0 | 36 | 62 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 1419 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 70 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 503 | 595 | 35 | 6186 | 13535 | 101.86
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 50 | 17 | 142 | 108 | 277 | 55 | 35 | 108 | 0 | 200 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 125 | 19 | 21 | 0 | 350 | 84 | 51 | 43 | 0 | 0 | 65 | 67 | 0 | 24 | 12 | 0 | 126 | 100 | 29 | 650 | 65 | 0 | 32 | 25 | 94 | 220 | 0 | 0 | 0 | 580 | 0 | 51 | 123 | 0 | 255 | 280 | 230 | 5 | 0 | 38 | 90 | 100 | 174 | 0 | 20 | 30 | 72 | 25 | 0 | 29 | 310 | 0 | 372 | 0 | 57 | 156 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 47 | 28 | 34 | 0 | 0 | 0 | 7335 | 905 | 232 | 0 | 36 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 0 | 1420 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 502 | 580 | 17 | 6093 | 13428 | 101.85
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 49.5 | 17 | 142 | 108 | 286 | 55 | 35 | 108 | 0 | 200 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 125 | 22 | 21 | 0 | 350 | 58 | 51 | 44 | 0 | 0 | 50 | 67 | 0 | 24 | 12 | 0 | 126 | 62 | 32 | 650 | 63 | 0 | 32 | 25 | 96 | 220 | 0 | 0 | 0 | 580 | 0 | 51 | 128 | 0 | 260 | 280 | 230 | 5 | 0 | 38 | 90 | 102 | 177 | 0 | 20 | 31 | 76 | 25 | 0 | 29 | 305 | 0 | 390 | 0 | 57 | 156 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 47 | 28 | 34 | 0 | 0 | 0 | 7304.5 | 903 | 224 | 0 | 36 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 1428.16 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 455 | 560 | 17 | 6019.16 | 13323.66 | 101.84
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 41.8 | 17 | 142 | 108 | 195 | 55 | 35 | 108 | 0 | 200 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 108 | 20 | 21 | 0 | 350 | 57 | 16 | 44 | 0 | 14 | 50 | 67 | 0 | 24 | 12 | 0 | 126 | 65 | 32 | 650 | 60 | 0 | 32 | 25 | 91 | 222 | 0 | 0 | 0 | 575 | 0 | 51 | 132 | 0 | 260 | 280 | 230 | 5 | 0 | 38 | 90 | 102 | 172 | 0 | 20 | 29 | 78 | 25 | 0 | 29 | 310 | 0 | 366 | 0 | 57 | 152 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 47 | 28 | 34 | 0 | 0 | 0 | 7122.8 | 903 | 224 | 0 | 35 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 0 | 1431.11 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 110 | 180 | 0 | 455 | 560 | 17 | 5934.11 | 13056.91 | 101.83
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 17.5 | 17 | 142 | 90 | 195 | 55 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 90 | 22 | 21 | 0 | 320 | 55 | 16 | 44 | 0 | 9 | 33 | 67 | 0 | 24 | 12 | 0 | 126 | 64 | 34 | 650 | 47 | 0 | 32 | 0 | 92 | 222 | 0 | 0 | 0 | 579 | 0 | 51 | 127 | 0 | 260 | 280 | 230 | 5 | 0 | 20 | 91 | 102 | 167 | 0 | 20 | 0 | 80 | 0 | 0 | 29 | 305 | 0 | 386 | 0 | 57 | 151 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 6876.5 | 903 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 1430.79 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 110 | 180 | 0 | 454 | 560 | 17 | 5764.79 | 12641.29 | 101.82
Total KWH | 0 | 1153920 | 444480 | 0 | 0 | 0 | 0 | 0 | 7362000 | 0 | 0 | 519120 | 256320 | 1938960 | 973920 | 3374727 | 678785 | 535211 | 1584000 | 0 | 5992000 | 0 | 0 | 0 | 142246 | 5917066 | 0 | 0 | 204049 | 1176000 | 478200 | 466920 | 0 | 7556363.64 | 573327 | 373855 | 383040 | 0 | 289440 | 368403 | 538752 | 64722 | 320640 | 192960 | 13320 | 3809947 | 879900 | 461280 | 15643636.36 | 490109 | 0 | 492960 | 126295.2 | 1451091 | 5077324 | 0 | 0 | 0 | 13805453 | 48060 | 1161472 | 1664363 | 0 | 6754500 | 7228700 | 6314000 | 216960 | 0 | 691488 | 1033920 | 2429620 | 2139360 | 0 | 446610 | 371640 | 1565760 | 270302 | 336600 | 289792 | 7539500 | 0 | 8817000 | 0 | 360840 | 3646964 | 165552 | 0 | 1878720 | 715776 | 0 | 0 | 3329600 | 189360 | 1021200 | 636000 | 1091520 | 13450 | 288340 | 0 | 148767711.2 | 21697454 | 6764256 | 0 | 159360 | 186624 | 912000 | 0 | 0 | 0 | 0 | 0 | 459360 | 25003640 | 0 | 27026545 | 0 | 0 | 0 | 35808 | 357504 | 0 | 215072 | 0 | 0 | 356018 | 662025 | 127866 | 0 | 396752 | 4344909 | 0 | 0 | 0 | 0 | 0 | 9022690 | 0 | 33840 | 0 | 0 | 508400 | 242051 | 680208 | 0 | 0 | 0 | 42100.32 | 1270850 | 3226 | 690336 | 0 | 2614000 | 5213580 | 0 | 10000777 | 13867636.36 | 138000 | 133032887.68 | 281800598.88

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-11-2025 | during | 05-11-2025 | during | 05-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 272 | 323 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 200 | 450 | 450 | 225 | 225 | GT-2 U/M
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 335 | 335 | 280 | 280 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 52 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 122 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 25 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 0 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 270 | 277 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 104 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 2 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 280 | 350 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1871.5 | 2260 | 5925.1 | 5892.1 | 4245.81 | 4284.81
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 23 | 35 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 126 | 126 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 88 | 100 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 67 | 48 | 70 | 48 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 17 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 60 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.03 | 0 | 1.34 | 0 | 1.34 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 83 | 300 | 300 | 100 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 7 | 0 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 39 | 102 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 10 | 95 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 100 | 159.86 | 159.86 | 159.86 | 159.86 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 582 | 572 | 612 | 612 | 582 | 582 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 28 | 0 | 28 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1828.03 | 2351 | 3054.06 | 3047.72 | 2556.7 | 2550.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 280 | 280 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 260 | 230 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 265 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 20 | 5 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 107 | 125 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 4 | 29 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 117 | 181 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 70 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 5 | 52.2 | 52.2 | 52.2 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 13.5 | 24.5 | 13.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1443 | 1605.2 | 2600.56 | 2551.56 | 2058.86 | 2009.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-11-2025 | during | 05-11-2025 | during | 05-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 34 | 157.5 | 157.5 | 114 | 114 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 28 | 28 | 28 | 28 | 28 | 28 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.94 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 6 | 6 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 157.94 | 127 | 361.9 | 310 | 264.9 | 213
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 40 | 30 | 30 | 0 | 0 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 161 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 334 | 386 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1075 | 1168 | 1235 | 1235 | 1094 | 1094
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 897 | 906 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 42 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 275 | 233 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 953 | 1102 | 0 | 0 | 1140 | 1140 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2238 | 2361 | 2403 | 2318 | 2782 | 2697
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 407 | 503 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 539 | 590 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1276.66 | 1550 | 1218 | 1217 | 1077 | 1076
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 55.03 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 178 | 190 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 367 | 409 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Engine Problem
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.1 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 926.37 | 1421 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.79 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1691.29 | 2152 | 3182.46 | 3015.87 | 3009.68 | 2843.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 104 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 190 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 233.4 | 174 | 497.8 | 262 | 463.8 | 228
System Total |  |  |  |  | 28823.2 | 28364.095 | 11814.82 | 13748.2 | 20477.88 | 19849.25 | 17552.75 | 16996.12
Forecast Scenario (05-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12720 |  | 0 |  | 12720
|  |  |  | 1:00 | 11830 |  | 0 |  | 11830
|  |  |  | 2:00 | 11250 |  | 0 |  | 11250
|  |  |  | 3:00 | 10810 |  | 0 |  | 10810
|  |  |  | 4:00 | 10520 |  | 0 |  | 10520
|  |  |  | 5:00 | 10000 |  | 0 |  | 10000
|  |  |  | 6:00 | 10100 |  | 0 |  | 10100
|  |  |  | 7:00 | 10560 |  | 0 |  | 10560
|  |  |  | 8:00 | 10540 |  | 0 |  | 10540
|  |  |  | 9:00 | 10550 |  | 0 |  | 10550
|  |  |  | 10:00 | 10690 |  | 0 |  | 10690
|  |  |  | 11:00 | 11070 |  | 0 |  | 11070
|  |  |  | 12:00 | 11910 |  | 0 |  | 11910
|  |  |  | 13:00 | 12320 |  | 0 |  | 12320
|  |  |  | 14:00 | 12250 |  | 0 |  | 12250
|  |  |  | 15:00 | 12220 |  | 0 |  | 12220
|  |  |  | 16:00 | 11970 |  | 0 |  | 11970
|  |  |  | 17:00 | 12120 |  | 0 |  | 12120
|  |  |  | 18:00 | 13850 |  | 0 |  | 13850
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 13920 |  | 0 |  | 13920
|  |  |  | 19:30 | 13700 |  | 0 |  | 13700
|  |  |  | 20:00 | 13580 |  | 0 |  | 13580
|  |  |  | 21:00 | 13470 |  | 0 |  | 13470
|  |  |  | 22:00 | 13200 |  | 0 |  | 13200
|  |  |  | 23:00 | 13000 |  | 0 |  | 13000
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 11910.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13920.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13920.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 284.45 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:48 hrs on 05-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11814.82 | MW | 12:00 Hr. | Energy Generated |  |  | 281.8006 |  | MKWHr.
| Day Peak Demand |  |  | 11814.82 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.309 |  | MKWHr.
| Evening Peak Generation |  |  | 13748.2 | MW | 19:00 Hr. | Energy Demand |  |  | 282.1096 |  | MKWHr.
| Evening Peak Demand |  |  | 13820.31 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.3 |  | °C
| Minimum Generation of the Day |  |  | 9756.21 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 816.46 |  | MMCFD
| Maximum Generation of the Day |  |  | 13748.2 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.4267 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 27.7725 | 0 | 12.7777 | 0 | 0 | 0.20405 | 0 | 0 | 40.7543 | Gas | 114.0594 | Gas | 399173626.7188
| Chattogram Zone |  |  | 5.5386 | 29.4491 | 6.2561 | 0 | 3.8099 | 0.06138 | 0 | 0.28944 | 45.4045 | Coal | 78.3211 | Coal | 506038068.1564
| Cumilla Zone |  |  | 25.2433 | 0 | 5.7694 | 0 | 0 | 0.3366 | 1.5658 | 0 | 32.9151 | HFO | 29.7489 | HFO | 527213684.488
| Mymensingh Zone |  |  | 1.0915 | 0 | 1.8466 | 0 | 0 | 0.30179 | 0 | 0 | 3.2399 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.454 | Hydro | 3.8099 | Hydro | 380994.7
| Khulna Zone |  |  | 6.7643 | 25.0036 | 0.34598 | 0 | 0 | 0.45936 | 22.6095 | 0 | 55.1827 | Solar | 4.37 | Solar | 70732727.2512
| Barishal Zone |  |  | 7.8276 | 23.8684 | 0.82834 | 0 | 0 | 0.003226 | 0 | 0 | 32.5276 | Import | 51.2018 | Import | 303256722.34
| Rajshahi Zone |  |  | 13.3676 | 0 | 0.73625 | 0 | 0 | 1.4486 | 27.0265 | 0 | 42.579 | Wind | 0.28944 | Wind | 4257662.4
| Rangpur Zone |  |  | 0 | 0 | 1.1886 | 0 | 0 | 1.555 | 0 | 0 | 2.7436
| Total |  |  | 114.0594 | 78.3211 | 29.7489 | 0 | 3.8099 | 4.37 | 51.2018 | 0.28944 | 281.8006
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 399173626.7188 |  | Hydro | 380994.7
|  |  |  | Coal | 506038068.1564 |  | Solar | 70732727.2512
|  |  |  | HFO | 527213684.488 |  | Import | 303256722.34
|  |  |  | HSD | 0 |  | Wind | 4257662.4
[5 empty] | Total: | 181,10,53,486 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6975 | Peak Hr Flow | 906.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50395474.26 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.0265 | Peak Hr Flow | 1421.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2326 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5658 | Peak Hr Flow | 70.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2684 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.2898 | Peak Hr Flow | 2397.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5080
|  |  |  | Chattogram |  | 0 |  | 1443
|  |  |  | Cumilla |  | 0 |  | 1328
|  |  |  | Mymensingh |  | 69 |  | 1042
|  |  |  | Sylhet |  | 0 |  | 618
|  |  |  | Khulna |  | 0 |  | 1457
|  |  |  | Barishal |  | 0 |  | 395
|  |  |  | Rajshahi |  | 0 |  | 1124
|  |  |  | Rangpur |  | 0 |  | 747
|  |  |  | Total |  | 69 |  | 13234
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:14 | 09:18 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Scheduled S/D Due to Annual
maintenance work
| 08:16 | 09:17 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Scheduled S/D Due to Annual
maintenance work
| 08:16 | 16:12 | Naogaon 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance.
| 08:17 | 16:12 | Naogaon 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance.
| 08:23 | 09:52 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to 33 Kv bus DS Redhot maintenance | [7 empty] | 20.0MW load
interrup.
| 08:23 | 09:52 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to 33 Kv bus DS Redhot maintenance | [7 empty] | 20.0MW load
interrup.
| 08:25 | 15:34 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to
Annual Maintenance and from Bog-Sherpur 132/33kV end Due to Annual maintenance work.
| 08:25 | 16:46 | Benapole 132/33kV S/S Bus-A Scheduled S/D Due to Annual Maintenance
| 08:42 | 18:00 | Jaldhaka-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance. and from Jaldhaka 132/33kV end Due to Annual maintenance work
| 08:44 | 14:42 | Keranigonj 230/132/33kV S/S ATR-3 HT Scheduled S/D Due to Annual Maintenance Work
| 08:55 | 16:53 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end Due to
Annual maintenance.
| 08:57 | 18:26 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Annual Maintenance.
| 08:57 | 16:44 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Annual Maintenance.
| 09:02 | 16:46 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Scheduled S/D Due to Annual
Maintenance
| 09:02 | 18:31 | New Tongi-Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance
| 09:06 | 16:22 | Panchagar-Thakurgaon 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due to
Annual Maintenance and from Panchagarh 132/33kV end Due to Annual Maintenance
| 09:07 | 16:56 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Scheduled S/D from BIPTC end Due to For annual
maintenance
| 09:29 |  | Gopalganj 400/132kV S/S 132kV Bus-01 Scheduled S/D Due to Annual Maintenance
| 09:32 | 16:42 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to Annual maintenance work
| 09:32 | 16:42 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to Annual maintenance work
|  | 09:44 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
|  | 09:44 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
| 09:56 | 14:42 | Mithapukur 132/33kV S/S TR-2 (414T) LT Scheduled S/D Due to for maintenance work
| 09:56 | 14:41 | Mithapukur 132/33kV S/S TR-2 (414T) HT Scheduled S/D Due to for maintenance work
| 09:59 | 15:30 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance of TR-02
| 10:00 | 15:30 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintenance of TR-02
| 10:20 | 11:25 | Baroirhat-Hathazari 132 kV Ckt-2 Forced S/D from Baroirhat 132/33kV end.
|  | 12:28 | Sylhet-Sylhet (South) 132KV Ckt-2 is restored.
| 12:45 |  | Meghnaghat 450 MW CCPP GT-2 was shut down due to gas shortage
|  | 13:45 | Gopalganj 132/33kV S/S T2 HT is restored.
|  | 13:45 | Gopalganj 132/33kV S/S T2 LT is restored.
| 13:52 | 16:41 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to 33 KV Bus DS Redhot maintenance | [7 empty] | 34.0MW load
interrup.
| 13:52 | 16:41 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to 33 KV Bus DS Redhot maintenance | [7 empty] | 34.0MW load
interrup.
|  | 14:12 | Juldah 132/33kV S/S 132/33 KV 406T T-1 HT is restored.
|  | 14:16 | Juldah 132/33kV S/S 132/33 KV 406T T-1 LT is restored.
|  | 14:47 | GPH 230/33kV S/S Transformer -2 (D07) HT is restored.
| 15:42 | 17:51 | Chandina 132/33kV S/S TR-2 LT Project Work S/D Due to For tariff meter testing work by
metering division power grid
| 15:42 | 17:50 | Chandina 132/33kV S/S TR-2 HT Project Work S/D Due to For tariff meter testing by
metering division power grid
|  | 15:55 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 is restored.
| 16:14 | 16:41 | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Barishal 132/33kV end Due to Charger load | [7 empty] | 22.0MW load
|  |  | shift | [7 empty] | interrup. Barishal
132/33kV end
| 16:18 | 16:35 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Charger load shift | [7 empty] | 30.0MW load
interrup.
| 16:19 | 16:35 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Charger load shift | [7 empty] | 50.0MW load
interrup.
|  | 16:36 | Barishal 230/132kV S/S Gopalgonj CKT-1 is restored.
|  | 16:37 | Gopalganj 400/132kV S/S 230kV Barisal CKT-01 is restored.
| 17:10 | 17:20 | Tongi 230/132/33kV S/S 132 kV Bus-1 Scheduled S/D Due to Maintenance work for Bus DS-671M
| 17:52 | 18:02 | Chandina 132/33kV S/S TR-3 LT Project Work S/D Due to For tariff meter testing work | [7 empty] | 6.0MW load
interrup.
| 19:00 |  | Evening peak Generation is 13748 MW
|  | 20:05 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 HT is restored.
|  | 20:05 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT is restored.
| 23:30 | 23:55 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing RET 670 REF615 relays Due to 33 KV | [7 empty] | 16.0MW load
|  |  | Kotbari feeder fault | [7 empty] | interrup.
| 06:00 |  | Minimum Generation: 10292 MW.
| 06:23 |  | Barishal 230/132kV S/S Gopalgonj CKT-2 Project Work S/D Due to Barishal(N) -Patuakhali
230 kv line conductor stringing purpose.
| 06:35 |  | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 Project Work S/D Due to Project work
| 06:45 | 06:55 | Ashuganj-Shahjibazar 132kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing Distance
Relay relays.
| 07:09 |  | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Annual Maintenance Work
| 07:10 |  | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Annual Maintenance Work
| 07:17 |  | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Also
Bay maintenance at Kallyanpur Grid.
| 07:20 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Scheduled S/D Due to Annual | [7 empty] | 35.0MW load
|  |  | Maintanance | [7 empty] | interrup.
| 07:21 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Scheduled S/D Due to Annual | [7 empty] | 35.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 07:31 |  | Nawabganj 132/33kV S/S TR-1 LT Scheduled S/D Due to Due to Annual Maintenance Work.
| 07:32 |  | Nawabganj 132/33kV S/S TR-1 HT Scheduled S/D Due to Due to Annual Maintenance Work.
| 07:40 |  | Goalpara 132/33kV S/S T-5 LT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 07:40 |  | Goalpara 132/33kV S/S T-6 LT Project Work S/D | [7 empty] | 2.0MW load
interrup.
| 07:41 |  | Goalpara 132/33kV S/S T-5 HT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 07:41 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 07:42 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T LT Scheduled S/D Due to ok
| 07:43 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Scheduled S/D Due to ok
| 07:46 |  | Goalpara 132/33kV S/S T1 LT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 07:47 |  | Goalpara 132/33kV S/S Bus 2 Scheduled S/D
| 07:47 |  | Goalpara 132/33kV S/S T1 HT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 07:50 |  | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D Due to Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 323 | 7362000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 200 | 5992000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 678785 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5917066 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 52 | 519120 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 973920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 535211 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 142246 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 478200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 466920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 444480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 3374727 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1938960 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1153920 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1584000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204049 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 256320 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 7556363.64 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1176000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2260 | 40754287.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 126295.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 48060 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 35 | 492960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 126 | 3809947 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5077324 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 100 | 1451091 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 538752 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 368403 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 320640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 461280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 383040 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 83 | 373855 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 64722 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 102 | 879900 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 192960 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 95 | 573327 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 100 | 490109 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 572 | 13805453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 289440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15643636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2351 | 45404514.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7228700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 230 | 6314000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 265 | 6754500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 691488 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 216960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1161472 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 1664363 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 289792 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2429620 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 2139360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 70 | 1565760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 270302 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 446610 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 371640 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1033920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 336600 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1605.2 | 32915087
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 1091520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 636000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1021200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 288340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 189360 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 127 | 3239870
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 360840 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3646964 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715776 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1878720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3329600 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 165552 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7539500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 8817000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1168 | 26453952
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 906 | 21697454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 159360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 186624 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 233 | 6764256 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 459360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1102 | 25003640 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2361 | 55182694
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 10000777 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 690336 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2614000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 13867636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5213580 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 138000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3226 | -
Barishal Area Total |  |  |  |  | 2858 | 1550 | 32527555.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 356018 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 190 | 4344909 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 409 | 9022690 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 127866 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 215072 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 357504 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 35808 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1421 | 27026545 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 396752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 662025 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2152 | 42579029
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 680208 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42100.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 508400 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 242051 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1270850 | -
Rangpur Area Total |  |  |  |  | 950 | 174 | 2743609.32
Eastern Grid Total |  |  |  |  | 17383.855 | 7511.2 | 148767711.2
Western Grid Total |  |  |  |  | 10980.24 | 6237 | 133032887.68
National Grid Total |  |  |  |  | 28364.095 | 13748.2 | 281800598.88
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-11-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9442.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3722.6 | MW
i) Dhaka area |  |  | 5080.35 |  | MW | i) Khulna area |  |  |  | 1457 | MW
ii) Chattogram area |  |  | 1442.8 |  | MW | ii) Barishal area |  |  |  | 395 | MW
iii) Cumilla area |  |  | 1328.16 |  | MW | iii) Rajshahi area |  |  |  | 1123.6 | MW
iv) Mymensingh area |  |  | 973 |  | MW | iv) Rangpur area |  |  |  | 747 | MW
v) Sylhet area |  |  | 618 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13164.91 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 86 | 18:30 | 133 | Niamatpur | 46 | 18:00
2 | AKSML | 141.1 | 06:00 | 68 | Ishurdi | 68 | 18:30 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 36 | 18:00 | 69 | Jaldhaka | 66 | 18:00 | 135 | PHP | 7 | 02:00
4 | Agargaon | 107 | 19:00 | 70 | Jamalpur | 90 | 20:00 | 136 | Pabna | 87 | 18:00
5 | Agrabad | 100 | 18:00 | 71 | Jashore | 116 | 18:30 | 137 | Palashbari | 92 | 18:30
6 | Amnura | 17 | 18:00 | 72 | Jhenaidah | 104 | 18:30 | 138 | Panchagarh | 50 | 18:00
7 | Ashuganj | 72 | 00:00 | 73 | Joydebpur | 146 | 18:30 | 139 | Patiya | 10 | 00:00
8 | BSRM | 200 | 07:00 | 74 | Joypurhat | 47 | 18:30 | 140 | Patuakhali | 61.5 | 22:00
9 | Bagerhat | 71 | 18:00 | 75 | Juldah | 17 | 15:00 | 141 | Payra | 28 | 20:00
10 | Bajitpur | 84 | 18:00 | 76 | KSRM | 29 | 14:00 | 142 | Postogola | 61 | 13:00
11 | Bakulia | 86 | 18:00 | 77 | Kabirpur | 245 | 18:00 | 143 | Purbachal | 16 | 13:00
12 | Banani | 46.2 | 13:00 | 78 | Kachua | 84 | 18:00 | 144 | Purbasadipur | 99 | 18:00
13 | Bangabhaban | 22 | 10:00 | 79 | Kallyanpur | 93 | 19:00 | 145 | Rahanpur | 24 | 18:30
14 | Barapukuria | 51 | 18:30 | 80 | Kalurghat | 50 | 16:00 | 146 | Rahim | 39 | 15:00
15 | Barguna | 18 | 20:00 | 81 | Kamrangirchar | 72 | 18:00 | 147 | Rajbari | 71 | 18:00
16 | Barishal | 105 | 18:30 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 122 | 18:30
17 | Barishal-230 | 84 | 18:00 | 83 | Kasba | 35 | 21:00 | 149 | Rajshahi | 108 | 18:00
18 | Baroaulia | 66 | 15:00 | 84 | Kazla | 102 | 19:00 | 150 | Rajshahi-230 | 44 | 13:00
19 | Baroirhat | 68 | 18:00 | 85 | Keranigonj | 76 | 18:30 | 151 | Ramganj | 96 | 18:00
20 | Bashundhara | 188 | 18:00 | 86 | Khagrachori | 32 | 18:00 | 152 | Rampur | 41 | 18:30
21 | BashundharaCement | 13 | 08:00 | 87 | Khulna | 65 | 13:00 | 153 | Rangamati | 17 | 18:00
22 | Beanibazar | 78 | 18:00 | 88 | Khulshi | 186 | 18:00 | 154 | Rangpur | 132 | 18:30
23 | Benapole | 53 | 18:30 | 89 | Kishoreganj | 116 | 18:00 | 155 | Ruppur | 6.4 | 10:00
24 | Bhaluka | 142 | 18:00 | 90 | Kodda | 310 | 18:00 | 156 | SSM | 3 | 00:00
25 | Bhandaria | 48 | 18:00 | 91 | Kulaura | 49 | 19:30 | 157 | Saidpur | 93 | 18:00
26 | Bhangura | 30 | 18:00 | 92 | Kurigram | 54 | 18:30 | 158 | Satkhira | 98 | 17:00
27 | Bheramara(GK) | 47 | 18:00 | 93 | Kushtia | 130 | 18:30 | 159 | Satmasjid | 95 | 14:00
28 | Bhulta | 208 | 15:00 | 94 | Laksam | 31 | 21:00 | 160 | Savar | 212 | 12:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 27 | 18:00 | 161 | SevenRings | 4.08 | 17:00
30 | Bogura | 136 | 19:00 | 96 | Lalbag | 61 | 18:00 | 162 | ShahCement | 19 | 23:00
31 | Borhanuddin | 83 | 22:00 | 97 | Lalmonirhat | 50 | 18:00 | 163 | Shahjadpur | 73 | 18:00
32 | Brahmanbaria | 133 | 21:00 | 98 | MI_Cement | 13.5 | 00:00 | 164 | Shahjibazar | 120 | 22:00
33 | Cantonment | 144 | 13:00 | 99 | Madanganj | 40 | 18:00 | 165 | Shahmirpur | 53 | 18:00
34 | Chandina | 13.16 | 19:00 | 100 | Madaripur | 89 | 21:00 | 166 | Shariatpur | 74 | 21:00
35 | Chandpur | 70 | 18:00 | 101 | Madartek | 84 | 21:00 | 167 | Sherpur | 102 | 07:00
36 | Chandraghona | 34 | 18:00 | 102 | Madunaghat | 54 | 18:00 | 168 | Shikalbaha | 29 | 00:00
37 | Chapai | 47 | 00:00 | 103 | Magura | 51 | 18:30 | 169 | Shitalakhya | 76.6 | 12:00
38 | Charsaidpur | 33 | 15:00 | 104 | Mahasthangarh | 58 | 18:30 | 170 | Sholosohor | 49 | 18:00
39 | Chauddagram | 66 | 22:00 | 105 | Maijdee | 33 | 21:00 | 171 | Shyampur | 124 | 09:00
40 | Chhatak | 37 | 21:00 | 106 | Manikganj | 113 | 18:30 | 172 | Siddhirganj | 117 | 16:00
41 | Chowmuhani | 156 | 18:00 | 107 | Maniknagar | 58 | 13:00 | 173 | Sirajganj | 96 | 18:00
42 | Chuadanga | 86 | 18:30 | 108 | Matarbari | 52 | 18:30 | 174 | Sonargaon | 132 | 16:00
43 | Coxsbazar | 128 | 00:00 | 109 | Matuail | 68 | 23:00 | 175 | Sreemongol | 84 | 18:00
44 | Cumilla(N) | 131 | 22:00 | 110 | Metrorail_Motijheel | 40 | 09:00 | 176 | Sreepur | 110 | 15:00
45 | Cumilla(S) | 152 | 18:00 | 111 | Metrorail_Uttara | 11 | 12:00 | 177 | Srinagar | 42.4 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 124 | 12:00 | 178 | Sunamganj | 62 | 22:00
47 | Daudkandi | 125 | 21:00 | 113 | Mirpur | 127 | 18:00 | 179 | Sylhet | 51 | 18:00
48 | DhakaUniversity | 82 | 13:00 | 114 | Mirsorai | 9 | 09:00 | 180 | Sylhet-132 | 123 | 18:00
49 | Dhamrai | 114 | 18:00 | 115 | Mirzapur | 37 | 14:00 | 181 | TK | 24 | 18:00
50 | Dhanmondi | 102 | 13:00 | 116 | Mithapukur | 58 | 14:00 | 182 | Tangail | 140 | 19:00
51 | Dohazari | 98 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 17 | 18:00
52 | Faridpur | 141 | 18:30 | 118 | Mogbazar | 94 | 13:00 | 184 | Thakurgaon | 83 | 18:00
53 | Fatullah | 106 | 16:00 | 119 | Mongla | 39 | 09:00 | 185 | Tongi | 110 | 11:00
54 | Fenchuganj | 38 | 20:00 | 120 | Motijheel | 41 | 13:00 | 186 | Ullahpara | 34 | 18:00
55 | Feni | 114 | 18:00 | 121 | Muktagacha | 30 | 18:00 | 187 | Ullon | 60 | 20:00
56 | GPH | 3 | 02:00 | 122 | Munshiganj | 100 | 21:00 | 188 | Uttara | 81 | 13:00
57 | Ghatail | 60 | 18:00 | 123 | Muradnagar | 39 | 19:00 | 189 | UttaraNew | 28 | 18:30
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 169 | 18:30 | 190 | Zigatola | 62 | 18:30
59 | Ghorashal-230 | 97 | 19:30 | 125 | Naogaon | 89 | 18:30
60 | Goalpara | 33 | 18:00 | 126 | Narail | 49.5 | 18:00
61 | Gollamari | 76 | 13:00 | 127 | Narinda | 72 | 13:00
62 | Gopalganj | 92 | 18:00 | 128 | Narshingdi | 168 | 21:00
63 | Gulshan | 114 | 12:00 | 129 | Natore | 123 | 18:00
64 | Halishahar | 66 | 18:00 | 130 | Nawabganj | 41 | 21:00
65 | HaripurSBU | 143 | 08:00 | 131 | Netrakona | 129 | 18:00
66 | Hasnabad | 89 | 19:00 | 132 | New | 53.6 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12019.69 | 0 |  | 12019.69
1:00 | 11237.56 | 0 |  | 11237.56
2:00 | 10756.38 | 0 |  | 10756.38
3:00 | 10409.5 | 0 |  | 10409.5
4:00 | 10120.06 | 0 |  | 10120.06
5:00 | 9756.21 | 0 |  | 9756.21
6:00 | 9820.31 | 0 |  | 9820.31
7:00 | 10364.03 | 0 |  | 10364.03
8:00 | 10447.42 | 0 |  | 10447.42
9:00 | 10457.33 | 0 |  | 10457.33
10:00 | 10594.16 | 0 |  | 10594.16
11:00 | 10972.34 | 0 |  | 10972.34
12:00 | 11814.82 | 0 |  | 11814.82
13:00 | 12220.9 | 0 |  | 12220.9
14:00 | 12151.09 | 0 |  | 12151.09
15:00 | 12121.22 | 0 |  | 12121.22
16:00 | 11873.64 | 0 |  | 11873.64
17:00 | 12024.91 | 0 |  | 12024.91
18:00 | 13657 | 89 |  | 13750.01
19:00 | 13748.2 | 69 |  | 13820.31
19:30 | 13535 | 62 |  | 13599.79
20:00 | 13428 | 50 |  | 13480.25
21:00 | 13323.66 | 45 |  | 13370.69
22:00 | 13056.91 | 32 |  | 13089.91
23:00 | 12641.29 | 24 |  | 12666.29
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 04-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3349 | 1524 | 903 | 38 | 66 | 1327.89 | 220 | 3615 | 0 | 186 | 770.8 | 0 | 0 | 20 | 0 | DAILY ENERGY CURVE
00:30 | 3291.5 | 1515.5 | 903.5 | 38 | 65 | 1323.525 | 219 | 3513.5 | 0 | 97 | 635.6 | 0 | 0 | 26.5 | 0 | 04-11-2025
01:00 | 3234 | 1507 | 904 | 38 | 64 | 1319.16 | 218 | 3412 | 0 | 8 | 500.4 | 0 | 0 | 33 | 0
01:30 | 3240.5 | 1504.25 | 904 | 38 | 63 | 1269.52 | 217 | 3367 | 0 | 8 | 358.2 | 0 | 0 | 27.5 | 0 | Energy Generated | 281.8006 |  | MKWHr
02:00 | 3247 | 1501.5 | 904 | 38 | 62 | 1219.88 | 216 | 3322 | 0 | 8 | 216 | 0 | 0 | 22 | 0 | Energy not Served | 0.309 |  | MKWHr
02:30 | 3240 | 1504.75 | 904 | 38 | 63 | 1150.19 | 216 | 3305 | 0 | 8 | 127.5 | 0 | 0 | 26.5 | 0 | Total Energy Requirement | 282.1096 |  | MKWHr
03:00 | 3233 | 1508 | 904 | 38 | 64 | 1080.5 | 216 | 3288 | 0 | 8 | 39 | 0 | 0 | 31 | 0
03:30 | 3232.5 | 1510.5 | 904 | 38 | 64 | 1007.28 | 216 | 3217 | 0 | 8 | 39 | 0 | 0 | 28.5 | 0
04:00 | 3232 | 1513 | 904 | 38 | 64 | 934.06 | 216 | 3146 | 0 | 8 | 39 | 0 | 0 | 26 | 0
04:30 | 3252.5 | 1500 | 891 | 38 | 63 | 892.135 | 216 | 3024 | 0 | 8 | 31.5 | 0 | 0 | 22 | 0
05:00 | 3273 | 1487 | 878 | 38 | 62 | 850.21 | 216 | 2902 | 0 | 8 | 24 | 0 | 0 | 18 | 0
05:30 | 3300.5 | 1499 | 878 | 38 | 57 | 845.76 | 216 | 2907 | 0 | 4 | 24 | 0 | 0 | 19 | 0
06:00 | 3328 | 1511 | 878 | 38 | 52 | 841.31 | 216 | 2912 | 0 | 0 | 24 | 0 | 0 | 20 | 0
06:30 | 3402 | 1503 | 878 | 38 | 51 | 903.5 | 216 | 3014.5 | 33.67 | 1 | 29 | 0 | 0 | 22.5 | 0
07:00 | 3476 | 1495 | 878 | 38 | 50 | 965.69 | 216 | 3117 | 67.34 | 2 | 34 | 0 | 0 | 25 | 0
07:30 | 3321 | 1448.5 | 878 | 38 | 52 | 1042.075 | 217.5 | 3075.5 | 173.4 | 17.5 | 119.25 | 0 | 0 | 23 | 0
08:00 | 3166 | 1402 | 878 | 38 | 54 | 1118.46 | 219 | 3034 | 279.46 | 33 | 204.5 | 0 | 0 | 21 | 0
08:30 | 3114 | 1390 | 878 | 38 | 55 | 1114.345 | 197.5 | 3034.5 | 362.53 | 33 | 219.5 | 0 | 0 | 16 | 0
09:00 | 3062 | 1378 | 878 | 38 | 56 | 1110.23 | 176 | 3035 | 445.6 | 33 | 234.5 | 0 | 0 | 11 | 0
09:30 | 3125.5 | 1392 | 878 | 38 | 58 | 1030.305 | 176 | 3047.5 | 508.44 | 33 | 231.5 | 0 | 0 | 7.5 | 0
10:00 | 3189 | 1406 | 878 | 38 | 60 | 950.38 | 176 | 3060 | 571.28 | 33 | 228.5 | 0 | 0 | 4 | 0
10:30 | 3195 | 1414 | 878 | 38 | 60 | 936.155 | 176 | 3043 | 595.595 | 43.5 | 402 | 0 | 0 | 2 | 0
11:00 | 3201 | 1422 | 878 | 38 | 60 | 921.93 | 176 | 3026 | 619.91 | 54 | 575.5 | 0 | 0 | 0 | 0
11:30 | 3183.5 | 1440 | 887.5 | 38 | 64 | 924.15 | 151 | 3078.5 | 655.93 | 120.5 | 849.5 | 0 | 0 | 1 | 0
12:00 | 3166 | 1458 | 897 | 38 | 68 | 926.37 | 126 | 3131 | 691.95 | 187 | 1123.5 | 0 | 0 | 2 | 0
12:30 | 3217.5 | 1431 | 897.5 | 38 | 64 | 972.35 | 126 | 3241 | 637.51 | 193.5 | 1197.5 | 0 | 0 | 2 | 0
13:00 | 3269 | 1404 | 898 | 38 | 60 | 1018.33 | 126 | 3351 | 583.07 | 200 | 1271.5 | 0 | 0 | 2 | 0
13:30 | 3288.5 | 1364.5 | 901.5 | 38 | 68 | 1021.665 | 126 | 3349.5 | 551.83 | 201.5 | 1273 | 0 | 0 | 2 | 0
14:00 | 3308 | 1325 | 905 | 38 | 76 | 1025 | 126 | 3348 | 520.59 | 203 | 1274.5 | 0 | 0 | 2 | 0
14:30 | 3329 | 1342 | 905.5 | 38 | 73 | 1032 | 126 | 3373 | 443.155 | 215.5 | 1258 | 0 | 0 | 1 | 0
15:00 | 3350 | 1359 | 906 | 38 | 70 | 1039 | 126 | 3398 | 365.72 | 228 | 1241.5 | 0 | 0 | 0 | 0
15:30 | 3325 | 1384.5 | 906 | 38 | 67 | 1063.5 | 103 | 3390 | 254.43 | 247 | 1216 | 0 | 0 | 3 | 0
16:00 | 3300 | 1410 | 906 | 38 | 64 | 1088 | 80 | 3382 | 143.14 | 266 | 1190.5 | 0 | 0 | 6 | 0
16:30 | 3240 | 1399.5 | 906 | 38 | 64 | 1129 | 80 | 3363 | 81.525 | 305 | 1337.25 | 0 | 0 | 6 | 0
17:00 | 3180 | 1389 | 906 | 38 | 64 | 1170 | 80 | 3344 | 19.91 | 344 | 1484 | 0 | 0 | 6 | 0
17:30 | 3233 | 1408.5 | 905.5 | 38 | 68 | 1312.5 | 103 | 3389.5 | 9.955 | 505.5 | 1860.5 | 0 | 0 | 7 | 44.5
18:00 | 3286 | 1428 | 905 | 38 | 72 | 1455 | 126 | 3435 | 0 | 667 | 2237 | 0 | 0 | 8 | 89
18:30 | 3286 | 1433.5 | 905.5 | 38 | 71 | 1438 | 126 | 3426 | 0 | 683 | 2291.6 | 0 | 0 | 4 | 79
19:00 | 3286 | 1439 | 906 | 38 | 70 | 1421 | 126 | 3417 | 0 | 699 | 2346.2 | 0 | 0 | 0 | 69
19:30 | 3299 | 1455 | 906 | 38 | 78 | 1419 | 126 | 3423 | 0 | 684 | 2107 | 0 | 0 | 0 | 62
20:00 | 3251 | 1467 | 905 | 38 | 72 | 1420 | 126 | 3410 | 0 | 672 | 2067 | 0 | 0 | 0 | 50
20:30 | 3259.5 | 1467.5 | 904 | 38 | 74 | 1424.08 | 126 | 3377.5 | 0 | 661 | 2044.25 | 0 | 0 | 0 | 47.5
21:00 | 3268 | 1468 | 903 | 38 | 76 | 1428.16 | 126 | 3345 | 0 | 650 | 2021.5 | 0 | 0 | 0 | 45
21:30 | 3246 | 1447.5 | 903 | 38 | 77 | 1429.635 | 126 | 3341.5 | 0 | 639.5 | 1935.15 | 0 | 0 | 7 | 38.5
22:00 | 3224 | 1427 | 903 | 38 | 78 | 1431.11 | 126 | 3338 | 0 | 629 | 1848.8 | 0 | 0 | 14 | 32
22:30 | 3222 | 1411 | 903 | 38 | 79 | 1430.95 | 126 | 3341.5 | 0 | 544 | 1742.15 | 0 | 0 | 11.5 | 28
23:00 | 3220 | 1395 | 903 | 38 | 80 | 1430.79 | 126 | 3345 | 0 | 459 | 1635.5 | 0 | 0 | 9 | 24
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6112.8 | 5906.89 | 12019.69 | DAILY GENERATION CURVE
00:30 | 5863.6 | 5765.025 | 11628.625
01:00 | 5614.4 | 5623.16 | 11237.56 | 04-11-2025
01:30 | 5461.45 | 5535.52 | 10996.97
02:00 | 5308.5 | 5447.88 | 10756.38
02:30 | 5229.75 | 5353.19 | 10582.94
03:00 | 5151 | 5258.5 | 10409.5
03:30 | 5145 | 5119.78 | 10264.78
04:00 | 5139 | 4981.06 | 10120.06
04:30 | 5116.5 | 4821.635 | 9938.135
05:00 | 5094 | 4662.21 | 9756.21
05:30 | 5125.5 | 4662.76 | 9788.26
06:00 | 5157 | 4663.31 | 9820.31
06:30 | 5232.38 | 4859.79 | 10092.17
07:00 | 5307.76 | 5056.27 | 10364.03
07:30 | 5317.77 | 5087.955 | 10405.725
08:00 | 5327.78 | 5119.64 | 10447.42
08:30 | 5257.545 | 5194.83 | 10452.375
09:00 | 5187.31 | 5270.02 | 10457.33
09:30 | 5267.835 | 5257.91 | 10525.745
10:00 | 5348.36 | 5245.8 | 10594.16
10:30 | 5540.26 | 5242.99 | 10783.25
11:00 | 5732.16 | 5240.18 | 10972.34
11:30 | 6053.815 | 5339.765 | 11393.58
12:00 | 6375.47 | 5439.35 | 11814.82
12:30 | 6426.905 | 5590.955 | 12017.86
13:00 | 6478.34 | 5742.56 | 12220.9
13:30 | 6495.74 | 5690.255 | 12185.995
14:00 | 6513.14 | 5637.95 | 12151.09
14:30 | 6496.23 | 5639.925 | 12136.155
15:00 | 6479.32 | 5641.9 | 12121.22
15:30 | 6452.87 | 5544.56 | 11997.43
16:00 | 6426.42 | 5447.22 | 11873.64
16:30 | 6492.29 | 5456.985 | 11949.275
17:00 | 6558.16 | 5466.75 | 12024.91
17:30 | 6976.08 | 5864.875 | 12840.955
18:00 | 7394 | 6263 | 13657
18:30 | 7452.6 | 6250 | 13702.6
19:00 | 7511.2 | 6237 | 13748.2
19:30 | 7349 | 6186 | 13535
20:00 | 7335 | 6093 | 13428
20:30 | 7319.75 | 6056.08 | 13375.83 |  | Executive Engineer
21:00 | 7304.5 | 6019.16 | 13323.66 |  | Network Operation Division
21:30 | 7213.65 | 5976.635 | 13190.285
22:00 | 7122.8 | 5934.11 | 13056.91
22:30 | 6999.65 | 5849.45 | 12849.1
23:00 | 6876.5 | 5764.79 | 12641.29

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 06:00 | 377 | 10:00 | Payra | 411 | 05:00 | 407 | 02:00
Ashuganj | 410 | 5:00 | 387 | 10:00 | Rahanpur | 413 | 04:00 | 399 | 18:00
Bhulta | 403 | 04:00 | 383 | 10:00 | Rampal | 407 | 04:00 | 399 | 15:00
Bibiana | 389 | 08:00 | 384 | 10:00
BIPTC | 407 | 03:00 | 395 | 18:00
Bogura | 406 | 04:00 | 389 | 18:00
Gopalganj | 400 | 06:00 | 392 | 13:00
Kaliakoir | 376 | 05:00 | 367 | 10:00
Madunaghat | 397 | 21:00 | 389 | 02:00
Meghnaghat | 386 | 05:00 | 379 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 04:00 | 224 | 10:00 | Kaliakoir | 236 | 21:00 | 228 | 10:00
AKSML | 237 | 19:00 | 225 | 01:00 | Keranigonj | 228 | 06:00 | 221 | 10:00
Aminbazar | 230 | 05:00 | 225 | 10:00 | Khulna(S) | 238 | 05:00 | 229 | 18:00
Ashuganj | 234 | 12:00 | 220 | 02:00 | Madunaghat | 236 | 21:00 | 229 | 00:00
Ashuganj-400 | 234 | 12:00 | 220 | 02:00 | Madunaghat-400 | 237 | 22:00 | 229 | 03:00
Baghabari | 236 | 06:00 | 229 | 16:00 | Maniknagar | 220 | 05:00 | 216 | 11:00
Barapukuria | 222 | 05:00 | 211 | 07:00 | Meghnaghat | 227 | 07:00 | 222 | 15:00
Barapukuria-230 | 222 | 05:00 | 211 | 07:00 | Meghnaghat-400 | 224 | 04:00 | 220 | 10:00
Barishal | 236 | 06:00 | 232 | 00:00 | Mirsorai | 236 | 18:30 | 222 | 02:00
Bheramara | 234 | 04:00 | 225 | 18:00 | Rajshahi | 235 | 04:00 | 224 | 18:00
Bhulta | 233 | 04:00 | 216 | 13:00 | Rampal | 235 | 04:00 | 227 | 13:00
Bibiana | 231 | 05:00 | 226 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 04:00 | 225 | 18:00 | Rampura | 233 | 22:00 | 218 | 10:00
Bogura | 235 | 04:00 | 227 | 18:00 | Shikalbaha | 236 | 18:30 | 227 | 05:00
Bogura-400 | 235 | 04:00 | 226 | 18:00 | Shyampur | 225 | 04:00 | 220 | 10:00
Borhanuddin | 238 | 05:00 | 235 | 00:00 | Siddhirganj | 222 | 05:00 | 219 | 00:00
BSRM | 233 | 18:30 | 222 | 02:00 | Sirajgonj | 240 | 04:00 | 232 | 18:30
Cumilla(N) | 226 | 06:00 | 222 | 10:00 | Sreepur | 229 | 04:00 | 222 | 10:00
Faridpur | 234 | 05:00 | 228 | 15:00 | Tongi | 233 | 21:00 | 220 | 10:00
Fenchuganj | 232 | 07:00 | 228 | 00:00
Ghorashal | 238 | 01:00 | 230 | 00:00
Ghorashal-230 | 231 | 05:00 | 220 | 10:00
Gopalganj | 235 | 05:00 | 229 | 13:00
GPH | 235 | 18:30 | 226 | 01:00
Haripur | 222 | 05:00 | 217 | 10:00
Hasnabad | 226 | 05:00 | 221 | 10:00
Hathazari | 233 | 19:30 | 32 | 19:00
Ishurdi | 238 | 04:00 | 228 | 18:00
Jhenaidah | 236 | 04:00 | 223 | 18:30
Kachua | 231 | 17:00 | 219 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 127 | 10:00 | Lalmonirhat | 130 | 03:00 | 124 | 14:00
Agargaon | 136 | 04:00 | 131 | 15:00 | Madanganj | 132 | 01:00 | 126 | 12:00
Agrabad | 135 | 18:30 | 130 | 00:00 | Madaripur | 136 | 06:00 | 133 | 00:00
AKS | 133 | 18:30 | 127 | 03:00 | Madartek | 136 | 06:00 | 126 | 10:00
Aminbazar | 136 | 00:00 | 132 | 10:00 | Madunaghat | 137 | 19:00 | 132 | 02:00
Amnura | 140 | 04:00 | 130 | 12:00 | Magura | 138 | 05:00 | 130 | 13:00
Ashuganj | 142 | 06:00 | 138 | 00:00 | Mahasthangarh | 133 | 04:00 | 128 | 07:00
Bagerhat | 134 | 06:00 | 125 | 18:00 | Maijdee | 132 | 12:00 | 127 | 01:00
Bajitpur | 134 | 11:00 | 127 | 18:00 | Manikganj | 135 | 05:00 | 130 | 10:00
Bakulia | 137 | 22:00 | 130 | 01:00 | Maniknagar | 134 | 05:00 | 129 | 11:00
Banani | 136 | 04:00 | 127 | 10:00 | Matarbari | 128 | 22:00 | 112 | 00:00
Bangabhaban | 134 | 04:00 | 129 | 11:00 | Matuail | 129 | 06:00 | 125.6 | 11:00
Barapukuria | 136 | 04:00 | 127 | 07:00 | Metrorail_Motijheel | 134 | 05:00 | 129 | 11:00
Barguna | 137 | 07:00 | 134 | 13:00 | Metrorail_Uttara | 138 | 03:00 | 132 | 22:00
Barishal | 137 | 06:00 | 133 | 13:00 | Millgate | 139 | 04:00 | 133 | 10:00
Barishal-230 | 136 | 04:00 | 133 | 00:00 | Mirpur | 136 | 00:00 | 132 | 09:00
Baroaulia | 135 | 17:00 | 130 | 02:00 | Mirzapur | 130 | 07:00 | 126 | 15:00
Baroirhat | 134 | 18:30 | 129 | 00:00 | Mithapukur | 134 | 04:00 | 127 | 07:00
Bashundhara | 136 | 03:00 | 126 | 10:00 | MI_Cement | 133 | 06:00 | 126 | 13:00
BashundharaCement | 132 | 01:00 | 126 | 12:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 132 | 08:00 | 125 | 18:00 | Mogbazar | 138 | 05:00 | 127 | 10:00
Benapole | 137 | 03:00 | 126 | 18:30 | Mongla | 133 | 07:00 | 126 | 18:00
Bhaluka | 132 | 12:00 | 126 | 10:00 | Motijheel | 134 | 04:00 | 129 | 11:00
Bhandaria | 140 | 07:00 | 129 | 00:00 | Muktagacha | 131 | 02:00 | 121 | 18:00
Bhangura | 135 | 03:00 | 129 | 18:30 | Munshiganj | 128 | 17:00 | 126 | 00:00
Bheramara | 140 | 04:00 | 136 | 18:00 | Muradnagar | 129 | 08:00 | 125 | 00:00
Bheramara(GK) | 139 | 05:00 | 135 | 18:00 | Mymensingh | 132 | 08:00 | 118 | 18:00
Bhulta | 127 | 07:00 | 123 | 19:30 | Naogaon | 132 | 06:00 | 126 | 13:00
Bog-Sherpur | 134 | 03:00 | 129 | 16:00 | Narail | 137 | 06:00 | 128 | 18:00
Bogura | 134 | 03:00 | 130 | 13:00 | Narinda | 134 | 05:00 | 129 | 11:00
Bogura-230 | 134 | 04:00 | 130 | 13:00 | Narshingdi | 134 | 06:00 | 120 | 11:00
Brahmanbaria | 136 | 07:00 | 130 | 18:30 | Natore | 135 | 06:00 | 129 | 18:00
Cantonment | 135 | 03:00 | 131 | 10:00 | Nawabganj | 136 | 06:00 | 131 | 11:00
Chandina | 132 | 08:00 | 129 | 00:00 | Netrakona | 129 | 05:00 | 117 | 18:00
Chandpur | 139 | 18:30 | 130 | 02:00 | New | 139 | 04:00 | 133 | 10:00
Chandraghona | 136 | 18:00 | 132 | 02:00 | Niamatpur | 141 | 05:00 | 135 | 18:00
Chapai | 141 | 05:00 | 135 | 18:00 | Noapara | 136 | 05:00 | 130 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:30 | 126 | 09:00 | Pabna | 138 | 04:00 | 131 | 18:00
Chauddagram | 132 | 18:30 | 127 | 01:00 | Palashbari | 132 | 06:00 | 125 | 13:00
Chhatak | 130 | 05:00 | 122 | 18:00 | Panchagarh | 139 | 22:00 | 127 | 07:00
Chowmuhani | 132 | 17:00 | 126 | 01:00 | Patiya | 136 | 22:00 | 127 | 02:00
Chuadanga | 139 | 06:00 | 128 | 18:00 | Patuakhali | 136 | 04:00 | 132 | 22:00
Coxsbazar | 125 | 22:00 | 111 | 00:00 | Payra | 137 | 05:00 | 135 | 00:00
Cumilla(N) | 132 | 17:00 | 128 | 04:00 | PHP | 133 | 18:30 | 127 | 01:00
Cumilla(S) | 132 | 08:00 | 127 | 18:00 | Postogola | 135 | 06:00 | 129 | 09:00
Daganbhuiyan | 133 | 18:30 | 128 | 00:00 | Purbachal | 137 | 22:00 | 125 | 10:00
Daudkandi | 127 | 07:00 | 121 | 00:00 | Purbasadipur | 134 | 04:00 | 124 | 13:00
DhakaUniversity | 137 | 21:00 | 128 | 10:00 | Rahanpur | 142 | 05:00 | 137 | 18:00
Dhamrai | 135 | 05:00 | 130 | 10:00 | Rahanpur-400 | 142 | 04:00 | 137 | 18:00
Dhanmondi | 137 | 06:00 | 127 | 10:00 | Rahim | 129 | 04:00 | 126 | 10:00
Dohazari | 133 | 22:00 | 125 | 00:00 | Rajbari | 137 | 04:00 | 133 | 00:00
Faridpur | 138 | 05:00 | 134 | 15:00 | Rajendrapur | 132 | 04:00 | 125 | 18:00
Fatullah | 137 | 05:00 | 128 | 09:00 | Rajshahi | 134 | 05:00 | 129 | 18:00
Fenchuganj | 137 | 07:00 | 134 | 00:00 | Rajshahi-230 | 135 | 04:00 | 129 | 18:00
Feni | 132 | 18:30 | 127 | 00:00 | Ramganj | 133 | 11:00 | 126 | 05:00
Ghatail | 129 | 00:00 | 120 | 18:00 | Rampur | 134 | 16:00 | 129 | 02:00
Ghorashal | 140 | 12:00 | 135 | 15:00 | Rampura | 137 | 22:00 | 127 | 10:00
Goalpara | 138 | 04:00 | 128 | 18:00 | Rangamati | 136 | 18:30 | 131 | 15:00
Gollamari | 137 | 06:00 | 132 | 18:00 | Rangpur | 134 | 05:00 | 126 | 16:00
Gopalganj | 136 | 04:00 | 132 | 12:00 | Ruppur | 138 | 04:00 | 135 | 00:00
Gopalganj-400 | 138 | 06:00 | 134 | 13:00 | Saidpur | 134 | 05:00 | 125 | 16:00
Gulshan | 137 | 22:00 | 127 | 10:00 | Satkhira | 135 | 04:00 | 128 | 17:00
Halishahar | 136 | 22:00 | 129 | 02:00 | Satmasjid | 136 | 05:00 | 131 | 10:00
Haripur | 129 | 04:00 | 126 | 11:00 | Savar | 137 | 00:00 | 130 | 10:00
HaripurSBU | 129 | 04:00 | 126 | 11:00 | SevenRings | 140 | 12:00 | 132 | 10:00
Hasnabad | 135 | 05:00 | 127 | 10:00 | ShahCement | 129 | 18:30 | 15 | 14:00
Hathazari | 137 | 18:30 | 132 | 01:00 | Shahjadpur | 137 | 03:00 | 134 | 17:00
Ishurdi | 140 | 03:00 | 135 | 18:00 | Shahjibazar | 136 | 06:00 | 130 | 18:00
Jaldhaka | 132 | 04:00 | 120 | 07:00 | Shahmirpur | 136 | 18:00 | 131 | 00:00
Jamalpur | 130 | 08:00 | 116 | 18:00 | Shariatpur | 136 | 04:00 | 131 | 00:00
Jashore | 138 | 04:00 | 128 | 13:00 | Sherpur | 125 | 09:00 | 112 | 18:00
Jhenaidah | 140 | 06:00 | 130 | 18:00 | Shikalbaha | 126 | 22:00 | 119 | 02:00
Jhenaidah-230 | 141 | 04:00 | 132 | 18:00 | Shikalbaha-230 | 137 | 18:30 | 131 | 02:00
Joydebpur | 140 | 19:00 | 127 | 10:00 | Shitalakhya | 133 | 06:00 | 126 | 13:00
Joypurhat | 131 | 06:00 | 124 | 18:00 | Sholosohor | 136 | 18:30 | 131 | 02:00
Juldah | 136 | 22:00 | 130 | 01:00 | Shyampur | 135 | 06:00 | 132 | 09:00
Kabirpur | 137 | 13:00 | 127 | 10:00 | Shyampur-230 | 137 | 04:00 | 133 | 10:00
Kachua | 137 | 17:00 | 130 | 04:00 | Siddhirganj | 129 | 04:00 | 126 | 10:00
Kaliakoir | 136 | 04:00 | 131 | 10:00 | Sirajganj | 133 | 05:00 | 126 | 18:00
Kallyanpur | 136 | 00:00 | 133 | 10:00 | Sonargaon | 127 | 07:00 | 124 | 11:00
Kalurghat | 137 | 18:30 | 131 | 02:00 | Sreemongol | 136 | 08:00 | 129 | 18:00
Kamrangirchar | 135 | 06:00 | 130 | 10:00 | Sreepur | 133 | 04:00 | 129 | 10:00
Kaptai | 138 | 21:00 | 135 | 1:00 | Srinagar | 135 | 04:00 | 131 | 10:00
Kasba | 128 | 08:00 | 124 | 00:00 | SSM | 138 | 17:00 | 132 | 01:00
Kazla | 134 | 06:00 | 129 | 11:00 | Sunamganj | 127 | 06:00 | 120 | 21:00
Keranigonj | 136 | 06:00 | 131 | 09:00 | Sylhet | 133 | 08:00 | 127 | 18:00
Khagrachori | 134 | 17:00 | 131 | 00:00 | Sylhet-132 | 130 | 03:00 | 127 | 18:00
Khulna | 136 | 05:00 | 131 | 13:00 | Tangail | 127 | 05:00 | 122 | 18:00
Khulna(S) | 138 | 04:00 | 132 | 13:00 | Taraganj | 132 | 22:00 | 124 | 07:00
Khulshi | 134 | 21:00 | 127 | 15:00 | Thakurgaon | 138 | 22:00 | 124 | 07:00
Kishoreganj | 133 | 12:00 | 124 | 18:00 | TK | 136 | 17:00 | 132 | 01:00
Kodda | 137 | 12:00 | 124 | 10:00 | Tongi | 141 | 21:00 | 135 | 10:00
KSRM | 136 | 17:00 | 131 | 00:00 | Ullahpara | 135 | 05:00 | 129 | 18:00
Kulaura | 136 | 08:00 | 132 | 00:00 | Ullon | 136 | 04:00 | 126 | 10:00
Kurigram | 133 | 04:00 | 122 | 16:00 | Uttara | 136 | 00:00 | 131 | 10:00
Kushtia | 138 | 06:00 | 132 | 18:00 | UttaraNew | 139 | 22:00 | 132 | 10:00
Laksam | 135 | 12:00 | 128 | 02:00 | Zigatola | 135 | 05:00 | 131 | 10:00
Lakshmipur | 133 | 18:30 | 127 | 02:00
Lalbag | 135 | 05:00 | 130 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division