## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-11-2025 | during | 06-11-2025 | during | 06-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 342 | 324 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 200 | 200 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 270 | 335 | 335 | 260 | 260 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 52 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 107 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 19 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 23 | 24 | 24 | 24 | 24 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 17 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 32 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 297 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 127 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 144 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 22 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 350 | 584 | 584 | 525.6 | 525.6 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1937.5 | 2321 | 5917.1 | 5892.1 | 4124.41 | 4171.41
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 29 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 158 | 130 | 130 | 130 | 130 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 225 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 106 | 100 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 62 | 48 | 70 | 48 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 18 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 23 | 44 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.81 | 0 | 3.36 | 0 | 3.36 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 48 | 16 | 300 | 300 | 100 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 81 | 101 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 45 | 97 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 126 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 580 | 612 | 612 | 582 | 582 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 20 | 16 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 2020.81 | 2369 | 2957.08 | 2967.72 | 2459.72 | 2470.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 270 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 220 | 220 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 219 | 393 | 393 | 305 | 305 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 5 | 38 | 46.7 | 46.7 | 39 | 39 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 112 | 137 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 9 | 29 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 103 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 49 | 189 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 66 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 26 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 107 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 56 | 70 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 18 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1203 | 1249.2 | 2606.56 | 2551.56 | 2002.86 | 1947.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-11-2025 | during | 06-11-2025 | during | 06-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 11 | 157.5 | 157.5 | 74 | 74 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 28 | 28 | 28 | 28 | 28 | 28 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 11.63 | 0 | 47 | 0 | 47 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 123.63 | 104 | 359.1 | 310 | 222.1 | 173
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 159 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 0 | 0 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 97 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 5 | 15 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 334 | 354 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 942 | 1076 | 1205 | 1205 | 1124 | 1124
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 908 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 200 | 151 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1061 | 1148 | 0 | 0 | 1100 | 1100 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2288 | 2340 | 2408 | 2318 | 2747 | 2657
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 502 | 502 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 108 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 550 | 580 | 1244 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1382.53 | 1537 | 1840 | 1217 | 1077 | 1076
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 36.5 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 180 | 187 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 365 | 412 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 110 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Engine Problem
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.77 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1103.57 | 1457.64 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.8 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 68 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1816.64 | 2436.64 | 3175.32 | 3008.87 | 3023.94 | 2857.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 170 | 0 | 197.04 | 0 | 197.04 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 212.3 | 228 | 494.84 | 262 | 460.84 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 11926.41 | 13660.84 | 20963 | 19732.25 | 17241.87 | 16705.12
Forecast Scenario (06-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12600 |  | 0 |  | 12600
|  |  |  | 1:00 | 12080 |  | 0 |  | 12080
|  |  |  | 2:00 | 11540 |  | 0 |  | 11540
|  |  |  | 3:00 | 11130 |  | 0 |  | 11130
|  |  |  | 4:00 | 10830 |  | 0 |  | 10830
|  |  |  | 5:00 | 10500 |  | 0 |  | 10500
|  |  |  | 6:00 | 10490 |  | 0 |  | 10490
|  |  |  | 7:00 | 10780 |  | 0 |  | 10780
|  |  |  | 8:00 | 11020 |  | 0 |  | 11020
|  |  |  | 9:00 | 10990 |  | 0 |  | 10990
|  |  |  | 10:00 | 10970 |  | 0 |  | 10970
|  |  |  | 11:00 | 11390 |  | 0 |  | 11390
|  |  |  | 12:00 | 12120 |  | 0 |  | 12120
|  |  |  | 13:00 | 12560 |  | 0 |  | 12560
|  |  |  | 14:00 | 12440 |  | 0 |  | 12440
|  |  |  | 15:00 | 12320 |  | 0 |  | 12320
|  |  |  | 16:00 | 12010 |  | 0 |  | 12010
|  |  |  | 17:00 | 12140 |  | 0 |  | 12140
|  |  |  | 18:00 | 13800 |  | 0 |  | 13800
|  |  |  | 18:30 | 13850 |  | 0 |  | 13850
|  |  |  | 19:00 | 13910 |  | 0 |  | 13910
|  |  |  | 19:30 | 13760 |  | 0 |  | 13760
|  |  |  | 20:00 | 13610 |  | 0 |  | 13610
|  |  |  | 21:00 | 13510 |  | 0 |  | 13510
|  |  |  | 22:00 | 13310 |  | 0 |  | 13310
|  |  |  | 23:00 | 13100 |  | 0 |  | 13100
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 12120.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13910.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13910.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 289.15 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:37 hrs on 06-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-11-2025 | [28 empty] | Date: | 05-11-2025 | [28 empty] | Date: | 05-11-2025 | [28 empty] | Date: | 05-11-2025 | [28 empty] | Date: | 05-11-2025 | [14 empty] | Date: | 05-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17.5 | 17 | 149 | 75 | 195 | 40 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 90 | 19.5 | 22 | 0 | 330 | 60 | 16 | 32 | 0 | 7 | 16 | 0 | 0 | 12 | 12 | 0 | 126 | 65 | 35 | 650 | 30 | 0 | 32 | 0 | 96 | 224 | 0 | 0 | 0 | 580 | 0 | 51 | 125 | 0 | 260 | 280 | 230 | 5 | 0 | 20 | 90 | 102 | 165 | 0 | 20 | 0 | 56 | 0 | 0 | 29 | 300 | 0 | 389 | 0 | 57 | 156 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 6720 | 902 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 1365.99 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 110 | 220 | 0 | 454 | 560 | 17 | 5686.99 | 12406.99 | 101.81
01:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17.5 | 0 | 120 | 60 | 195 | 15 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 90 | 19.5 | 21 | 0 | 320 | 30 | 0 | 18 | 0 | 40 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 67 | 35 | 650 | 0 | 0 | 32 | 0 | 96 | 224 | 0 | 0 | 0 | 575 | 0 | 51 | 127 | 0 | 240 | 280 | 230 | 0 | 0 | 20 | 90 | 103 | 144 | 0 | 20 | 0 | 52 | 0 | 0 | 0 | 300 | 0 | 372 | 0 | 30 | 155 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 6379 | 903 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1097 | 0 | 1306.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 455 | 555 | 0 | 5502.92 | 11881.92 | 101.81
02:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17.5 | 0 | 95 | 30 | 95 | 0 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 70 | 19.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 37 | 650 | 0 | 0 | 32 | 0 | 92 | 224 | 0 | 0 | 0 | 572 | 0 | 51 | 80 | 0 | 240 | 280 | 230 | 0 | 0 | 20 | 88 | 103 | 139 | 0 | 20 | 0 | 52 | 0 | 0 | 0 | 305 | 0 | 362 | 0 | 30 | 151 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 5942 | 903 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1097 | 0 | 1300.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 455 | 540 | 0 | 5401.15 | 11343.15 | 101.81
03:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 17.5 | 0 | 87 | 30 | 0 | 0 | 0 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 52 | 19.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 36 | 650 | 0 | 0 | 32 | 0 | 50 | 225 | 0 | 0 | 0 | 570 | 0 | 51 | 40 | 0 | 240 | 280 | 230 | 0 | 0 | 20 | 71 | 102 | 135 | 0 | 20 | 0 | 50 | 0 | 0 | 0 | 300 | 0 | 361 | 0 | 30 | 150 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 5659 | 906 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 0 | 1197.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 454 | 535 | 0 | 5278.31 | 10937.31 | 101.81
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 17.5 | 0 | 75 | 15 | 0 | 0 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 35 | 19.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 38 | 650 | 0 | 0 | 0 | 0 | 17 | 225 | 0 | 0 | 0 | 577 | 0 | 51 | 0 | 0 | 240 | 280 | 230 | 0 | 0 | 20 | 51 | 104 | 100 | 0 | 20 | 0 | 48 | 0 | 0 | 0 | 300 | 0 | 372 | 0 | 30 | 151 | 8 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 5413 | 906 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 1118.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 454 | 535 | 0 | 5223.73 | 10636.73 | 101.81
05:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 68 | 15 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 35 | 19.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 38 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 0 | 240 | 280 | 230 | 0 | 0 | 20 | 0 | 104 | 34 | 0 | 20 | 0 | 48 | 0 | 0 | 0 | 305 | 0 | 388 | 0 | 30 | 156 | 6 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 5249.5 | 906 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 1026.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 352 | 540 | 0 | 5055.97 | 10305.47 | 101.81
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 68 | 15 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 35 | 19.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 0 | 240 | 280 | 220 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 20 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 383 | 0 | 30 | 158 | 6 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 0 | 0 | 5230.5 | 906 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 1027.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 355 | 542 | 0 | 5062.96 | 10293.46 | 101.81
07:00 | 0 | 40 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 68 | 45 | 0 | 0 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 2 | 35 | 19 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 0.16 | 126 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 5 | 225 | 0 | 0 | 0 | 580 | 1 | 51 | 0 | 0 | 240 | 280 | 220 | 0 | 0 | 5 | 5 | 103 | 23 | 0 | 20 | 0 | 40 | 0 | 1 | 0 | 310 | 0 | 386 | 0 | 30 | 159 | 6 | 0 | 0 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 34 | 0 | 10.9 | 0 | 5265.06 | 906 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 1113 | 0 | 1032.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 7 | 0 | 0 | 2.84 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.25 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.5 | 26 | 0.01 | 0 | 0 | 110 | 220 | 0 | 470 | 550 | 0 | 5316.23 | 10581.29 | 101.81
08:00 | 0 | 52 | 10 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 102 | 45 | 45 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 13 | 35 | 19 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 9 | 650 | 0 | 0 | 0 | 0 | 98 | 225 | 0 | 0 | 0 | 565 | 0 | 51 | 25 | 0 | 240 | 280 | 220 | 0 | 0 | 5 | 29 | 104 | 94 | 0 | 20 | 0 | 40 | 0 | 3 | 0 | 310 | 0 | 311 | 0 | 30 | 149 | 6 | 0 | 75 | 30 | 0 | 0 | 160 | 17 | 48 | 28 | 33 | 1 | 4.34 | 0 | 5487.34 | 905 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1079 | 0 | 1006.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.54 | 42 | 0 | 0 | 17.25 | 180 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 1.5 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 1.1 | 66 | 0.11 | 0 | 0 | 110 | 180 | 0 | 501 | 540 | 0 | 5339.4 | 10826.74 | 101.81
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 101 | 60 | 45 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 15 | 35 | 26 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 5 | 650 | 0 | 0 | 0 | 0 | 51 | 225 | 0 | 0 | 0 | 576 | 2 | 43 | 50 | 0 | 250 | 280 | 220 | 0 | 0 | 5 | 30 | 104 | 51 | 0 | 20 | 0 | 52 | 0 | 16 | 0 | 300 | 0 | 314 | 0 | 30 | 140 | 5 | 0 | 76 | 30 | 0 | 0 | 159 | 17 | 48 | 28 | 32 | 2 | 34.16 | 0 | 5520.16 | 907 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 995 | 0 | 941.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.23 | 73 | 0 | 0 | 33.1 | 167 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 2.52 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.3 | 136 | 0.18 | 0 | 0 | 110 | 180 | 0 | 501 | 530 | 0 | 5277.12 | 10797.28 | 101.81
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 72 | 60 | 47 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 15 | 35 | 25 | 21 | 0 | 324 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 1.09 | 126 | 0 | 3 | 650 | 0 | 0 | 0 | 0 | 50 | 224 | 0 | 0 | 0 | 585 | 1 | 0 | 61 | 0 | 235 | 280 | 220 | 0 | 0 | 5 | 31 | 103 | 48 | 0 | 20 | 0 | 52 | 0 | 7 | 0 | 305 | 0 | 350 | 0 | 30 | 150 | 5 | 0 | 76 | 30 | 0 | 0 | 161 | 17 | 48 | 28 | 27 | 1 | 16.55 | 2 | 5511.64 | 905 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 945 | 0 | 919.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.58 | 102 | 0 | 0 | 41.49 | 140 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 2.25 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5.4 | 168 | 0.22 | 0 | 0 | 110 | 220 | 0 | 501 | 545 | 0 | 5260.49 | 10772.13 | 101.81
11:00 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17.5 | 0 | 75 | 75 | 158 | 4 | 6 | 54 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 15 | 63 | 24 | 21 | 0 | 324 | 6 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 1.02 | 126 | 7 | 5 | 650 | 17 | 0 | 9 | 0 | 93 | 224 | 0 | 0 | 0 | 582 | 0 | 0 | 98 | 0 | 215 | 280 | 220 | 0 | 0 | 5 | 43 | 102 | 52 | 0 | 17 | 21 | 48 | 2 | 20 | 0 | 320 | 0 | 350 | 0 | 30 | 161 | 5 | 0 | 78 | 30 | 0 | 0 | 0 | 17 | 48 | 28 | 27 | 1 | 29.71 | 6 | 5776.23 | 906 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 80 | 976 | 0 | 934.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.78 | 85 | 0 | 0 | 32.4 | 145 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 4.17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 5 | 188 | 0.46 | 0 | 0 | 110 | 220 | 0 | 501 | 560 | 0 | 5422.69 | 11198.92 | 101.81
12:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17.5 | 0 | 127 | 107 | 195 | 40 | 19 | 54 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 22 | 70 | 23 | 21 | 0 | 320 | 45 | 48 | 23 | 0 | 20 | 0 | 0 | 0 | 12 | 12 | 0.81 | 166 | 81 | 8 | 650 | 17 | 0 | 29 | 0 | 106 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 112 | 0 | 215 | 270 | 220 | 0 | 0 | 5 | 56 | 100 | 49 | 0 | 17 | 52 | 54 | 26 | 18 | 9 | 310 | 0 | 334 | 0 | 30 | 158 | 5 | 0 | 75 | 30 | 0 | 0 | 0 | 17 | 48 | 28 | 11 | 2 | 11.63 | 6 | 6226.94 | 905 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 1061 | 0 | 1103.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.5 | 68 | 0 | 0 | 59.8 | 180 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 3.77 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 6.3 | 170 | 0.53 | 0 | 0 | 110 | 220 | 0 | 502 | 550 | 0 | 5699.47 | 11926.41 | 101.81
13:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17.5 | 0 | 144 | 107 | 245 | 40 | 35 | 54 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 31 | 108 | 24 | 21 | 0 | 300 | 57 | 45 | 42 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 1.28 | 166 | 92 | 5 | 650 | 17 | 0 | 32 | 2 | 102 | 222 | 0 | 0 | 0 | 565 | 1 | 0 | 115 | 0 | 215 | 270 | 220 | 0 | 0 | 5 | 54 | 102 | 50 | 0 | 17 | 70 | 60 | 52.2 | 11 | 29 | 325 | 0 | 370 | 0 | 30 | 160 | 5 | 0 | 79 | 30 | 0 | 0 | 0 | 17 | 48 | 28 | 10 | 2 | 48.19 | 0 | 6529.17 | 906 | 192 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 1107 | 0 | 1159.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.57 | 68 | 0 | 0 | 49.53 | 195 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 5.3 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 5.8 | 129 | 0.38 | 0 | 0 | 110 | 220 | 0 | 502 | 575 | 0 | 5838.76 | 12367.93 | 101.81
14:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17.5 | 1 | 149 | 107 | 245 | 40 | 35 | 54 | 0 | 200 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 25 | 108 | 25 | 21 | 0 | 300 | 87 | 45 | 44 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 0.33 | 166 | 102 | 6 | 650 | 17 | 0 | 32 | 25 | 94 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 115 | 0 | 210 | 270 | 220 | 0 | 0 | 5 | 48 | 103 | 47 | 0 | 15 | 70 | 62 | 52.2 | 8 | 29 | 310 | 0 | 386 | 0 | 30 | 147 | 5 | 0 | 79 | 30 | 0 | 0 | 80 | 17 | 48 | 28 | 10 | 0 | 36.02 | 0 | 6612.05 | 906 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 1087 | 0 | 1171.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 86 | 0 | 0 | 43.72 | 177 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 2.83 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 4.9 | 110 | 0.32 | 0 | 0 | 110 | 180 | 0 | 501 | 550 | 0 | 5628.91 | 12240.96 | 101.81
15:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 17.5 | 17 | 149 | 104 | 245 | 40 | 35 | 54 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 18 | 90 | 23.7 | 21 | 0 | 300 | 90 | 45 | 32 | 0 | 22 | 0 | 0 | 0 | 12 | 12 | 0.73 | 166 | 103 | 5 | 650 | 17 | 0 | 32 | 8 | 95 | 224 | 0 | 0 | 0 | 578 | 0 | 0 | 120 | 0 | 210 | 270 | 220 | 0 | 0 | 5 | 50 | 103 | 51 | 0 | 15 | 34 | 54 | 25 | 7 | 29 | 310 | 0 | 386 | 0 | 30 | 147 | 5 | 0 | 79 | 30 | 0 | 0 | 97 | 17 | 48 | 28 | 10 | 1 | 28.09 | 0 | 6495.02 | 902 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1100 | 0 | 1214.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 69 | 0 | 0 | 33.84 | 175 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 3.27 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3.5 | 96 | 0.13 | 0 | 0 | 100 | 220 | 0 | 502 | 540 | 0 | 5633.99 | 12129.01 | 101.8
16:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 27.5 | 17 | 149 | 60 | 245 | 40 | 35 | 62 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 7 | 70 | 23 | 21 | 0 | 320 | 60 | 16 | 24 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 0.11 | 166 | 101 | 6 | 650 | 17 | 0 | 33 | 8 | 96 | 224 | 0 | 0 | 0 | 580 | 1 | 0 | 122 | 0 | 210 | 270 | 220 | 0 | 0 | 5 | 51 | 102 | 51 | 0 | 15 | 34 | 52 | 25 | 7 | 29 | 310 | 0 | 387 | 0 | 30 | 147 | 5 | 0 | 81 | 30 | 0 | 0 | 80 | 17 | 48 | 28 | 10 | 0 | 11.94 | 0 | 6334.55 | 902 | 178 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 1101 | 0 | 1235.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.36 | 26 | 0 | 0 | 8.7 | 175 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0.63 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.5 | 26 | 0.11 | 4 | 0 | 100 | 220 | 0 | 503 | 541 | 0 | 5475.18 | 11809.73 | 101.8
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 38.2 | 17 | 149 | 60 | 245 | 49 | 35 | 67 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 82 | 23 | 9 | 0 | 314 | 65 | 16 | 24 | 0 | 20 | 0 | 9 | 0 | 24 | 12 | 0.01 | 126 | 103 | 9 | 650 | 54 | 0 | 33 | 8 | 101 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 127 | 0 | 205 | 270 | 220 | 0 | 0 | 5 | 51 | 102 | 52 | 0 | 12 | 34 | 62 | 25 | 0 | 29 | 315 | 0 | 387 | 0 | 30 | 157 | 5 | 0 | 81 | 30 | 0 | 0 | 80 | 17 | 48 | 28 | 11 | 0 | 0.7 | 0 | 6369.91 | 902 | 170 | 0 | 3 | 15 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 1115 | 0 | 1264.78 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8 | 1.19 | 3 | 10 | 0 | 2.75 | 182 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0.19 | 0 | 0 | 50 | 1 | 34 | 0 | 0 | 0 | 0.2 | 2 | 0.1 | 16 | 0 | 100 | 190 | 0 | 502 | 543 | 0 | 5544.21 | 11914.12 | 101.79
18:00 | 0 | 63 | 16 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 51.3 | 17 | 149 | 125 | 293 | 55 | 35 | 126 | 0 | 200 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 142 | 23 | 0 | 0 | 380 | 84 | 16 | 34 | 0 | 21 | 65 | 47 | 0 | 24 | 12 | 0 | 126 | 102 | 15 | 650 | 126 | 0 | 39 | 18 | 102 | 223 | 0 | 0 | 0 | 600 | 0 | 0 | 128 | 0 | 218 | 138 | 235 | 0 | 0 | 37 | 53 | 102 | 146 | 0 | 19 | 114 | 66 | 41 | 0 | 29 | 320 | 0 | 388 | 0 | 30 | 157 | 15 | 0 | 81 | 30 | 0 | 0 | 97 | 17 | 48 | 28 | 11 | 0 | 0 | 0 | 7189.3 | 908 | 162 | 0 | 19 | 68 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 1455.43 | 0 | 30 | 0 | 20 | 68 | 0 | 55 | 15 | 34 | 0 | 0 | 25 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 109 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 110 | 220 | 0 | 502 | 555 | 17 | 6338.43 | 13527.73 | 101.79
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 52 | 17 | 149 | 125 | 297 | 55 | 35 | 144 | 0 | 200 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 142 | 23 | 17 | 0 | 350 | 97 | 16 | 44 | 0 | 16 | 65 | 62 | 0 | 24 | 12 | 0 | 158 | 101 | 18 | 650 | 126 | 0 | 50 | 25 | 100 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 137 | 0 | 219 | 0 | 220 | 0 | 0 | 38 | 70 | 103 | 189 | 0 | 19 | 107 | 66 | 52.2 | 0 | 29 | 310 | 0 | 354 | 0 | 30 | 159 | 15 | 0 | 81 | 30 | 0 | 0 | 97 | 17 | 48 | 28 | 11 | 0 | 0 | 0 | 7119.2 | 908 | 151 | 0 | 35 | 60 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 1457.64 | 0 | 48 | 0 | 35 | 110 | 0 | 97 | 22 | 43 | 0 | 0 | 25 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 110 | 220 | 0 | 502 | 580 | 17 | 6541.64 | 13660.84 | 101.78
19:30 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 49.4 | 17 | 149 | 125 | 297 | 55 | 35 | 144 | 0 | 200 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 350 | 93 | 16 | 24 | 0 | 18 | 50 | 62 | 0 | 24 | 24 | 0 | 166 | 101 | 22 | 650 | 126 | 0 | 33 | 25 | 95 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 136 | 0 | 250 | 0 | 280 | 0 | 0 | 38 | 70 | 103 | 177 | 0 | 19 | 70 | 68 | 52.2 | 0 | 29 | 310 | 0 | 371 | 0 | 30 | 154 | 23 | 0 | 81 | 30 | 0 | 0 | 97 | 17 | 48 | 28 | 11 | 0 | 0 | 0 | 7160.6 | 908 | 151 | 0 | 31 | 55 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 1444.44 | 0 | 48 | 0 | 35 | 70 | 0 | 97 | 26 | 16 | 0 | 0 | 25 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 502 | 585 | 17 | 6352.44 | 13513.04 | 0
20:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 47.8 | 17 | 149 | 125 | 297 | 55 | 35 | 144 | 0 | 200 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 350 | 89 | 16 | 27 | 0 | 13 | 34 | 62 | 0 | 24 | 24 | 0 | 166 | 102 | 27 | 650 | 126 | 0 | 33 | 25 | 94 | 225 | 0 | 0 | 0 | 577 | 0 | 0 | 137 | 0 | 270 | 0 | 330 | 0 | 0 | 38 | 70 | 103 | 173 | 0 | 19 | 43 | 62 | 25 | 0 | 29 | 305 | 0 | 355 | 0 | 30 | 154 | 23 | 0 | 81 | 30 | 0 | 0 | 97 | 17 | 48 | 28 | 11 | 0 | 0 | 0 | 7102.8 | 907 | 151 | 0 | 31 | 53 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 1437.65 | 0 | 48 | 0 | 35 | 70 | 0 | 97 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 110 | 220 | 0 | 502 | 582 | 17 | 6275.65 | 13378.45 | 101.78
21:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 46.4 | 17 | 149 | 125 | 297 | 55 | 35 | 144 | 0 | 200 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 90 | 24.5 | 21 | 0 | 360 | 60 | 16 | 15 | 0 | 18 | 34 | 62 | 6 | 24 | 24 | 0 | 166 | 103 | 32 | 650 | 85 | 0 | 33 | 8 | 95 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 142 | 0 | 375 | 0 | 330 | 2 | 0 | 38 | 52 | 103 | 174 | 0 | 19 | 34 | 70 | 25 | 0 | 29 | 310 | 0 | 370 | 0 | 30 | 156 | 23 | 0 | 81 | 30 | 0 | 0 | 97 | 17 | 49 | 28 | 11 | 0 | 0 | 0 | 7101.9 | 908 | 154 | 0 | 13 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 1449 | 0 | 47 | 0 | 0 | 70 | 0 | 97 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 504 | 550 | 17 | 6159 | 13260.9 | 101.77
22:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 50.5 | 17 | 149 | 125 | 294 | 55 | 35 | 108 | 0 | 200 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 90 | 24.5 | 21 | 0 | 350 | 60 | 16 | 12 | 0 | 13 | 33 | 54 | 17 | 24 | 24 | 0 | 166 | 104 | 33 | 650 | 85 | 0 | 33 | 8 | 99 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 143 | 0 | 345 | 0 | 330 | 18 | 0 | 38 | 34 | 103 | 184 | 0 | 19 | 34 | 66 | 25 | 0 | 29 | 315 | 0 | 373 | 0 | 30 | 161 | 23 | 0 | 81 | 30 | 0 | 0 | 97 | 17 | 49 | 28 | 18 | 0 | 0 | 0 | 7067 | 908 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 1413 | 0 | 40 | 0 | 0 | 70 | 0 | 97 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 504 | 545 | 17 | 6047 | 13114 | 101.77
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17.5 | 0 | 149 | 126 | 294 | 55 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 90 | 20 | 21 | 0 | 300 | 60 | 16 | 12 | 0 | 12 | 33 | 53 | 17 | 24 | 24 | 0 | 166 | 103 | 35 | 650 | 85 | 0 | 33 | 8 | 97 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 143 | 0 | 335 | 0 | 330 | 20 | 0 | 35 | 34 | 103 | 176 | 0 | 19 | 34 | 66 | 25 | 0 | 29 | 310 | 0 | 370 | 0 | 30 | 157 | 23 | 0 | 81 | 30 | 0 | 0 | 97 | 17 | 49 | 28 | 18 | 0 | 0 | 0 | 6848.5 | 907 | 166 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 1424 | 0 | 40 | 0 | 0 | 50 | 0 | 97 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 70 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 503 | 542 | 17 | 6021 | 12869.5 | 101.76
Total KWH | 0 | 1536000 | 433440 | 0 | 0 | 0 | 0 | 0 | 8186400 | 0 | 0 | 518400 | 151560 | 2885616 | 1868640 | 3975905 | 676403 | 531058 | 1563840 | 0 | 4694500 | 0 | 0 | 0 | 140232 | 6291548 | 0 | 0 | 169380 | 1833600 | 523800 | 467280 | 0 | 7904090.91 | 1035000 | 371345 | 369600 | 0 | 450720 | 302136 | 379104 | 62007 | 349440 | 317760 | 7184 | 3404940 | 1489600 | 526560 | 15621818.18 | 824655 | 0 | 567840 | 168557.4 | 1968799 | 5465720 | 0 | 0 | 0 | 13909089 | 7020 | 487688 | 2246472 | 0 | 6072500 | 5293200 | 5936000 | 67680 | 0 | 431568 | 1120320 | 2461243 | 2439360 | 0 | 418870 | 697680 | 1304640 | 466944 | 99736 | 344176 | 7522500 | 0 | 9189000 | 0 | 757440 | 3707182 | 198432 | 0 | 1835520 | 716832 | 0 | 0 | 3027540 | 430560 | 1152000 | 660000 | 476160 | 9200 | 212720 | 18720 | 151752470.49 | 21923636 | 4793472 | 0 | 91200 | 179840 | 912000 | 0 | 0 | 0 | 0 | 0 | 501840 | 26021820 | 0 | 29356364 | 0 | 275612 | 0 | 111456 | 552768 | 0 | 532464 | 149694 | 85843 | 286442 | 610971 | 157956 | 0 | 310496 | 4467127 | 0 | 0 | 0 | 0 | 0 | 8738327 | 0 | 25260 | 0 | 0 | 667689 | 233538 | 664752 | 0 | 0 | 0 | 39457.44 | 1096560 | 2866 | 784032 | 0 | 2600000 | 5319900 | 0 | 11489424 | 13538909.09 | 134400 | 136656115.53 | 288408586.02

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11926.41 | MW | 12:00 Hr. | Energy Generated |  |  | 288.4086 |  | MKWHr.
| Day Peak Demand |  |  | 11926.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.32 |  | MKWHr.
| Evening Peak Generation |  |  | 13660.84 | MW | 19:00 Hr. | Energy Demand |  |  | 288.7286 |  | MKWHr.
| Evening Peak Demand |  |  | 13710.84 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.8 |  | °C
| Minimum Generation of the Day |  |  | 10293.46 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 783.62 |  | MMCFD
| Maximum Generation of the Day |  |  | 13660.84 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.8337 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.0676 | 0 | 16.1147 | 0 | 0 | 0.16938 | 0 | 0 | 44.3517 | Gas | 108.5781 | Gas | 378440146.3347
| Chattogram Zone |  |  | 5.9923 | 29.5309 | 8.2058 | 0 | 3.4049 | 0.014204 | 0 | 0.45072 | 47.5989 | Coal | 80.5811 | Coal | 523185194.4064
| Cumilla Zone |  |  | 21.1687 | 0 | 7.315 | 0 | 0 | 0.099736 | 1.3046 | 0 | 29.8881 | HFO | 38.2845 | HFO | 684664274.876
| Mymensingh Zone |  |  | 0.47616 | 0 | 2.2613 | 0 | 0 | 0.22192 | 0 | 0 | 2.9594 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9544 | Hydro | 3.4049 | Hydro | 340494
| Khulna Zone |  |  | 4.7935 | 26.0218 | 0.27104 | 0 | 0 | 0.50184 | 22.8356 | 0 | 54.4238 | Solar | 3.6127 | Solar | 59606119.4804
| Barishal Zone |  |  | 7.9199 | 25.0283 | 0.91843 | 0 | 0 | 0.002866 | 0 | 0 | 33.8695 | Import | 53.4966 | Import | 318034358.2
| Rajshahi Zone |  |  | 13.2055 | 0 | 1.8658 | 0 | 0 | 1.2332 | 29.3564 | 0 | 45.6608 | Wind | 0.45072 | Wind | 6630091.2
| Rangpur Zone |  |  | 0 | 0 | 1.3324 | 0 | 0 | 1.3696 | 0 | 0 | 2.702
| Total |  |  | 108.5781 | 80.5811 | 38.2845 | 0 | 3.4049 | 3.6127 | 53.4966 | 0.45072 | 288.4086
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 378440146.3347 |  | Hydro | 340494
|  |  |  | Coal | 523185194.4064 |  | Solar | 59606119.4804
|  |  |  | HFO | 684664274.876 |  | Import | 318034358.2
|  |  |  | HSD | 0 |  | Wind | 6630091.2
[5 empty] | Total: | 197,09,00,678 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9236 | Peak Hr Flow | 908.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49460018.25 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.3564 | Peak Hr Flow | 1457.64 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2402 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3046 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2612 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.5846 | Peak Hr Flow | 2431.64 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5205
|  |  |  | Chattogram |  | 0 |  | 1275
|  |  |  | Cumilla |  | 0 |  | 1219
|  |  |  | Mymensingh |  | 48 |  | 950
|  |  |  | Sylhet |  | 0 |  | 534
|  |  |  | Khulna |  | 0 |  | 1531
|  |  |  | Barishal |  | 0 |  | 413
|  |  |  | Rajshahi |  | 0 |  | 1178
|  |  |  | Rangpur |  | 0 |  | 772
|  |  |  | Total |  | 48 |  | 13077
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 15:57 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Annual maintenance
vwork.
| 08:04 | 18:31 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to 132/33 kv TR-01 bay annual
maintenance.
| 08:04 | 18:31 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to 132/33 kv TR-01 bay annual
maintenance.
| 08:13 | 11:35 | Srinagar 132/33kV S/S 33 kV bus Scheduled S/D Due to 132/33 kv TR-01 bay annual
maintenance.
| 08:15 | 16:21 | Panchagar-Thakurgaon 132kV Ckt-1 Scheduled S/D from Panchagarh 132/33kV end Due to
Annual maintenance work
| 08:17 | 16:27 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Meghnaghat 230/132kV end Due to
Annual maintenance work, and from Cumilla(N) 230/132/33kVend.
| 08:18 |  | Naogaon 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintanence.
| 08:19 |  | Naogaon 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintanence
| 08:20 | 16:24 | Amnura 132/33kV S/S Amnura - 100MW PPP Scheduled S/D Due to Annual Maintenance
| 08:22 | 10:37 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Faridpur 132/33kV end.
| 08:27 | 16:20 | Panchagar-Thakurgaon 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due to For
Annual Maintenance
| 08:30 | 16:25 | Shahjadpur 132/33kV S/S T-2(415T) LT Scheduled S/D Due to Annual maintenance
| 08:30 | 16:25 | Shahjadpur 132/33kV S/S T-2(415T) HT Scheduled S/D Due to Annual maintenance
| 08:33 | 14:51 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to Annual maintenance work at
Bhaluka end.
| 08:34 | 10:37 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Gopalganj 400/132kV end Due to
Annual Maintenance
| 08:35 | 17:10 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Annual maintenance.
| 08:35 | 17:22 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Annual Maintenance.
| 08:40 | 17:03 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annual maintenance
| 08:43 | 16:13 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Scheduled S/D from Bog-Sherpur 132/33kV end Due
to Annual Maintenance Work. and from Bogura 230/132kV end Due to Annual Maintenance Work
| 08:45 | 17:02 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual maintenance
| 08:58 | 15:08 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 09:15 | 11:36 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to Annual Maintenance
| 09:15 | 11:36 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to Annual Maintenance
| 09:23 | 17:18 | New Tongi-Tongi 132kV Ckt-2 Scheduled S/D from New Tongi end Due to Annual Maintenance
and from Tongi 230/132/33kV end Due to Annual maintenance work
| 09:25 | 12:40 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Annual maintenance.
| 09:26 | 12:39 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Annual maintenance.
| 09:30 | 16:59 | BSRM-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end.
| 09:30 | 13:54 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end.
| 09:40 | 10:53 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing siemens
7sa87, L8b relays Due to distance protection operated and from Ghorashal 230kV end
showing Siprotec 7SA611 relays Due to Unknown
| 09:55 | 17:07 | GPH 230/33kV S/S Transformer-01(D05) HT Forced S/D Due to bushing check of 11kv .
| 10:07 | 14:37 | Mithapukur 132/33kV S/S TR-2 (414T) LT Scheduled S/D Due to For annual maintenance work.
| 10:08 | 14:37 | Mithapukur 132/33kV S/S TR-2 (414T) HT Scheduled S/D Due to For annual maintenance work.
| 10:35 | 12:37 | Saidpur 132/33kV S/S TR-01 HT Scheduled S/D Due to Oil filling.
| 10:38 | 12:31 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Scheduled S/D
| 10:38 | 12:31 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
|  | 10:39 | Goalpara 132/33kV S/S T-5 HT is restored.
|  | 10:40 | Goalpara 132/33kV S/S T-5 LT is restored.
|  | 10:41 | Goalpara 132/33kV S/S T-6 HT is restored.
|  | 10:42 | Goalpara 132/33kV S/S T-6 LT is restored.
| 10:55 |  | Sylhet 225MW tripped showing generator protection relay.
| 10:58 |  | Sylhet (South) S/S Sylhet (S)-Biyanibazar 132KV Ckt-1 Scheduled S/D Due to for project
work,
| 10:58 |  | Sylhet (South) S/S Sylhet (S)-Biyanibazar 132KV Ckt-2 Scheduled S/D Due to project work
| 11:02 | 17:07 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance of TR-02
| 11:02 | 16:50 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintenance of TR-02
| 11:44 |  | Kaptai-2 was sync.
| 12:00 |  | Day peak Generation is 11921 MW
|  | 12:10 | Bibiana 400/230kV S/S Bibiyana-South is restored.
| 12:23 | 12:54 | Coxsbazar 132/33kV S/S 405T-T1 LT Tripped showing 1. OC/EF 2.Lockout relays Due to | [7 empty] | 38.0MW load
|  |  | Kolatoli-1 triped due to eagle fall in line | [7 empty] | interrup.
| 12:40 | 14:07 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
| 13:04 | 14:01 | BIPTC S/S 10CF25 Tripped showing 87 relays Due to Tripped by bird flashover
| 13:04 | 14:01 | BIPTC S/S 10CF25 Tripped showing 87 relays Due to Tripped by bird flashover
| 13:14 | 14:47 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual maintenance Work.
| 13:15 | 14:49 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual Maintenance Work.
| 13:20 | 14:32 | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Red hot maintenance. | [7 empty] | 8.0MW load
interrup.
| 13:21 | 14:32 | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to Red hot maintenance. | [7 empty] | 8.0MW load
interrup.
| 13:24 |  | Sylhet 225MW GT was sync.
| 13:32 | 14:01 | BIPTC S/S 10CF25 Scheduled S/D Due to Tripped by bird flashover
| 14:09 | 17:28 | Gopalganj 132/33kV S/S T1 LT Tripped showing Siprotec 7sj82 relays Due to Gpbs-2& bpbs-1 | [7 empty] | 30.0MW load
|  |  | trip | [7 empty] | interrup.
| 14:21 |  | Hathazari 230/132/33kV S/S T-02 LT Forced S/D Due to oil leakage
| 14:21 |  | Hathazari 230/132/33kV S/S T-02 HT Forced S/D Due to oil leakage
|  | 14:22 | Juldah 132/33kV S/S 133/33 KV T-2 416T LT is restored.
|  | 14:25 | Goalpara 132/33kV S/S Bus 2 is restored.
|  | 14:27 | Juldah 132/33kV S/S 133/33 KV T-2 416T HT is restored.
|  | 14:28 | Goalpara 132/33kV S/S T1 HT is restored.
|  | 14:29 | Goalpara 132/33kV S/S T1 LT is restored.
| 14:56 | 16:34 | Jaldhaka-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to For annual
maintanance. and from Jaldhaka 132/33kV end Due to Anual Maintenance
| 15:06 |  | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Annual Maintenance Work
| 15:07 |  | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Annual Maintenance Work
| 15:23 | 17:28 | Gopalganj 132/33kV S/S T1 HT Forced S/D Due to 33kv Incomer-1 Trip by Under frequency -1
& 2, trip ckt unhealthy
| 16:00 | 16:40 | Gopalganj 400/132kV S/S ATR-01 LT Forced S/D Due to Annual Maintenance
| 16:01 |  | Kaptai Unit-2 was forced shutdown due to cooler leakage
| 16:02 | 16:51 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kv Nabinagar feeder bus DS | [7 empty] | 100.0MW load
|  |  | redhot maintenance work. | [7 empty] | interrup.
| 16:02 | 16:39 | Gopalganj 400/132kV S/S ATR-01 HT Forced S/D Due to Annual Maintenance
| 16:02 | 17:50 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kv Nabinagar feeder bus DS | [7 empty] | 100.0MW load
|  |  | redhot maintenance work. | [7 empty] | interrup.
|  | 16:05 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT is restored.
| 16:06 | 16:17 | Kachua 230/132/33kV S/S ATR-2 HT Project Work S/D Due to for meter accuracy checking
| 16:06 | 16:17 | Kachua 230/132/33kV S/S ATR-2 LT Project Work S/D Due to for meter accuracy checking
|  | 16:14 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
|  | 16:15 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
|  | 16:15 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT is restored.
| 16:27 | 16:52 | Lakshmipur 132/33kV S/S Transformer-1 LT Forced S/D Due to Metering Test.
| 16:40 | 16:55 | Gopalganj 400/132kV S/S ATR-02 HT Forced S/D Due to Annual Maintenance
| 16:41 | 16:56 | Gopalganj 400/132kV S/S ATR-02 LT Forced S/D Due to Annual Maintenance
|  | 16:42 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 is restored.
| 17:00 | 17:05 | Lakshmipur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Metering Test.
|  | 17:02 | Aminbazar-Kallyanpur 132kV Ckt-1 is restored.
|  | 17:36 | Nawabganj 132/33kV S/S TR-1 HT is restored.
|  | 17:37 | Nawabganj 132/33kV S/S TR-1 LT is restored.
| 17:56 |  | Ashuganj North CCPP ST was shutdown due to gas shortage
| 18:05 |  | Kaptai unit-2 was synchronized
|  | 18:07 | Gopalganj 400/132kV S/S 132kV Bus-01 is restored.
| 18:59 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 19:14 | 20:02 | Natore 132/33kV S/S TR-4 (435 T) LT Forced S/D Due to Red Hot Maintenance Work | [7 empty] | 27.0MW load
interrup.
| 19:14 | 20:01 | Natore 132/33kV S/S TR-4 (435 T) HT Forced S/D Due to Red Hot Maintenance Work | [7 empty] | 27.0MW load
interrup.
| 20:40 | 20:51 | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Protection Test | [7 empty] | 30.0MW load
interrup.
| 20:41 | 20:49 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Protection Teat | [7 empty] | 30.0MW load
interrup.
| 05:01 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- ST
| 05:18 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
| 06:00 |  | Minimum Generation is 10555 MW
| 07:00 | 08:00 | Meghnaghat 400/230kV S/S ATR - 2 LT Scheduled S/D Due to Maintanace Work
| 07:01 | 07:59 | Meghnaghat 400/230kV S/S ATR - 2 HT Scheduled S/D Due to Maintanace Work
| 07:03 |  | Bakulia 132/33kV S/S T-4 (432T) HT Scheduled S/D Due to Annual Maintenance.
| 07:11 |  | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Annual maintenance work.
| 07:12 |  | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Annual maintenance work.
| 07:26 |  | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to For annual maintenance
| 07:27 |  | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to For annual maintenance
| 07:49 |  | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Meghnaghat 230/132kV end Due to For
annual maintenance work.
| 07:57 |  | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 324 | 8186400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 200 | 4694500 | GT-2 U/M
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 676403 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6291548 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 52 | 518400 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1868640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 531058 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 140232 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 523800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 467280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 433440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 297 | 3975905 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2885616 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1536000 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1563840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 169380 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 151560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 7904090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1833600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2321 | 44351692.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 168557.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 7020 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 567840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3404940 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 5465720 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 100 | 1968799 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 62 | 379104 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 302136 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 349440 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 526560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 369600 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 7184 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 371345 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 62007 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 101 | 1489600 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 317760 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 97 | 1035000 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 126 | 824655 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 13909089 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 16 | 450720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15621818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2369 | 47598894.58
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 5293200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 220 | 5936000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 219 | 6072500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 431568 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 67680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 487688 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 2246472 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 344176 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2461243 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 189 | 2439360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1304640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 466944 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 418870 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 107 | 697680 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 70 | 1120320 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 99736 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1249.2 | 29888077
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 476160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 660000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1152000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 212720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 18720 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 430560 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 104 | 2959360
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 757440 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 159 | 3707182 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716832 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1835520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 3027540 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 15 | 198432 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7522500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 354 | 9189000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1076 | 26954446
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 908 | 21923636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 91200 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 179840 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 151 | 4793472 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 501840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1148 | 26021820 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2340 | 54423808
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 502 | 11489424 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 108 | 784032 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2600000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 580 | 13538909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5319900 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 134400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2866 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1537 | 33869531.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 286442 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 275612 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 149694 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 187 | 4467127 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 412 | 8738327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 157956 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 85843 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 532464 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 110 | 552768 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 111456 | Engine Problem
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25260 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1457.64 | 29356364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 310496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 610971 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2436.64 | 45660780
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 664752 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39457.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 667689 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 233538 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1096560 | -
Rangpur Area Total |  |  |  |  | 950 | 228 | 2701996.44
Eastern Grid Total |  |  |  |  | 17383.855 | 7119.2 | 151752470.49
Western Grid Total |  |  |  |  | 10821.56 | 6541.64 | 136656115.53
National Grid Total |  |  |  |  | 28205.415 | 13660.84 | 288408586.02
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-11-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9135.57 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3894.2 | MW
i) Dhaka area |  |  | 5205.39 |  | MW | i) Khulna area |  |  |  | 1531 | MW
ii) Chattogram area |  |  | 1275 |  | MW | ii) Barishal area |  |  |  | 413 | MW
iii) Cumilla area |  |  | 1219.18 |  | MW | iii) Rajshahi area |  |  |  | 1178.2 | MW
iv) Mymensingh area |  |  | 902 |  | MW | iv) Rangpur area |  |  |  | 772 | MW
v) Sylhet area |  |  | 534 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13029.77 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 77 | 00:00 | 133 | Niamatpur | 49 | 21:00
2 | AKSML | 118 | 22:00 | 68 | Ishurdi | 69 | 18:30 | 134 | Noapara | 42 | 18:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jaldhaka | 70 | 18:00 | 135 | PHP | 7 | 14:00
4 | Agargaon | 122 | 13:00 | 70 | Jamalpur | 85 | 00:00 | 136 | Pabna | 90 | 18:00
5 | Agrabad | 86 | 14:00 | 71 | Jashore | 122 | 18:00 | 137 | Palashbari | 101 | 18:30
6 | Amnura | 17 | 20:00 | 72 | Jhenaidah | 121 | 18:00 | 138 | Panchagarh | 50 | 18:00
7 | Ashuganj | 71 | 23:00 | 73 | Joydebpur | 158 | 18:00 | 139 | Patiya | 7.3 | 19:30
8 | BSRM | 202 | 17:00 | 74 | Joypurhat | 48 | 18:00 | 140 | Patuakhali | 58 | 21:00
9 | Bagerhat | 74 | 18:00 | 75 | Juldah | 15.5 | 18:00 | 141 | Payra | 28 | 00:00
10 | Bajitpur | 79 | 00:00 | 76 | KSRM | 40 | 23:00 | 142 | Postogola | 61 | 12:00
11 | Bakulia | 78 | 18:00 | 77 | Kabirpur | 259 | 15:00 | 143 | Purbachal | 16 | 12:00
12 | Banani | 46.8 | 13:00 | 78 | Kachua | 77 | 00:00 | 144 | Purbasadipur | 99 | 18:00
13 | Bangabhaban | 23 | 10:00 | 79 | Kallyanpur | 105 | 19:00 | 145 | Rahanpur | 26 | 20:00
14 | Barapukuria | 54 | 18:30 | 80 | Kalurghat | 48 | 12:00 | 146 | Rahim | 42 | 16:00
15 | Barguna | 18 | 01:00 | 81 | Kamrangirchar | 76 | 18:30 | 147 | Rajbari | 74 | 18:00
16 | Barishal | 95 | 18:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 114 | 19:00
17 | Barishal-230 | 98 | 18:00 | 83 | Kasba | 32 | 00:00 | 149 | Rajshahi | 112 | 18:30
18 | Baroaulia | 64 | 16:00 | 84 | Kazla | 111 | 18:30 | 150 | Rajshahi-230 | 44 | 18:00
19 | Baroirhat | 61 | 00:00 | 85 | Keranigonj | 79 | 19:00 | 151 | Ramganj | 94 | 18:00
20 | Bashundhara | 192 | 13:00 | 86 | Khagrachori | 26 | 17:00 | 152 | Rampur | 41 | 00:00
21 | BashundharaCement | 8 | 15:00 | 87 | Khulna | 72 | 12:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 72 | 00:00 | 88 | Khulshi | 158 | 14:00 | 154 | Rangpur | 133 | 18:00
23 | Benapole | 56 | 18:30 | 89 | Kishoreganj | 106 | 22:00 | 155 | Ruppur | 6.6 | 10:00
24 | Bhaluka | 137 | 18:00 | 90 | Kodda | 311 | 12:00 | 156 | SSM | 3 | 00:00
25 | Bhandaria | 46 | 21:00 | 91 | Kulaura | 45 | 00:00 | 157 | Saidpur | 98 | 18:00
26 | Bhangura | 33 | 18:30 | 92 | Kurigram | 56 | 18:00 | 158 | Satkhira | 98 | 18:00
27 | Bheramara(GK) | 55 | 18:00 | 93 | Kushtia | 136 | 18:00 | 159 | Satmasjid | 99 | 19:00
28 | Bhulta | 232 | 22:00 | 94 | Laksam | 30 | 00:00 | 160 | Savar | 232 | 12:00
29 | Bog-Sherpur | 54 | 18:00 | 95 | Lakshmipur | 28 | 18:30 | 161 | SevenRings | 2.35 | 08:00
30 | Bogura | 147 | 18:30 | 96 | Lalbag | 62 | 18:00 | 162 | ShahCement | 30 | 23:00
31 | Borhanuddin | 87 | 21:00 | 97 | Lalmonirhat | 52 | 18:00 | 163 | Shahjadpur | 84 | 18:30
32 | Brahmanbaria | 123 | 00:00 | 98 | MI_Cement | 16 | 05:00 | 164 | Shahjibazar | 116 | 00:00
33 | Cantonment | 134 | 13:00 | 99 | Madanganj | 40 | 00:00 | 165 | Shahmirpur | 46 | 18:00
34 | Chandina | 10.57 | 00:00 | 100 | Madaripur | 94 | 22:00 | 166 | Shariatpur | 78 | 21:00
35 | Chandpur | 72 | 18:00 | 101 | Madartek | 82 | 22:00 | 167 | Sherpur | 98 | 00:00
36 | Chandraghona | 31 | 18:00 | 102 | Madunaghat | 49 | 19:30 | 168 | Shikalbaha | 22 | 00:00
37 | Chapai | 50 | 18:30 | 103 | Magura | 58 | 18:00 | 169 | Shitalakhya | 74.6 | 12:00
38 | Charsaidpur | 33 | 00:00 | 104 | Mahasthangarh | 62 | 18:00 | 170 | Sholosohor | 44 | 12:00
39 | Chauddagram | 64 | 00:00 | 105 | Maijdee | 32 | 20:00 | 171 | Shyampur | 128 | 12:00
40 | Chhatak | 35 | 00:00 | 106 | Manikganj | 120 | 18:30 | 172 | Siddhirganj | 119 | 11:00
41 | Chowmuhani | 146 | 18:00 | 107 | Maniknagar | 62 | 13:00 | 173 | Sirajganj | 102 | 18:30
42 | Chuadanga | 95 | 18:00 | 108 | Matarbari | 41 | 18:00 | 174 | Sonargaon | 129 | 00:00
43 | Coxsbazar | 125 | 19:00 | 109 | Matuail | 72 | 15:00 | 175 | Sreemongol | 72 | 00:00
44 | Cumilla(N) | 150 | 01:00 | 110 | Metrorail_Motijheel | 29 | 19:30 | 176 | Sreepur | 98 | 12:00
45 | Cumilla(S) | 135 | 18:30 | 111 | Metrorail_Uttara | 7 | 17:00 | 177 | Srinagar | 44.56 | 22:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 128 | 12:00 | 178 | Sunamganj | 58 | 00:00
47 | Daudkandi | 134 | 22:00 | 113 | Mirpur | 132 | 18:00 | 179 | Sylhet | 49 | 00:00
48 | DhakaUniversity | 88 | 13:00 | 114 | Mirsorai | 10 | 11:00 | 180 | Sylhet-132 | 108 | 19:00
49 | Dhamrai | 122 | 18:00 | 115 | Mirzapur | 38 | 13:00 | 181 | TK | 24 | 00:00
50 | Dhanmondi | 129.5 | 13:00 | 116 | Mithapukur | 52 | 18:00 | 182 | Tangail | 154 | 20:00
51 | Dohazari | 81 | 01:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 19 | 18:00
52 | Faridpur | 148 | 19:00 | 118 | Mogbazar | 89.8 | 15:00 | 184 | Thakurgaon | 82 | 18:30
53 | Fatullah | 106 | 15:00 | 119 | Mongla | 35 | 18:00 | 185 | Tongi | 112 | 15:00
54 | Fenchuganj | 38 | 00:00 | 120 | Motijheel | 43 | 13:00 | 186 | Ullahpara | 33 | 18:30
55 | Feni | 103 | 18:00 | 121 | Muktagacha | 26 | 00:00 | 187 | Ullon | 62 | 18:00
56 | GPH | 3 | 13:00 | 122 | Munshiganj | 107 | 19:30 | 188 | Uttara | 81 | 13:00
57 | Ghatail | 60 | 07:00 | 123 | Muradnagar | 35 | 00:00 | 189 | UttaraNew | 31 | 14:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 167 | 18:00 | 190 | Zigatola | 70 | 13:00
59 | Ghorashal-230 | 97 | 12:00 | 125 | Naogaon | 94 | 18:30
60 | Goalpara | 33 | 18:00 | 126 | Narail | 50 | 18:00
61 | Gollamari | 86 | 18:00 | 127 | Narinda | 72 | 13:00
62 | Gopalganj | 104 | 18:00 | 128 | Narshingdi | 164 | 21:00
63 | Gulshan | 118 | 13:00 | 129 | Natore | 123 | 18:00
64 | Halishahar | 66.5 | 15:00 | 130 | Nawabganj | 42.8 | 22:00
65 | HaripurSBU | 148 | 23:00 | 131 | Netrakona | 118 | 20:00
66 | Hasnabad | 92 | 19:00 | 132 | New | 56 | 11:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12406.99 | 0 |  | 12406.99
1:00 | 11881.92 | 0 |  | 11881.92
2:00 | 11343.15 | 0 |  | 11343.15
3:00 | 10937.31 | 0 |  | 10937.31
4:00 | 10636.73 | 0 |  | 10636.73
5:00 | 10305.47 | 0 |  | 10305.47
6:00 | 10293.46 | 0 |  | 10293.46
7:00 | 10581.29 | 0 |  | 10581.29
8:00 | 10826.74 | 0 |  | 10826.74
9:00 | 10797.28 | 0 |  | 10797.28
10:00 | 10772.13 | 0 |  | 10772.13
11:00 | 11198.92 | 0 |  | 11198.92
12:00 | 11926.41 | 0 |  | 11926.41
13:00 | 12367.93 | 0 |  | 12367.93
14:00 | 12240.96 | 0 |  | 12240.96
15:00 | 12129.01 | 0 |  | 12129.01
16:00 | 11809.73 | 0 |  | 11809.73
17:00 | 11914.12 | 28 |  | 11943.12
18:00 | 13527.73 | 70 |  | 13600.73
19:00 | 13660.84 | 48 |  | 13710.84
19:30 | 13513.04 | 46 |  | 13561.04
20:00 | 13378.45 | 32 |  | 13411.45
21:00 | 13260.9 | 48 |  | 13310.9
22:00 | 13114 | 50 |  | 13166.25
23:00 | 12869.5 | 44 |  | 12915.48
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6720 | 5686.99 | 12406.99 | DAILY GENERATION CURVE
00:30 | 6549.5 | 5594.955 | 12144.455
01:00 | 6379 | 5502.92 | 11881.92 | 05-11-2025
01:30 | 6160.5 | 5452.035 | 11612.535
02:00 | 5942 | 5401.15 | 11343.15
02:30 | 5800.5 | 5339.73 | 11140.23
03:00 | 5659 | 5278.31 | 10937.31
03:30 | 5536 | 5251.02 | 10787.02
04:00 | 5413 | 5223.73 | 10636.73
04:30 | 5331.25 | 5139.85 | 10471.1
05:00 | 5249.5 | 5055.97 | 10305.47
05:30 | 5240 | 5059.465 | 10299.465
06:00 | 5230.5 | 5062.96 | 10293.46
06:30 | 5247.78 | 5189.595 | 10437.375
07:00 | 5265.06 | 5316.23 | 10581.29
07:30 | 5376.2 | 5327.815 | 10704.015
08:00 | 5487.34 | 5339.4 | 10826.74
08:30 | 5503.75 | 5308.26 | 10812.01
09:00 | 5520.16 | 5277.12 | 10797.28
09:30 | 5515.9 | 5268.805 | 10784.705
10:00 | 5511.64 | 5260.49 | 10772.13
10:30 | 5643.935 | 5341.59 | 10985.525
11:00 | 5776.23 | 5422.69 | 11198.92
11:30 | 6001.585 | 5561.08 | 11562.665
12:00 | 6226.94 | 5699.47 | 11926.41
12:30 | 6378.055 | 5769.115 | 12147.17
13:00 | 6529.17 | 5838.76 | 12367.93
13:30 | 6570.61 | 5733.835 | 12304.445
14:00 | 6612.05 | 5628.91 | 12240.96
14:30 | 6553.535 | 5631.45 | 12184.985
15:00 | 6495.02 | 5633.99 | 12129.01
15:30 | 6414.785 | 5554.585 | 11969.37
16:00 | 6334.55 | 5475.18 | 11809.73
16:30 | 6352.23 | 5509.695 | 11861.925
17:00 | 6369.91 | 5544.21 | 11914.12
17:30 | 6779.605 | 5941.32 | 12720.925
18:00 | 7189.3 | 6338.43 | 13527.73
18:30 | 7154.25 | 6440.035 | 13594.285
19:00 | 7119.2 | 6541.64 | 13660.84
19:30 | 7160.6 | 6352.44 | 13513.04
20:00 | 7102.8 | 6275.65 | 13378.45
20:30 | 7102.35 | 6217.325 | 13319.675 |  | Executive Engineer
21:00 | 7101.9 | 6159 | 13260.9 |  | Network Operation Division
21:30 | 7084.45 | 6103 | 13187.45
22:00 | 7067 | 6047 | 13114
22:30 | 6957.75 | 6034 | 12991.75
23:00 | 6848.5 | 6021 | 12869.5

## En-Curve
QF-LDC-12
Date | 05-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3252 | 1444.5 | 902 | 38 | 56 | 1365.99 | 126 | 3353 | 0 | 340 | 1522.5 | 0 | 0 | 7 | 0 | DAILY ENERGY CURVE
00:30 | 3214 | 1436 | 902.5 | 38 | 54 | 1336.455 | 126 | 3342.5 | 0 | 288 | 1383.5 | 0 | 0 | 23.5 | 0 | 05-11-2025
01:00 | 3176 | 1427.5 | 903 | 38 | 52 | 1306.92 | 126 | 3332 | 0 | 236 | 1244.5 | 0 | 0 | 40 | 0
01:30 | 3158.5 | 1429 | 903 | 38 | 52 | 1303.535 | 126 | 3323 | 0 | 197 | 1053.5 | 0 | 0 | 29 | 0 | Energy Generated | 288.4086 |  | MKWHr
02:00 | 3141 | 1430.5 | 903 | 38 | 52 | 1300.15 | 126 | 3314 | 0 | 158 | 862.5 | 0 | 0 | 18 | 0 | Energy not Served | 0.32 |  | MKWHr
02:30 | 3137 | 1427 | 904.5 | 38 | 51 | 1248.73 | 126 | 3303 | 0 | 149 | 742 | 0 | 0 | 14 | 0 | Total Energy Requirement | 288.7286 |  | MKWHr
03:00 | 3133 | 1423.5 | 906 | 38 | 50 | 1197.31 | 126 | 3292 | 0 | 140 | 621.5 | 0 | 0 | 10 | 0
03:30 | 3147 | 1425 | 906 | 38 | 49 | 1158.02 | 126 | 3301.5 | 0 | 116 | 508 | 0 | 0 | 12.5 | 0
04:00 | 3161 | 1426.5 | 906 | 38 | 48 | 1118.73 | 126 | 3311 | 0 | 92 | 394.5 | 0 | 0 | 15 | 0
04:30 | 3182.5 | 1430.5 | 906 | 38 | 48 | 1072.85 | 126 | 3268 | 0 | 92 | 294.75 | 0 | 0 | 12.5 | 0
05:00 | 3204 | 1434.5 | 906 | 38 | 48 | 1026.97 | 126 | 3225 | 0 | 92 | 195 | 0 | 0 | 10 | 0
05:30 | 3197 | 1439 | 906 | 38 | 45 | 1027.465 | 126 | 3230 | 0 | 92 | 178 | 0 | 0 | 21 | 0
06:00 | 3190 | 1443.5 | 906 | 38 | 42 | 1027.96 | 126 | 3235 | 0 | 92 | 161 | 0 | 0 | 32 | 0
06:30 | 3226.5 | 1403.25 | 906 | 38 | 41 | 1029.995 | 126 | 3299 | 31.63 | 110 | 198 | 0 | 0 | 28 | 0
07:00 | 3263 | 1363 | 906 | 38 | 40 | 1032.03 | 126 | 3363 | 63.26 | 128 | 235 | 0 | 0 | 24 | 0
07:30 | 3197 | 1351.5 | 905.5 | 38 | 40 | 1019.465 | 126 | 3349 | 133.55 | 135 | 390 | 0 | 0 | 19 | 0
08:00 | 3131 | 1340 | 905 | 38 | 40 | 1006.9 | 126 | 3335 | 203.84 | 142 | 545 | 0 | 0 | 14 | 0
08:30 | 3088.5 | 1328 | 906 | 38 | 46 | 974.345 | 126 | 3293.5 | 317.165 | 157 | 521 | 0 | 0 | 16.5 | 0
09:00 | 3046 | 1316 | 907 | 38 | 52 | 941.79 | 126 | 3252 | 430.49 | 172 | 497 | 0 | 0 | 19 | 0
09:30 | 3022 | 1332.5 | 906 | 38 | 52 | 930.67 | 126 | 3239 | 460.535 | 172 | 488.5 | 0 | 0 | 17.5 | 0
10:00 | 2998 | 1349 | 905 | 38 | 52 | 919.55 | 126 | 3226 | 490.58 | 172 | 480 | 0 | 0 | 16 | 0
10:30 | 2970.5 | 1362 | 905.5 | 38 | 50 | 927.215 | 126 | 3247.5 | 503.06 | 197.5 | 642.75 | 0 | 0 | 15.5 | 0
11:00 | 2943 | 1375 | 906 | 38 | 48 | 934.88 | 126 | 3269 | 515.54 | 223 | 805.5 | 0 | 0 | 15 | 0
11:30 | 2919 | 1366 | 905.5 | 38 | 51 | 1019.225 | 146 | 3306 | 517.44 | 264.5 | 1012.5 | 0 | 0 | 17.5 | 0
12:00 | 2895 | 1357 | 905 | 38 | 54 | 1103.57 | 166 | 3343 | 519.34 | 306 | 1219.5 | 0 | 0 | 20 | 0
12:30 | 2943.5 | 1356.5 | 905.5 | 38 | 57 | 1131.375 | 166 | 3371 | 520.195 | 335 | 1301.1 | 0 | 0 | 22 | 0
13:00 | 2992 | 1356 | 906 | 38 | 60 | 1159.18 | 166 | 3399 | 521.05 | 364 | 1382.7 | 0 | 0 | 24 | 0
13:30 | 2987.5 | 1322 | 906 | 38 | 61 | 1165.16 | 166 | 3383.5 | 481.585 | 360 | 1409.7 | 0 | 0 | 24 | 0
14:00 | 2983 | 1288 | 906 | 38 | 62 | 1171.14 | 166 | 3368 | 442.12 | 356 | 1436.7 | 0 | 0 | 24 | 0
14:30 | 2981.5 | 1306.85 | 904 | 38 | 58 | 1192.695 | 166 | 3369 | 397.84 | 341.5 | 1406.6 | 0 | 0 | 23 | 0
15:00 | 2980 | 1325.7 | 902 | 38 | 54 | 1214.25 | 166 | 3370 | 353.56 | 327 | 1376.5 | 0 | 0 | 22 | 0
15:30 | 2978 | 1336.85 | 902 | 38 | 53 | 1225.065 | 166 | 3372.5 | 239.455 | 286 | 1355.5 | 0 | 0 | 17 | 0
16:00 | 2976 | 1348 | 902 | 38 | 52 | 1235.88 | 166 | 3375 | 125.35 | 245 | 1334.5 | 0 | 0 | 12 | 0
16:30 | 2982.5 | 1331.5 | 902 | 38 | 57 | 1250.33 | 146 | 3382.5 | 70.745 | 251.5 | 1433.85 | 0 | 0 | 16 | 14
17:00 | 2989 | 1315 | 902 | 38 | 62 | 1264.78 | 126 | 3390 | 16.14 | 258 | 1533.2 | 0 | 0 | 20 | 28
17:30 | 3008.5 | 1372.5 | 905 | 38 | 64 | 1360.105 | 126 | 3422.5 | 8.07 | 478.5 | 1917.25 | 0 | 0 | 20.5 | 49
18:00 | 3028 | 1430 | 908 | 38 | 66 | 1455.43 | 126 | 3455 | 0 | 699 | 2301.3 | 0 | 0 | 21 | 70
18:30 | 2904.5 | 1421 | 908 | 38 | 66 | 1456.535 | 142 | 3457.5 | 0 | 756.5 | 2425.75 | 0 | 0 | 18.5 | 59
19:00 | 2781 | 1412 | 908 | 38 | 66 | 1457.64 | 158 | 3460 | 0 | 814 | 2550.2 | 0 | 0 | 16 | 48
19:30 | 2832 | 1423 | 908 | 38 | 68 | 1444.44 | 166 | 3465 | 0 | 794 | 2356.6 | 0 | 0 | 18 | 46
20:00 | 2857 | 1423 | 907 | 38 | 62 | 1437.65 | 166 | 3436 | 0 | 764 | 2274.8 | 0 | 0 | 13 | 32
20:30 | 2934.5 | 1435.75 | 907.5 | 38 | 66 | 1443.325 | 166 | 3406 | 0 | 704.5 | 2202.6 | 0 | 0 | 15.5 | 40
21:00 | 3012 | 1448.5 | 908 | 38 | 70 | 1449 | 166 | 3376 | 0 | 645 | 2130.4 | 0 | 0 | 18 | 48
21:30 | 3002.5 | 1457 | 908 | 38 | 68 | 1431 | 166 | 3379 | 0 | 628 | 2094.45 | 0 | 0 | 15.5 | 49
22:00 | 2993 | 1465.5 | 908 | 38 | 66 | 1413 | 166 | 3382 | 0 | 611 | 2058.5 | 0 | 0 | 13 | 50
22:30 | 2968.5 | 1435.75 | 907.5 | 38 | 66 | 1418.5 | 166 | 3379.5 | 0 | 611 | 1988.5 | 0 | 0 | 12.5 | 47
23:00 | 2944 | 1406 | 907 | 38 | 66 | 1424 | 166 | 3377 | 0 | 611 | 1918.5 | 0 | 0 | 12 | 44
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 05:00 | 375 | 16:00 | Payra | 410 | 05:00 | 405 | 11:00
Ashuganj | 402 | 05:00 | 386 | 18:00 | Rahanpur | 410 | 05:00 | 396 | 18:00
Bhulta | 399 | 01:00 | 382 | 10:00 | Rampal | 406 | 05:00 | 397 | 16:00
Bibiana | 389 | 08:00 | 384 | 12:00
BIPTC | 407 | 04:00 | 397 | 18:30
Bogura | 402 | 05:00 | 386 | 18:00
Gopalganj | 398 | 06:00 | 391 | 12:00
Kaliakoir | 376 | 08:00 | 367 | 12:00
Madunaghat | 398 | 19:00 | 391 | 04:00
Meghnaghat | 386 | 08:00 | 378 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 01:00 | 223 | 10:00 | Kaliakoir | 235 | 01:00 | 228 | 10:00
AKSML | 237 | 18:30 | 229 | 05:00 | Keranigonj | 226 | 01:00 | 220 | 10:00
Aminbazar | 230 | 04:00 | 223 | 12:00 | Khulna(S) | 235 | 05:00 | 226 | 18:00
Ashuganj | 232 | 08:00 | 227 | 10:00 | Madunaghat | 237 | 18:00 | 231 | 05:00
Ashuganj-400 | 232 | 08:00 | 227 | 10:00 | Madunaghat-400 | 238 | 19:00 | 231 | 05:00
Baghabari | 234 | 09:00 | 226 | 17:00 | Maniknagar | 220 | 08:00 | 214 | 12:00
Barapukuria | 220 | 05:00 | 208 | 07:00 | Meghnaghat | 225 | 05:00 | 222 | 11:00
Barapukuria-230 | 220 | 05:00 | 208 | 07:00 | Meghnaghat-400 | 224 | 08:00 | 219 | 10:00
Barishal | 235 | 06:00 | 231 | 12:00 | Mirsorai | 237 | 19:00 | 224 | 04:00
Bheramara | 233 | 05:00 | 223 | 18:00 | Rajshahi | 233 | 06:00 | 223 | 18:00
Bhulta | 232 | 01:00 | 214 | 12:00 | Rampal | 234 | 09:00 | 225 | 18:00
Bibiana | 231 | 06:00 | 226 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 236 | 05:00 | 223 | 18:00 | Rampura | 231 | 06:00 | 218 | 10:00
Bogura | 233 | 05:00 | 224 | 18:00 | Shikalbaha | 237 | 18:00 | 229 | 07:00
Bogura-400 | 233 | 09:00 | 224 | 18:00 | Shyampur | 224 | 01:00 | 218 | 12:00
Borhanuddin | 236 | 01:00 | 234 | 12:00 | Siddhirganj | 221 | 04:00 | 216 | 12:00
BSRM | 235 | 19:00 | 225 | 01:00 | Sirajgonj | 237 | 01:00 | 232 | 22:00
Cumilla(N) | 226 | 19:00 | 221 | 10:00 | Sreepur | 229 | 08:00 | 223 | 10:00
Faridpur | 233 | 06:00 | 227 | 12:00 | Tongi | 233 | 04:00 | 225 | 11:00
Fenchuganj | 233 | 08:00 | 228 | 01:00
Ghorashal | 236 | 08:00 | 230 | 10:00
Ghorashal-230 | 230 | 08:00 | 219 | 10:00
Gopalganj | 234 | 05:00 | 228 | 12:00
GPH | 236 | 19:00 | 228 | 10:00
Haripur | 221 | 06:00 | 216 | 10:00
Hasnabad | 226 | 07:00 | 218 | 13:00
Hathazari | 236 | 19:00 | 226 | 10:00
Ishurdi | 236 | 05:00 | 226 | 18:00
Jhenaidah | 235 | 06:00 | 218 | 18:00
Kachua | 233 | 18:00 | 221 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 01:00 | 126 | 11:00 | Lalmonirhat | 129 | 19:00 | 121 | 13:00
Agargaon | 135 | 01:00 | 130 | 10:00 | Madanganj | 130 | 07:00 | 125 | 09:00
Agrabad | 136 | 19:30 | 131 | 04:00 | Madaripur | 136 | 07:00 | 132 | 18:30
AKS | 134 | 18:00 | 130 | 09:00 | Madartek | 135 | 00:00 | 125 | 10:00
Aminbazar | 136 | 00:00 | 131 | 10:00 | Madunaghat | 138 | 20:00 | 133 | 03:00
Amnura | 140 | 05:00 | 128 | 16:00 | Magura | 138 | 05:00 | 123 | 18:00
Ashuganj | 142 | 09:00 | 137 | 08:00 | Mahasthangarh | 131 | 05:00 | 126 | 13:00
Bagerhat | 133 | 09:00 | 123 | 18:00 | Maijdee | 134 | 08:00 | 130 | 00:00
Bajitpur | 131 | 06:00 | 128 | 00:00 | Manikganj | 134 | 13:00 | 129 | 19:00
Bakulia | 137 | 18:30 | 132 | 10:00 | Maniknagar | 133 | 03:00 | 128 | 12:00
Banani | 135 | 06:00 | 13 | 03:00 | Matarbari | 125 | 12:00 | 119 | 00:00
Bangabhaban | 133 | 07:00 | 128 | 12:00 | Matuail | 128.2 | 20:00 | 125 | 12:00
Barapukuria | 134 | 01:00 | 125 | 13:00 | Metrorail_Motijheel | 133 | 03:00 | 128 | 12:00
Barguna | 136 | 09:00 | 133 | 13:00 | Metrorail_Uttara | 138 | 00:00 | 132 | 10:00
Barishal | 137 | 19:30 | 132 | 12:00 | Millgate | 139 | 01:00 | 133 | 10:00
Barishal-230 | 135 | 05:00 | 132 | 12:00 | Mirpur | 135 | 00:00 | 129 | 12:00
Baroaulia | 137 | 19:00 | 133 | 00:00 | Mirzapur | 131 | 17:00 | 126 | 12:00
Baroirhat | 135 | 18:00 | 129 | 01:00 | Mithapukur | 132 | 06:00 | 123 | 13:00
Bashundhara | 134 | 01:00 | 126 | 10:00 | MI_Cement | 132 | 03:00 | 126 | 12:00
BashundharaCement | 130 | 07:00 | 123 | 04:00 | Modern | 0 | 00:00 | 0 | 00:00
Beanibazar | 131 | 07:00 | 126 | 00:00 | Mogbazar | 138 | 04:00 | 126 | 11:00
Benapole | 137 | 05:00 | 117 | 18:00 | Mongla | 133 | 06:00 | 123 | 18:00
Bhaluka | 131 | 13:00 | 127 | 02:00 | Motijheel | 133 | 07:00 | 128 | 12:00
Bhandaria | 133 | 07:00 | 13 | 03:00 | Muktagacha | 131 | 09:00 | 118 | 19:30
Bhangura | 134 | 04:00 | 129 | 18:30 | Munshiganj | 128 | 17:00 | 125 | 10:00
Bheramara | 140 | 06:00 | 134 | 18:00 | Muradnagar | 129 | 18:00 | 125 | 00:00
Bheramara(GK) | 139 | 05:00 | 134 | 18:00 | Mymensingh | 130 | 09:00 | 113 | 21:00
Bhulta | 128 | 09:00 | 124 | 10:00 | Naogaon | 130 | 06:00 | 124 | 14:00
Bog-Sherpur | 133 | 05:00 | 127 | 16:00 | Narail | 138 | 06:00 | 122 | 18:00
Bogura | 133 | 04:00 | 128 | 13:00 | Narinda | 133 | 03:00 | 128 | 12:00
Bogura-230 | 133 | 05:00 | 128 | 13:00 | Narshingdi | 134 | 07:00 | 121 | 10:00
Brahmanbaria | 137 | 08:00 | 131 | 00:00 | Natore | 134 | 05:00 | 128 | 18:00
Cantonment | 135 | 01:00 | 129 | 12:00 | Nawabganj | 134 | 06:00 | 128 | 12:00
Chandina | 132 | 08:00 | 129 | 00:00 | Netrakona | 127 | 15:00 | 122 | 00:00
Chandpur | 140 | 18:30 | 133 | 05:00 | New | 139 | 00:00 | 134 | 16:00
Chandraghona | 138 | 19:00 | 35 | 05:00 | Niamatpur | 140 | 06:00 | 134 | 18:00
Chapai | 139 | 06:00 | 135 | 00:00 | Noapara | 137 | 06:00 | 127 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 17:00 | 125 | 10:00 | Pabna | 137 | 05:00 | 15 | 08:00
Chauddagram | 134 | 19:00 | 128 | 00:00 | Palashbari | 129 | 03:00 | 122 | 16:00
Chhatak | 129 | 09:00 | 123 | 00:00 | Panchagarh | 141 | 19:00 | 124 | 12:00
Chowmuhani | 133 | 07:00 | 130 | 00:00 | Patiya | 136 | 19:00 | 128 | 01:00
Chuadanga | 138 | 06:00 | 122 | 18:00 | Patuakhali | 135 | 07:00 | 132 | 00:00
Coxsbazar | 123 | 01:00 | 119 | 23:00 | Payra | 138 | 12:00 | 135 | 07:00
Cumilla(N) | 132 | 14:00 | 129 | 00:00 | PHP | 134 | 18:00 | 128 | 01:00
Cumilla(S) | 133 | 02:00 | 128 | 00:00 | Postogola | 133 | 01:00 | 128 | 12:00
Daganbhuiyan | 135 | 19:00 | 130 | 00:00 | Purbachal | 135 | 05:00 | 125 | 10:00
Daudkandi | 127 | 17:00 | 123 | 00:00 | Purbasadipur | 132 | 19:00 | 121 | 13:00
DhakaUniversity | 135 | 01:00 | 126 | 10:00 | Rahanpur | 141 | 05:00 | 136 | 18:00
Dhamrai | 134 | 07:00 | 130 | 10:00 | Rahanpur-400 | 141 | 04:00 | 136 | 18:00
Dhanmondi | 136 | 03:00 | 126.5 | 11:00 | Rahim | 128 | 00:00 | 126 | 10:00
Dohazari | 133 | 19:00 | 128 | 04:00 | Rajbari | 136 | 04:00 | 132 | 18:00
Faridpur | 136 | 05:00 | 134 | 12:00 | Rajendrapur | 130 | 06:00 | 126 | 13:00
Fatullah | 137 | 08:00 | 127 | 12:00 | Rajshahi | 134 | 03:00 | 128 | 13:00
Fenchuganj | 138 | 08:00 | 132 | 10:00 | Rajshahi-230 | 134 | 05:00 | 128 | 14:00
Feni | 133 | 12:00 | 129 | 00:00 | Ramganj | 134 | 07:00 | 130 | 05:00
Ghatail | 128 | 09:00 | 117 | 21:00 | Rampur | 135 | 19:00 | 131 | 10:00
Ghorashal | 140 | 08:00 | 133 | 10:00 | Rampura | 135 | 01:00 | 126 | 10:00
Goalpara | 137 | 05:00 | 129 | 10:00 | Rangamati | 136 | 13:00 | 133 | 01:00
Gollamari | 137 | 06:00 | 130 | 18:00 | Rangpur | 133 | 04:00 | 123 | 13:00
Gopalganj | 136 | 05:00 | 130 | 13:00 | Ruppur | 139 | 05:00 | 133 | 18:00
Gopalganj-400 | 137 | 05:00 | 133 | 16:00 | Saidpur | 132 | 02:00 | 121 | 07:00
Gulshan | 135 | 04:00 | 126 | 10:00 | Satkhira | 134 | 04:00 | 125 | 18:00
Halishahar | 137 | 19:00 | 132 | 10:00 | Satmasjid | 135 | 01:00 | 130 | 11:00
Haripur | 129 | 20:00 | 126 | 10:00 | Savar | 135 | 00:00 | 128 | 10:00
HaripurSBU | 128 | 00:00 | 126 | 10:00 | SevenRings | 140 | 08:00 | 133 | 10:00
Hasnabad | 134 | 08:00 | 128 | 12:00 | ShahCement | 129 | 17:00 | 125 | 10:00
Hathazari | 138 | 19:00 | 133 | 10:00 | Shahjadpur | 137 | 04:00 | 133 | 18:00
Ishurdi | 139 | 04:00 | 134 | 18:00 | Shahjibazar | 137 | 08:00 | 130 | 07:00
Jaldhaka | 128 | 03:00 | 117 | 14:00 | Shahmirpur | 137 | 19:00 | 133 | 05:00
Jamalpur | 127 | 09:00 | 115 | 23:00 | Shariatpur | 135 | 05:00 | 131 | 18:00
Jashore | 139 | 06:00 | 118 | 18:00 | Sherpur | 124 | 10:00 | 112 | 19:00
Jhenaidah | 140 | 04:00 | 126 | 18:00 | Shikalbaha | 127 | 19:00 | 121 | 08:00
Jhenaidah-230 | 140 | 05:00 | 127 | 18:00 | Shikalbaha-230 | 139 | 19:00 | 134 | 05:00
Joydebpur | 140 | 00:00 | 129 | 10:00 | Shitalakhya | 132 | 03:00 | 126 | 12:00
Joypurhat | 130 | 06:00 | 122 | 18:00 | Sholosohor | 138 | 19:00 | 133 | 10:00
Juldah | 138 | 19:00 | 132 | 10:00 | Shyampur | 135 | 05:00 | 128 | 12:00
Kabirpur | 137 | 01:00 | 125 | 07:00 | Shyampur-230 | 136 | 01:00 | 131 | 12:00
Kachua | 138 | 18:00 | 133 | 05:00 | Siddhirganj | 128 | 00:00 | 126 | 10:00
Kaliakoir | 136 | 00:00 | 132 | 10:00 | Sirajganj | 132 | 02:00 | 126 | 16:00
Kallyanpur | 136 | 00:00 | 130 | 11:00 | Sonargaon | 127 | 08:00 | 124 | 10:00
Kalurghat | 138 | 18:30 | 133 | 01:00 | Sreemongol | 136 | 08:00 | 130 | 00:00
Kamrangirchar | 135 | 06:00 | 128 | 12:00 | Sreepur | 133 | 06:00 | 129 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 135 | 08:00 | 129 | 12:00
Kasba | 129 | 08:00 | 125 | 00:00 | SSM | 140 | 18:00 | 138 | 00:00
Kazla | 133 | 03:00 | 128 | 13:00 | Sunamganj | 126 | 10:00 | 120 | 01:00
Keranigonj | 135 | 06:00 | 129 | 12:00 | Sylhet | 131 | 08:00 | 126 | 13:00
Khagrachori | 136 | 19:00 | 132 | 13:00 | Sylhet-132 | 131 | 09:00 | 127 | 00:00
Khulna | 136 | 05:00 | 128 | 18:00 | Tangail | 128 | 05:00 | 119 | 20:00
Khulna(S) | 137 | 05:00 | 130 | 18:00 | Taraganj | 131 | 18:30 | 123 | 14:00
Khulshi | 135 | 19:00 | 131 | 00:00 | Thakurgaon | 139 | 19:00 | 120 | 14:00
Kishoreganj | 131 | 13:00 | 127 | 18:00 | TK | 137 | 18:00 | 134 | 02:00
Kodda | 137 | 08:00 | 129 | 06:00 | Tongi | 141 | 04:00 | 134 | 15:00
KSRM | 136 | 14:00 | 132 | 04:00 | Ullahpara | 135 | 05:00 | 128 | 18:00
Kulaura | 137 | 08:00 | 132 | 00:00 | Ullon | 135 | 01:00 | 126 | 10:00
Kurigram | 130 | 09:00 | 118 | 07:00 | Uttara | 136 | 01:00 | 129 | 10:00
Kushtia | 138 | 05:00 | 130 | 18:00 | UttaraNew | 138 | 00:00 | 132 | 10:00
Laksam | 136 | 08:00 | 132 | 05:00 | Zigatola | 135 | 08:00 | 128 | 13:00
Lakshmipur | 134 | 08:00 | 130 | 00:00
Lalbag | 134 | 05:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division