## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-11-2025 | during | 07-11-2025 | during | 07-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 368 | 362 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 94 | 0 | 208.13 | 208.13 | 97 | 97 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 332 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 123 | 122 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 23.5 | 24 | 24 | 24 | 24 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 294 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 108 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 22 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 78 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1909 | 2098.5 | 5917.1 | 5892.1 | 4354.81 | 4401.81
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 132 | 80 | 130 | 130 | 130 | 130 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 223 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 92 | 97 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 9 | 60 | 60 | 60 | 60 | 60 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 27 | 35 | 40 | 35 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 7 | 18 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.2 | 0 | 3.26 | 0 | 3.26 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 52 | 300 | 300 | 100 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 63 | 102 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 43 | 92 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 126 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 595 | 612 | 612 | 612 | 582 | 582 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 8 | 1 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 315 | 315 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1961.2 | 2311 | 2677.98 | 2674.72 | 2515.62 | 2512.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 315 | 320 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 36 | 35 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 105 | 125 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 28 | 28 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 102 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 108 | 199 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 68 | 160 | 160 | 70 | 70 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 93 | 110 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 90 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 47 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1363 | 1517.2 | 2601.56 | 2551.56 | 2070.56 | 2020.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-11-2025 | during | 07-11-2025 | during | 07-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 27 | 20 | 157.5 | 157.5 | 34 | 34 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 28 | 28 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 48 | 18 | 18 | 18 | 18 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.27 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 6 | 6 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 153.27 | 113 | 362.1 | 312 | 185.1 | 135
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 57 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 162 | 146 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 99 | 100 | 100 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 396 | 369 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1112 | 1119 | 1157 | 1157 | 1139 | 1139
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 930 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 36 | 36 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 219 | 194 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1103 | 1106 | 0 | 0 | 1100 | 1100 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2340 | 2338 | 2402 | 2312 | 2741 | 2651
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 503 | 502 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 580 | 602 | 622 | 622 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.36 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1430.36 | 1467 | 1218 | 1217 | 1077 | 1076
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 48.61 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 178 | 130 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 408 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Engine Problem
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.69 | 0 | 5.45 | 0 | 5.45 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1126.03 | 1224.97 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.06 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 41 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1877.39 | 2133.17 | 3181.32 | 3014.87 | 3008.54 | 2842.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 90 | 0 | 196.86 | 0 | 196.86 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 126.1 | 228 | 494.66 | 262 | 460.66 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 12272.32 | 13324.87 | 20011.72 | 19393.25 | 17552.29 | 17005.82
Forecast Scenario (07-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13170 |  | 0 |  | 13170
|  |  |  | 1:00 | 12810 |  | 0 |  | 12810
|  |  |  | 2:00 | 12370 |  | 0 |  | 12370
|  |  |  | 3:00 | 11950 |  | 0 |  | 11950
|  |  |  | 4:00 | 11650 |  | 0 |  | 11650
|  |  |  | 5:00 | 11410 |  | 0 |  | 11410
|  |  |  | 6:00 | 11010 |  | 0 |  | 11010
|  |  |  | 7:00 | 10760 |  | 0 |  | 10760
|  |  |  | 8:00 | 10750 |  | 0 |  | 10750
|  |  |  | 9:00 | 10570 |  | 0 |  | 10570
|  |  |  | 10:00 | 10460 |  | 0 |  | 10460
|  |  |  | 11:00 | 10850 |  | 0 |  | 10850
|  |  |  | 12:00 | 11470 |  | 0 |  | 11470
|  |  |  | 13:00 | 12140 |  | 0 |  | 12140
|  |  |  | 14:00 | 11620 |  | 0 |  | 11620
|  |  |  | 15:00 | 11600 |  | 0 |  | 11600
|  |  |  | 16:00 | 11160 |  | 0 |  | 11160
|  |  |  | 17:00 | 11100 |  | 0 |  | 11100
|  |  |  | 18:00 | 12890 |  | 0 |  | 12890
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13210 |  | 0 |  | 13210
|  |  |  | 19:30 | 13280 |  | 0 |  | 13280
|  |  |  | 20:00 | 13300 |  | 0 |  | 13300
|  |  |  | 21:00 | 13270 |  | 0 |  | 13270
|  |  |  | 22:00 | 13130 |  | 0 |  | 13130
|  |  |  | 23:00 | 13080 |  | 0 |  | 13080
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 11470.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 285.73 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:54 hrs on 07-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-11-2025 | [28 empty] | Date: | 06-11-2025 | [28 empty] | Date: | 06-11-2025 | [28 empty] | Date: | 06-11-2025 | [28 empty] | Date: | 06-11-2025 | [14 empty] | Date: | 06-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 17.5 | 0 | 149 | 126 | 294 | 55 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 90 | 20 | 21 | 0 | 300 | 58 | 16 | 12 | 0 | 14 | 33 | 53 | 17 | 12 | 12 | 0 | 126 | 103 | 36 | 650 | 76 | 0 | 19 | 8 | 96 | 225 | 0 | 0 | 0 | 565 | 0 | 0 | 142 | 0 | 340 | 0 | 330 | 20 | 0 | 39 | 34 | 103 | 176 | 0 | 20 | 28 | 64 | 25 | 0 | 29 | 300 | 0 | 359 | 0 | 30 | 155 | 23 | 0 | 81 | 30 | 0 | 0 | 98 | 17 | 48 | 28 | 28 | 0 | 0 | 0 | 6714.5 | 908 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 1420 | 0 | 40 | 0 | 0 | 50 | 0 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 110 | 220 | 0 | 502 | 540 | 17 | 5880 | 12594.5 | 101.76
01:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 17.5 | 0 | 149 | 125 | 294 | 0 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 35 | 19 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 0 | 53 | 0 | 12 | 12 | 0 | 126 | 102 | 36 | 650 | 0 | 0 | 19 | 0 | 95 | 225 | 0 | 0 | 0 | 578 | 0 | 0 | 140 | 0 | 340 | 0 | 330 | 20 | 0 | 39 | 57 | 103 | 128 | 0 | 19 | 0 | 68 | 0 | 0 | 29 | 300 | 0 | 371 | 0 | 30 | 151 | 23 | 0 | 81 | 30 | 0 | 0 | 98 | 17 | 49 | 28 | 27 | 0 | 0 | 0 | 6312.5 | 908 | 183 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1074 | 0 | 1412 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 504 | 537 | 0 | 5666 | 11978.5 | 101.76
02:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17.5 | 0 | 118 | 75 | 195 | 0 | 35 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 35 | 19 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 42 | 36 | 650 | 0 | 0 | 0 | 0 | 97 | 225 | 0 | 0 | 0 | 575 | 0 | 0 | 132 | 0 | 355 | 0 | 330 | 20 | 0 | 39 | 69 | 103 | 106 | 0 | 19 | 0 | 60 | 0 | 0 | 29 | 310 | 0 | 362 | 0 | 30 | 156 | 23 | 0 | 81 | 30 | 0 | 0 | 98 | 17 | 49 | 28 | 31 | 0 | 0 | 0 | 6009.5 | 908 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 0 | 1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 503 | 544 | 0 | 5551 | 11560.5 | 101.76
03:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17.5 | 0 | 45 | 30 | 45 | 0 | 0 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 17 | 19.5 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 75 | 225 | 0 | 0 | 0 | 575 | 0 | 0 | 80 | 0 | 360 | 0 | 330 | 20 | 0 | 39 | 69 | 103 | 103 | 0 | 19 | 0 | 62 | 0 | 0 | 29 | 305 | 0 | 364 | 0 | 30 | 155 | 23 | 0 | 81 | 30 | 0 | 0 | 98 | 17 | 49 | 28 | 31 | 0 | 0 | 0 | 5575 | 908 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 1407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 543 | 0 | 5534 | 11109 | 101.76
04:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 17.5 | 0 | 17 | 15 | 0 | 0 | 0 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 17 | 19 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 370 | 0 | 330 | 20 | 0 | 39 | 16 | 104 | 51 | 0 | 19 | 0 | 56 | 0 | 0 | 29 | 315 | 0 | 360 | 0 | 30 | 158 | 16 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 49 | 28 | 32 | 0 | 0 | 0 | 5242.5 | 907 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 503 | 544 | 0 | 5494 | 10736.5 | 101.75
05:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17.5 | 0 | 18 | 15 | 0 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 17 | 19 | 18 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 355 | 0 | 330 | 20 | 0 | 39 | 16 | 104 | 51 | 0 | 19 | 0 | 62 | 0 | 0 | 29 | 310 | 0 | 344 | 0 | 30 | 156 | 11 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 49 | 28 | 32 | 0 | 0 | 0 | 5129.5 | 908 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 1335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 542 | 0 | 5463 | 10592.5 | 101.75
06:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17.5 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 370 | 0 | 330 | 20 | 0 | 39 | 17 | 104 | 52 | 0 | 19 | 0 | 60 | 0 | 0 | 29 | 305 | 0 | 352 | 0 | 30 | 159 | 11 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 49 | 28 | 32 | 0 | 0 | 0 | 5077.5 | 907 | 228 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 1306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 545 | 0 | 5478 | 10555.5 | 101.75
07:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 86 | 45 | 25 | 0 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 3 | 35 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 0 | 126 | 0 | 36 | 648 | 0 | 0 | 0 | 0 | 18 | 226 | 0 | 0 | 0 | 585 | 2 | 0 | 20 | 0 | 365 | 0 | 330 | 21 | 0 | 39 | 31 | 103 | 93 | 0 | 19 | 0 | 50 | 0 | 3 | 29 | 305 | 0 | 382 | 0 | 30 | 159 | 11 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 49 | 28 | 32 | 0 | 4.71 | 0 | 5247.71 | 908 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.88 | 1118 | 0 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.73 | 8 | 0 | 0 | 2.91 | 160 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0.28 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.5 | 15 | 0.05 | 0 | 0 | 110 | 220 | 0 | 503 | 548 | 0 | 5580.35 | 10828.06 | 101.75
08:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 102 | 75 | 75 | 0 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 7 | 35 | 24 | 14 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 132 | 16 | 8 | 650 | 0 | 0 | 13 | 0 | 60 | 226 | 0 | 0 | 0 | 575 | 7 | 0 | 68 | 0 | 345 | 0 | 330 | 30 | 0 | 39 | 35 | 103 | 100 | 0 | 19 | 0 | 54 | 0 | 14 | 29 | 320 | 0 | 364 | 0 | 30 | 159 | 11 | 0 | 81 | 30 | 0 | 0 | 98 | 0 | 49 | 28 | 33 | 0 | 9.01 | 0 | 5482.01 | 907 | 234 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.22 | 1110 | 0 | 1325.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6 | 34 | 0 | 0 | 18.28 | 170 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1.79 | 0 | 0 | 25 | 5 | 8 | 0 | 0 | 0 | 2.4 | 32 | 0.19 | 0 | 0 | 110 | 220 | 0 | 504 | 550 | 0 | 5679.65 | 11161.66 | 101.74
09:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 120 | 75 | 75 | 4 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 19 | 52 | 24 | 14 | 0 | 0 | 13 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 0 | 132 | 45 | 3 | 650 | 0 | 0 | 32 | 0 | 85 | 225 | 0 | 0 | 0 | 582 | 12 | 0 | 80 | 0 | 335 | 0 | 330 | 36 | 0 | 35 | 33 | 102 | 94 | 0 | 19 | 0 | 58 | 0 | 39 | 29 | 305 | 0 | 310 | 0 | 30 | 149 | 11 | 0 | 78 | 30 | 0 | 0 | 98 | 0 | 49 | 28 | 27 | 1 | 11.01 | 0 | 5549.01 | 908 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45.92 | 1084 | 0 | 1154.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.08 | 63 | 0 | 0 | 42.9 | 171 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 3.83 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 4.3 | 50 | 0.3 | 0 | 0 | 110 | 220 | 0 | 503 | 535 | 0 | 5558.61 | 11107.62 | 101.74
10:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 122 | 75 | 290 | 15 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 17 | 331 | 97 | 0 | 24 | 70 | 25 | 14 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.81 | 132 | 33 | 3 | 650 | 0 | 0 | 36 | 0 | 34 | 225 | 0 | 0 | 0 | 580 | 16 | 0 | 92 | 0 | 330 | 0 | 330 | 35 | 0 | 38 | 34 | 101 | 97 | 0 | 19 | 0 | 60 | 0 | 44 | 29 | 310 | 0 | 306 | 0 | 30 | 152 | 16 | 0 | 79 | 30 | 0 | 0 | 98 | 0 | 49 | 28 | 27 | 1 | 41.08 | 0 | 5934.89 | 908 | 228 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62 | 1079 | 0 | 1014.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.46 | 80 | 0 | 0 | 37.59 | 174 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 2.88 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 5.4 | 129 | 0.46 | 0 | 0 | 110 | 220 | 0 | 503 | 540 | 0 | 5533.61 | 11468.5 | 101.74
11:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 143 | 115 | 293 | 15 | 17 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 333 | 95 | 0 | 33 | 70 | 24 | 21 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.17 | 132 | 34 | 2 | 650 | 17 | 0 | 50 | 2 | 45 | 222 | 0 | 0 | 0 | 588 | 17 | 0 | 110 | 0 | 310 | 0 | 330 | 35 | 0 | 38 | 34 | 100 | 106 | 0 | 19 | 23 | 62 | 2 | 28 | 28 | 310 | 0 | 390 | 0 | 30 | 157 | 16 | 0 | 79 | 30 | 0 | 0 | 99 | 0 | 49 | 28 | 27 | 3 | 22.56 | 0 | 6154.73 | 908 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 1102 | 0 | 1029.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.45 | 93 | 0 | 0 | 62.5 | 177 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 3.72 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 5.9 | 179 | 0.53 | 0 | 0 | 110 | 220 | 0 | 503 | 540 | 0 | 5697.56 | 11852.29 | 101.74
12:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 149 | 123 | 294 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 94 | 0 | 22 | 70 | 23 | 21 | 0 | 0 | 43 | 16 | 7 | 0 | 0 | 0 | 9 | 0 | 12 | 12 | 2.2 | 132 | 63 | 5 | 650 | 17 | 0 | 50 | 17 | 92 | 222 | 0 | 0 | 0 | 595 | 17 | 0 | 105 | 0 | 315 | 0 | 330 | 36 | 0 | 37 | 34 | 100 | 108 | 0 | 19 | 93 | 68 | 43 | 47 | 28 | 310 | 0 | 396 | 0 | 30 | 162 | 6 | 0 | 79 | 30 | 0 | 0 | 99 | 0 | 48 | 28 | 27 | 2 | 48.27 | 0 | 6498.47 | 908 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 1103 | 0 | 1126.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.61 | 41 | 0 | 0 | 64.06 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.69 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 6.1 | 90 | 0.36 | 0 | 0 | 110 | 220 | 0 | 503 | 580 | 17 | 5773.85 | 12272.32 | 101.74
13:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17.5 | 0 | 149 | 122 | 294 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 95 | 0 | 8 | 70 | 23 | 21 | 0 | 0 | 97 | 16 | 19 | 0 | 0 | 0 | 21 | 0 | 12 | 12 | 0 | 132 | 108 | 3 | 650 | 17 | 0 | 50 | 17 | 100 | 223 | 0 | 0 | 0 | 570 | 14 | 0 | 112 | 0 | 325 | 0 | 330 | 35 | 0 | 37 | 34 | 98 | 107 | 0 | 19 | 105 | 64 | 43 | 51 | 28 | 315 | 0 | 370 | 0 | 30 | 158 | 6 | 0 | 81 | 30 | 0 | 0 | 99 | 0 | 48 | 28 | 11 | 2 | 13 | 0 | 6561.5 | 919 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 1125 | 0 | 1270.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5 | 84 | 0 | 0 | 58.32 | 189 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 5.34 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 4.3 | 112 | 0.53 | 0 | 0 | 110 | 220 | 0 | 503 | 600 | 17 | 5933.62 | 12495.12 | 101.74
14:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17.5 | 2 | 149 | 123 | 278 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 290 | 36 | 0 | 26 | 70 | 23 | 21 | 0 | 75 | 86 | 16 | 18 | 0 | 0 | 0 | 22 | 0 | 12 | 12 | 1.34 | 130 | 101 | 2 | 650 | 17 | 0 | 40 | 0 | 94 | 216 | 0 | 0 | 0 | 580 | 12 | 0 | 117 | 0 | 325 | 0 | 330 | 36 | 0 | 34 | 34 | 100 | 103 | 0 | 19 | 95 | 66 | 43 | 47 | 27 | 310 | 0 | 381 | 0 | 50 | 146 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 9 | 49 | 28 | 0 | 2 | 34.73 | 0 | 6499.57 | 930 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 1107 | 0 | 1409.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.96 | 79 | 0 | 0 | 52.63 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 1.08 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 4.7 | 126 | 0.37 | 0 | 0 | 110 | 180 | 0 | 502 | 600 | 17 | 5878.1 | 12377.67 | 101.74
15:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17.5 | 17 | 149 | 123 | 294 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 95 | 0 | 17 | 52 | 23 | 21 | 0 | 78 | 95 | 16 | 18 | 0 | 0 | 0 | 23 | 0 | 12 | 12 | 0.74 | 86 | 102 | 5 | 650 | 17 | 0 | 40 | 0 | 100 | 222 | 0 | 0 | 0 | 600 | 9 | 0 | 113 | 0 | 315 | 0 | 330 | 35 | 0 | 34 | 37 | 100 | 106 | 6 | 19 | 107 | 64 | 52.2 | 33 | 27 | 315 | 0 | 390 | 0 | 58 | 157 | 22 | 0 | 79 | 30 | 0 | 0 | 99 | 17 | 49 | 28 | 0 | 1 | 26.74 | 0 | 6659.18 | 929 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 1128 | 0 | 1238.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.74 | 32 | 0 | 0 | 37.95 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.11 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3 | 94 | 0.13 | 0 | 0 | 110 | 220 | 0 | 500 | 590 | 17 | 5662.36 | 12321.54 | 101.74
16:00 | 0 | 55 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 35 | 17 | 141 | 123 | 294 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 37 | 0 | 7 | 52 | 23 | 21 | 0 | 76 | 99 | 16 | 18 | 0 | 0 | 0 | 23 | 0 | 12 | 12 | 0.3 | 86 | 99 | 0 | 650 | 17 | 0 | 0 | 0 | 103 | 221 | 0 | 0 | 0 | 612 | 3 | 0 | 113 | 0 | 320 | 0 | 330 | 35 | 0 | 34 | 50 | 100 | 110 | 8 | 20 | 106 | 64 | 52.2 | 12 | 31 | 325 | 0 | 391 | 0 | 57 | 158 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 48 | 28 | 0 | 1 | 11.86 | 0 | 6561.36 | 930 | 206 | 0 | 0.4 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1132 | 0 | 1218.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.82 | 23 | 0 | 0 | 13.21 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.82 | 0 | 0 | 18 | 9 | 0 | 0 | 0 | 0 | 1.4 | 44 | 0.11 | 16 | 0 | 110 | 220 | 0 | 502 | 582 | 17 | 5568.36 | 12129.72 | 101.74
17:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 38 | 17 | 137 | 123 | 294 | 15 | 35 | 90 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 37 | 0 | 0 | 52 | 23 | 21 | 0 | 78 | 97 | 49 | 18 | 0 | 0 | 0 | 23 | 0 | 24 | 12 | 0 | 86 | 101 | 8 | 650 | 17 | 0 | 19 | 0 | 102 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 118 | 0 | 320 | 0 | 330 | 35 | 0 | 34 | 51 | 100 | 147 | 9 | 20 | 106 | 66 | 52.2 | 1 | 34 | 320 | 0 | 365 | 0 | 57 | 157 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 48 | 28 | 0 | 0 | 0.86 | 0 | 6672.06 | 930 | 202 | 0 | 25 | 34 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1129 | 0 | 1221.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 1 | 2 | 12 | 0 | 1 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.09 | 0 | 0 | 36 | 1 | 39 | 0 | 0 | 0 | 0.1 | 2 | 0.01 | 16 | 0 | 110 | 220 | 0 | 503 | 581 | 17 | 5560.89 | 12232.95 | 101.74
18:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 149 | 123 | 294 | 15 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 17 | 328 | 37 | 0 | 0 | 142 | 23 | 21 | 0 | 78 | 99 | 49 | 18 | 0 | 0 | 65 | 53 | 0 | 24 | 12 | 0 | 70 | 103 | 8 | 650 | 126 | 0 | 50 | 14 | 103 | 222 | 0 | 0 | 0 | 612 | 0 | 0 | 123 | 0 | 320 | 0 | 330 | 35 | 0 | 34 | 62 | 100 | 189 | 0 | 20 | 110 | 76 | 52.2 | 0 | 28 | 315 | 0 | 390 | 0 | 58 | 155 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 48 | 28 | 20 | 0 | 0 | 0 | 7173.2 | 930 | 200 | 0 | 29 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 1215.96 | 0 | 32 | 0 | 20 | 15 | 0 | 90 | 24 | 43 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 113 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 504 | 590 | 17 | 6002.96 | 13176.16 | 101.74
19:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 54 | 17 | 149 | 123 | 294 | 15 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 78 | 96 | 49 | 18 | 0 | 0 | 65 | 54 | 0 | 24 | 12 | 0 | 80 | 102 | 24 | 650 | 126 | 0 | 50 | 23 | 98 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 128 | 0 | 320 | 0 | 330 | 35 | 0 | 34 | 73 | 102 | 199 | 0 | 20 | 100 | 76 | 52.2 | 0 | 28 | 320 | 0 | 352 | 0 | 57 | 151 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 48 | 28 | 20 | 0 | 0 | 0 | 7121.2 | 930 | 197 | 0 | 35 | 62 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 0 | 1230.2 | 0 | 41 | 0 | 35 | 60 | 0 | 95 | 32 | 52.2 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 602 | 17 | 6184.4 | 13305.6 | 101.74
19:30 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 35 | 149 | 122 | 294 | 15 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 142 | 23.5 | 21 | 0 | 78 | 92 | 52 | 18 | 0 | 0 | 65 | 60 | 0 | 24 | 12 | 0 | 80 | 102 | 27 | 650 | 126 | 0 | 46 | 25 | 97 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 125 | 0 | 320 | 0 | 330 | 35 | 0 | 38 | 90 | 102 | 199 | 0 | 20 | 110 | 68 | 52.2 | 0 | 28 | 315 | 0 | 369 | 0 | 57 | 146 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 48 | 28 | 20 | 0 | 0 | 0 | 7158.7 | 930 | 194 | 0 | 30 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 1224.97 | 0 | 41 | 0 | 35 | 90 | 0 | 95 | 32 | 52.2 | 0 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 602 | 17 | 6166.17 | 13324.87
20:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 35 | 149 | 122 | 294 | 15 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 78 | 92 | 52 | 18 | 0 | 0 | 65 | 60 | 0 | 24 | 24 | 0 | 80 | 101 | 29 | 650 | 126 | 0 | 33 | 25 | 93 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 127 | 0 | 320 | 0 | 330 | 35 | 0 | 38 | 90 | 103 | 199 | 0 | 20 | 105 | 68 | 52.2 | 0 | 28 | 315 | 0 | 350 | 0 | 57 | 143 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 49 | 28 | 20 | 0 | 0 | 0 | 7127.2 | 930 | 191 | 0 | 30 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1221.36 | 0 | 41 | 0 | 35 | 90 | 0 | 95 | 32 | 52.2 | 0 | 0 | 25 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 504 | 603 | 17 | 6176.56 | 13303.76 | 101.74
21:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 54 | 17 | 149 | 122 | 294 | 15 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 77 | 114 | 52 | 18 | 0 | 0 | 65 | 60 | 0 | 24 | 24 | 0 | 84 | 102 | 31 | 650 | 72 | 0 | 33 | 25 | 95 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 128 | 0 | 305 | 0 | 330 | 35 | 0 | 38 | 83 | 103 | 200 | 0 | 20 | 105 | 62 | 52.2 | 0 | 29 | 305 | 0 | 386 | 0 | 57 | 143 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 49 | 28 | 20 | 0 | 0 | 0 | 7084.2 | 930 | 189 | 0 | 29 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 1212.58 | 0 | 41 | 0 | 35 | 90 | 0 | 95 | 32 | 52.2 | 0 | 0 | 25 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 503 | 603 | 17 | 6182.78 | 13266.98 | 101.74
22:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17 | 0 | 149 | 45 | 294 | 15 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 142 | 22.5 | 21 | 0 | 77 | 115 | 16 | 22 | 0 | 0 | 65 | 60 | 16 | 24 | 24 | 0 | 84 | 102 | 32 | 650 | 54 | 0 | 33 | 25 | 101 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 138 | 0 | 305 | 0 | 330 | 34 | 0 | 38 | 66 | 103 | 199 | 0 | 20 | 107 | 60 | 52.2 | 0 | 29 | 320 | 0 | 379 | 0 | 57 | 156 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 49 | 28 | 20 | 0 | 0 | 0 | 6924.7 | 930 | 180 | 0 | 29 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1135 | 0 | 1214.99 | 0 | 41 | 0 | 35 | 90 | 0 | 95 | 32 | 52.2 | 0 | 0 | 22 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 603 | 17 | 6130.19 | 13054.89 | 101.74
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 17 | 0 | 149 | 45 | 294 | 8 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 23.2 | 21 | 0 | 80 | 115 | 16 | 18 | 0 | 0 | 65 | 60 | 17 | 24 | 12 | 0 | 84 | 107 | 36 | 650 | 17 | 0 | 33 | 25 | 103 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 130 | 0 | 310 | 0 | 330 | 35 | 0 | 38 | 34 | 103 | 194 | 0 | 20 | 109 | 68 | 52.2 | 0 | 30 | 315 | 0 | 378 | 0 | 57 | 154 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 49 | 28 | 20 | 0 | 0 | 0 | 6811.4 | 930 | 160 | 0 | 29 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 1215.82 | 0 | 41 | 0 | 35 | 70 | 0 | 95 | 32 | 52.2 | 0 | 0 | 24 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 603 | 17 | 6087.02 | 12898.42 | 101.74
Total KWH | 0 | 1668480 | 408000 | 0 | 0 | 0 | 0 | 0 | 8805600 | 0 | 0 | 522000 | 150840 | 2970432 | 2096160 | 5067611 | 266829 | 531682 | 1568160 | 0 | 4990000 | 0 | 0 | 0 | 139744 | 7473749 | 657000 | 0 | 158895 | 1720800 | 522600 | 464760 | 0 | 2295000 | 1369964 | 366327 | 232320 | 0 | 57600 | 436799 | 551040 | 64278 | 381120 | 325440 | 8379 | 2685220 | 1727091 | 484800 | 15614545.46 | 689164 | 0 | 638400 | 210119.4 | 1937855 | 5224254 | 0 | 0 | 0 | 14176362 | 109215 | 0 | 2403709 | 0 | 8036500 | 0 | 7994000 | 737760 | 0 | 896256 | 1126080 | 2457087 | 3070560 | 25200 | 467330 | 1438680 | 1489920 | 661046 | 346882 | 693920 | 7611000 | 0 | 9207000 | 0 | 993360 | 3722236 | 440352 | 0 | 1934400 | 717504 | 0 | 0 | 2371310 | 245160 | 1168800 | 662400 | 464640 | 10100 | 234560 | 0 | 151396386.86 | 22224727 | 5102784 | 0 | 206400 | 290176 | 912000 | 0 | 0 | 0 | 0 | 0 | 466560 | 26545460 | 0 | 29976273 | 0 | 282140 | 0 | 235200 | 541536 | 0 | 562032 | 184010 | 339019 | 316376 | 577800 | 203295 | 0 | 390000 | 3893273 | 0 | 0 | 0 | 0 | 0 | 8800218 | 0 | 30180 | 0 | 0 | 921191 | 161863 | 637776 | 0 | 0 | 0 | 37248.9 | 882000 | 2965 | 212544 | 0 | 2646000 | 5416250 | 0 | 12086064 | 13986909.09 | 249600 | 139319869.99 | 290716256.85

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12272.32 | MW | 12:00 Hr. | Energy Generated |  |  | 290.7163 |  | MKWHr.
| Day Peak Demand |  |  | 12302.32 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.117 |  | MKWHr.
| Evening Peak Generation |  |  | 13324.87 | MW | 19:30 Hr. | Energy Demand |  |  | 293.8333 |  | MKWHr.
| Evening Peak Demand |  |  | 13801.39 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.5 |  | °C
| Minimum Generation of the Day |  |  | 10555.5 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 794.65 |  | MMCFD
| Maximum Generation of the Day |  |  | 13324.87 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.0559 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.2087 | 0 | 17.1107 | 0 | 0 | 0.1589 | 0 | 0 | 42.4783 | Gas | 104.827 | Gas | 370900086.52
| Chattogram Zone |  |  | 5.7091 | 29.7909 | 8.9299 | 0 | 2.6852 | 0.11759 | 0 | 0.0576 | 47.2903 | Coal | 82.4093 | Coal | 535646114.018
| Cumilla Zone |  |  | 20.5889 | 0 | 9.4192 | 0 | 0 | 0.34688 | 1.4899 | 0 | 31.8449 | HFO | 42.4011 | HFO | 758962056.896
| Mymensingh Zone |  |  | 0.46464 | 0 | 2.0764 | 0 | 0 | 0.24466 | 0 | 0 | 2.7857 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9972 | Hydro | 2.6852 | Hydro | 268522
| Khulna Zone |  |  | 5.1028 | 26.5455 | 0.49658 | 0 | 0 | 0.46656 | 23.1367 | 0 | 55.7481 | Solar | 3.733 | Solar | 59275368.619
| Barishal Zone |  |  | 8.0623 | 26.073 | 0.46214 | 0 | 0 | 0.002965 | 0 | 0 | 34.6003 | Import | 54.6029 | Import | 325358614.25
| Rajshahi Zone |  |  | 12.6935 | 0 | 2.3472 | 0 | 0 | 1.3144 | 29.9763 | 0 | 46.3314 | Wind | 0.0576 | Wind | 847296
| Rangpur Zone |  |  | 0 | 0 | 1.559 | 0 | 0 | 1.0811 | 0 | 0 | 2.6401
| Total |  |  | 104.827 | 82.4093 | 42.4011 | 0 | 2.6852 | 3.733 | 54.6029 | 0.0576 | 290.7163
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 370900086.52 |  | Hydro | 268522
|  |  |  | Coal | 535646114.018 |  | Solar | 59275368.619
|  |  |  | HFO | 758962056.896 |  | Import | 325358614.25
|  |  |  | HSD | 0 |  | Wind | 847296
[5 empty] | Total: | 205,12,58,058 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2247 | Peak Hr Flow | 930.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51850327.35 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.9763 | Peak Hr Flow | 1224.97 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2461 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4899 | Peak Hr Flow | 68.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2692 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.6909 | Peak Hr Flow | 2222.97 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 10 |  | 5195
|  |  |  | Chattogram |  | 20 |  | 1362
|  |  |  | Cumilla |  | 80 |  | 1270
|  |  |  | Mymensingh |  | 80 |  | 1030
|  |  |  | Sylhet |  | 0 |  | 557
|  |  |  | Khulna |  | 140 |  | 1471
|  |  |  | Barishal |  | 0 |  | 424
|  |  |  | Rajshahi |  | 76 |  | 1149
|  |  |  | Rangpur |  | 50 |  | 764
|  |  |  | Total |  | 456 |  | 13222
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:00 | Meghnaghat 400/230kV S/S ATR - 2 LT is restored.
| 08:14 | 10:57 | Meghnaghat 400/230kV S/S ATR-1 LT Scheduled S/D Due to ATR- 1 shutdown for maintenance
work.
| 08:15 | 10:58 | Meghnaghat 400/230kV S/S ATR-1 HT Scheduled S/D Due to ATR- 1 shutdown for maintenace
work.
| 08:16 | 14:44 | Amnura 132/33kV S/S Amnura - 100MW PPP Scheduled S/D Due to Annual Maintenance
| 08:22 | 18:01 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end Due to
annual maintenance
| 08:24 | 15:40 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Scheduled S/D Due to Annual
maintenance
| 08:25 | 17:39 | Jaldhaka-Saidpur 132kV Ckt-2 Scheduled S/D from Jaldhaka 132/33kV end Due to Annual
Maintenance. and from Saidpur 132/33kV end Due to Annual Maintenance.
| 08:27 | 15:44 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Scheduled S/D Due to Annual
maintenance
| 08:32 | 14:19 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Tripped showing REF615, RET 650, RET 670 relays | [7 empty] | 18.0MW load
|  |  | Due to 33 KV BUS flashing | [7 empty] | interrup.
| 08:33 | 16:32 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to 132/33 kv TR-01 bay annual
maintenance.
| 08:33 | 16:32 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to 132/33 kv TR-01 bay annual
maintenance.
| 08:34 | 15:42 | Panchagar-Thakurgaon 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due to
Annual Maintenance and from Panchagarh 132/33kV end Due to Annual Maintenance
| 08:35 | 18:00 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Scheduled S/D from BIPTC end Due to Annual
Maintenance Work
| 08:36 | 14:50 | Goalpara 132/33kV S/S Bus 2 Scheduled S/D Due to Annual Maintenance
| 08:36 | 09:00 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Tripped showing REF 615, RET650, RET670 relays | [7 empty] | 18.0MW load
|  |  | Due to 33KV Bus flashing | [7 empty] | interrup.
| 08:38 | 15:27 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end. and
from Bog-Sherpur 132/33kVend.
| 08:41 |  | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to
Maintenance Work
| 08:42 | 10:25 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to 33kv Kachuadanga feeder Maintenance. | [7 empty] | 50.0MW load
interrup.
| 08:42 | 10:22 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33kv Kachuadanga feeder Maintenance. | [7 empty] | 50.0MW load
interrup.
| 08:51 |  | Mirsorai 230/33kV S/S TR-2, 728T HT Scheduled S/D Due to Annual Maintenance
| 08:54 | 14:49 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintenance of TR-02
| 08:54 | 14:50 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance of TR-02
| 09:04 | 15:23 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to Annual Maintenance
| 09:31 |  | Siddhirganj 2*120 MW GT-2 was sync.
| 09:32 | 15:10 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Annual maintenance
| 09:32 | 15:11 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Annual Maintenance
| 09:38 | 16:09 | Noapara 132/33kV S/S T-2 HT Project Work S/D
| 09:38 | 16:09 | Noapara 132/33kV S/S T-2 LT Project Work S/D
| 09:40 | 17:06 | Gopalganj 400/132kV S/S 132kV Bus-02 Scheduled S/D Due to Annual Maintenance
| 09:59 | 12:53 | Aminbazar 400/230/132kV S/S 132 kv Bus 02 Scheduled S/D Due to Scheduled shutdown
| 09:59 | 16:38 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Scheduled shutdown
| 10:01 | 11:32 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Forced S/D Due to OLTC oil refilling.
| 10:01 | 11:32 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Forced S/D Due to OLTC oil refilling.
| 10:31 | 15:03 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annaual maintenance.
| 10:32 | 15:01 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annaual Maintenance.
| 10:35 | 10:41 | Chhatak 132/33kV S/S T-1 LT Tripped showing MCGG relays Due to feeder Fault | [7 empty] | 5.0MW load
interrup.
| 10:35 | 10:39 | Chhatak 132/33kV S/S T-3 LT Tripped showing MCGG relays Due to Feeder Fault | [7 empty] | 11.0MW load
interrup.
| 10:42 | 16:24 | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end.
| 10:44 | 12:08 | Amnura 132/33kV S/S T-1 (406T) HT Forced S/D Due to Load Shift for Bus-2
| 10:56 | 16:07 | Tongi 230/132/33kV S/S Tongi-Mill Gate Ckt-1 Scheduled S/D Due to Annual maintenance
| 11:43 | 12:09 | Amnura 132/33kV S/S T-1 (406T) LT Forced S/D Due to Load Shift for Bus-2
| 11:43 | 11:56 | Amnura 132/33kV S/S T-3 (426T) LT Forced S/D Due to Load Shift for Bus-2 | [7 empty] | 3.0MW load
interrup.
| 11:44 | 11:56 | Amnura 132/33kV S/S T-3 (426T) HT Forced S/D Due to Load Shift for Bus-2
| 11:44 | 12:10 | Amnura 132/33kV S/S T-2 (416T) LT Forced S/D Due to Load Shift for Bus-2 | [7 empty] | 6.0MW load
interrup.
| 11:44 | 12:09 | Amnura 132/33kV S/S T-2 (416T) HT Forced S/D Due to Load Shift for Bus-2
| 12:00 |  | Day Peak Generation: 12270 MW.
| 12:32 | 14:19 | Kalurghat 132/33kV S/S TRFO-02(516T) HT Forced S/D Due to 33 KV Bus Maintenance.
| 13:26 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
|  | 14:08 | Bakulia 132/33kV S/S T-4 (432T) HT is restored.
|  | 14:23 | Khulna(S) 230/132kV S/S Rupsha Ckt-1 is restored.
| 14:39 |  | Aminbazar - Kaliakoire 400 kv line was shut down due to project work
|  | 15:02 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 15:03 | Naogaon 132/33kV S/S T-3 LT is restored.
|  | 15:11 | Sherpur 132/33kV S/S Transformer- 04 LT is restored.
|  | 15:20 | Sherpur 132/33kV S/S Bus A is restored.
|  | 16:36 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
|  | 16:37 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
|  | 17:09 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 is restored.
| 17:32 |  | Aminbazar - Kaliakoire 400 kv line was switched on.
|  | 18:08 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 is restored.
|  | 18:08 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 is restored.
| 18:21 |  | Siddhirganj 2*120 MW was shut down.
| 19:13 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
PGNS Project works and from Kaliakoir 400/230/132kV end Due to Testing purpose
| 19:30 |  | Evening Peak Gen. 13324 MW
| 06:00 |  | Minimum Generation is 10308 MW
| 07:02 |  | Shyampur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to Annual Maintenance
| 07:02 |  | Shyampur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to Annual Maintenance
| 07:14 |  | Amnura-Chapainawabganj-132kV Ckt-1 Project Work S/D from Chapai 132/33kV end Due to Tr-01
bay upgrading
| 07:14 |  | C.nawabganj-Rajshahi 132 kV Ckt-1 Project Work S/D from Chapai 132/33kV end Due to Tr-01
bay upgrading.
| 07:16 |  | Chapainawabganj-Rahanpur 132kV Ckt-1 Project Work S/D from Chapai 132/33kV end Due to
Tr-01 bay upgrading and from Rahanpur 400/132kV end Due to Work at Chapainawabganj end
| 07:20 |  | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to Project work. | [7 empty] | 5.0MW load
interrup.
| 07:20 |  | Chapai 132/33kV S/S Main Bus Project Work S/D Due to TR-01 Bay upgradation. | [7 empty] | 38.0MW load
interrup.
| 07:20 |  | Chapai 132/33kV S/S Chapai Rahanpur ckt 2 Project Work S/D Due to Tr-01 bay upgrading
| 07:21 |  | Saidpur 132/33kV S/S TR-5 (434T) HT Scheduled S/D Due to Project work. | [7 empty] | 5.0MW load
interrup.
| 07:23 |  | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 Scheduled S/D Due to
Work at Chapainawabganj end
| 07:30 |  | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance works
| 07:40 |  | Saidpur 132/33kV S/S BUS B Scheduled S/D Due to Project work.
| 07:52 |  | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Meghnaghat 230/132kV end Due to
Annual maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 362 | 8805600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4990000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 266829 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 657000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7473749 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 522000 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 2096160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 531682 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 139744 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23.5 | 522600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 464760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 408000 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 5067611 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2970432 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1668480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1568160 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 158895 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 150840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 78 | 2295000 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1720800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2098.5 | 42478342
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 210119.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109215 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 638400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 2685220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5224254 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 1937855 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 551040 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 436799 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 381120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 484800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 18 | 232320 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 8379 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 366327 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 64278 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 102 | 1727091 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 325440 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 1369964 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 126 | 689164 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14176362 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 57600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15614545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2311 | 47290292.86
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7994000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 320 | 8036500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 896256 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 35 | 737760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 2403709 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 693920 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2457087 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 199 | 3070560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 68 | 1489920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 661046 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 467330 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 110 | 1438680 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 25200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1126080 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 346882 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1517.2 | 31844930
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 20 | 464640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 662400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1168800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 234560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 245160 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 113 | 2785660
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 993360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3722236 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717504 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1934400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2371310 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 440352 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7611000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 369 | 9207000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1119 | 26997162
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 930 | 22224727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 206400 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 290176 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 194 | 5102784 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 466560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1106 | 26545460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2338 | 55748107
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 502 | 12086064 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 212544 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2646000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 602 | 13986909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5416250 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 249600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2965 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1467 | 34600332.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 316376 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 282140 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 184010 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 130 | 3893273 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 408 | 8800218 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 203295 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 339019 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 562032 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 541536 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 235200 | Engine Problem
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30180 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1224.97 | 29976273 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 390000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 577800 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2133.17 | 46331352
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 637776 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37248.9 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 921191 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 161863 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 882000 | -
Rangpur Area Total |  |  |  |  | 950 | 228 | 2640078.9
Eastern Grid Total |  |  |  |  | 17383.855 | 7158.7 | 151396386.86
Western Grid Total |  |  |  |  | 10821.56 | 6166.17 | 139319869.99
National Grid Total |  |  |  |  | 28205.415 | 13324.87 | 290716256.85
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-11-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9223.61 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3541.6 | MW
i) Dhaka area |  |  | 5185.43 |  | MW | i) Khulna area |  |  |  | 1331 | MW
ii) Chattogram area |  |  | 1341.5 |  | MW | ii) Barishal area |  |  |  | 424 | MW
iii) Cumilla area |  |  | 1189.68 |  | MW | iii) Rajshahi area |  |  |  | 1072.6 | MW
iv) Mymensingh area |  |  | 950 |  | MW | iv) Rangpur area |  |  |  | 714 | MW
v) Sylhet area |  |  | 557 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12765.21 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 81 | 18:00 | 133 | Niamatpur | 51 | 21:00
2 | AKSML | 146 | 09:00 | 68 | Ishurdi | 66 | 13:00 | 134 | Noapara | 36 | 13:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jaldhaka | 70 | 18:00 | 135 | PHP | 7 | 19:00
4 | Agargaon | 119 | 13:00 | 70 | Jamalpur | 85 | 07:00 | 136 | Pabna | 89 | 19:00
5 | Agrabad | 92 | 18:00 | 71 | Jashore | 115 | 21:00 | 137 | Palashbari | 88 | 21:00
6 | Amnura | 20 | 18:00 | 72 | Jhenaidah | 99 | 21:00 | 138 | Panchagarh | 45 | 19:00
7 | Ashuganj | 75 | 00:00 | 73 | Joydebpur | 146 | 12:00 | 139 | Patiya | 9.3 | 18:00
8 | BSRM | 205 | 06:00 | 74 | Joypurhat | 48 | 18:00 | 140 | Patuakhali | 58.5 | 22:00
9 | Bagerhat | 71 | 22:00 | 75 | Juldah | 16.5 | 18:30 | 141 | Payra | 32 | 19:00
10 | Bajitpur | 69 | 23:00 | 76 | KSRM | 28 | 10:00 | 142 | Postogola | 65 | 13:00
11 | Bakulia | 96 | 12:00 | 77 | Kabirpur | 252 | 19:30 | 143 | Purbachal | 17 | 13:00
12 | Banani | 46.4 | 13:00 | 78 | Kachua | 77 | 21:00 | 144 | Purbasadipur | 99 | 19:00
13 | Bangabhaban | 23 | 10:00 | 79 | Kallyanpur | 102 | 19:00 | 145 | Rahanpur | 23 | 18:00
14 | Barapukuria | 48 | 21:00 | 80 | Kalurghat | 48 | 15:00 | 146 | Rahim | 48 | 10:00
15 | Barguna | 18 | 18:00 | 81 | Kamrangirchar | 76 | 18:00 | 147 | Rajbari | 67 | 22:00
16 | Barishal | 97 | 18:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 117 | 19:30
17 | Barishal-230 | 98 | 18:00 | 83 | Kasba | 29 | 00:00 | 149 | Rajshahi | 102 | 00:00
18 | Baroaulia | 64 | 15:00 | 84 | Kazla | 107 | 13:00 | 150 | Rajshahi-230 | 69 | 19:30
19 | Baroirhat | 59 | 18:00 | 85 | Keranigonj | 86 | 18:30 | 151 | Ramganj | 94 | 21:00
20 | Bashundhara | 199 | 18:00 | 86 | Khagrachori | 28 | 18:00 | 152 | Rampur | 37 | 18:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 63 | 20:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 66 | 18:00 | 88 | Khulshi | 175 | 20:00 | 154 | Rangpur | 133 | 18:30
23 | Benapole | 52 | 19:30 | 89 | Kishoreganj | 118 | 20:00 | 155 | Ruppur | 6.4 | 10:00
24 | Bhaluka | 144 | 18:00 | 90 | Kodda | 290 | 12:00 | 156 | SSM | 2 | 00:00
25 | Bhandaria | 48 | 19:30 | 91 | Kulaura | 44 | 18:00 | 157 | Saidpur | 84 | 18:30
26 | Bhangura | 34 | 18:00 | 92 | Kurigram | 48 | 07:00 | 158 | Satkhira | 101 | 21:00
27 | Bheramara(GK) | 51 | 19:30 | 93 | Kushtia | 122 | 22:00 | 159 | Satmasjid | 98 | 14:00
28 | Bhulta | 215 | 12:00 | 94 | Laksam | 28 | 21:00 | 160 | Savar | 224 | 12:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 28 | 18:00 | 161 | SevenRings | 14.87 | 18:30
30 | Bogura | 146 | 19:00 | 96 | Lalbag | 61 | 18:30 | 162 | ShahCement | 32 | 07:00
31 | Borhanuddin | 85 | 22:00 | 97 | Lalmonirhat | 51 | 18:00 | 163 | Shahjadpur | 70 | 12:00
32 | Brahmanbaria | 131 | 18:00 | 98 | MI_Cement | 16 | 00:00 | 164 | Shahjibazar | 113 | 18:00
33 | Cantonment | 156 | 13:00 | 99 | Madanganj | 36 | 09:00 | 165 | Shahmirpur | 57 | 17:00
34 | Chandina | 13.29 | 18:00 | 100 | Madaripur | 87 | 22:00 | 166 | Shariatpur | 71 | 00:00
35 | Chandpur | 74 | 20:00 | 101 | Madartek | 84 | 22:00 | 167 | Sherpur | 100 | 01:00
36 | Chandraghona | 31 | 18:00 | 102 | Madunaghat | 50 | 14:00 | 168 | Shikalbaha | 28 | 18:30
37 | Chapai | 48 | 21:00 | 103 | Magura | 50 | 18:00 | 169 | Shitalakhya | 78.8 | 16:00
38 | Charsaidpur | 33 | 00:00 | 104 | Mahasthangarh | 58 | 00:00 | 170 | Sholosohor | 46 | 12:00
39 | Chauddagram | 60 | 21:00 | 105 | Maijdee | 30 | 00:00 | 171 | Shyampur | 138 | 00:00
40 | Chhatak | 34 | 01:00 | 106 | Manikganj | 120 | 20:00 | 172 | Siddhirganj | 119 | 15:00
41 | Chowmuhani | 142 | 00:00 | 107 | Maniknagar | 66 | 13:00 | 173 | Sirajganj | 98 | 19:00
42 | Chuadanga | 91 | 21:00 | 108 | Matarbari | 48 | 19:00 | 174 | Sonargaon | 138 | 16:00
43 | Coxsbazar | 128 | 19:00 | 109 | Matuail | 72 | 12:00 | 175 | Sreemongol | 71 | 20:00
44 | Cumilla(N) | 130 | 20:00 | 110 | Metrorail_Motijheel | 34 | 14:00 | 176 | Sreepur | 110 | 18:00
45 | Cumilla(S) | 139 | 18:00 | 111 | Metrorail_Uttara | 12 | 11:00 | 177 | Srinagar | 44.9 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 119 | 11:00 | 178 | Sunamganj | 56 | 21:00
47 | Daudkandi | 130 | 00:00 | 113 | Mirpur | 124 | 11:00 | 179 | Sylhet | 47 | 20:00
48 | DhakaUniversity | 84 | 13:00 | 114 | Mirsorai | 9 | 10:00 | 180 | Sylhet-132 | 116 | 18:00
49 | Dhamrai | 118 | 20:00 | 115 | Mirzapur | 42 | 03:00 | 181 | TK | 19 | 18:00
50 | Dhanmondi | 130.5 | 13:00 | 116 | Mithapukur | 50 | 18:00 | 182 | Tangail | 152 | 19:00
51 | Dohazari | 86 | 21:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 18 | 18:30
52 | Faridpur | 130 | 23:00 | 118 | Mogbazar | 87 | 13:00 | 184 | Thakurgaon | 71 | 19:00
53 | Fatullah | 114 | 10:00 | 119 | Mongla | 42 | 12:00 | 185 | Tongi | 113 | 15:00
54 | Fenchuganj | 37 | 15:00 | 120 | Motijheel | 42 | 13:00 | 186 | Ullahpara | 34 | 18:00
55 | Feni | 100 | 15:00 | 121 | Muktagacha | 27 | 07:00 | 187 | Ullon | 61 | 19:30
56 | GPH | 3 | 11:00 | 122 | Munshiganj | 103 | 00:00 | 188 | Uttara | 84 | 13:00
57 | Ghatail | 64 | 07:00 | 123 | Muradnagar | 37 | 21:00 | 189 | UttaraNew | 50 | 03:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 188 | 18:00 | 190 | Zigatola | 68 | 18:00
59 | Ghorashal-230 | 98 | 18:30 | 125 | Naogaon | 100 | 20:00
60 | Goalpara | 33 | 18:00 | 126 | Narail | 47 | 21:00
61 | Gollamari | 78 | 00:00 | 127 | Narinda | 73 | 13:00
62 | Gopalganj | 81 | 18:00 | 128 | Narshingdi | 169 | 19:00
63 | Gulshan | 120 | 13:00 | 129 | Natore | 119 | 18:00
64 | Halishahar | 68.5 | 13:00 | 130 | Nawabganj | 42.8 | 22:00
65 | HaripurSBU | 168 | 12:00 | 131 | Netrakona | 119 | 19:00
66 | Hasnabad | 86 | 18:00 | 132 | New | 56.4 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12594.5 | 30 |  | 12625.85
1:00 | 11978.5 | 0 |  | 11978.5
2:00 | 11560.5 | 0 |  | 11560.5
3:00 | 11109 | 0 |  | 11109
4:00 | 10736.5 | 0 |  | 10736.5
5:00 | 10592.5 | 0 |  | 10592.5
6:00 | 10555.5 | 0 |  | 10555.5
7:00 | 10828.06 | 0 |  | 10828.06
8:00 | 11161.66 | 0 |  | 11161.66
9:00 | 11107.62 | 0 |  | 11107.62
10:00 | 11468.5 | 0 |  | 11468.5
11:00 | 11852.29 | 0 |  | 11852.29
12:00 | 12272.32 | 29 |  | 12302.32
13:00 | 12495.12 | 246 |  | 12752.12
14:00 | 12377.67 | 169 |  | 12554.28
15:00 | 12321.54 | 270 |  | 12603.69
16:00 | 12129.72 | 263 |  | 12404.56
17:00 | 12232.95 | 257 |  | 12501.52
18:00 | 13176.16 | 406 |  | 13600.16
19:00 | 13305.6 | 425 |  | 13749.6
19:30 | 13324.87 | 456 |  | 13801.39
20:00 | 13303.76 | 398 |  | 13719.76
21:00 | 13266.98 | 223 |  | 13499.98
22:00 | 13054.89 | 207 |  | 13271.21
23:00 | 12898.42 | 194 |  | 13101.42
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6714.5 | 5880 | 12594.5 | DAILY GENERATION CURVE
00:30 | 6513.5 | 5773 | 12286.5
01:00 | 6312.5 | 5666 | 11978.5 | 06-11-2025
01:30 | 6161 | 5608.5 | 11769.5
02:00 | 6009.5 | 5551 | 11560.5
02:30 | 5792.25 | 5542.5 | 11334.75
03:00 | 5575 | 5534 | 11109
03:30 | 5408.75 | 5514 | 10922.75
04:00 | 5242.5 | 5494 | 10736.5
04:30 | 5186 | 5478.5 | 10664.5
05:00 | 5129.5 | 5463 | 10592.5
05:30 | 5103.5 | 5470.5 | 10574
06:00 | 5077.5 | 5478 | 10555.5
06:30 | 5162.605 | 5529.175 | 10691.78
07:00 | 5247.71 | 5580.35 | 10828.06
07:30 | 5364.86 | 5630 | 10994.86
08:00 | 5482.01 | 5679.65 | 11161.66
08:30 | 5515.51 | 5619.13 | 11134.64
09:00 | 5549.01 | 5558.61 | 11107.62
09:30 | 5741.95 | 5546.11 | 11288.06
10:00 | 5934.89 | 5533.61 | 11468.5
10:30 | 6044.81 | 5615.585 | 11660.395
11:00 | 6154.73 | 5697.56 | 11852.29
11:30 | 6326.6 | 5735.705 | 12062.305
12:00 | 6498.47 | 5773.85 | 12272.32
12:30 | 6529.985 | 5853.735 | 12383.72
13:00 | 6561.5 | 5933.62 | 12495.12
13:30 | 6530.535 | 5905.86 | 12436.395
14:00 | 6499.57 | 5878.1 | 12377.67
14:30 | 6579.375 | 5770.23 | 12349.605
15:00 | 6659.18 | 5662.36 | 12321.54
15:30 | 6610.27 | 5615.36 | 12225.63
16:00 | 6561.36 | 5568.36 | 12129.72
16:30 | 6616.71 | 5564.625 | 12181.335
17:00 | 6672.06 | 5560.89 | 12232.95
17:30 | 6922.63 | 5781.925 | 12704.555
18:00 | 7173.2 | 6002.96 | 13176.16
18:30 | 7147.2 | 6093.68 | 13240.88
19:00 | 7121.2 | 6184.4 | 13305.6
19:30 | 7158.7 | 6166.17 | 13324.87
20:00 | 7127.2 | 6176.56 | 13303.76
20:30 | 7105.7 | 6179.67 | 13285.37 |  | Executive Engineer
21:00 | 7084.2 | 6182.78 | 13266.98 |  | Network Operation Division
21:30 | 7004.45 | 6156.485 | 13160.935
22:00 | 6924.7 | 6130.19 | 13054.89
22:30 | 6868.05 | 6108.605 | 12976.655
23:00 | 6811.4 | 6087.02 | 12898.42

## En-Curve
QF-LDC-12
Date | 06-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2938 | 1396 | 908 | 38 | 64 | 1420 | 126 | 3348 | 0 | 512 | 1830.5 | 0 | 0 | 14 | 30 | DAILY ENERGY CURVE
00:30 | 2950.5 | 1393 | 908 | 38 | 66 | 1416 | 126 | 3345.5 | 0 | 432.5 | 1598 | 0 | 0 | 13 | 15 | 06-11-2025
01:00 | 2963 | 1390 | 908 | 38 | 68 | 1412 | 126 | 3343 | 0 | 353 | 1365.5 | 0 | 0 | 12 | 0
01:30 | 2973.5 | 1397.5 | 908 | 38 | 64 | 1413.5 | 126 | 3348 | 0 | 289 | 1200.5 | 0 | 0 | 11.5 | 0 | Energy Generated | 290.7163 |  | MKWHr
02:00 | 2984 | 1405 | 908 | 38 | 60 | 1415 | 126 | 3353 | 0 | 225 | 1035.5 | 0 | 0 | 11 | 0 | Energy not Served | 3.117 |  | MKWHr
02:30 | 2997 | 1402.25 | 908 | 38 | 61 | 1411 | 126 | 3355.5 | 0 | 193.5 | 830 | 0 | 0 | 12.5 | 0 | Total Energy Requirement | 293.8333 |  | MKWHr
03:00 | 3010 | 1399.5 | 908 | 38 | 62 | 1407 | 126 | 3358 | 0 | 162 | 624.5 | 0 | 0 | 14 | 0
03:30 | 3031 | 1412.25 | 907.5 | 38 | 59 | 1365 | 126 | 3368.5 | 0 | 154.5 | 449.5 | 0 | 0 | 11.5 | 0
04:00 | 3052 | 1425 | 907 | 38 | 56 | 1323 | 126 | 3379 | 0 | 147 | 274.5 | 0 | 0 | 9 | 0
04:30 | 3020 | 1407.5 | 907.5 | 38 | 59 | 1329 | 126 | 3369.5 | 0 | 147 | 256.5 | 0 | 0 | 4.5 | 0
05:00 | 2988 | 1390 | 908 | 38 | 62 | 1335 | 126 | 3360 | 0 | 147 | 238.5 | 0 | 0 | 0 | 0
05:30 | 3072 | 1247 | 907.5 | 38 | 61 | 1320.5 | 126 | 3373 | 0 | 154.5 | 273.5 | 0 | 0 | 1 | 0
06:00 | 3156 | 1104 | 907 | 38 | 60 | 1306 | 126 | 3386 | 0 | 162 | 308.5 | 0 | 0 | 2 | 0
06:30 | 3186.5 | 1104.5 | 907.5 | 38 | 55 | 1315 | 126 | 3394 | 26.53 | 178.5 | 358.75 | 0 | 0 | 1.5 | 0
07:00 | 3217 | 1105 | 908 | 38 | 50 | 1324 | 126 | 3402 | 53.06 | 195 | 409 | 0 | 0 | 1 | 0
07:30 | 3189.5 | 1108 | 907.5 | 38 | 52 | 1324.585 | 129 | 3395.5 | 114.275 | 210 | 526 | 0 | 0 | 0.5 | 0
08:00 | 3162 | 1111 | 907 | 38 | 54 | 1325.17 | 132 | 3389 | 175.49 | 225 | 643 | 0 | 0 | 0 | 0
08:30 | 3114.5 | 1097.5 | 907.5 | 38 | 56 | 1239.725 | 132 | 3371.5 | 254.415 | 233.5 | 688.5 | 0 | 0 | 1.5 | 0
09:00 | 3067 | 1084 | 908 | 38 | 58 | 1154.28 | 132 | 3354 | 333.34 | 242 | 734 | 0 | 0 | 3 | 0
09:30 | 3118 | 1091 | 908 | 38 | 59 | 1084.55 | 132 | 3353 | 416.01 | 251 | 836 | 0 | 0 | 1.5 | 0
10:00 | 3169 | 1098 | 908 | 38 | 60 | 1014.82 | 132 | 3352 | 498.68 | 260 | 938 | 0 | 0 | 0 | 0
10:30 | 3209 | 1103 | 908 | 38 | 61 | 1022.14 | 132 | 3367.5 | 540.755 | 279.5 | 999.5 | 0 | 0 | 0 | 0
11:00 | 3249 | 1108 | 908 | 38 | 62 | 1029.46 | 132 | 3383 | 582.83 | 299 | 1061 | 0 | 0 | 0 | 0
11:30 | 3274 | 1107 | 908 | 38 | 65 | 1077.745 | 132 | 3407 | 539.56 | 307.5 | 1206.5 | 0 | 0 | 0 | 14.5
12:00 | 3299 | 1106 | 908 | 38 | 68 | 1126.03 | 132 | 3431 | 496.29 | 316 | 1352 | 0 | 0 | 0 | 29
12:30 | 3256.5 | 1106 | 913.5 | 38 | 66 | 1198.33 | 132 | 3439.5 | 483.14 | 321.5 | 1429.25 | 0 | 0 | 0 | 137.5
13:00 | 3214 | 1106 | 919 | 38 | 64 | 1270.63 | 132 | 3448 | 469.99 | 327 | 1506.5 | 0 | 0 | 0 | 246
13:30 | 3074.5 | 1123 | 924.5 | 38 | 65 | 1339.995 | 131 | 3443.5 | 495.4 | 327.5 | 1474 | 0 | 0 | 0 | 207.5
14:00 | 2935 | 1140 | 930 | 38 | 66 | 1409.36 | 130 | 3439 | 520.81 | 328 | 1441.5 | 0 | 0 | 0 | 169
14:30 | 3025.5 | 1169.5 | 929.5 | 38 | 65 | 1323.895 | 108 | 3453.5 | 433.61 | 319.5 | 1483.6 | 0 | 0 | 0 | 219.5
15:00 | 3116 | 1199 | 929 | 38 | 64 | 1238.43 | 86 | 3468 | 346.41 | 311 | 1525.7 | 0 | 0 | 0 | 270
15:30 | 3095.5 | 1202.5 | 929.5 | 38 | 64 | 1228.515 | 86 | 3473 | 249.965 | 320.7 | 1537.95 | 0 | 0 | 0 | 266.5
16:00 | 3075 | 1206 | 930 | 38 | 64 | 1218.6 | 86 | 3478 | 153.52 | 330.4 | 1550.2 | 0 | 0 | 0 | 263
16:30 | 3062 | 1208 | 930 | 38 | 65 | 1220.145 | 86 | 3476.5 | 82.29 | 363.7 | 1649.7 | 0 | 0 | 0 | 260
17:00 | 3049 | 1210 | 930 | 38 | 66 | 1221.69 | 86 | 3475 | 11.06 | 397 | 1749.2 | 0 | 0 | 0 | 257
17:30 | 3124.5 | 1206.5 | 930 | 38 | 71 | 1218.825 | 78 | 3483.5 | 5.53 | 567 | 1981.7 | 0 | 0 | 0 | 331.5
18:00 | 3200 | 1203 | 930 | 38 | 76 | 1215.96 | 70 | 3492 | 0 | 737 | 2214.2 | 0 | 0 | 0 | 406
18:30 | 3158 | 1211.5 | 930 | 38 | 76 | 1223.08 | 75 | 3489.5 | 0 | 762.5 | 2277.3 | 0 | 0 | 0 | 415.5
19:00 | 3116 | 1220 | 930 | 38 | 76 | 1230.2 | 80 | 3487 | 0 | 788 | 2340.4 | 0 | 0 | 0 | 425
19:30 | 3124 | 1213.5 | 930 | 38 | 68 | 1224.97 | 80 | 3472 | 0 | 766 | 2408.4 | 0 | 0 | 0 | 456
20:00 | 3109 | 1213 | 930 | 38 | 68 | 1221.36 | 80 | 3481 | 0 | 763 | 2400.4 | 0 | 0 | 0 | 398
20:30 | 3129 | 1208.5 | 930 | 38 | 65 | 1216.97 | 82 | 3478.5 | 0 | 763 | 2374.4 | 0 | 0 | 0 | 310.5
21:00 | 3149 | 1204 | 930 | 38 | 62 | 1212.58 | 84 | 3476 | 0 | 763 | 2348.4 | 0 | 0 | 0 | 223
21:30 | 3158.5 | 1217.25 | 930 | 38 | 61 | 1213.785 | 84 | 3489 | 0 | 722 | 2247.4 | 0 | 0 | 0 | 215
22:00 | 3168 | 1230.5 | 930 | 38 | 60 | 1214.99 | 84 | 3502 | 0 | 681 | 2146.4 | 0 | 0 | 0 | 207
22:30 | 3158.5 | 1231.35 | 930 | 38 | 64 | 1215.405 | 84 | 3483.5 | 0 | 683 | 2088.9 | 0 | 0 | 0 | 200.5
23:00 | 3149 | 1232.2 | 930 | 38 | 68 | 1215.82 | 84 | 3465 | 0 | 685 | 2031.4 | 0 | 0 | 0 | 194
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 00:00 | 372 | 11:00 | Payra | 408 | 00:00 | 405 | 11:00
Ashuganj | 397 | 21:00 | 377 | 11:00 | Rahanpur | 408 | 20:00 | 397 | 14:00
Bhulta | 393 | 00:00 | 376 | 12:00 | Rampal | 404 | 01:00 | 396 | 12:00
Bibiana | 389 | 00:00 | 383 | 15:00
BIPTC | 407 | 03:00 | 394 | 18:00
Bogura | 400 | 10:00 | 386 | 14:00
Gopalganj | 394 | 00:00 | 387 | 14:00
Kaliakoir | 376 | 00:00 | 364 | 12:00
Madunaghat | 397 | 21:00 | 391 | 06:00
Meghnaghat | 384 | 00:00 | 372 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 01:00 | 221 | 12:00 | Kaliakoir | 235 | 00:00 | 226 | 12:00
AKSML | 236 | 18:30 | 226 | 04:00 | Keranigonj | 225 | 00:00 | 217 | 12:00
Aminbazar | 230 | 04:00 | 222 | 13:00 | Khulna(S) | 233 | 05:00 | 227 | 13:00
Ashuganj | 232 | 22:00 | 223 | 08:00 | Madunaghat | 237 | 19:00 | 232 | 04:00
Ashuganj-400 | 232 | 22:00 | 223 | 08:00 | Madunaghat-400 | 238 | 21:00 | 231 | 06:00
Baghabari | 234 | 19:00 | 227 | 14:00 | Maniknagar | 219 | 05:00 | 210 | 12:00
Barapukuria | 223 | 20:00 | 203 | 07:00 | Meghnaghat | 226 | 00:00 | 220 | 12:00
Barapukuria-230 | 223 | 20:00 | 203 | 07:00 | Meghnaghat-400 | 222 | 00:00 | 216 | 12:00
Barishal | 234 | 00:00 | 230 | 12:00 | Mirsorai | 237 | 19:30 | 223 | 04:00
Bheramara | 230 | 05:00 | 225 | 13:00 | Rajshahi | 232 | 19:00 | 223 | 14:00
Bhulta | 229 | 00:00 | 212 | 12:00 | Rampal | 232 | 05:00 | 225 | 12:00
Bibiana | 230 | 02:00 | 225 | 15:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 234 | 06:00 | 226 | 14:00 | Rampura | 228 | 21:00 | 212 | 11:00
Bogura | 233 | 19:30 | 223 | 14:00 | Shikalbaha | 237 | 17:00 | 229 | 05:00
Bogura-400 | 232 | 19:30 | 224 | 07:00 | Shyampur | 223 | 01:00 | 216 | 12:00
Borhanuddin | 237 | 00:00 | 234 | 01:00 | Siddhirganj | 221 | 04:00 | 214 | 11:00
BSRM | 234 | 20:00 | 223 | 04:00 | Sirajgonj | 238 | 19:30 | 233 | 07:00
Cumilla(N) | 227 | 02:00 | 222 | 09:00 | Sreepur | 227 | 00:00 | 221 | 07:00
Faridpur | 230 | 05:00 | 225 | 12:00 | Tongi | 231 | 01:00 | 222 | 23:00
Fenchuganj | 232 | 06:00 | 228 | 12:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 229 | 23:00 | 218 | 07:00
Gopalganj | 235 | 19:00 | 224 | 23:00
GPH | 236 | 20:00 | 227 | 04:00
Haripur | 220 | 05:00 | 214 | 12:00
Hasnabad | 224 | 00:00 | 218 | 12:00
Hathazari | 236 | 20:00 | 228 | 04:00
Ishurdi | 234 | 06:00 | 228 | 14:00
Jhenaidah | 230 | 05:00 | 219 | 13:00
Kachua | 230 | 00:00 | 225 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 22:00 | 125 | 10:00 | Lalmonirhat | 130 | 19:00 | 121 | 07:00
Agargaon | 135 | 01:00 | 128 | 12:00 | Madanganj | 129 | 18:00 | 124 | 12:00
Agrabad | 136 | 20:00 | 131 | 01:00 | Madaripur | 134 | 00:00 | 132 | 13:00
AKS | 134 | 18:30 | 131 | 01:00 | Madartek | 135 | 23:00 | 125 | 08:00
Aminbazar | 136 | 01:00 | 130 | 10:00 | Madunaghat | 138 | 20:00 | 133 | 04:00
Amnura | 138 | 10:00 | 129 | 13:00 | Magura | 133 | 04:00 | 125 | 13:00
Ashuganj | 140 | 00:00 | 138 | 07:00 | Mahasthangarh | 133 | 20:00 | 125 | 14:00
Bagerhat | 131 | 05:00 | 124 | 22:00 | Maijdee | 134 | 18:00 | 130 | 01:00
Bajitpur | 131 | 00:00 | 125 | 09:00 | Manikganj | 133 | 00:00 | 127 | 08:00
Bakulia | 137 | 18:30 | 133 | 04:00 | Maniknagar | 133 | 08:00 | 127 | 12:00
Banani | 134 | 22:00 | 124 | 11:00 | Matarbari | 125 | 09:00 | 117 | 19:30
Bangabhaban | 133 | 06:00 | 126 | 12:00 | Matuail | 128 | 06:00 | 124 | 12:00
Barapukuria | 137 | 19:30 | 122 | 07:00 | Metrorail_Motijheel | 133 | 08:00 | 126 | 16:00
Barguna | 135 | 00:00 | 134 | 07:00 | Metrorail_Uttara | 138 | 00:00 | 131 | 11:00
Barishal | 137 | 00:00 | 130 | 12:00 | Millgate | 138 | 01:00 | 131 | 09:00
Barishal-230 | 136 | 00:00 | 131 | 12:00 | Mirpur | 134 | 01:00 | 128 | 12:00
Baroaulia | 136 | 18:00 | 132 | 05:00 | Mirzapur | 130 | 02:00 | 125 | 19:30
Baroirhat | 135 | 19:30 | 129 | 05:00 | Mithapukur | 134 | 19:30 | 124 | 07:00
Bashundhara | 134 | 01:00 | 125 | 09:00 | MI_Cement | 131 | 01:00 | 124 | 12:00
BashundharaCement | 129 | 18:00 | 124 | 12:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 131 | 06:00 | 126 | 18:00 | Mogbazar | 137 | 04:00 | 121 | 13:00
Benapole | 130 | 04:00 | 119 | 13:00 | Mongla | 132 | 07:00 | 124 | 22:00
Bhaluka | 132 | 20:00 | 126 | 06:00 | Motijheel | 133 | 06:00 | 126 | 12:00
Bhandaria | 134 | 00:00 | 126 | 22:00 | Muktagacha | 130 | 10:00 | 116 | 13:00
Bhangura | 133 | 19:30 | 129 | 13:00 | Munshiganj | 127 | 00:00 | 123 | 12:00
Bheramara | 137 | 03:00 | 134 | 15:00 | Muradnagar | 128 | 07:00 | 126 | 01:00
Bheramara(GK) | 137 | 03:00 | 135 | 12:00 | Mymensingh | 130 | 10:00 | 115 | 13:00
Bhulta | 126 | 08:00 | 122 | 12:00 | Naogaon | 130 | 19:00 | 122 | 13:00
Bog-Sherpur | 133 | 19:30 | 127 | 07:00 | Narail | 135 | 06:00 | 125 | 13:00
Bogura | 134 | 19:30 | 128 | 07:00 | Narinda | 133 | 08:00 | 127 | 12:00
Bogura-230 | 134 | 19:30 | 127 | 07:00 | Narshingdi | 132 | 04:00 | 120 | 12:00
Brahmanbaria | 133 | 00:00 | 128 | 12:00 | Natore | 134 | 19:30 | 129 | 13:00
Cantonment | 134 | 01:00 | 127 | 12:00 | Nawabganj | 133 | 02:00 | 127 | 12:00
Chandina | 133 | 20:00 | 130 | 04:00 | Netrakona | 127 | 10:00 | 119 | 18:00
Chandpur | 140 | 17:00 | 133 | 04:00 | New | 139 | 00:00 | 132 | 10:00
Chandraghona | 138 | 19:00 | 134 | 03:00 | Niamatpur | 139 | 10:00 | 136 | 00:00
Chapai | 140 | 18:00 | 136 | 01:00 | Noapara | 133 | 09:00 | 127 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 18:00 | 123 | 12:00 | Pabna | 137 | 04:00 | 132 | 12:00
Chauddagram | 134 | 19:30 | 129 | 04:00 | Palashbari | 131 | 19:30 | 120 | 07:00
Chhatak | 129 | 06:00 | 123 | 18:00 | Panchagarh | 141 | 20:00 | 123 | 07:00
Chowmuhani | 133 | 12:00 | 131 | 01:00 | Patiya | 136 | 18:30 | 131 | 04:00
Chuadanga | 133 | 06:00 | 125 | 13:00 | Patuakhali | 135 | 17:00 | 134 | 00:00
Coxsbazar | 124 | 14:00 | 115 | 19:00 | Payra | 136 | 00:00 | 135 | 11:00
Cumilla(N) | 133 | 02:00 | 130 | 10:00 | PHP | 134 | 18:30 | 129 | 04:00
Cumilla(S) | 133 | 17:00 | 127 | 15:00 | Postogola | 133 | 01:00 | 127 | 12:00
Daganbhuiyan | 135 | 20:00 | 129 | 04:00 | Purbachal | 133 | 01:00 | 123 | 11:00
Daudkandi | 127 | 08:00 | 123 | 12:00 | Purbasadipur | 136 | 19:30 | 116 | 07:00
DhakaUniversity | 134 | 00:00 | 125 | 10:00 | Rahanpur | 140 | 07:00 | 136 | 14:00
Dhamrai | 134 | 19:00 | 130 | 09:00 | Rahanpur-400 | 140 | 10:00 | 137 | 07:00
Dhanmondi | 134 | 21:00 | 125 | 11:00 | Rahim | 128 | 06:00 | 124 | 12:00
Dohazari | 133 | 22:00 | 125 | 19:30 | Rajbari | 135 | 05:00 | 132 | 12:00
Faridpur | 136 | 18:30 | 133 | 12:00 | Rajendrapur | 130 | 00:00 | 125 | 14:00
Fatullah | 136 | 01:00 | 125 | 12:00 | Rajshahi | 134 | 20:00 | 128 | 13:00
Fenchuganj | 139 | 05:00 | 134 | 12:00 | Rajshahi-230 | 133 | 05:00 | 128 | 14:00
Feni | 134 | 17:00 | 128 | 11:00 | Ramganj | 135 | 19:00 | 131 | 04:00
Ghatail | 128 | 09:00 | 117 | 13:00 | Rampur | 137 | 23:00 | 131 | 11:00
Ghorashal | 138 | 00:00 | 132 | 09:00 | Rampura | 133 | 21:00 | 123 | 11:00
Goalpara | 136 | 05:00 | 130 | 12:00 | Rangamati | 137 | 20:00 | 133 | 03:00
Gollamari | 134 | 03:00 | 131 | 12:00 | Rangpur | 135 | 19:30 | 122 | 07:00
Gopalganj | 135 | 05:00 | 130 | 12:00 | Ruppur | 137 | 03:00 | 134 | 14:00
Gopalganj-400 | 135 | 00:00 | 132 | 23:00 | Saidpur | 134 | 19:30 | 122 | 07:00
Gulshan | 135 | 23:00 | 126 | 08:00 | Satkhira | 132 | 03:00 | 126 | 21:00
Halishahar | 137 | 20:00 | 132 | 03:00 | Satmasjid | 134 | 03:00 | 127 | 13:00
Haripur | 128 | 00:00 | 124 | 12:00 | Savar | 136 | 02:00 | 128 | 11:00
HaripurSBU | 128 | 00:00 | 126 | 13:00 | SevenRings | 139 | 23:00 | 132 | 07:00
Hasnabad | 133 | 04:00 | 127 | 12:00 | ShahCement | 128 | 18:00 | 123 | 12:00
Hathazari | 138 | 20:00 | 134 | 16:00 | Shahjadpur | 136 | 19:30 | 134 | 00:00
Ishurdi | 138 | 05:00 | 135 | 14:00 | Shahjibazar | 134 | 01:00 | 130 | 18:00
Jaldhaka | 133 | 19:30 | 122 | 14:00 | Shahmirpur | 137 | 17:00 | 133 | 02:00
Jamalpur | 128 | 09:00 | 113 | 20:00 | Shariatpur | 134 | 06:00 | 131 | 12:00
Jashore | 132 | 06:00 | 120 | 13:00 | Sherpur | 125 | 09:00 | 117 | 22:00
Jhenaidah | 138 | 05:00 | 128 | 15:00 | Shikalbaha | 127 | 20:00 | 122 | 02:00
Jhenaidah-230 | 136 | 05:00 | 128 | 13:00 | Shikalbaha-230 | 138 | 17:00 | 134 | 01:00
Joydebpur | 140 | 16:00 | 128 | 09:00 | Shitalakhya | 131 | 01:00 | 124 | 12:00
Joypurhat | 129 | 19:30 | 121 | 15:00 | Sholosohor | 138 | 20:00 | 133 | 04:00
Juldah | 137 | 22:00 | 133 | 03:00 | Shyampur | 134 | 00:00 | 132 | 09:00
Kabirpur | 135 | 00:00 | 129 | 09:00 | Shyampur-230 | 135 | 01:00 | 130 | 12:00
Kachua | 138 | 17:00 | 133 | 04:00 | Siddhirganj | 128 | 00:00 | 124 | 12:00
Kaliakoir | 136 | 00:00 | 130 | 12:00 | Sirajganj | 131 | 04:00 | 127 | 07:00
Kallyanpur | 135 | 00:00 | 128 | 12:00 | Sonargaon | 127 | 08:00 | 123 | 12:00
Kalurghat | 138 | 19:30 | 134 | 04:00 | Sreemongol | 133 | 00:00 | 130 | 18:30
Kamrangirchar | 134 | 04:00 | 127 | 12:00 | Sreepur | 133 | 00:00 | 128 | 15:00
Kaptai | 137 | 19:30 | 131 | 02:00 | Srinagar | 134 | 08:00 | 127 | 12:00
Kasba | 129 | 20:00 | 125 | 04:00 | SSM | 140 | 18:00 | 138 | 00:00
Kazla | 132 | 01:00 | 126 | 13:00 | Sunamganj | 126 | 07:00 | 120 | 18:00
Keranigonj | 133 | 00:00 | 128 | 12:00 | Sylhet | 131 | 05:00 | 128 | 13:00
Khagrachori | 136 | 19:30 | 133 | 02:00 | Sylhet-132 | 130 | 00:00 | 128 | 12:00
Khulna | 134 | 03:00 | 129 | 12:00 | Tangail | 128 | 10:00 | 120 | 18:30
Khulna(S) | 135 | 05:00 | 130 | 22:00 | Taraganj | 134 | 19:30 | 123 | 15:00
Khulshi | 135 | 19:30 | 131 | 04:00 | Thakurgaon | 140 | 19:00 | 119 | 07:00
Kishoreganj | 130 | 00:00 | 125 | 18:00 | TK | 137 | 01:00 | 134 | 10:00
Kodda | 138 | 22:00 | 128 | 12:00 | Tongi | 139 | 21:00 | 133 | 10:00
KSRM | 136 | 22:00 | 132 | 02:00 | Ullahpara | 133 | 03:00 | 129 | 15:00
Kulaura | 136 | 04:00 | 133 | 13:00 | Ullon | 134 | 23:00 | 123 | 11:00
Kurigram | 130 | 10:00 | 114 | 07:00 | Uttara | 135 | 00:00 | 128 | 12:00
Kushtia | 136 | 05:00 | 132 | 14:00 | UttaraNew | 138 | 00:00 | 131 | 11:00
Laksam | 137 | 18:30 | 131 | 17:00 | Zigatola | 134 | 05:00 | 128 | 12:00
Lakshmipur | 133 | 17:00 | 128 | 04:00
Lalbag | 133 | 02:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division