## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-11-2025 | during | 08-11-2025 | during | 08-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 190 | 190 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 97.7 | 97.7 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 363 | 361 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 329 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17.5 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 40 | 123 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 0 | 24.75 | 24.75 | 24.75 | 24.75 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 30 | 31 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 47 | 34 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 65 | 0 | 584 | 584 | 584 | 584 | ST Under Maintenance, GT Gas Shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1323 | 1663.5 | 5922.85 | 5892.85 | 5584.39 | 5626.39
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 2 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 130 | 130 | 130 | 130 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 221 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 82 | 101 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 62 | 60 | 60 | 60 | 60 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 20 | 23 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 26 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.21 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 100 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 14 | 104 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 8 | 89 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 54 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 596 | 585 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 0 | 6 | 10 | 6 | 10 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 370 | 315 | 650 | 650 | 315 | 315 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1485.21 | 1853 | 2992 | 2983.72 | 2189.64 | 2181.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 310 | 280 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 42 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 33 | 127 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 11 | 22 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 102 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 38 | 180 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 64 | 72 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 51 | 98 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 36 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1112 | 1399.2 | 2606.56 | 2551.56 | 2338.56 | 2283.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-11-2025 | during | 08-11-2025 | during | 08-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 104 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 59 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 18 | 26 | 18.5 | 18.5 | 18 | 18 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.94 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 6 | 6 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 154.94 | 188 | 364.6 | 312.5 | 310.6 | 258.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 57 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 149 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 99 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 12 | 12 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 391 | 387 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1168 | 1142 | 1203 | 1203 | 1141 | 1141
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 930 | 915 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 35 | 35 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 48 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 216 | 300 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1045 | 1110 | 0 | 0 | 1100 | 1100 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2307 | 2436 | 2390 | 2305 | 2736 | 2651
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 374 | 502 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 545 | 600 | 622 | 622 | 592 | 592 | U-1 Machine Problem,U-2 Under Maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1249.58 | 1465 | 1218 | 1217 | 1047 | 1046
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54.75 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 168 | 193 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 384 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Engine Problem
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.4 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 964.88 | 1222.44 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.65 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1762.68 | 2134.64 | 3174.46 | 3007.87 | 2568.68 | 2402.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 146 | 0 | 181.82 | 0 | 181.82 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 185 | 185 | 465.62 | 248 | 445.62 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 10747.41 | 12466.34 | 20337.09 | 19721.5 | 18361.49 | 17817.9
Forecast Scenario (08-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12220 |  | 0 |  | 12220
|  |  |  | 1:00 | 11810 |  | 0 |  | 11810
|  |  |  | 2:00 | 11330 |  | 0 |  | 11330
|  |  |  | 3:00 | 11010 |  | 0 |  | 11010
|  |  |  | 4:00 | 10740 |  | 0 |  | 10740
|  |  |  | 5:00 | 10560 |  | 0 |  | 10560
|  |  |  | 6:00 | 10390 |  | 0 |  | 10390
|  |  |  | 7:00 | 10190 |  | 0 |  | 10190
|  |  |  | 8:00 | 10500 |  | 0 |  | 10500
|  |  |  | 9:00 | 10720 |  | 0 |  | 10720
|  |  |  | 10:00 | 10750 |  | 0 |  | 10750
|  |  |  | 11:00 | 11090 |  | 0 |  | 11090
|  |  |  | 12:00 | 11630 |  | 0 |  | 11630
|  |  |  | 13:00 | 11980 |  | 0 |  | 11980
|  |  |  | 14:00 | 11970 |  | 0 |  | 11970
|  |  |  | 15:00 | 11980 |  | 0 |  | 11980
|  |  |  | 16:00 | 11760 |  | 0 |  | 11760
|  |  |  | 17:00 | 12000 |  | 0 |  | 12000
|  |  |  | 18:00 | 12600 |  | 0 |  | 12600
|  |  |  | 18:30 | 12700 |  | 0 |  | 12700
|  |  |  | 19:00 | 12780 |  | 0 |  | 12780
|  |  |  | 19:30 | 12660 |  | 0 |  | 12660
|  |  |  | 20:00 | 12570 |  | 0 |  | 12570
|  |  |  | 21:00 | 12560 |  | 0 |  | 12560
|  |  |  | 22:00 | 12450 |  | 0 |  | 12450
|  |  |  | 23:00 | 12400 |  | 0 |  | 12400
Probable Maximum Temperature: |  |  | 32.50°C
Probable Maximum Demand at Day Peak: |  |  | 11630.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12780.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12780.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 277.99 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:37 hrs on 08-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-11-2025 | [28 empty] | Date: | 07-11-2025 | [28 empty] | Date: | 07-11-2025 | [28 empty] | Date: | 07-11-2025 | [28 empty] | Date: | 07-11-2025 | [14 empty] | Date: | 07-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [14 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17 | 0 | 149 | 45 | 294 | 4 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 23.2 | 21 | 0 | 77 | 92 | 16 | 19 | 0 | 0 | 65 | 60 | 17 | 12 | 12 | 0 | 84 | 105 | 37 | 650 | 17 | 0 | 26 | 25.5 | 104 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 130 | 0 | 310 | 0 | 330 | 35 | 0 | 38 | 34 | 103 | 181 | 0 | 20 | 110 | 68 | 52.2 | 0 | 30 | 315 | 0 | 376 | 0 | 57 | 157 | 22 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 49 | 28 | 21 | 0 | 0 | 0 | 6639.9 | 930 | 165 | 0 | 29 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 1217.83 | 0 | 41 | 0 | 35 | 50 | 0 | 0 | 32 | 52.2 | 0 | 0 | 24 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 504 | 603 | 17 | 5989.03 | 12628.93 | 101.74
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 0 | 149 | 45 | 294 | 55 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 23.8 | 21 | 0 | 77 | 99 | 16 | 18 | 0 | 0 | 33 | 60 | 17 | 12 | 12 | 0 | 84 | 102 | 37 | 650 | 17 | 0 | 26 | 25.5 | 102 | 225 | 0 | 0 | 0 | 578 | 0 | 0 | 117 | 0 | 310 | 0 | 330 | 35 | 0 | 38 | 34 | 102 | 187 | 0 | 20 | 95 | 62 | 52.2 | 0 | 30 | 310 | 0 | 369 | 0 | 57 | 152 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 56 | 22 | 0 | 0 | 0 | 6473.5 | 930 | 165 | 0 | 29 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 1213.93 | 0 | 32 | 0 | 0 | 35 | 0 | 0 | 32 | 52.2 | 0 | 0 | 24 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 504 | 560 | 17 | 5852.13 | 12325.63 | 101.74
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 0 | 149 | 30 | 294 | 55 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 24.5 | 21 | 0 | 77 | 92 | 16 | 18 | 0 | 0 | 0 | 60 | 17 | 12 | 12 | 0 | 84 | 103 | 37 | 650 | 17 | 0 | 26 | 25 | 101 | 225 | 0 | 0 | 0 | 575 | 0 | 0 | 107 | 0 | 315 | 0 | 330 | 35 | 0 | 38 | 34 | 104 | 182 | 0 | 20 | 14 | 56 | 52.2 | 0 | 30 | 310 | 0 | 352 | 0 | 57 | 149 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 56 | 22 | 0 | 0 | 0 | 6295.7 | 930 | 165 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 1221.39 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 501 | 550 | 17 | 5663.39 | 11959.09 | 101.74
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 0 | 149 | 30 | 294 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 24.5 | 21 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 12 | 12 | 0 | 84 | 101 | 37 | 650 | 0 | 0 | 26 | 0 | 96 | 225 | 0 | 0 | 0 | 576 | 0 | 0 | 110 | 0 | 330 | 0 | 330 | 35 | 0 | 35 | 34 | 104 | 168 | 0 | 20 | 0 | 58 | 0 | 0 | 0 | 305 | 0 | 346 | 0 | 57 | 141 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 58 | 23 | 0 | 0 | 0 | 5902.5 | 829 | 165 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 1212.38 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 535 | 0 | 5446.38 | 11348.88 | 101.74
04:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 0 | 121 | 30 | 145 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 24.5 | 21 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 84 | 34 | 37 | 650 | 0 | 0 | 10 | 0 | 51 | 225 | 0 | 0 | 0 | 578 | 0 | 0 | 60 | 0 | 340 | 0 | 330 | 35 | 0 | 35 | 33 | 104 | 173 | 0 | 20 | 0 | 56 | 0 | 0 | 0 | 300 | 0 | 360 | 0 | 57 | 145 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 58 | 23 | 0 | 0 | 0 | 5510.5 | 930 | 164 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 1217.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 501 | 540 | 0 | 5441.85 | 10952.35 | 101.74
05:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 113 | 30 | 145 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 24.5 | 21 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 84 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 50 | 225 | 0 | 0 | 0 | 578 | 0 | 0 | 60 | 0 | 345 | 0 | 330 | 35 | 0 | 35 | 20 | 104 | 176 | 0 | 20 | 0 | 54 | 0 | 0 | 0 | 305 | 0 | 344 | 0 | 57 | 145 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 58 | 24 | 0 | 0 | 0 | 5431.5 | 930 | 166 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 1212.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 452 | 544 | 0 | 5318.47 | 10749.97 | 101.74
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 116 | 30 | 155 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 22.5 | 21 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 84 | 0 | 39 | 650 | 0 | 0 | 0 | 0 | 17 | 226 | 0 | 0 | 0 | 566 | 0 | 0 | 60 | 0 | 350 | 0 | 330 | 36 | 0 | 35 | 17 | 105 | 120 | 0 | 20 | 0 | 52 | 0 | 0 | 0 | 305 | 0 | 340 | 0 | 57 | 143 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 58 | 24 | 0 | 0 | 0 | 5330.5 | 930 | 166 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1064 | 0 | 1165.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 401 | 500 | 0 | 5060.81 | 10391.31 | 101.74
07:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 149 | 30 | 195 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 17 | 0 | 21 | 0 | 66 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 0.35 | 84 | 0 | 41 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 505 | 2 | 0 | 60 | 0 | 335 | 0 | 330 | 40 | 0 | 38 | 17 | 104 | 17 | 0 | 20 | 0 | 50 | 0 | 6 | 0 | 310 | 0 | 350 | 0 | 57 | 148 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 58 | 23 | 0 | 5.51 | 0 | 5252.86 | 930 | 174 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 1021 | 0 | 1141.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.22 | 7 | 0 | 0 | 4.47 | 161 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0.39 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.6 | 13 | 0.05 | 0 | 0 | 110 | 220 | 0 | 353 | 500 | 0 | 5058.69 | 10311.55 | 101.74
08:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 147 | 45 | 160 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 22.5 | 21 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.21 | 84 | 0 | 42 | 650 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 505 | 8 | 0 | 50 | 0 | 320 | 0 | 295 | 41 | 0 | 38 | 17 | 103 | 0 | 0 | 20 | 0 | 48 | 0 | 15 | 0 | 305 | 0 | 330 | 0 | 57 | 146 | 21 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 18 | 59 | 24 | 1 | 22.13 | 0 | 5193.84 | 930 | 181 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 998 | 0 | 1119.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.41 | 28 | 0 | 0 | 15.16 | 160 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 1.91 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1.9 | 53 | 0.17 | 0 | 0 | 110 | 220 | 0 | 303 | 500 | 0 | 5054.27 | 10248.11 | 101.74
09:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 106 | 45 | 45 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 19 | 35 | 16 | 21 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 2.15 | 84 | 0 | 33 | 650 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 503 | 13 | 0 | 15 | 0 | 330 | 0 | 315 | 45 | 0 | 38 | 17 | 102 | 0 | 0 | 20 | 0 | 56 | 0 | 39 | 0 | 305 | 0 | 320 | 0 | 58 | 146 | 21 | 0 | 78 | 30 | 0 | 0 | 99 | 0 | 18 | 59 | 24 | 1 | 35.19 | 0 | 5017.34 | 930 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 946 | 0 | 1026.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.36 | 51 | 0 | 0 | 33.62 | 154 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 3.41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 3.9 | 104 | 0.32 | 0 | 0 | 110 | 180 | 0 | 305 | 490 | 0 | 4994 | 10011.34 | 101.74
10:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 70 | 15 | 45 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 28 | 35 | 16 | 22 | 0 | 63 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 2.14 | 86 | 0 | 33 | 500 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 504 | 17 | 0 | 10 | 0 | 315 | 0 | 330 | 44 | 0 | 38 | 17 | 100 | 0 | 0 | 20 | 0 | 58 | 0 | 58 | 0 | 305 | 0 | 321 | 0 | 58 | 146 | 21 | 0 | 78 | 30 | 0 | 0 | 99 | 0.72 | 18 | 59 | 23 | 2 | 44.02 | 0 | 4849.88 | 931 | 193 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 894 | 0 | 1035.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.39 | 76 | 0 | 0 | 53.59 | 160 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 4.55 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.9 | 138 | 0.56 | 0 | 0 | 110 | 180 | 0 | 304 | 500 | 0 | 5111.24 | 9961.12 | 101.74
11:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 70 | 15 | 90 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 30 | 52 | 0 | 21 | 0 | 65 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 12 | 3.32 | 86 | 0 | 26 | 441 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 580 | 18 | 0 | 10 | 0 | 315 | 0 | 330 | 44 | 0 | 37 | 17 | 98 | 1 | 0 | 20 | 0 | 58 | 0 | 71 | 0 | 310 | 0 | 322 | 0 | 58 | 152 | 21 | 0 | 81 | 30 | 0 | 16 | 99 | 17 | 18 | 59 | 35 | 2 | 42.49 | 0 | 5011.81 | 930 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 905 | 0 | 981.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.82 | 89 | 0 | 0 | 60.51 | 164 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 5.29 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 4.8 | 162 | 0.48 | 0 | 0 | 110 | 220 | 0 | 304 | 505 | 0 | 5214.13 | 10225.94 | 101.74
12:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 0 | 47 | 40 | 30 | 0 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 33 | 70 | 0 | 22 | 0 | 65 | 8 | 16 | 0 | 0 | 13 | 0 | 0 | 0 | 12 | 12 | 3.21 | 86 | 14 | 20 | 370 | 17 | 0 | 2 | 1 | 82 | 215 | 0 | 0 | 0 | 596 | 18 | 0 | 33 | 0 | 310 | 0 | 330 | 43 | 0 | 34 | 16 | 98 | 38 | 0 | 20 | 51 | 64 | 0 | 64 | 11 | 320 | 0 | 391 | 0 | 57 | 157 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 17 | 18 | 59 | 10 | 2 | 48.94 | 0 | 5243.15 | 930 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 1045 | 0 | 964.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.75 | 93 | 0 | 0 | 62.65 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.4 | 0 | 0 | 0 | 33 | 2 | 0 | 0 | 0 | 4 | 146 | 0.58 | 0 | 0 | 110 | 220 | 0 | 374 | 545 | 0 | 5504.26 | 10747.41 | 101.74
13:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 17.5 | 0 | 17 | 45 | 70 | 40 | 0 | 54 | 0 | 250 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 28 | 70 | 0 | 14 | 0 | 65 | 91 | 16 | 5 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 2.9 | 86 | 90 | 0 | 315 | 54 | 0 | 40 | 17 | 89 | 215 | 0 | 0 | 0 | 583 | 13 | 0 | 100 | 0 | 295 | 0 | 330 | 41 | 0 | 36 | 17 | 98 | 141 | 0 | 7 | 114 | 70 | 34 | 65 | 15 | 320 | 0 | 387 | 0 | 57 | 156 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 17 | 18 | 59 | 16 | 2 | 46.18 | 0 | 5783.58 | 931 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 1116 | 0 | 1119.42 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 51.81 | 89 | 0 | 0 | 58.08 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.15 | 0 | 0 | 35 | 30 | 23 | 0 | 0 | 0 | 0 | 142 | 0.54 | 0 | 0 | 110 | 220 | 0 | 407 | 557 | 0 | 5844 | 11627.58 | 101.74
14:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 17.5 | 4 | 17 | 45 | 80 | 48 | 17 | 54 | 0 | 305 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 25 | 52 | 0 | 14 | 0 | 0 | 86 | 16 | 7 | 0 | 10 | 0 | 0 | 0 | 12 | 12 | 2.37 | 84 | 90 | 17 | 315 | 54 | 0 | 1 | 25 | 95 | 194 | 0 | 0 | 0 | 570 | 11 | 0 | 112 | 0 | 295 | 0 | 300 | 41 | 0 | 37 | 17 | 97 | 160 | 0 | 20 | 108 | 76 | 52.2 | 52 | 15 | 300 | 0 | 320 | 0 | 57 | 143 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 17 | 18 | 58 | 16 | 2 | 38.23 | 0 | 5602.3 | 930 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 1067 | 0 | 1182.47 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 41.81 | 61 | 0 | 0 | 49.85 | 201 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 4.15 | 0 | 0 | 35 | 23 | 33 | 0 | 0 | 0 | 4.3 | 122 | 0.39 | 0 | 0 | 110 | 180 | 0 | 303 | 500 | 0 | 5560.97 | 11163.27 | 101.74
15:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 17.5 | 8 | 17 | 45 | 31 | 45 | 19 | 54 | 0 | 350 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 18 | 52 | 0 | 14 | 0 | 0 | 89 | 16 | 11 | 0 | 7 | 0 | 0 | 0 | 12 | 12 | 1.35 | 84 | 96 | 15 | 315 | 17 | 0 | 31 | 25 | 98 | 181 | 0 | 0 | 0 | 570 | 6 | 0 | 117 | 0 | 300 | 0 | 300 | 40 | 0 | 37 | 17 | 98 | 163 | 0 | 20 | 105 | 74 | 52.2 | 35 | 15 | 310 | 0 | 362 | 0 | 57 | 151 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 17 | 18 | 58 | 33 | 1 | 27.05 | 0 | 5610.1 | 930 | 236 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1000 | 0 | 1180.16 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 26.01 | 50 | 0 | 0 | 34.83 | 171 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 3.09 | 0 | 0 | 35 | 13 | 20 | 0 | 0 | 0 | 3.1 | 90 | 0.24 | 0 | 0 | 110 | 180 | 0 | 301 | 498 | 0 | 5343.43 | 10953.53 | 101.74
16:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17.5 | 17 | 17 | 45 | 31 | 15 | 35 | 54 | 0 | 350 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 8 | 52 | 0 | 14 | 0 | 0 | 87 | 16 | 12 | 0 | 5 | 0 | 3 | 0 | 12 | 12 | 0.62 | 84 | 95 | 17 | 315 | 17 | 0 | 32 | 25 | 97 | 181 | 0 | 0 | 0 | 575 | 3 | 0 | 113 | 0 | 320 | 0 | 300 | 40 | 0 | 37 | 23 | 99 | 161 | 0 | 20 | 50 | 70 | 52.2 | 13 | 15 | 310 | 0 | 341 | 0 | 57 | 155 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 17 | 22 | 58 | 47 | 1 | 11.36 | 0 | 5521.68 | 930 | 246 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 920 | 0 | 1156.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.01 | 22 | 0 | 0 | 10.41 | 168 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 1.13 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.3 | 30 | 0.11 | 0 | 0 | 110 | 180 | 0 | 303 | 491 | 0 | 5009.38 | 10531.06 | 101.74
17:00 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 17 | 30 | 45 | 31 | 15 | 35 | 54 | 0 | 350 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 1 | 52 | 0 | 14 | 0 | 0 | 89 | 16 | 12 | 0 | 8 | 3 | 54 | 0 | 24 | 12 | 0.03 | 84 | 94 | 20 | 315 | 17 | 0 | 32 | 25 | 96 | 181 | 0 | 0 | 0 | 565 | 0 | 0 | 113 | 0 | 310 | 0 | 283 | 40 | 0 | 37 | 17 | 99 | 172 | 0 | 17 | 60 | 64 | 52.2 | 1 | 19 | 305 | 0 | 316 | 0 | 57 | 155 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 22 | 58 | 70 | 0 | 0.76 | 0 | 5508.49 | 930 | 255 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.85 | 843 | 0 | 1151.44 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 10 | 0 | 1.21 | 2 | 15 | 0 | 0.85 | 169 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0 | 0 | 110 | 180 | 0 | 303 | 491 | 17 | 4872.6 | 10381.09 | 101.74
18:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17.5 | 17 | 34 | 122 | 31 | 15 | 35 | 54 | 0 | 330 | 0 | 0 | 0 | 17 | 328 | 0 | 0 | 0 | 142 | 0 | 14 | 0 | 0 | 89 | 16 | 24 | 0 | 20 | 65 | 62 | 0 | 24 | 12 | 0 | 83 | 100 | 22 | 315 | 126 | 0 | 32 | 25 | 95 | 217 | 0 | 0 | 0 | 580 | 0 | 0 | 118 | 0 | 330 | 0 | 330 | 42 | 0 | 38 | 30 | 99 | 180 | 0 | 20 | 97 | 76 | 52.2 | 0 | 21 | 310 | 0 | 320 | 0 | 57 | 152 | 24 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 21 | 58 | 102 | 0 | 0 | 0 | 6212.7 | 929 | 265 | 0 | 23 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 1226.57 | 0 | 41 | 0 | 20 | 10 | 0 | 98 | 21 | 43 | 0 | 0 | 25 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 110 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 434 | 538 | 17 | 5839.57 | 12052.27 | 101.74
19:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 17.5 | 17 | 34 | 123 | 48 | 15 | 35 | 54 | 0 | 370 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 142 | 0 | 21 | 0 | 0 | 85 | 16 | 31 | 0 | 23 | 65 | 62 | 0 | 24 | 12 | 0 | 86 | 104 | 22 | 315 | 126 | 0 | 33 | 25 | 100 | 219 | 0 | 0 | 0 | 577 | 0 | 0 | 130 | 0 | 285 | 0 | 330 | 42 | 0 | 38 | 34 | 100 | 173 | 0 | 20 | 98 | 68 | 52.2 | 0 | 22 | 305 | 0 | 347 | 0 | 57 | 148 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 24 | 58 | 104 | 0 | 0 | 0 | 6242.7 | 929 | 273 | 0 | 29 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 1238.16 | 0 | 40 | 0 | 35 | 50 | 0 | 98 | 32 | 52.2 | 0 | 0 | 28 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 510 | 17 | 6071.36 | 12314.06 | 101.74
19:30 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17.5 | 17 | 34 | 123 | 31 | 15 | 35 | 54 | 0 | 400 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 142 | 0 | 21 | 0 | 0 | 85 | 16 | 31 | 0 | 13 | 65 | 62 | 0 | 24 | 12 | 0 | 86 | 104 | 22 | 315 | 126 | 0 | 33 | 25 | 97 | 219 | 0 | 0 | 0 | 575 | 0 | 0 | 124 | 0 | 285 | 0 | 330 | 42 | 0 | 38 | 34 | 101 | 176 | 0 | 20 | 98 | 66 | 52.2 | 0 | 22 | 310 | 0 | 360 | 0 | 57 | 145 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 26 | 58 | 104 | 0 | 0 | 0 | 6268.7 | 930 | 285 | 0 | 25 | 65 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 1213.67 | 0 | 40 | 0 | 35 | 50 | 0 | 98 | 32 | 52.2 | 0 | 0 | 28 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 500 | 17 | 6060.87 | 12329.57
20:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17.5 | 17 | 34 | 123 | 31 | 15 | 35 | 54 | 0 | 400 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 142 | 0 | 21 | 0 | 0 | 85 | 16 | 31 | 0 | 5 | 65 | 60 | 0 | 24 | 24 | 0 | 86 | 103 | 24 | 315 | 126 | 0 | 33 | 25 | 93 | 220 | 0 | 0 | 0 | 580 | 0 | 0 | 125 | 0 | 285 | 0 | 330 | 42 | 0 | 38 | 36 | 100 | 177 | 0 | 20 | 97 | 64 | 52.2 | 0 | 22 | 310 | 0 | 370 | 0 | 57 | 143 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 58 | 104 | 0 | 0 | 0 | 6274.7 | 928 | 287 | 0 | 25 | 55 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 1225.13 | 0 | 40 | 0 | 35 | 50 | 0 | 98 | 32 | 52.2 | 0 | 0 | 28 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 514 | 17 | 6148.33 | 12423.03 | 101.74
21:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17.5 | 17 | 34 | 123 | 31 | 15 | 35 | 35 | 0 | 400 | 0 | 0 | 0 | 17 | 329 | 0 | 0 | 0 | 142 | 0 | 21 | 0 | 0 | 89 | 16 | 26 | 0 | 0 | 65 | 62 | 0 | 24 | 24 | 0 | 86 | 104 | 23 | 315 | 54 | 0 | 33 | 25 | 101 | 221 | 0 | 0 | 0 | 585 | 0 | 0 | 127 | 0 | 280 | 0 | 330 | 42 | 0 | 38 | 36 | 102 | 180 | 0 | 20 | 98 | 72 | 52.2 | 0 | 22 | 305 | 0 | 387 | 0 | 57 | 149 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 26 | 58 | 104 | 0 | 0 | 0 | 6245.7 | 915 | 300 | 0 | 25 | 48 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 1222.44 | 0 | 40 | 0 | 35 | 50 | 0 | 98 | 32 | 52.2 | 0 | 0 | 28 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 600 | 17 | 6220.64 | 12466.34 | 101.74
22:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17.5 | 17 | 34 | 45 | 31 | 15 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 17 | 329 | 0 | 0 | 0 | 142 | 0 | 21 | 0 | 0 | 94 | 16 | 31 | 0 | 0 | 65 | 62 | 0 | 24 | 24 | 0 | 86 | 101 | 23 | 315 | 54 | 0 | 33 | 25 | 100 | 221 | 0 | 0 | 0 | 582 | 0 | 0 | 130 | 0 | 295 | 0 | 330 | 42 | 0 | 38 | 26 | 102 | 174 | 0 | 20 | 97 | 68 | 52.2 | 0 | 22 | 315 | 0 | 391 | 20 | 57 | 159 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 28 | 58 | 97 | 0 | 0 | 0 | 6139.7 | 915 | 317 | 0 | 25 | 44 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 1226.97 | 0 | 40 | 0 | 35 | 35 | 0 | 98 | 32 | 52.2 | 0 | 0 | 28 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 605 | 17 | 6243.17 | 12382.87 | 101.74
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 34 | 45 | 31 | 15 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 35 | 0 | 21 | 0 | 0 | 102 | 16 | 31 | 0 | 0 | 65 | 60 | 0 | 24 | 12 | 0 | 86 | 101 | 23 | 315 | 17 | 0 | 33 | 25 | 103 | 222 | 0 | 0 | 0 | 575 | 0 | 0 | 135 | 0 | 295 | 0 | 330 | 42 | 0 | 38 | 17 | 103 | 182 | 0 | 20 | 98 | 70 | 52.2 | 0 | 22 | 310 | 0 | 366 | 20 | 57 | 154 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 24 | 58 | 97 | 0 | 0 | 0 | 5910.2 | 915 | 325 | 0 | 25 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 1234.27 | 0 | 40 | 0 | 35 | 35 | 0 | 98 | 30 | 52.2 | 0 | 0 | 28 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 504 | 600 | 17 | 6206.47 | 12116.67 | 101.74
Total KWH | 0 | 1279680 | 411840 | 0 | 0 | 0 | 0 | 0 | 8650800 | 0 | 0 | 259560 | 149760 | 1741248 | 1233120 | 2571065 | 449377 | 265028 | 790560 | 0 | 6646000 | 0 | 0 | 0 | 140294 | 7839031 | 0 | 0 | 170289 | 1412400 | 208200 | 474840 | 0 | 887272.73 | 1382509 | 238364 | 296640 | 0 | 110880 | 481378 | 599616 | 62388 | 377280 | 327360 | 20160 | 2052040 | 1617530 | 698880 | 11236363.64 | 689164 | 0 | 480960 | 341251.3 | 1730436 | 5066440 | 0 | 0 | 0 | 13521817 | 109215 | 0 | 2259854 | 0 | 7614500 | 0 | 7826000 | 966240 | 0 | 903186 | 570240 | 2409413 | 3219360 | 0 | 437740 | 1311000 | 1482240 | 728645 | 418809 | 312928 | 7520500 | 0 | 8774000 | 5000 | 1344240 | 3598036 | 541200 | 0 | 1943040 | 716448 | 0 | 168000 | 2381000 | 270720 | 492000 | 1375200 | 1070400 | 12650 | 318810 | 0 | 138012435.67 | 22469090 | 5516928 | 0 | 165600 | 276608 | 912000 | 0 | 0 | 0 | 0 | 0 | 456480 | 25025460 | 0 | 27992727 | 0 | 316521 | 0 | 242304 | 548352 | 0 | 649328 | 188940 | 414096 | 325110 | 593560 | 273665 | 0 | 384000 | 4144182 | 0 | 0 | 0 | 0 | 0 | 9144800 | 0 | 33360 | 0 | 0 | 1251028 | 170436 | 659836 | 0 | 0 | 0 | 31998.36 | 990720 | 3139 | 141216 | 0 | 2630000 | 5241320 | 0 | 9904464 | 13154909.09 | 194400 | 134446577.45 | 272459013.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10747.41 | MW | 12:00 Hr. | Energy Generated |  |  | 272.459 |  | MKWHr.
| Day Peak Demand |  |  | 10747.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.959 |  | MKWHr.
| Evening Peak Generation |  |  | 12466.34 | MW | 21:00 Hr. | Energy Demand |  |  | 273.418 |  | MKWHr.
| Evening Peak Demand |  |  | 12480.06 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.5 |  | °C
| Minimum Generation of the Day |  |  | 9961.12 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 809.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 12628.93 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.8308 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.7061 | 0 | 10.7039 | 0 | 0 | 0.17029 | 0 | 0 | 35.5804 | Gas | 105.3676 | Gas | 375481261.0541
| Chattogram Zone |  |  | 5.7653 | 24.7582 | 8.6249 | 0 | 2.052 | 0.12937 | 0 | 0.11088 | 41.4407 | Coal | 72.843 | Coal | 473198534.8026
| Cumilla Zone |  |  | 20.1571 | 0 | 8.402 | 0 | 0 | 0.41881 | 1.4822 | 0 | 30.4602 | HFO | 35.1906 | HFO | 633583548.847
| Mymensingh Zone |  |  | 1.0704 | 0 | 2.1379 | 0 | 0 | 0.33146 | 0 | 0 | 3.5398 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9915 | Hydro | 2.052 | Hydro | 205204
| Khulna Zone |  |  | 5.5169 | 25.0255 | 0.44221 | 0 | 0 | 0.45648 | 23.3811 | 0 | 54.8222 | Solar | 4.0387 | Solar | 64466844.5676
| Barishal Zone |  |  | 7.8713 | 23.0594 | 0.33562 | 0 | 0 | 0.003139 | 0 | 0 | 31.2694 | Import | 52.8561 | Import | 312535375.42
| Rajshahi Zone |  |  | 13.289 | 0 | 2.6332 | 0 | 0 | 1.336 | 27.9927 | 0 | 45.2509 | Wind | 0.11088 | Wind | 1631044.8
| Rangpur Zone |  |  | 0 | 0 | 1.9109 | 0 | 0 | 1.1932 | 0 | 0 | 3.104
| Total |  |  | 105.3676 | 72.843 | 35.1906 | 0 | 2.052 | 4.0387 | 52.8561 | 0.11088 | 272.459
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 375481261.0541 |  | Hydro | 205204
|  |  |  | Coal | 473198534.8026 |  | Solar | 64466844.5676
|  |  |  | HFO | 633583548.847 |  | Import | 312535375.42
|  |  |  | HSD | 0 |  | Wind | 1631044.8
[5 empty] | Total: | 186,11,01,813 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.4691 | Peak Hr Flow | 915.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50466527.35 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.9927 | Peak Hr Flow | 1222.44 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2563 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4822 | Peak Hr Flow | 72.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2795 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.9441 | Peak Hr Flow | 2209.44 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4499
|  |  |  | Chattogram |  | 0 |  | 1305
|  |  |  | Cumilla |  | 0 |  | 1243
|  |  |  | Mymensingh |  | 0 |  | 960
|  |  |  | Sylhet |  | 0 |  | 545
|  |  |  | Khulna |  | 0 |  | 1378
|  |  |  | Barishal |  | 0 |  | 414
|  |  |  | Rajshahi |  | 0 |  | 1027
|  |  |  | Rangpur |  | 0 |  | 620
|  |  |  | Total |  | 0 |  | 11991
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:24 | 16:16 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end.
| 08:32 | 16:05 | Ashuganj 230/132/33kV S/S 132kv Busbar-1 Scheduled S/D Due to 132 KV busbar-1 shutdown
| 08:45 | 12:54 | Mymensingh RPCL-Tangail 132kV Ckt-1 Project Work S/D from Muktagacha 132/33kV end.
|  | 09:19 | Saidpur 132/33kV S/S BUS B is restored.
|  | 09:25 | Saidpur 132/33kV S/S TR-5 (434T) HT is restored.
|  | 09:26 | Saidpur 132/33kV S/S TR-5 (434T) LT is restored.
|  | 09:31 | Hathazari 230/132/33kV S/S T-02 LT is restored.
|  | 09:31 | Hathazari 230/132/33kV S/S T-02 HT is restored.
| 10:28 | 15:32 | BIPTC S/S 10CF26 Tripped showing lockout Relay 186, 286 relays Due to Two dead birds were
notice.
| 11:14 | 11:46 | Rampur 230/132/33 S/S Halishahar-1 Tripped showing REL670 relays.
| 12:00 |  | Day peak Generation: 10742 MW.
| 12:15 |  | Chandina 132/33kV S/S TR-3 HT Tripped showing 1)Lockout relay 1(k861) 2)lockout relay | [7 empty] | 5.0MW load
|  |  | 2(K862) 3)Bay control unit 1 4)Transformer main-1 relay 5)Transformer main-2 relay | [7 empty] | interrup.
relays Due to From SAS: *Mechanical Trip *Protection Trip to HVS K861 *Protection Trip
to HVS K862 *TRAFO OLTC BUCHOLZ Trip *Lockout-1 operate *Lockout-2 operate *Initiate
BFP *TR3 Bucholz Trip From CRP: *Mechanical Trip *T86 Operated
| 12:15 |  | Chandina 132/33kV S/S TR-3 LT Tripped showing 1)Lockout Relay -1 2)Lockout Relay | [7 empty] | 5.0MW load
|  |  | -2 3)Bay Control Unit-1 relays Due to From SAS: 1)Protection Trip to LVS | [7 empty] | interrup.
K86L1 2)Protection Trip to LVS K86L2 3)Lockout Relay trip From CRP: T86
operate Mechanical Trip
|  | 12:19 | Chapai 132/33kV S/S Main Bus is restored.
|  | 12:19 | Chapainawabganj-Rahanpur 132kV Ckt-1 is restored.
|  | 13:01 | Nawabganj 132/33kV S/S TR-2 HT is restored.
|  | 13:05 | Nawabganj 132/33kV S/S TR-2 LT is restored.
| 13:26 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
| 13:36 |  | Unique Meghnaghat Power Limited (UMPL) GT Shutdown with remarks:- None
| 13:37 |  | Unique Meghnaghat Power Limited (UMPL) ST Shutdown with remarks:- None
| 14:10 | 14:42 | Amnura 132/33kV S/S T-2 (416T) HT Forced S/D Due to 132kV Bus-2 হইতে Bus-1এ স্থানান্তর. | [7 empty] | 5.0MW load
interrup.
| 14:10 | 14:40 | Amnura 132/33kV S/S T-1 (406T) HT Forced S/D Due to 132kV Bus-2 হইতে Bus-1এ স্থানান্তর | [7 empty] | 5.0MW load
interrup.
| 14:12 | 15:42 | Amnura 132/33kV S/S T-3 (426T) HT Forced S/D Due to 132kV Bus-2 হইতে Bus-1এ স্থানান্তর. | [7 empty] | 3.0MW load
interrup.
|  | 14:38 | Amnura-Chapainawabganj-132kV Ckt-1 is restored.
| 14:39 | 17:07 | Muktagacha 132/33kV S/S RPCL-2 Scheduled S/D Due to Work by CCCE
| 14:47 | 17:23 | Nawabganj 132/33kV S/S TR-1 LT Scheduled S/D Due to Due to annual maintenance.
| 14:48 | 17:21 | Nawabganj 132/33kV S/S TR-1 HT Scheduled S/D Due to Due to annual maintenance
| 14:49 | 15:32 | BIPTC S/S 10CF26 Scheduled S/D Due to Corrective Maintenance
|  | 15:34 | C.nawabganj-Rajshahi 132 kV Ckt-1 is restored.
| 15:52 | 18:10 | Borhanuddin 230/33kV S/S Tr-Load HT Forced S/D Due to 33 kv Bass bar riser red hot for | [7 empty] | 62.0MW load
|  |  | maintenance & replacement . | [7 empty] | interrup.
|  | 15:59 | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 is restored.
|  | 16:04 | Chapai 132/33kV S/S Chapai Rahanpur ckt 2 is restored.
|  | 16:24 | Shyampur 230/132kV S/S Auto TR-1 HT is restored.
| 16:32 | 20:56 | Barishal 230/132kV S/S ATR-2 HT Forced S/D Due to OLTC PRD Trip
| 16:32 | 20:53 | Barishal 230/132kV S/S ATR-2 LT Forced S/D Due to OLTC PRD trip
|  | 16:32 | Shyampur 230/132kV S/S Auto TR-1 LT is restored.
|  | 16:49 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 is restored.
|  | 16:49 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 is restored.
| 17:00 |  | Chandina 132/33kV S/S TR-3 HT Project Work S/D Due to To solve the TR-3 mechanical fault
.
| 17:00 |  | Chandina 132/33kV S/S TR-3 LT Project Work S/D Due to To solve the TR-3 mechanical fault
.
| 18:53 |  | Aminbazar- Kaliakoir 400kV circuit was switched ON.
|  | 19:27 | Ashuganj 230/132/33kV S/S TR-OAT-11 LT is restored.
| 21:00 |  | Evening Peak Generation: 12465 MW.
| 06:00 |  | Minimum Generation is 9646 MW
| 06:02 |  | Baghabari 230/132kV S/S T-2 Bank HT Tripped showing General trip Mechanical protection
trip Mechanical protection alarm relays Due to Bucholz OL Temp Trip
| 07:04 |  | Bakulia 132/33kV S/S T-1 (402T) HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 5.0MW load
interrup.
| 07:06 |  | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to Shutdown for | [7 empty] | 8.0MW load
|  |  | annual maintenance. and from Sylhet 132/33kV end Due to Annual Maintenance | [7 empty] | interrup. Chhatak
132/33kV end and
25.0MW load
interrup. Sylhet
132/33kV end
| 07:20 |  | Full interruption (around 60 MW) is occurring under Ashuganj 132/33kV grid substation
from 07:20 hrs due to the tripping of T3 and T4 transformers caused by blast of CT in
Lalpur 33kV feeder.
| 07:46 |  | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Meghnaghat 230/132kV end Due to For
annual maintenance work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 361 | 8650800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 6646000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 449377 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 329 | 7839031 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 123 | 1233120 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265028 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 140294 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 208200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 474840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 411840 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 31 | 2571065 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 1741248 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1279680 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 790560 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 170289 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 149760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 887272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1412400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1663.5 | 35580364.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 341251.3 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109215 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 480960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2052040 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5066440 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 101 | 1730436 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 62 | 599616 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 481378 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 377280 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 698880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 26 | 296640 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 238364 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 62388 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 104 | 1617530 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 327360 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 1382509 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 54 | 689164 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 585 | 13521817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 110880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 315 | 11236363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 1853 | 41440671.94
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7826000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 280 | 7614500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 903186 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 42 | 966240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 127 | 2259854 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 312928 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2409413 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 3219360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 72 | 1482240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 728645 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 437740 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1311000 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 36 | 570240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 418809 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1399.2 | 30460155
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 104 | 1070400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1375200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 26 | 492000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 318810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 270720 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 188 | 3539780
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 5000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1344240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3598036 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716448 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1943040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2381000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 168000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 541200 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7520500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 8774000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 1142 | 26991464
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 22469090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 165600 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 48 | 276608 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 300 | 5516928 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 456480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1110 | 25025460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2436 | 54822166
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 502 | 9904464 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 141216 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2630000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 600 | 13154909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5241320 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 194400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3139 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1465 | 31269448.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 325110 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 316521 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 188940 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 193 | 4144182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 384 | 9144800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 273665 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 414096 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 649328 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 548352 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 242304 | Engine Problem
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1222.44 | 27992727 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 384000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 593560 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2134.64 | 45250945
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 659836 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31998.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1251028 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 170436 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 990720 | -
Rangpur Area Total |  |  |  |  | 950 | 185 | 3104018.36
Eastern Grid Total |  |  |  |  | 17383.855 | 6245.7 | 138012435.67
Western Grid Total |  |  |  |  | 10821.56 | 6220.64 | 134446577.45
National Grid Total |  |  |  |  | 28205.415 | 12466.34 | 272459013.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-11-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8552.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3439.2 | MW
i) Dhaka area |  |  | 4499.21 |  | MW | i) Khulna area |  |  |  | 1378.5 | MW
ii) Chattogram area |  |  | 1305 |  | MW | ii) Barishal area |  |  |  | 413.7 | MW
iii) Cumilla area |  |  | 1243 |  | MW | iii) Rajshahi area |  |  |  | 1027 | MW
iv) Mymensingh area |  |  | 960 |  | MW | iv) Rangpur area |  |  |  | 620 | MW
v) Sylhet area |  |  | 545 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11991.41 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 72 | 18:00 | 133 | Niamatpur | 46 | 18:00
2 | AKSML | 167 | 09:00 | 68 | Ishurdi | 60 | 13:00 | 134 | Noapara | 34 | 18:00
3 | Aftabnagar | 34 | 18:00 | 69 | Jaldhaka | 67 | 18:00 | 135 | PHP | 9 | 19:00
4 | Agargaon | 102 | 13:00 | 70 | Jamalpur | 93 | 20:00 | 136 | Pabna | 72 | 18:00
5 | Agrabad | 82 | 21:00 | 71 | Jashore | 112 | 18:00 | 137 | Palashbari | 93 | 18:00
6 | Amnura | 19 | 18:00 | 72 | Jhenaidah | 114 | 18:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 79 | 00:00 | 73 | Joydebpur | 116 | 00:00 | 139 | Patiya | 11 | 18:00
8 | BSRM | 203 | 19:30 | 74 | Joypurhat | 44 | 18:00 | 140 | Patuakhali | 58 | 22:00
9 | Bagerhat | 68 | 18:00 | 75 | Juldah | 16 | 00:00 | 141 | Payra | 30 | 22:00
10 | Bajitpur | 87 | 20:00 | 76 | KSRM | 30 | 18:30 | 142 | Postogola | 58 | 00:00
11 | Bakulia | 70 | 19:00 | 77 | Kabirpur | 223 | 20:00 | 143 | Purbachal | 14 | 18:00
12 | Banani | 34.6 | 19:30 | 78 | Kachua | 79 | 19:00 | 144 | Purbasadipur | 94 | 18:00
13 | Bangabhaban | 6 | 19:00 | 79 | Kallyanpur | 93 | 12:00 | 145 | Rahanpur | 22 | 18:00
14 | Barapukuria | 45 | 17:00 | 80 | Kalurghat | 38 | 00:00 | 146 | Rahim | 44 | 00:00
15 | Barguna | 18 | 18:00 | 81 | Kamrangirchar | 68 | 00:00 | 147 | Rajbari | 67 | 18:00
16 | Barishal | 99 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 104 | 00:00
17 | Barishal-230 | 86 | 18:30 | 83 | Kasba | 32 | 18:00 | 149 | Rajshahi | 94 | 00:00
18 | Baroaulia | 59 | 21:00 | 84 | Kazla | 90 | 00:00 | 150 | Rajshahi-230 | 61 | 13:00
19 | Baroirhat | 55 | 18:30 | 85 | Keranigonj | 76 | 00:00 | 151 | Ramganj | 90 | 20:00
20 | Bashundhara | 182 | 13:00 | 86 | Khagrachori | 30 | 18:00 | 152 | Rampur | 38 | 23:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 66 | 12:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 68 | 20:00 | 88 | Khulshi | 167 | 18:00 | 154 | Rangpur | 112 | 18:00
23 | Benapole | 50 | 18:00 | 89 | Kishoreganj | 114 | 21:00 | 155 | Ruppur | 6.2 | 11:00
24 | Bhaluka | 122 | 13:00 | 90 | Kodda | 269 | 21:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 46 | 21:00 | 91 | Kulaura | 40 | 21:00 | 157 | Saidpur | 69 | 11:00
26 | Bhangura | 30 | 18:00 | 92 | Kurigram | 52 | 18:00 | 158 | Satkhira | 104 | 18:30
27 | Bheramara(GK) | 50 | 18:00 | 93 | Kushtia | 114 | 01:00 | 159 | Satmasjid | 87 | 13:00
28 | Bhulta | 213 | 04:00 | 94 | Laksam | 29 | 22:00 | 160 | Savar | 180 | 00:00
29 | Bog-Sherpur | 50 | 00:00 | 95 | Lakshmipur | 26 | 18:00 | 161 | SevenRings | 15.97 | 19:00
30 | Bogura | 126 | 18:30 | 96 | Lalbag | 56 | 00:00 | 162 | ShahCement | 26 | 07:00
31 | Borhanuddin | 93 | 19:00 | 97 | Lalmonirhat | 47 | 18:00 | 163 | Shahjadpur | 65 | 18:00
32 | Brahmanbaria | 124 | 20:00 | 98 | MI_Cement | 14.8 | 16:00 | 164 | Shahjibazar | 108 | 00:00
33 | Cantonment | 136 | 12:00 | 99 | Madanganj | 26 | 19:30 | 165 | Shahmirpur | 40 | 18:30
34 | Chandina | 12.92 | 05:00 | 100 | Madaripur | 87 | 20:00 | 166 | Shariatpur | 74 | 21:00
35 | Chandpur | 70 | 21:00 | 101 | Madartek | 80 | 00:00 | 167 | Sherpur | 108 | 18:00
36 | Chandraghona | 33 | 18:00 | 102 | Madunaghat | 46 | 19:00 | 168 | Shikalbaha | 27 | 14:00
37 | Chapai | 49 | 18:30 | 103 | Magura | 53 | 18:00 | 169 | Shitalakhya | 55.6 | 00:00
38 | Charsaidpur | 33 | 06:00 | 104 | Mahasthangarh | 58 | 00:00 | 170 | Sholosohor | 40 | 18:00
39 | Chauddagram | 60 | 18:30 | 105 | Maijdee | 32 | 18:00 | 171 | Shyampur | 116 | 00:00
40 | Chhatak | 34 | 21:00 | 106 | Manikganj | 113 | 18:30 | 172 | Siddhirganj | 96 | 00:00
41 | Chowmuhani | 150 | 20:00 | 107 | Maniknagar | 60 | 13:00 | 173 | Sirajganj | 80 | 18:00
42 | Chuadanga | 88 | 18:00 | 108 | Matarbari | 51 | 18:30 | 174 | Sonargaon | 128 | 00:00
43 | Coxsbazar | 126 | 19:30 | 109 | Matuail | 68 | 00:00 | 175 | Sreemongol | 69 | 21:00
44 | Cumilla(N) | 134 | 18:30 | 110 | Metrorail_Motijheel | 19 | 17:00 | 176 | Sreepur | 92 | 00:00
45 | Cumilla(S) | 123 | 00:00 | 111 | Metrorail_Uttara | 4 | 16:00 | 177 | Srinagar | 42.75 | 22:00
46 | Daganbhuiyan | 0 | 01:00 | 112 | Millgate | 100 | 00:00 | 178 | Sunamganj | 60 | 20:00
47 | Daudkandi | 135 | 18:30 | 113 | Mirpur | 109 | 12:00 | 179 | Sylhet | 47 | 20:00
48 | DhakaUniversity | 40 | 12:00 | 114 | Mirsorai | 8 | 17:00 | 180 | Sylhet-132 | 106 | 20:00
49 | Dhamrai | 108 | 00:00 | 115 | Mirzapur | 43 | 18:00 | 181 | TK | 22 | 18:30
50 | Dhanmondi | 101.6 | 19:30 | 116 | Mithapukur | 48 | 18:00 | 182 | Tangail | 148 | 19:00
51 | Dohazari | 98 | 20:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 13 | 00:00
52 | Faridpur | 136 | 00:00 | 118 | Mogbazar | 72.2 | 13:00 | 184 | Thakurgaon | 77 | 18:00
53 | Fatullah | 96 | 00:00 | 119 | Mongla | 40 | 00:00 | 185 | Tongi | 88 | 00:00
54 | Fenchuganj | 34 | 21:00 | 120 | Motijheel | 35 | 13:00 | 186 | Ullahpara | 32 | 18:00
55 | Feni | 99 | 18:00 | 121 | Muktagacha | 30 | 18:00 | 187 | Ullon | 59 | 13:00
56 | GPH | 8 | 17:00 | 122 | Munshiganj | 99 | 00:00 | 188 | Uttara | 75 | 18:30
57 | Ghatail | 70 | 18:00 | 123 | Muradnagar | 36 | 19:00 | 189 | UttaraNew | 29 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 167 | 22:00 | 190 | Zigatola | 66 | 13:00
59 | Ghorashal-230 | 100 | 00:00 | 125 | Naogaon | 88 | 18:00
60 | Goalpara | 33 | 13:00 | 126 | Narail | 50 | 18:00
61 | Gollamari | 78 | 00:00 | 127 | Narinda | 48 | 13:00
62 | Gopalganj | 91 | 18:30 | 128 | Narshingdi | 163 | 00:00
63 | Gulshan | 84 | 12:00 | 129 | Natore | 111 | 00:00
64 | Halishahar | 43 | 04:00 | 130 | Nawabganj | 40.2 | 22:00
65 | HaripurSBU | 137 | 00:00 | 131 | Netrakona | 123 | 20:00
66 | Hasnabad | 80 | 00:00 | 132 | New | 46 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12628.93 | 165 |  | 12801.36
1:00 | 12325.63 | 26 |  | 12352.63
2:00 | 11959.09 | 21 |  | 11981.09
3:00 | 11348.88 | 21 |  | 11370.88
4:00 | 10952.35 | 0 |  | 10952.35
5:00 | 10749.97 | 0 |  | 10749.97
6:00 | 10391.31 | 0 |  | 10391.31
7:00 | 10311.55 | 0 |  | 10311.55
8:00 | 10248.11 | 0 |  | 10248.11
9:00 | 10011.34 | 0 |  | 10011.34
10:00 | 9961.12 | 0 |  | 9961.12
11:00 | 10225.94 | 0 |  | 10225.94
12:00 | 10747.41 | 0 |  | 10747.41
13:00 | 11627.58 | 73 |  | 11703.58
14:00 | 11163.27 | 77 |  | 11243.27
15:00 | 10953.53 | 32 |  | 10986.53
16:00 | 10531.06 | 0 |  | 10531.06
17:00 | 10381.09 | 0 |  | 10381.09
18:00 | 12052.27 | 286 |  | 12351.27
19:00 | 12314.06 | 159 |  | 12480.06
19:30 | 12329.57 | 117 |  | 12451.57
20:00 | 12423.03 | 0 |  | 12423.03
21:00 | 12466.34 | 0 |  | 12466.34
22:00 | 12382.87 | 47 |  | 12431.99
23:00 | 12116.67 | 52 |  | 12171.01
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6639.9 | 5989.03 | 12628.93 | DAILY GENERATION CURVE
00:30 | 6556.7 | 5920.58 | 12477.28
01:00 | 6473.5 | 5852.13 | 12325.63 | 07-11-2025
01:30 | 6384.6 | 5757.76 | 12142.36
02:00 | 6295.7 | 5663.39 | 11959.09
02:30 | 6099.1 | 5554.885 | 11653.985
03:00 | 5902.5 | 5446.38 | 11348.88
03:30 | 5706.5 | 5444.115 | 11150.615
04:00 | 5510.5 | 5441.85 | 10952.35
04:30 | 5471 | 5380.16 | 10851.16
05:00 | 5431.5 | 5318.47 | 10749.97
05:30 | 5381 | 5189.64 | 10570.64
06:00 | 5330.5 | 5060.81 | 10391.31
06:30 | 5291.68 | 5059.75 | 10351.43
07:00 | 5252.86 | 5058.69 | 10311.55
07:30 | 5223.35 | 5056.48 | 10279.83
08:00 | 5193.84 | 5054.27 | 10248.11
08:30 | 5105.59 | 5024.135 | 10129.725
09:00 | 5017.34 | 4994 | 10011.34
09:30 | 4933.61 | 5052.62 | 9986.23
10:00 | 4849.88 | 5111.24 | 9961.12
10:30 | 4930.845 | 5162.685 | 10093.53
11:00 | 5011.81 | 5214.13 | 10225.94
11:30 | 5127.48 | 5359.195 | 10486.675
12:00 | 5243.15 | 5504.26 | 10747.41
12:30 | 5513.365 | 5674.13 | 11187.495
13:00 | 5783.58 | 5844 | 11627.58
13:30 | 5692.94 | 5702.485 | 11395.425
14:00 | 5602.3 | 5560.97 | 11163.27
14:30 | 5606.2 | 5452.2 | 11058.4
15:00 | 5610.1 | 5343.43 | 10953.53
15:30 | 5565.89 | 5176.405 | 10742.295
16:00 | 5521.68 | 5009.38 | 10531.06
16:30 | 5515.085 | 4940.99 | 10456.075
17:00 | 5508.49 | 4872.6 | 10381.09
17:30 | 5860.595 | 5356.085 | 11216.68
18:00 | 6212.7 | 5839.57 | 12052.27
18:30 | 6227.7 | 5955.465 | 12183.165
19:00 | 6242.7 | 6071.36 | 12314.06
19:30 | 6268.7 | 6060.87 | 12329.57
20:00 | 6274.7 | 6148.33 | 12423.03
20:30 | 6260.2 | 6184.485 | 12444.685 |  | Executive Engineer
21:00 | 6245.7 | 6220.64 | 12466.34 |  | Network Operation Division
21:30 | 6192.7 | 6231.905 | 12424.605
22:00 | 6139.7 | 6243.17 | 12382.87
22:30 | 6024.95 | 6224.82 | 12249.77
23:00 | 5910.2 | 6206.47 | 12116.67

## En-Curve
QF-LDC-12
Date | 07-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3165 | 1233.2 | 930 | 38 | 68 | 1217.83 | 84 | 3473 | 0 | 483 | 1936.9 | 0 | 0 | 0 | 165 | DAILY ENERGY CURVE
00:30 | 3154 | 1228 | 930 | 38 | 65 | 1215.88 | 84 | 3445 | 0 | 428 | 1889.4 | 0 | 0 | 0 | 95.5 | 07-11-2025
01:00 | 3143 | 1222.8 | 930 | 38 | 62 | 1213.93 | 84 | 3417 | 0 | 373 | 1841.9 | 0 | 0 | 0 | 26
01:30 | 3132 | 1221.65 | 930 | 38 | 59 | 1217.66 | 84 | 3403.5 | 0 | 292.5 | 1764.05 | 0 | 0 | 0 | 23.5 | Energy Generated | 272.459 |  | MKWHr
02:00 | 3121 | 1220.5 | 930 | 38 | 56 | 1221.39 | 84 | 3390 | 0 | 212 | 1686.2 | 0 | 0 | 0 | 21 | Energy not Served | 0.959 |  | MKWHr
02:30 | 3111.5 | 1214 | 879.5 | 38 | 57 | 1216.885 | 84 | 3379 | 0 | 197 | 1477.1 | 0 | 0 | 0 | 21 | Total Energy Requirement | 273.418 |  | MKWHr
03:00 | 3102 | 1207.5 | 829 | 38 | 58 | 1212.38 | 84 | 3368 | 0 | 182 | 1268 | 0 | 0 | 0 | 21
03:30 | 3119.5 | 1201.5 | 879.5 | 38 | 57 | 1215.115 | 84 | 3376 | 0 | 140 | 1040 | 0 | 0 | 0 | 10.5
04:00 | 3137 | 1195.5 | 930 | 38 | 56 | 1217.85 | 84 | 3384 | 0 | 98 | 812 | 0 | 0 | 0 | 0
04:30 | 3100.5 | 1199.5 | 930 | 38 | 55 | 1215.16 | 84 | 3359 | 0 | 98 | 772 | 0 | 0 | 0 | 0
05:00 | 3064 | 1203.5 | 930 | 38 | 54 | 1212.47 | 84 | 3334 | 0 | 98 | 732 | 0 | 0 | 0 | 0
05:30 | 3059 | 1181.5 | 930 | 38 | 53 | 1189.14 | 84 | 3257.5 | 0 | 98 | 680.5 | 0 | 0 | 0 | 0
06:00 | 3054 | 1159.5 | 930 | 38 | 52 | 1165.81 | 84 | 3181 | 0 | 98 | 629 | 0 | 0 | 0 | 0
06:30 | 3078.5 | 1176.25 | 930 | 38 | 51 | 1153.885 | 84 | 3105 | 27.295 | 106.5 | 600.5 | 0 | 0 | 0.5 | 0
07:00 | 3103 | 1193 | 930 | 38 | 50 | 1141.96 | 84 | 3029 | 54.59 | 115 | 572 | 0 | 0 | 1 | 0
07:30 | 3054.5 | 1202.25 | 930 | 38 | 49 | 1130.84 | 84 | 2992.5 | 126.24 | 131.5 | 540.5 | 0 | 0 | 0.5 | 0
08:00 | 3006 | 1211.5 | 930 | 38 | 48 | 1119.72 | 84 | 2956 | 197.89 | 148 | 509 | 0 | 0 | 0 | 0
08:30 | 2986 | 1182.25 | 930 | 38 | 52 | 1073.055 | 84 | 2925 | 297.92 | 148 | 413.5 | 0 | 0 | 0 | 0
09:00 | 2966 | 1153 | 930 | 38 | 56 | 1026.39 | 84 | 2894 | 397.95 | 148 | 318 | 0 | 0 | 0 | 0
09:30 | 2986.5 | 1153 | 930.5 | 38 | 57 | 1030.82 | 85 | 2798 | 476.05 | 133 | 297.86 | 0 | 0 | 0.5 | 0
10:00 | 3007 | 1153 | 931 | 38 | 58 | 1035.25 | 86 | 2702 | 554.15 | 118 | 277.72 | 0 | 0 | 1 | 0
10:30 | 3049.5 | 1169 | 930.5 | 38 | 58 | 1008.24 | 86 | 2718.5 | 603.43 | 126.5 | 300.36 | 0 | 0 | 5.5 | 0
11:00 | 3092 | 1185 | 930 | 38 | 58 | 981.23 | 86 | 2735 | 652.71 | 135 | 323 | 0 | 0 | 10 | 0
11:30 | 3137.5 | 1189.5 | 930 | 38 | 61 | 973.055 | 86 | 2832.5 | 649.62 | 162 | 416 | 0 | 0 | 11.5 | 0
12:00 | 3183 | 1194 | 930 | 38 | 64 | 964.88 | 86 | 2930 | 646.53 | 189 | 509 | 0 | 0 | 13 | 0
12:30 | 3198.5 | 1184.5 | 930.5 | 38 | 67 | 1042.15 | 86 | 2954 | 626.095 | 193.5 | 855.25 | 0 | 0 | 12 | 36.5
13:00 | 3214 | 1175 | 931 | 38 | 70 | 1119.42 | 86 | 2978 | 605.66 | 198 | 1201.5 | 0 | 0 | 11 | 73
13:30 | 3111 | 1148.5 | 930.5 | 38 | 73 | 1150.945 | 85 | 2866.5 | 551.38 | 189 | 1241.1 | 0 | 0 | 10.5 | 75
14:00 | 3008 | 1122 | 930 | 38 | 76 | 1182.47 | 84 | 2755 | 497.1 | 180 | 1280.7 | 0 | 0 | 10 | 77
14:30 | 3006.5 | 1152 | 930 | 38 | 75 | 1181.315 | 84 | 2719.5 | 425.385 | 180 | 1258.2 | 0 | 0 | 8.5 | 54.5
15:00 | 3005 | 1182 | 930 | 38 | 74 | 1180.16 | 84 | 2684 | 353.67 | 180 | 1235.7 | 0 | 0 | 7 | 32
15:30 | 3030.5 | 1185 | 930 | 38 | 72 | 1168.29 | 84 | 2644 | 241.305 | 181.5 | 1161.7 | 0 | 0 | 6 | 16
16:00 | 3056 | 1188 | 930 | 38 | 70 | 1156.42 | 84 | 2604 | 128.94 | 183 | 1087.7 | 0 | 0 | 5 | 0
16:30 | 3022 | 1185.5 | 930 | 38 | 67 | 1153.93 | 84 | 2560.5 | 69.445 | 231.5 | 1107.7 | 0 | 0 | 6.5 | 0
17:00 | 2988 | 1183 | 930 | 38 | 64 | 1151.44 | 84 | 2517 | 9.95 | 280 | 1127.7 | 0 | 0 | 8 | 0
17:30 | 3113 | 1199 | 929.5 | 38 | 70 | 1189.005 | 83.5 | 2706 | 4.975 | 508 | 1361.7 | 0 | 0 | 14 | 143
18:00 | 3238 | 1215 | 929 | 38 | 76 | 1226.57 | 83 | 2895 | 0 | 736 | 1595.7 | 0 | 0 | 20 | 286
18:30 | 3209.5 | 1233 | 929 | 38 | 72 | 1232.365 | 84.5 | 2950 | 0 | 756.5 | 1656.8 | 0 | 0 | 21.5 | 222.5
19:00 | 3181 | 1251 | 929 | 38 | 68 | 1238.16 | 86 | 3005 | 0 | 777 | 1717.9 | 0 | 0 | 23 | 159
19:30 | 3215 | 1283 | 930 | 38 | 66 | 1213.67 | 86 | 3000 | 0 | 788 | 1696.9 | 0 | 0 | 13 | 117
20:00 | 3298 | 1283 | 928 | 38 | 64 | 1225.13 | 86 | 3020 | 0 | 776 | 1699.9 | 0 | 0 | 5 | 0
20:30 | 3317.5 | 1283 | 921.5 | 38 | 68 | 1223.785 | 86 | 3066 | 0 | 773.5 | 1664.9 | 0 | 0 | 2.5 | 0
21:00 | 3337 | 1283 | 915 | 38 | 72 | 1222.44 | 86 | 3112 | 0 | 771 | 1629.9 | 0 | 0 | 0 | 0
21:30 | 3380.5 | 1283 | 915 | 38 | 70 | 1224.705 | 86 | 3115 | 0 | 730 | 1582.4 | 0 | 0 | 0 | 23.5
22:00 | 3424 | 1283 | 915 | 38 | 68 | 1226.97 | 86 | 3118 | 0 | 689 | 1534.9 | 0 | 0 | 0 | 47
22:30 | 3403.5 | 1278 | 915 | 38 | 69 | 1230.62 | 86 | 3106 | 0 | 632 | 1491.65 | 0 | 0 | 0 | 49.5
23:00 | 3383 | 1273 | 915 | 38 | 70 | 1234.27 | 86 | 3094 | 0 | 575 | 1448.4 | 0 | 0 | 0 | 52
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 16:00 | 376 | 00:00 | Payra | 413 | 17:00 | 407 | 00:00
Ashuganj | 405 | 6:00 | 386 | 23:00 | Rahanpur | 411 | 09:00 | 405 | 04:00
Bhulta | 402 | 06:00 | 378 | 11:00 | Rampal | 408 | 17:00 | 397 | 00:00
Bibiana | 390 | 06:00 | 380 | 12:00
BIPTC | 406 | 03:00 | 396 | 18:00
Bogura | 402 | 09:00 | 397 | 00:00
Gopalganj | 402 | 17:00 | 392 | 00:00
Kaliakoir | 378 | 06:00 | 357 | 12:00
Madunaghat | 401 | 17:00 | 392 | 05:00
Meghnaghat | 391 | 17:00 | 380 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 17:00 | 224 | 12:00 | Kaliakoir | 237 | 06:00 | 224 | 12:00
AKSML | 238 | 18:00 | 229 | 07:00 | Keranigonj | 229 | 17:00 | 222 | 12:00
Aminbazar | 231 | 05:00 | 227 | 00:00 | Khulna(S) | 236 | 09:00 | 229 | 00:00
Ashuganj | 235 | 06:00 | 228 | 13:00 | Madunaghat | 238 | 18:00 | 232 | 05:00
Ashuganj-400 | 235 | 06:00 | 228 | 13:00 | Madunaghat-400 | 239 | 17:00 | 232 | 05:00
Baghabari | 236 | 06:00 | 230 | 13:00 | Maniknagar | 224 | 17:00 | 217 | 00:00
Barapukuria | 223 | 21:00 | 213 | 08:00 | Meghnaghat | 231 | 17:00 | 222 | 05:00
Barapukuria-230 | 223 | 21:00 | 213 | 08:00 | Meghnaghat-400 | 228 | 17:00 | 221 | 00:00
Barishal | 236 | 09:00 | 231 | 00:00 | Mirsorai | 237 | 19:00 | 225 | 04:00
Bheramara | 234 | 06:00 | 228 | 13:00 | Rajshahi | 233 | 09:00 | 226 | 13:00
Bhulta | 233 | 06:00 | 216 | 00:00 | Rampal | 235 | 09:00 | 228 | 00:00
Bibiana | 231 | 05:00 | 224 | 12:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 237 | 06:00 | 228 | 13:00 | Rampura | 232 | 06:00 | 217 | 12:00
Bogura | 234 | 19:30 | 230 | 01:00 | Shikalbaha | 238 | 18:00 | 228 | 06:00
Bogura-400 | 233 | 19:30 | 229 | 04:00 | Shyampur | 228 | 17:00 | 220 | 00:00
Borhanuddin | 238 | 10:00 | 232 | 20:00 | Siddhirganj | 226 | 17:00 | 218 | 00:00
BSRM | 235 | 18:00 | 224 | 04:00 | Sirajgonj | 239 | 06:00 | 236 | 00:00
Cumilla(N) | 230 | 17:00 | 225 | 00:00 | Sreepur | 229 | 06:00 | 223 | 12:00
Faridpur | 233 | 07:00 | 228 | 00:00 | Tongi | 230 | 04:00 | 220 | 12:00
Fenchuganj | 233 | 19:00 | 227 | 02:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 232 | 07:00 | 219 | 12:00
Gopalganj | 235 | 02:00 | 229 | 00:00
GPH | 238 | 18:00 | 229 | 03:00
Haripur | 226 | 17:00 | 218 | 00:00
Hasnabad | 229 | 17:00 | 220 | 00:00
Hathazari | 236 | 14:00 | 229 | 05:00
Ishurdi | 237 | 09:00 | 231 | 13:00
Jhenaidah | 233 | 06:00 | 224 | 13:00
Kachua | 235 | 16:00 | 224 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 126 | 12:00 | Lalmonirhat | 132 | 19:30 | 122 | 08:00
Agargaon | 136 | 06:00 | 131 | 12:00 | Madanganj | 131 | 04:00 | 128 | 11:00
Agrabad | 137 | 18:00 | 131 | 05:00 | Madaripur | 136 | 08:00 | 133 | 00:00
AKS | 134 | 01:00 | 129 | 05:00 | Madartek | 136 | 06:00 | 125 | 12:00
Aminbazar | 137 | 04:00 | 127 | 13:00 | Madunaghat | 138 | 16:00 | 134 | 05:00
Amnura | 139 | 04:00 | 130 | 13:00 | Magura | 135 | 05:00 | 128 | 13:00
Ashuganj | 141 | 06:00 | 135 | 12:00 | Mahasthangarh | 132 | 19:00 | 129 | 01:00
Bagerhat | 134 | 09:00 | 125 | 00:00 | Maijdee | 133 | 12:00 | 131 | 01:00
Bajitpur | 135 | 05:00 | 127 | 12:00 | Manikganj | 137 | 08:00 | 130 | 12:00
Bakulia | 138 | 17:00 | 133 | 06:00 | Maniknagar | 136 | 17:00 | 130 | 00:00
Banani | 136 | 07:00 | 126 | 12:00 | Matarbari | 125 | 18:00 | 116 | 22:00
Bangabhaban | 136 | 17:00 | 130 | 00:00 | Matuail | 132 | 17:00 | 127 | 00:00
Barapukuria | 137 | 19:30 | 128 | 12:00 | Metrorail_Motijheel | 136 | 17:00 | 130 | 00:00
Barguna | 137 | 09:00 | 134 | 00:00 | Metrorail_Uttara | 140 | 07:00 | 131 | 13:00
Barishal | 136 | 05:00 | 132 | 18:30 | Millgate | 141 | 06:00 | 132 | 12:00
Barishal-230 | 136 | 08:00 | 132 | 12:00 | Mirpur | 136 | 04:00 | 130 | 12:00
Baroaulia | 138 | 18:30 | 132 | 04:00 | Mirzapur | 131 | 06:00 | 124 | 12:00
Baroirhat | 135 | 15:00 | 131 | 07:00 | Mithapukur | 134 | 19:00 | 127 | 08:00
Bashundhara | 136 | 05:00 | 126 | 12:00 | MI_Cement | 134.5 | 17:00 | 129 | 00:00
BashundharaCement | 131 | 04:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 131 | 08:00 | 127 | 00:00 | Mogbazar | 137 | 04:00 | 127 | 12:00
Benapole | 132 | 06:00 | 122 | 13:00 | Mongla | 133 | 08:00 | 124 | 00:00
Bhaluka | 132 | 18:00 | 127 | 00:00 | Motijheel | 136 | 17:00 | 131 | 01:00
Bhandaria | 132 | 08:00 | 125 | 00:00 | Muktagacha | 128 | 22:00 | 117 | 00:00
Bhangura | 135 | 06:00 | 132 | 00:00 | Munshiganj | 131 | 17:00 | 126 | 00:00
Bheramara | 139 | 07:00 | 136 | 13:00 | Muradnagar | 132 | 17:00 | 125 | 04:00
Bheramara(GK) | 139 | 06:00 | 136 | 13:00 | Mymensingh | 128 | 06:00 | 116 | 01:00
Bhulta | 130 | 14:00 | 125 | 00:00 | Naogaon | 130 | 17:00 | 127 | 01:00
Bog-Sherpur | 134 | 15:00 | 131 | 00:00 | Narail | 135 | 06:00 | 127 | 13:00
Bogura | 134 | 20:00 | 131 | 01:00 | Narinda | 136 | 17:00 | 130 | 00:00
Bogura-230 | 134 | 19:00 | 131 | 01:00 | Narshingdi | 133 | 18:00 | 121 | 23:00
Brahmanbaria | 134 | 04:00 | 128 | 12:00 | Natore | 135 | 19:00 | 131 | 13:00
Cantonment | 136 | 17:00 | 130 | 12:00 | Nawabganj | 136 | 17:00 | 130 | 00:00
Chandina | 135 | 14:00 | 130 | 04:00 | Netrakona | 128 | 19:30 | 118 | 20:00
Chandpur | 140 | 17:00 | 134 | 10:00 | New | 141 | 05:00 | 133 | 12:00
Chandraghona | 138 | 17:00 | 134 | 03:00 | Niamatpur | 141 | 11:00 | 138 | 00:00
Chapai | 139 | 00:00 | 137 | 18:00 | Noapara | 136 | 09:00 | 130 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 14:00 | 127 | 00:00 | Pabna | 137 | 05:00 | 133 | 13:00
Chauddagram | 135 | 17:00 | 130 | 03:00 | Palashbari | 132 | 19:30 | 127 | 12:00
Chhatak | 130 | 08:00 | 123 | 20:00 | Panchagarh | 138 | 19:00 | 124 | 07:00
Chowmuhani | 133 | 07:00 | 130 | 20:00 | Patiya | 137 | 18:00 | 131 | 04:00
Chuadanga | 135 | 06:00 | 127 | 13:00 | Patuakhali | 136 | 16:00 | 134 | 00:00
Coxsbazar | 123 | 18:00 | 115 | 23:00 | Payra | 136 | 00:00 | 133 | 12:00
Cumilla(N) | 136 | 17:00 | 130 | 11:00 | PHP | 134 | 14:00 | 130 | 03:00
Cumilla(S) | 136 | 17:00 | 128 | 13:00 | Postogola | 136 | 17:00 | 131 | 00:00
Daganbhuiyan | 134 | 17:00 | 131 | 03:00 | Purbachal | 136 | 06:00 | 126 | 12:00
Daudkandi | 130 | 17:00 | 123 | 11:00 | Purbasadipur | 135 | 19:30 | 124 | 08:00
DhakaUniversity | 136 | 07:00 | 126 | 12:00 | Rahanpur | 141 | 08:00 | 139 | 01:00
Dhamrai | 135 | 07:00 | 127 | 11:00 | Rahanpur-400 | 142 | 09:00 | 139 | 18:00
Dhanmondi | 137 | 06:00 | 126.6 | 12:00 | Rahim | 130 | 07:00 | 126 | 00:00
Dohazari | 133 | 18:00 | 127 | 05:00 | Rajbari | 137 | 08:00 | 133 | 00:00
Faridpur | 138 | 17:00 | 134 | 23:00 | Rajendrapur | 132 | 17:00 | 127 | 00:00
Fatullah | 139 | 17:00 | 130 | 00:00 | Rajshahi | 135 | 19:30 | 131 | 12:00
Fenchuganj | 137 | 09:00 | 134 | 01:00 | Rajshahi-230 | 134 | 06:00 | 130 | 13:00
Feni | 134 | 15:00 | 120 | 05:00 | Ramganj | 135 | 14:00 | 132 | 06:00
Ghatail | 127 | 05:00 | 119 | 13:00 | Rampur | 136 | 17:00 | 131 | 04:00
Ghorashal | 140 | 04:00 | 134 | 15:00 | Rampura | 136 | 06:00 | 126 | 12:00
Goalpara | 137 | 08:00 | 131 | 00:00 | Rangamati | 137 | 16:00 | 133 | 04:00
Gollamari | 137 | 09:00 | 131 | 00:00 | Rangpur | 135 | 19:30 | 127 | 12:00
Gopalganj | 136 | 09:00 | 132 | 00:00 | Ruppur | 139 | 05:00 | 136 | 00:00
Gopalganj-400 | 138 | 08:00 | 134 | 00:00 | Saidpur | 134 | 19:30 | 123 | 07:00
Gulshan | 136 | 05:00 | 126 | 12:00 | Satkhira | 134 | 09:00 | 127 | 00:00
Halishahar | 137 | 17:00 | 132 | 04:00 | Satmasjid | 135 | 05:00 | 130 | 12:00
Haripur | 132 | 17:00 | 127 | 00:00 | Savar | 136 | 17:00 | 130 | 12:00
HaripurSBU | 132 | 17:00 | 127 | 03:00 | SevenRings | 140 | 05:00 | 132 | 12:00
Hasnabad | 136 | 17:00 | 131 | 00:00 | ShahCement | 131 | 14:00 | 127 | 00:00
Hathazari | 138 | 17:00 | 135 | 05:00 | Shahjadpur | 139 | 04:00 | 135 | 11:00
Ishurdi | 140 | 09:00 | 136 | 13:00 | Shahjibazar | 136 | 06:00 | 130 | 12:00
Jaldhaka | 132 | 19:30 | 121 | 08:00 | Shahmirpur | 138 | 18:00 | 132 | 07:00
Jamalpur | 126 | 09:00 | 114 | 13:00 | Shariatpur | 135 | 07:00 | 131 | 23:00
Jashore | 133 | 06:00 | 124 | 13:00 | Sherpur | 124 | 06:00 | 110 | 02:00
Jhenaidah | 137 | 05:00 | 130 | 13:00 | Shikalbaha | 126 | 16:00 | 118 | 13:00
Jhenaidah-230 | 138 | 06:00 | 131 | 13:00 | Shikalbaha-230 | 139 | 18:00 | 134 | 04:00
Joydebpur | 142 | 02:00 | 128 | 15:00 | Shitalakhya | 134.5 | 17:00 | 129 | 00:00
Joypurhat | 129 | 09:00 | 126 | 00:00 | Sholosohor | 138 | 17:00 | 134 | 03:00
Juldah | 138 | 18:00 | 132 | 05:00 | Shyampur | 137 | 18:00 | 131 | 13:00
Kabirpur | 139 | 06:00 | 126 | 12:00 | Shyampur-230 | 139 | 17:00 | 133 | 12:00
Kachua | 139 | 16:00 | 133 | 10:00 | Siddhirganj | 132 | 17:00 | 127 | 00:00
Kaliakoir | 136 | 02:00 | 128 | 16:00 | Sirajganj | 134 | 10:00 | 130 | 00:00
Kallyanpur | 139 | 08:00 | 131 | 12:00 | Sonargaon | 130 | 14:00 | 125 | 00:00
Kalurghat | 138 | 17:00 | 133 | 05:00 | Sreemongol | 135 | 06:00 | 130 | 12:00
Kamrangirchar | 136 | 17:00 | 131 | 00:00 | Sreepur | 134 | 19:30 | 129 | 00:00
Kaptai | 138 | 17:00 | 135 | 6:00 | Srinagar | 135 | 07:00 | 130 | 00:00
Kasba | 131 | 17:00 | 126 | 03:00 | SSM | 140 | 00:00 | 132 | 11:00
Kazla | 135 | 17:00 | 130 | 00:00 | Sunamganj | 128 | 07:00 | 121 | 20:00
Keranigonj | 137 | 17:00 | 131 | 00:00 | Sylhet | 132 | 07:00 | 128 | 13:00
Khagrachori | 136 | 00:00 | 133 | 04:00 | Sylhet-132 | 132 | 08:00 | 129 | 00:00
Khulna | 136 | 17:00 | 130 | 00:00 | Tangail | 128 | 05:00 | 120 | 13:00
Khulna(S) | 137 | 06:00 | 132 | 00:00 | Taraganj | 134 | 19:30 | 123 | 08:00
Khulshi | 136 | 17:00 | 131 | 05:00 | Thakurgaon | 139 | 19:30 | 122 | 08:00
Kishoreganj | 132 | 19:30 | 123 | 20:00 | TK | 138 | 17:00 | 134 | 07:00
Kodda | 138 | 01:00 | 125 | 12:00 | Tongi | 140 | 04:00 | 134 | 12:00
KSRM | 138 | 19:00 | 133 | 04:00 | Ullahpara | 135 | 06:00 | 132 | 01:00
Kulaura | 136 | 05:00 | 133 | 12:00 | Ullon | 136 | 06:00 | 126 | 12:00
Kurigram | 133 | 21:00 | 122 | 08:00 | Uttara | 137 | 17:00 | 130 | 12:00
Kushtia | 138 | 04:00 | 133 | 00:00 | UttaraNew | 140 | 07:00 | 131 | 13:00
Laksam | 138 | 14:00 | 133 | 10:00 | Zigatola | 136 | 17:00 | 125 | 06:00
Lakshmipur | 133 | 16:00 | 130 | 03:00
Lalbag | 135 | 08:00 | 129 | 01:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division