## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-11-2025 | during | 09-11-2025 | during | 09-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 381 | 331 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 380 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 332 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 47 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 122 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 20.5 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 0 | 21 | 21 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 31 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 34 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 25 | 88 | 88 | 88 | 105 | 105 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 45 | 125 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1308.5 | 1682.5 | 5891.9 | 5859.9 | 3364.24 | 3404.24
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 130 | 130 | 130 | 130 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 98 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 68 | 60 | 60 | 60 | 60 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 9 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 65 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.31 | 0 | 3.21 | 0 | 3.21 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 80 | 300 | 300 | 100 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 35 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 105 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 90 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 126 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 550 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 13 | 19 | 13 | 19 | 13 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 315 | 315 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1653.31 | 2396.5 | 3006.93 | 2993.72 | 2205.57 | 2192.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 380 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 37 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 39 | 40 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 5 | 133 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 21 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 103 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 4 | 186 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 66 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 16 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 107 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1054 | 1522.2 | 2621.56 | 2551.56 | 2300.56 | 2230.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-11-2025 | during | 09-11-2025 | during | 09-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 73 | 73 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 32 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 18 | 18.5 | 18.5 | 18 | 18 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.32 | 0 | 48.5 | 0 | 48.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 6 | 6 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 173.32 | 149 | 363.1 | 312.5 | 309.1 | 258.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 67 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 149 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 82 | 81 | 81 | 81 | 81 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 99 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 12 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 395 | 361 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1166 | 1129 | 1145 | 1145 | 1067 | 1067
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 915 | 916 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 36 | 36 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 70 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 396 | 350 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 83 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1065 | 1086 | 0 | 0 | 1100 | 1100 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2497 | 2491 | 2056 | 1976 | 2731 | 2651
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 400 | 503 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 220 | 260 | 622 | 622 | 592 | 592 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 950.59 | 1126 | 1218 | 1217 | 1047 | 1046
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 61.97 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 186 | 185 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 388 | 345 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 98 | 98 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 80 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Engine Problem
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.37 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 875 | 1216.58 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.97 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 109 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1689.31 | 2076.78 | 3175.46 | 3008.87 | 2568.68 | 2402.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 89 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 171 | 0 | 179.12 | 0 | 179.12 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 199 | 204 | 462.92 | 248 | 442.92 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 10691.03 | 12776.98 | 19940.87 | 19312.55 | 16036.07 | 15479.75
Forecast Scenario (09-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12021 |  | 0 |  | 12021
|  |  |  | 1:00 | 11336 |  | 0 |  | 11336
|  |  |  | 2:00 | 10886 |  | 0 |  | 10886
|  |  |  | 3:00 | 10516 |  | 0 |  | 10516
|  |  |  | 4:00 | 10237 |  | 0 |  | 10237
|  |  |  | 5:00 | 9954 |  | 0 |  | 9954
|  |  |  | 6:00 | 9831 |  | 0 |  | 9831
|  |  |  | 7:00 | 10305 |  | 0 |  | 10305
|  |  |  | 8:00 | 10499 |  | 0 |  | 10499
|  |  |  | 9:00 | 10531 |  | 0 |  | 10531
|  |  |  | 10:00 | 10673 |  | 0 |  | 10673
|  |  |  | 11:00 | 11008 |  | 0 |  | 11008
|  |  |  | 12:00 | 11712 |  | 0 |  | 11712
|  |  |  | 13:00 | 12326 |  | 0 |  | 12326
|  |  |  | 14:00 | 12224 |  | 0 |  | 12224
|  |  |  | 15:00 | 12211 |  | 0 |  | 12211
|  |  |  | 16:00 | 12537 |  | 0 |  | 12537
|  |  |  | 17:00 | 12743 |  | 0 |  | 12743
|  |  |  | 18:00 | 13283 |  | 0 |  | 13283
|  |  |  | 18:30 | 13294 |  | 0 |  | 13294
|  |  |  | 19:00 | 13533 |  | 0 |  | 13533
|  |  |  | 19:30 | 13640 |  | 0 |  | 13640
|  |  |  | 20:00 | 13444 |  | 0 |  | 13444
|  |  |  | 21:00 | 12915 |  | 0 |  | 12915
|  |  |  | 22:00 | 12457 |  | 0 |  | 12457
|  |  |  | 23:00 | 12161 |  | 0 |  | 12161
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 11712.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13640.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13640.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 279.343 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:25 hrs on 09-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-11-2025 | [28 empty] | Date: | 08-11-2025 | [28 empty] | Date: | 08-11-2025 | [28 empty] | Date: | 08-11-2025 | [28 empty] | Date: | 08-11-2025 | [14 empty] | Date: | 08-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 20 | 45 | 31 | 55 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 0 | 116 | 16 | 30 | 0 | 6 | 65 | 60 | 17 | 12 | 12 | 0 | 86 | 110 | 23 | 315 | 17 | 0 | 33 | 25.5 | 105 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 142 | 0 | 295 | 0 | 330 | 42 | 0 | 38 | 17 | 103 | 197 | 0 | 20 | 98 | 66 | 52.2 | 0 | 22 | 310 | 0 | 332 | 20 | 57 | 151 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 58 | 97 | 0 | 0 | 0 | 5910.7 | 916 | 333 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 1228.44 | 0 | 40 | 0 | 35 | 35 | 0 | 98 | 30 | 52.2 | 0 | 0 | 27 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 100 | 180 | 0 | 503 | 540 | 17 | 6052.64 | 11963.34 | 101.74
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 17 | 30 | 31 | 55 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 0 | 115 | 16 | 31 | 0 | 22 | 0 | 60 | 17 | 12 | 12 | 0 | 86 | 110 | 23 | 315 | 17 | 0 | 33 | 25.5 | 105 | 225 | 0 | 0 | 0 | 575 | 0 | 0 | 137 | 0 | 295 | 0 | 330 | 42 | 0 | 38 | 30 | 104 | 200 | 0 | 20 | 98 | 66 | 52.2 | 0 | 0 | 310 | 0 | 368 | 0 | 57 | 155 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 58 | 101 | 0 | 0 | 0 | 5834.7 | 915 | 345 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 1219.58 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 12 | 0 | 0 | 0 | 5 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 506 | 315 | 17 | 5520.58 | 11355.28 | 101.74
02:00 | 0 | 36 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 17 | 30 | 31 | 55 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 0 | 53 | 16 | 0 | 0 | 24 | 0 | 0 | 17 | 12 | 12 | 0 | 86 | 110 | 27 | 315 | 17 | 0 | 33 | 25.5 | 105 | 225 | 0 | 0 | 0 | 564 | 0 | 0 | 135 | 0 | 305 | 0 | 330 | 42 | 0 | 38 | 35 | 104 | 93 | 0 | 20 | 35 | 62 | 25 | 0 | 0 | 305 | 0 | 361 | 0 | 57 | 154 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 58 | 102 | 0 | 0 | 0 | 5476.5 | 915 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 1222.07 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 504 | 265 | 17 | 5449.07 | 10925.57 | 101.74
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 17 | 4 | 31 | 15 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 0 | 15 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 68 | 42 | 315 | 0 | 0 | 0 | 0 | 105 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 135 | 0 | 330 | 0 | 330 | 42 | 0 | 38 | 35 | 103 | 51 | 0 | 20 | 0 | 58 | 0 | 0 | 0 | 305 | 0 | 384 | 0 | 57 | 155 | 22 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 58 | 107 | 0 | 0 | 0 | 5159 | 915 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 0 | 1205.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 504 | 265 | 0 | 5274.51 | 10433.51 | 101.74
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 0 | 42 | 315 | 0 | 0 | 0 | 0 | 68 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 345 | 0 | 330 | 43 | 0 | 38 | 15 | 104 | 52 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 300 | 0 | 375 | 0 | 57 | 153 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 45 | 107 | 0 | 0 | 0 | 4812 | 916 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 1210.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 504 | 265 | 0 | 5257.53 | 10069.53 | 101.74
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 315 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 350 | 0 | 330 | 42 | 0 | 39 | 0 | 104 | 0 | 0 | 20 | 0 | 62 | 0 | 0 | 0 | 300 | 0 | 377 | 0 | 57 | 153 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 45 | 108 | 0 | 0 | 0 | 4635 | 916 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 1182.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 504 | 265 | 0 | 5239.95 | 9874.95 | 101.74
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 315 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 0 | 320 | 0 | 300 | 43 | 0 | 39 | 0 | 104 | 0 | 0 | 20 | 0 | 58 | 0 | 0 | 0 | 310 | 0 | 360 | 0 | 57 | 153 | 21 | 0 | 81 | 30 | 0 | 12 | 99 | 0 | 19 | 45 | 108 | 0 | 0 | 0 | 4451 | 916 | 385 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1177.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 504 | 265 | 0 | 5195.19 | 9646.19 | 101.74
07:00 | 0 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 1 | 30 | 0 | 15 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 4 | 5 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 12 | 10 | 0.74 | 86 | 0 | 42 | 315 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 572 | 3 | 0 | 0 | 0 | 393 | 0 | 330 | 43 | 0 | 35 | 0 | 104 | 0 | 0 | 20 | 0 | 52 | 0 | 10 | 0 | 315 | 0 | 366 | 0 | 57 | 160 | 21 | 0 | 79 | 30 | 0 | 12 | 99 | 0 | 19 | 58 | 107 | 0 | 5.54 | 0 | 4771.28 | 915 | 395 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.84 | 1112 | 0 | 1157.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.56 | 10 | 0 | 0 | 5 | 181 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0.45 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.5 | 17 | 0.05 | 0 | 0 | 110 | 180 | 0 | 504 | 265 | 0 | 5250.97 | 10022.25 | 101.74
08:00 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 17 | 46 | 5 | 15 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 13 | 35 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 12 | 12 | 0.94 | 86 | 26 | 16 | 315 | 0 | 0 | 13 | 0 | 92 | 187 | 0 | 0 | 0 | 528 | 9 | 0 | 55 | 0 | 320 | 0 | 280 | 35 | 0 | 35 | 15 | 104 | 48 | 0 | 20 | 0 | 46 | 0 | 34 | 0 | 300 | 0 | 330 | 0 | 57 | 147 | 21 | 0 | 40 | 30 | 0 | 12 | 100 | 0 | 19 | 58 | 107 | 1 | 20.56 | 0 | 4696.5 | 916 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 1082 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.91 | 44 | 0 | 0 | 25.43 | 166 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 2.17 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 2.1 | 68 | 0.19 | 0 | 0 | 100 | 180 | 0 | 491 | 265 | 0 | 5244.8 | 9941.3 | 101.74
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 15 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 22 | 17 | 18.8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 2.55 | 86 | 32 | 4 | 420 | 0 | 0 | 32 | 0 | 17 | 188 | 0 | 0 | 0 | 477 | 14 | 0 | 50 | 0 | 300 | 0 | 280 | 10 | 0 | 38 | 0 | 103 | 17 | 0 | 20 | 0 | 52 | 0 | 52 | 0 | 305 | 0 | 333 | 0 | 57 | 142 | 21 | 0 | 41 | 30 | 0 | 12 | 100 | 0 | 19 | 58 | 102 | 1 | 33.91 | 0 | 4614.26 | 865 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 985 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.07 | 74 | 0 | 0 | 43.72 | 167 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 3.8 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 3.8 | 116 | 0.37 | 0 | 0 | 100 | 180 | 0 | 307 | 250 | 0 | 4946.76 | 9561.02 | 101.74
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 15 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 28 | 17 | 18.5 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 10 | 0 | 0 | 0 | 12 | 12 | 3.01 | 86 | 0 | 6 | 500 | 0 | 0 | 33 | 0 | 14 | 188 | 0 | 0 | 0 | 469 | 18 | 0 | 8 | 0 | 305 | 0 | 280 | 10 | 0 | 38 | 0 | 101 | 0 | 0 | 20 | 0 | 54 | 0 | 65 | 0 | 310 | 0 | 335 | 0 | 57 | 151 | 21 | 0 | 41 | 30 | 0 | 12 | 100 | 0 | 19 | 25 | 86 | 2 | 43.15 | 0 | 4558.66 | 916 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 862 | 0 | 884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.47 | 97 | 0 | 0 | 55.85 | 176 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 4.92 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 5 | 149 | 0.51 | 0 | 0 | 100 | 180 | 0 | 304 | 225 | 0 | 4888.75 | 9447.41 | 101.74
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 31 | 17 | 20.5 | 21 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 0 | 0 | 12 | 12 | 3.29 | 86 | 0 | 6 | 650 | 0 | 0 | 33 | 0 | 0 | 217 | 0 | 0 | 0 | 520 | 19 | 0 | 0 | 0 | 393 | 0 | 330 | 16 | 0 | 38 | 0 | 102 | 0 | 0 | 20 | 0 | 60 | 0 | 68 | 0 | 320 | 0 | 388 | 0 | 57 | 158 | 21 | 0 | 76 | 30 | 0 | 12 | 100 | 0 | 19 | 25 | 73 | 2 | 47.42 | 0 | 5152.21 | 916 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 855 | 0 | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.53 | 108 | 0 | 0 | 59.5 | 180 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 5.39 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 5.7 | 167 | 0.57 | 0 | 0 | 110 | 220 | 0 | 307 | 225 | 0 | 4994.69 | 10146.9 | 101.74
12:00 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 15 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 32 | 45 | 20.5 | 21 | 0 | 0 | 0 | 0 | 24 | 0 | 12 | 0 | 0 | 0 | 12 | 12 | 3.31 | 86 | 0 | 7 | 650 | 0 | 0 | 44 | 0 | 17 | 217 | 0 | 0 | 0 | 550 | 19 | 0 | 5 | 0 | 393 | 0 | 330 | 39 | 0 | 37 | 0 | 100 | 4 | 0 | 20 | 0 | 58 | 0 | 68 | 0 | 320 | 0 | 395 | 0 | 50 | 159 | 21 | 0 | 79 | 30 | 0 | 12 | 100 | 0 | 19 | 32 | 73 | 2 | 47.32 | 0 | 5355.13 | 915 | 396 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 1065 | 0 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.97 | 109 | 0 | 0 | 63.97 | 186 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 5.37 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 6 | 171 | 0.59 | 0 | 0 | 110 | 220 | 0 | 400 | 220 | 0 | 5335.9 | 10691.03 | 101.74
13:00 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 17 | 15 | 31 | 15 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 30 | 70 | 20.2 | 21 | 0 | 0 | 17 | 0 | 42 | 0 | 18 | 0 | 0 | 0 | 12 | 12 | 3.03 | 86 | 75 | 13 | 650 | 0 | 0 | 46 | 0 | 87 | 216 | 0 | 0 | 0 | 563 | 18 | 0 | 68 | 0 | 393 | 0 | 330 | 40 | 0 | 37 | 5 | 100 | 51 | 5 | 20 | 0 | 60 | 0 | 64 | 0 | 320 | 0 | 387 | 0 | 50 | 158 | 21 | 0 | 79 | 30 | 0 | 12 | 100 | 6 | 28 | 57 | 73 | 2 | 41.99 | 0 | 5774.22 | 915 | 393 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75 | 1124 | 0 | 1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.93 | 100 | 0 | 0 | 61.29 | 185 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 5.4 | 120 | 0.53 | 0 | 0 | 110 | 220 | 0 | 501 | 220 | 0 | 5558.15 | 11332.37 | 101.74
14:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 2 | 17 | 15 | 31 | 15 | 17 | 35 | 0 | 380 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 26 | 70 | 20.2 | 21 | 0 | 0 | 60 | 0 | 43 | 0 | 16 | 0 | 28 | 0 | 12 | 12 | 2.44 | 86 | 95 | 9 | 650 | 0 | 0 | 46 | 0 | 101 | 216 | 0 | 0 | 0 | 562 | 15 | 0 | 113 | 0 | 360 | 0 | 330 | 40 | 0 | 37 | 17 | 100 | 53 | 9 | 20 | 0 | 66 | 0 | 53 | 0 | 310 | 0 | 391 | 0 | 57 | 150 | 21 | 0 | 79 | 30 | 0 | 12 | 99 | 17 | 19 | 58 | 73 | 2 | 36.5 | 0 | 5903.14 | 915 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 63 | 1114 | 0 | 1116.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.29 | 84 | 0 | 0 | 51.44 | 177 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0.06 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 4.4 | 140 | 0.42 | 0 | 0 | 110 | 180 | 0 | 501 | 220 | 0 | 5534.95 | 11438.09 | 101.74
15:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 17 | 17 | 15 | 31 | 15 | 35 | 35 | 0 | 380 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 19 | 70 | 20 | 22 | 0 | 0 | 67 | 0 | 44 | 0 | 18 | 0 | 31 | 0 | 12 | 12 | 1.63 | 86 | 95 | 3 | 650 | 0 | 0 | 46 | 0 | 104 | 215 | 0 | 0 | 0 | 575 | 11 | 0 | 122 | 0 | 393 | 0 | 330 | 40 | 0 | 37 | 18 | 100 | 53 | 8 | 20 | 0 | 64 | 0 | 38 | 4 | 315 | 0 | 390 | 0 | 67 | 154 | 21 | 0 | 79 | 30 | 0 | 12 | 100 | 17 | 19 | 58 | 73 | 1 | 25 | 0 | 5995.63 | 915 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1128 | 0 | 1125.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.06 | 63 | 0 | 0 | 35.7 | 182 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 3.12 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 2.9 | 87 | 0.29 | 0 | 0 | 110 | 220 | 0 | 502 | 220 | 17 | 5517.32 | 11512.95 | 101.74
16:00 | 0 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 17 | 30 | 15 | 31 | 15 | 35 | 35 | 0 | 380 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 9 | 70 | 20 | 22 | 0 | 0 | 89 | 10 | 44 | 0 | 18 | 0 | 68 | 0 | 12 | 12 | 0.71 | 86 | 94 | 3 | 650 | 0 | 0 | 46 | 3 | 102 | 215 | 0 | 0 | 0 | 570 | 5 | 0 | 110 | 0 | 393 | 0 | 330 | 40 | 0 | 29 | 23 | 100 | 53 | 0 | 20 | 17 | 68 | 6 | 16 | 21 | 325 | 0 | 391 | 0 | 67 | 155 | 21 | 0 | 79 | 30 | 0 | 12 | 99 | 17 | 18 | 58 | 73 | 1 | 9.9 | 0 | 6035.61 | 915 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 1106 | 0 | 1121.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.22 | 24 | 0 | 0 | 11.53 | 179 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 1.14 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.3 | 39 | 0.13 | 0 | 0 | 110 | 220 | 0 | 501 | 220 | 17 | 5302.31 | 11337.92 | 101.74
17:00 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17 | 17 | 15 | 70 | 31 | 15 | 35 | 54 | 0 | 380 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 1 | 95 | 20.5 | 0 | 0 | 0 | 99 | 15 | 43 | 0 | 18 | 0 | 68 | 0 | 20 | 12 | 0.04 | 86 | 95 | 5 | 650 | 60 | 0 | 49 | 25.5 | 104 | 217 | 0 | 0 | 0 | 560 | 0 | 0 | 107 | 0 | 393 | 0 | 330 | 40 | 0 | 36 | 34 | 100 | 53 | 0 | 14 | 50 | 64 | 16 | 1 | 21 | 320 | 0 | 380 | 0 | 67 | 156 | 21 | 0 | 81 | 30 | 0 | 15 | 99 | 17 | 18 | 58 | 73 | 0 | 0.66 | 0 | 6243.7 | 915 | 368 | 0 | 9 | 10 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1115 | 0 | 1117.98 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 10 | 1 | 1.12 | 3 | 24 | 0 | 1 | 182 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0.09 | 0 | 0 | 35 | 1 | 8 | 0 | 0 | 0 | 0.1 | 2 | 0.11 | 0 | 0 | 110 | 220 | 0 | 502 | 220 | 17 | 5320.4 | 11564.1 | 101.74
18:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 17 | 17 | 28 | 122 | 31 | 15 | 35 | 71 | 0 | 380 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 0 | 125 | 20.5 | 22 | 0 | 0 | 94 | 30 | 50 | 0 | 22 | 65 | 68 | 0 | 24 | 12 | 0 | 86 | 104 | 16 | 650 | 127 | 0 | 50 | 25.5 | 101 | 217 | 0 | 0 | 0 | 588 | 0 | 0 | 127 | 0 | 400 | 0 | 330 | 41 | 0 | 34 | 37 | 103 | 146 | 0 | 16 | 100 | 74 | 52.2 | 0 | 21 | 315 | 0 | 384 | 0 | 67 | 156 | 23 | 0 | 82 | 30 | 0 | 15 | 99 | 0 | 18 | 58 | 73 | 0 | 0 | 0 | 6851.2 | 917 | 358 | 0 | 36 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 1180.49 | 0 | 41 | 0 | 0 | 20 | 0 | 98 | 28 | 43 | 0 | 0 | 27 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 105 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 110 | 220 | 0 | 503 | 235 | 17 | 5824.49 | 12675.69 | 101.74
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 47 | 17 | 34 | 122 | 31 | 15 | 35 | 72 | 0 | 380 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 125 | 20.5 | 0 | 0 | 0 | 90 | 80 | 65 | 0 | 13 | 65 | 68 | 0 | 24 | 12 | 0 | 86 | 105 | 9 | 650 | 126 | 0 | 50 | 25.5 | 98 | 218 | 0 | 0 | 0 | 612 | 0 | 0 | 133 | 0 | 380 | 0 | 330 | 40 | 0 | 37 | 51 | 103 | 186 | 0 | 16 | 107 | 66 | 52.2 | 0 | 21 | 310 | 0 | 361 | 0 | 67 | 149 | 16 | 0 | 82 | 30 | 0 | 15 | 99 | 0 | 18 | 58 | 73 | 0 | 0 | 0 | 6879.2 | 916 | 350 | 0 | 31 | 70 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1086 | 0 | 1216.58 | 0 | 41 | 0 | 0 | 80 | 0 | 98 | 32 | 52.2 | 0 | 0 | 27 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 115 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 503 | 260 | 17 | 5897.78 | 12776.98 | 101.74
19:30 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 45 | 35 | 34 | 106 | 31 | 15 | 35 | 72 | 0 | 380 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 125 | 20.5 | 0 | 0 | 0 | 86 | 80 | 50 | 0 | 13 | 65 | 68 | 0 | 24 | 12 | 0 | 86 | 105 | 15 | 650 | 126 | 0 | 50 | 22 | 96 | 218 | 0 | 0 | 0 | 612 | 0 | 0 | 128 | 0 | 393 | 0 | 330 | 41 | 0 | 34 | 51 | 103 | 170 | 0 | 20 | 55 | 66 | 25 | 0 | 21 | 305 | 0 | 378 | 0 | 67 | 142 | 23 | 0 | 82 | 30 | 0 | 15 | 99 | 17 | 19 | 58 | 73 | 0 | 0 | 0 | 6811.5 | 917 | 346 | 0 | 31 | 60 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 1223.19 | 0 | 48 | 0 | 0 | 90 | 0 | 98 | 32 | 25 | 0 | 0 | 27 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 265 | 17 | 5875.19 | 12686.69
20:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 47 | 35 | 34 | 90 | 31 | 15 | 35 | 72 | 0 | 380 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 125 | 20.8 | 22 | 0 | 0 | 84 | 80 | 46 | 0 | 11 | 65 | 68 | 0 | 24 | 24 | 0 | 86 | 105 | 12 | 650 | 126 | 0 | 50 | 8 | 96 | 220 | 0 | 0 | 0 | 612 | 0 | 0 | 128 | 0 | 370 | 0 | 330 | 41 | 0 | 38 | 52 | 103 | 170 | 0 | 20 | 17 | 64 | 8 | 0 | 21 | 310 | 0 | 381 | 0 | 67 | 142 | 23 | 0 | 82 | 30 | 0 | 15 | 99 | 15 | 18 | 58 | 74 | 0 | 0 | 0 | 6743.8 | 916 | 342 | 0 | 31 | 52 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 0 | 1211.88 | 0 | 48 | 0 | 0 | 90 | 0 | 98 | 32 | 8 | 0 | 0 | 27 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 260 | 17 | 5827.88 | 12571.68 | 101.74
21:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 45 | 17 | 34 | 45 | 31 | 15 | 35 | 72 | 0 | 380 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 125 | 20.8 | 22 | 0 | 0 | 84 | 52 | 0 | 0 | 12 | 65 | 68 | 0 | 24 | 24 | 0 | 86 | 104 | 22 | 650 | 15 | 0 | 40 | 8 | 97 | 220 | 0 | 0 | 0 | 580 | 0 | 0 | 133 | 0 | 290 | 0 | 330 | 41 | 0 | 38 | 52 | 102 | 172 | 0 | 20 | 0 | 66 | 8 | 0 | 22 | 305 | 0 | 386 | 0 | 67 | 143 | 23 | 0 | 82 | 30 | 0 | 18 | 99 | 17 | 19 | 58 | 74 | 0 | 0 | 0 | 6378.8 | 916 | 338 | 0 | 31 | 52 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 0 | 1218 | 0 | 48 | 0 | 0 | 90 | 0 | 98 | 32 | 0 | 0 | 0 | 27 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 260 | 17 | 5830 | 12208.8 | 101.74
22:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 46.2 | 0 | 34 | 45 | 31 | 15 | 0 | 72 | 0 | 380 | 0 | 0 | 0 | 17 | 334 | 0 | 0 | 0 | 125 | 20.8 | 22 | 0 | 0 | 87 | 16 | 0 | 0 | 11 | 65 | 68 | 0 | 24 | 24 | 0 | 86 | 106 | 28 | 650 | 15 | 0 | 39 | 8 | 98 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 143 | 0 | 250 | 0 | 330 | 40 | 0 | 38 | 49 | 103 | 174 | 0 | 20 | 0 | 72 | 8 | 0 | 22 | 310 | 0 | 383 | 0 | 67 | 145 | 23 | 0 | 82 | 30 | 0 | 18 | 99 | 17 | 19 | 58 | 74 | 0 | 0 | 0 | 6290 | 915 | 250 | 0 | 31 | 52 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 0 | 1233 | 0 | 48 | 0 | 0 | 70 | 0 | 100 | 32 | 0 | 0 | 0 | 27 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 260 | 17 | 5749 | 12039 | 101.74
23:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 40.2 | 0 | 34 | 30 | 31 | 15 | 0 | 54 | 0 | 380 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 35 | 20.8 | 22 | 0 | 0 | 84 | 16 | 0 | 0 | 12 | 65 | 0 | 17 | 24 | 12 | 0 | 86 | 104 | 30 | 650 | 15 | 0 | 39 | 8 | 96 | 225 | 0 | 0 | 0 | 556 | 0 | 0 | 145 | 0 | 235 | 0 | 250 | 42 | 0 | 38 | 34 | 104 | 174 | 0 | 20 | 0 | 74 | 8 | 0 | 22 | 305 | 0 | 350 | 0 | 67 | 142 | 23 | 0 | 82 | 30 | 0 | 17 | 99 | 17 | 19 | 58 | 74 | 0 | 0 | 0 | 5877 | 916 | 250 | 0 | 31 | 52 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1228 | 0 | 48 | 0 | 0 | 35 | 0 | 100 | 32 | 0 | 0 | 0 | 27 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 115 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 501 | 260 | 17 | 5655 | 11532 | 101.74
Total KWH | 0 | 1079040 | 307680 | 0 | 0 | 0 | 0 | 0 | 8708400 | 0 | 0 | 259200 | 150120 | 456480 | 728640 | 518629 | 444264 | 265031 | 786240 | 0 | 8869000 | 0 | 0 | 0 | 139876 | 7808712 | 0 | 0 | 214248 | 1252800 | 310200 | 430200 | 0 | 0 | 1220673 | 356291 | 539520 | 0 | 413760 | 457773 | 595456 | 54727 | 345600 | 294720 | 21480 | 2069580 | 1630070 | 532800 | 12450909.09 | 495127 | 0 | 796800 | 190643.4 | 1848363 | 5235618 | 0 | 0 | 0 | 13516362 | 128925 | 0 | 2141090 | 0 | 8316500 | 0 | 7710000 | 895200 | 0 | 876600 | 567360 | 2416797 | 1996800 | 25200 | 448780 | 483360 | 1500480 | 265939 | 475264 | 210767 | 7572000 | 0 | 9302000 | 0 | 1344240 | 3650727 | 546936 | 0 | 1816320 | 720864 | 0 | 323000 | 2386010 | 156960 | 454800 | 1291200 | 2008320 | 13550 | 313410 | 0 | 136154431.49 | 22144000 | 8751744 | 0 | 170400 | 274944 | 912000 | 0 | 0 | 0 | 0 | 0 | 525600 | 25745460 | 0 | 27196511 | 0 | 297173 | 0 | 9120 | 546048 | 0 | 683648 | 178296 | 120514 | 413520 | 733020 | 215040 | 0 | 416256 | 4232000 | 0 | 0 | 0 | 0 | 0 | 8877163 | 0 | 24480 | 0 | 0 | 932429 | 176424 | 643977 | 0 | 0 | 0 | 36647.64 | 1102320 | 3636 | 148800 | 0 | 2610000 | 5261880 | 0 | 11425454 | 6365090.91 | 216000 | 131389595.55 | 267544027.04

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10691.03 | MW | 12:00 Hr. | Energy Generated |  |  | 267.544 |  | MKWHr.
| Day Peak Demand |  |  | 10703.57 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.55 |  | MKWHr.
| Evening Peak Generation |  |  | 12776.98 | MW | 19:00 Hr. | Energy Demand |  |  | 268.094 |  | MKWHr.
| Evening Peak Demand |  |  | 12851.98 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.7 |  | °C
| Minimum Generation of the Day |  |  | 9447.41 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 814.51 |  | MMCFD
| Maximum Generation of the Day |  |  | 12776.98 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.4604 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.1265 | 0 | 6.388 | 0 | 0 | 0.21425 | 0 | 0 | 32.7288 | Gas | 111.962 | Gas | 398577351.36
| Chattogram Zone |  |  | 5.7684 | 25.9673 | 8.8258 | 0 | 2.0696 | 0.15041 | 0 | 0.41376 | 43.1952 | Coal | 69.5033 | Coal | 456415070.9455
| Cumilla Zone |  |  | 20.6639 | 0 | 5.6905 | 0 | 0 | 0.47526 | 1.5005 | 0 | 28.3301 | HFO | 27.2436 | HFO | 488463425.546
| Mymensingh Zone |  |  | 2.0083 | 0 | 1.903 | 0 | 0 | 0.32696 | 0 | 0 | 4.2382 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.6621 | Hydro | 2.0696 | Hydro | 206958
| Khulna Zone |  |  | 8.7517 | 25.7455 | 0.44534 | 0 | 0 | 0.5256 | 23.056 | 0 | 58.5241 | Solar | 4.5988 | Solar | 72937702.4224
| Barishal Zone |  |  | 7.8719 | 17.7905 | 0.3648 | 0 | 0 | 0.003636 | 0 | 0 | 26.0309 | Import | 51.753 | Import | 305761111.76
| Rajshahi Zone |  |  | 13.1092 | 0 | 2.0498 | 0 | 0 | 1.5873 | 27.1965 | 0 | 43.9428 | Wind | 0.41376 | Wind | 6086409.6
| Rangpur Zone |  |  | 0 | 0 | 1.5764 | 0 | 0 | 1.3154 | 0 | 0 | 2.8918
| Total |  |  | 111.962 | 69.5033 | 27.2436 | 0 | 2.0696 | 4.5988 | 51.753 | 0.41376 | 267.544
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 398577351.36 |  | Hydro | 206958
|  |  |  | Coal | 456415070.9455 |  | Solar | 72937702.4224
|  |  |  | HFO | 488463425.546 |  | Import | 305761111.76
|  |  |  | HSD | 0 |  | Wind | 6086409.6
[5 empty] | Total: | 172,84,48,029 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.144 | Peak Hr Flow | 916.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52331163.72 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.1965 | Peak Hr Flow | 1216.58 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2347 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5005 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2768 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.841 | Peak Hr Flow | 2198.58 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 5 |  | 4740
|  |  |  | Chattogram |  | 0 |  | 1425
|  |  |  | Cumilla |  | 0 |  | 1225
|  |  |  | Mymensingh |  | 30 |  | 929
|  |  |  | Sylhet |  | 37 |  | 545
|  |  |  | Khulna |  | 0 |  | 1319
|  |  |  | Barishal |  | 0 |  | 380
|  |  |  | Rajshahi |  | 0 |  | 998
|  |  |  | Rangpur |  | 0 |  | 689
|  |  |  | Total |  | 72 |  | 12250
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 | 16:27 | Amnura 132/33kV S/S T-1 (406T) LT Scheduled S/D Due to Annual maintenance.
| 08:22 | 16:25 | Amnura 132/33kV S/S T-1 (406T) HT Scheduled S/D Due to Annual maintenance.
| 08:34 | 16:59 | Jaldhaka-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to For annual
maintenance work and from Jaldhaka 132/33kV end Due to Annual Maintenance
| 08:35 | 16:05 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end. and
from Bog-Sherpur 132/33kV end Due to annual maintenance
| 08:36 | 17:21 | Khagrachori 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance
| 08:36 | 17:27 | Khagrachori 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual Maintenance
| 08:37 | 14:13 | Noapara 132/33kV S/S BUS A Scheduled S/D Due to Annual Maintenance of 132kV BUS-A
| 08:44 | 14:39 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by pbs Due to
Feeder shifting.
| 08:44 | 15:46 | Madunaghat-Sikalbaha 132kV Ckt-2 Project Work S/D from Madunaghat 132/33kV end Due to
Bangladesh Army Project work.
| 08:46 | 14:37 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by pbs Due to
Feeder shifting.
| 08:48 | 12:34 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end. and from
Ghatail 132/33kV end Due to Maintenance work by Muktagacha grid.
| 08:50 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:-
| 08:52 | 14:50 | Kaliakoir 400/230/132kV S/S 230kV Bus 1 Scheduled S/D Due to Annual Maintenance
| 08:56 | 09:17 | Bheramara(GK) 132/33kV S/S TR-3 HT Tripped showing Instantaneous over current relays Due | [7 empty] | 9.0MW load
|  |  | to 33kV feeder fault | [7 empty] | interrup.
| 08:56 | 09:19 | Bheramara(GK) 132/33kV S/S TR-3 LT Tripped showing Instantaneous over current relays Due | [7 empty] | 9.0MW load
|  |  | to 33kV feeder fault | [7 empty] | interrup.
| 09:01 | 14:35 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Shutdown taken by pbs Due to
Feeder shifting.
| 09:01 | 16:42 | Faridpur 132/33kV S/S ATR-1 LT Scheduled S/D
| 09:02 | 14:30 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Shutdown taken by pbs Due to
Feeder shifting.
| 09:02 | 16:41 | Faridpur 132/33kV S/S ATR-1 HT Scheduled S/D
| 09:15 | 16:25 | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Scheduled S/D Due to Annual maintenance.
| 09:16 | 16:20 | Sreemongol 132/33kV S/S 132/33kv T-1AB HT Scheduled S/D Due to Annual maintenance.
| 09:35 | 16:50 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Annual Maintenance.
| 09:35 | 16:50 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintenance.
| 09:36 |  | Maniknagar 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual Maintenance
| 09:46 | 15:48 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Scheduled S/D Due to Annual
maintenance work
| 09:49 | 15:45 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Scheduled S/D Due to Annual
maintenance work
| 09:50 | 15:36 | Maniknagar 132/33kV S/S Motijheel Ckt-1 Scheduled S/D Due to Annual Maintenance
| 09:52 | 16:25 | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end.
| 10:38 | 16:46 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Annual
Maintenance
| 10:47 | 14:50 | Mithapukur 132/33kV S/S BUS-1 (132KV) Scheduled S/D Due to For annual maintenance work
| 12:00 |  | Day peak Generation is 10687 MW
| 12:00 |  | Day peak Generation: 10687 MW.
| 12:42 |  | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Muktagacha 132/33kV end. and from
Ghatail 132/33kVend.
|  | 13:50 | Baghabari 230/132kV S/S T-2 Bank HT is restored.
| 14:23 | 17:48 | Sylhet 132/33kV S/S T1 LT Forced S/D Due to Sylhet-Chhatak Ckt-II CB pole( Y phase)
Replacement.
| 14:24 | 17:45 | Sylhet 132/33kV S/S T1 HT Forced S/D Due to Sylhet-Chhatak Ckt-II CB pole( Y phase)
Replacement.
| 15:47 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:- FGMO OFF at 14:11
|  | 16:05 | Bakulia 132/33kV S/S T-1 (402T) HT is restored.
| 16:19 | 17:07 | Bakulia 132/33kV S/S Bus-A Forced S/D
|  | 17:00 | Savar 132/33kV S/S T-1 LT is restored.
|  | 17:00 | Savar 132/33kV S/S T-1 HT is restored.
|  | 17:03 | Meghnaghat 230/132kV S/S Meghnaghat-Aminbazar-01 is restored.
|  | 17:06 | Savar 132/33kV S/S Main Bus-II is restored.
|  | 17:10 | Savar 132/33kV S/S Bus-A is restored.
|  | 17:24 | Chandina 132/33kV S/S TR-3 HT is restored.
|  | 17:25 | Chandina 132/33kV S/S TR-3 LT is restored.
| 19:00 |  | Evening Peak Generation: 12775 MW.
| 02:35 | 03:01 | Khulna (C) S/S TR-1 425T LT Tripped showing No relays Due to 33 kV khulna Sadar PBS | [7 empty] | 18.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 02:35 | 03:12 | Khulna (C) S/S Tr-2 415 T LT Tripped showing OC IDMT relays Due to 33 KV khulna Sadar PBS | [7 empty] | 9.0MW load
|  |  | feeder fault. | [7 empty] | interrup.
| 02:35 | 03:04 | Khulna (C) S/S Tr-2 415 T HT Tripped showing No relays Due to 33KV khulna Sadar PBS | [7 empty] | 9.0MW load
|  |  | feeder fault. | [7 empty] | interrup.
| 06:00 |  | Minimum Generation: 9336 MW.
| 07:09 |  | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Scheduled S/D Due to Annual maintenance work.
| 07:11 |  | Khagrachori 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual Bay Maintenance.
| 07:13 |  | Khagrachori 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual Bay Maintenance.
| 07:31 |  | Keraniganj-Nawabganj 132kV Ckt-1 Scheduled S/D from Nawabganj 132/33kV end Due to Annual
maintenance and from Keranigonj 230/132/33kV end Due to Annual maintenance work
| 07:32 |  | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to Annual Maintenance
| 07:32 |  | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 331 | 8708400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8869000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 444264 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7808712 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47 | 259200 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 728640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265031 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 139876 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 310200 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 430200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 307680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 31 | 518629 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 456480 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1079040 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 786240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 214248 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 150120 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1252800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1682.5 | 32728760
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 190643.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128925 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 796800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2069580 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5235618 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 98 | 1848363 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 595456 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 457773 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 345600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 532800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 65 | 539520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 356291 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 54727 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 1630070 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 294720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 1220673 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 126 | 495127 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13516362 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 413760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 12450909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2396.5 | 43195197.49
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7710000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 380 | 8316500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 876600 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 895200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 133 | 2141090 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 210767 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2416797 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 186 | 1996800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1500480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 265939 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 448780 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 107 | 483360 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 25200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 567360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 475264 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1522.2 | 28330137
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 73 | 2008320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1291200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 18 | 454800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 313410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 156960 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 149 | 4238240
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1344240 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3650727 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 720864 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1816320 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2386010 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 323000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 546936 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7572000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 9302000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1129 | 27662097
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 916 | 22144000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 170400 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 70 | 274944 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 350 | 8751744 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 525600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1086 | 25745460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2491 | 58524148
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 11425454 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 148800 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2610000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 260 | 6365090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5261880 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 216000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3636 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1126 | 26030860.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 413520 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 297173 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 178296 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 185 | 4232000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 345 | 8877163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 215040 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 120514 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 683648 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 80 | 546048 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 9120 | Engine Problem
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1216.58 | 27196511 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 416256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 733020 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2076.78 | 43942789
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 89 | 643977 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36647.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 932429 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 176424 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1102320 | -
Rangpur Area Total |  |  |  |  | 950 | 204 | 2891797.64
Eastern Grid Total |  |  |  |  | 17383.855 | 6879.2 | 136154431.49
Western Grid Total |  |  |  |  | 10821.56 | 5897.78 | 131389595.55
National Grid Total |  |  |  |  | 28205.415 | 12776.98 | 267544027.04
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-11-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8791.25 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3386.8 | MW
i) Dhaka area |  |  | 4734.71 |  | MW | i) Khulna area |  |  |  | 1319 | MW
ii) Chattogram area |  |  | 1425 |  | MW | ii) Barishal area |  |  |  | 380.4 | MW
iii) Cumilla area |  |  | 1224.54 |  | MW | iii) Rajshahi area |  |  |  | 998.4 | MW
iv) Mymensingh area |  |  | 899 |  | MW | iv) Rangpur area |  |  |  | 689 | MW
v) Sylhet area |  |  | 508 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12178.05 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 80 | 18:30 | 133 | Niamatpur | 43 | 18:00
2 | AKSML | 151 | 01:00 | 68 | Ishurdi | 62 | 18:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 34 | 13:00 | 69 | Jaldhaka | 68 | 16:00 | 135 | PHP | 8 | 07:00
4 | Agargaon | 106 | 13:00 | 70 | Jamalpur | 91 | 18:30 | 136 | Pabna | 78 | 18:00
5 | Agrabad | 94 | 18:00 | 71 | Jashore | 110 | 18:00 | 137 | Palashbari | 84 | 18:30
6 | Amnura | 16 | 00:00 | 72 | Jhenaidah | 104 | 18:00 | 138 | Panchagarh | 45 | 18:00
7 | Ashuganj | 77 | 00:00 | 73 | Joydebpur | 142 | 18:30 | 139 | Patiya | 9.7 | 18:00
8 | BSRM | 192 | 02:00 | 74 | Joypurhat | 41 | 19:00 | 140 | Patuakhali | 54 | 18:00
9 | Bagerhat | 65 | 19:30 | 75 | Juldah | 16 | 10:00 | 141 | Payra | 30 | 00:00
10 | Bajitpur | 74 | 18:00 | 76 | KSRM | 27 | 08:00 | 142 | Postogola | 60 | 13:00
11 | Bakulia | 80 | 19:00 | 77 | Kabirpur | 233 | 09:00 | 143 | Purbachal | 14 | 13:00
12 | Banani | 38.8 | 14:00 | 78 | Kachua | 74 | 18:30 | 144 | Purbasadipur | 86 | 18:30
13 | Bangabhaban | 10 | 13:00 | 79 | Kallyanpur | 93 | 18:00 | 145 | Rahanpur | 21 | 18:30
14 | Barapukuria | 52 | 18:30 | 80 | Kalurghat | 46 | 12:00 | 146 | Rahim | 34 | 15:00
15 | Barguna | 16 | 00:00 | 81 | Kamrangirchar | 70 | 18:00 | 147 | Rajbari | 55 | 18:00
16 | Barishal | 99 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 124 | 18:00
17 | Barishal-230 | 82 | 18:00 | 83 | Kasba | 32 | 20:00 | 149 | Rajshahi | 86 | 18:00
18 | Baroaulia | 64 | 14:00 | 84 | Kazla | 95 | 13:00 | 150 | Rajshahi-230 | 54 | 13:00
19 | Baroirhat | 59 | 18:00 | 85 | Keranigonj | 79 | 18:30 | 151 | Ramganj | 92 | 18:00
20 | Bashundhara | 184 | 13:00 | 86 | Khagrachori | 28 | 18:30 | 152 | Rampur | 39 | 15:00
21 | BashundharaCement | 8 | 12:00 | 87 | Khulna | 73 | 13:00 | 153 | Rangamati | 16 | 18:00
22 | Beanibazar | 64 | 18:00 | 88 | Khulshi | 181 | 18:00 | 154 | Rangpur | 109 | 18:30
23 | Benapole | 47 | 18:00 | 89 | Kishoreganj | 109 | 18:00 | 155 | Ruppur | 4.2 | 12:00
24 | Bhaluka | 121 | 19:30 | 90 | Kodda | 281 | 16:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 45 | 00:00 | 91 | Kulaura | 43 | 18:30 | 157 | Saidpur | 88 | 18:30
26 | Bhangura | 28 | 18:00 | 92 | Kurigram | 46 | 19:00 | 158 | Satkhira | 98 | 18:00
27 | Bheramara(GK) | 42 | 13:00 | 93 | Kushtia | 118 | 18:30 | 159 | Satmasjid | 90 | 14:00
28 | Bhulta | 207 | 20:00 | 94 | Laksam | 28 | 18:00 | 160 | Savar | 202 | 16:00
29 | Bog-Sherpur | 48 | 18:00 | 95 | Lakshmipur | 28 | 18:00 | 161 | SevenRings | 14.89 | 00:00
30 | Bogura | 124 | 18:00 | 96 | Lalbag | 62 | 13:00 | 162 | ShahCement | 29 | 23:00
31 | Borhanuddin | 82 | 00:00 | 97 | Lalmonirhat | 47 | 18:00 | 163 | Shahjadpur | 60 | 18:00
32 | Brahmanbaria | 128 | 18:30 | 98 | MI_Cement | 15.8 | 02:00 | 164 | Shahjibazar | 113 | 18:00
33 | Cantonment | 138 | 13:00 | 99 | Madanganj | 34 | 22:00 | 165 | Shahmirpur | 52 | 18:00
34 | Chandina | 11.18 | 19:30 | 100 | Madaripur | 80 | 18:00 | 166 | Shariatpur | 67 | 00:00
35 | Chandpur | 68 | 18:30 | 101 | Madartek | 78 | 13:00 | 167 | Sherpur | 106 | 19:30
36 | Chandraghona | 35 | 18:00 | 102 | Madunaghat | 51 | 18:00 | 168 | Shikalbaha | 34 | 19:00
37 | Chapai | 42 | 19:30 | 103 | Magura | 51 | 18:00 | 169 | Shitalakhya | 74.9 | 13:00
38 | Charsaidpur | 36 | 15:00 | 104 | Mahasthangarh | 54 | 18:00 | 170 | Sholosohor | 47 | 18:00
39 | Chauddagram | 57 | 00:00 | 105 | Maijdee | 34 | 19:30 | 171 | Shyampur | 120 | 12:00
40 | Chhatak | 32 | 00:00 | 106 | Manikganj | 101 | 00:00 | 172 | Siddhirganj | 116 | 12:00
41 | Chowmuhani | 148 | 19:30 | 107 | Maniknagar | 54 | 00:00 | 173 | Sirajganj | 83 | 18:30
42 | Chuadanga | 71 | 00:00 | 108 | Matarbari | 52 | 18:30 | 174 | Sonargaon | 139 | 16:00
43 | Coxsbazar | 130 | 19:00 | 109 | Matuail | 74 | 15:00 | 175 | Sreemongol | 75 | 19:00
44 | Cumilla(N) | 116 | 19:30 | 110 | Metrorail_Motijheel | 18 | 11:00 | 176 | Sreepur | 97 | 18:00
45 | Cumilla(S) | 147 | 18:00 | 111 | Metrorail_Uttara | 7 | 19:00 | 177 | Srinagar | 39.3 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 115 | 13:00 | 178 | Sunamganj | 54 | 00:00
47 | Daudkandi | 133 | 18:00 | 113 | Mirpur | 126 | 18:00 | 179 | Sylhet | 51 | 18:00
48 | DhakaUniversity | 64 | 13:00 | 114 | Mirsorai | 11 | 18:00 | 180 | Sylhet-132 | 111 | 21:00
49 | Dhamrai | 120 | 18:00 | 115 | Mirzapur | 38 | 18:00 | 181 | TK | 22 | 18:00
50 | Dhanmondi | 117 | 13:00 | 116 | Mithapukur | 46 | 18:00 | 182 | Tangail | 136 | 17:00
51 | Dohazari | 94 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 17 | 18:00
52 | Faridpur | 123 | 19:00 | 118 | Mogbazar | 80.4 | 13:00 | 184 | Thakurgaon | 73 | 18:00
53 | Fatullah | 110 | 15:00 | 119 | Mongla | 31 | 16:00 | 185 | Tongi | 131 | 15:00
54 | Fenchuganj | 36 | 18:00 | 120 | Motijheel | 38 | 13:00 | 186 | Ullahpara | 31 | 18:00
55 | Feni | 110 | 18:30 | 121 | Muktagacha | 30 | 18:00 | 187 | Ullon | 58 | 13:00
56 | GPH | 9 | 18:30 | 122 | Munshiganj | 102 | 18:00 | 188 | Uttara | 76 | 13:00
57 | Ghatail | 78 | 18:00 | 123 | Muradnagar | 36 | 18:00 | 189 | UttaraNew | 31 | 18:30
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 174 | 19:00 | 190 | Zigatola | 64 | 13:00
59 | Ghorashal-230 | 90 | 15:00 | 125 | Naogaon | 85 | 18:30
60 | Goalpara | 30 | 18:00 | 126 | Narail | 49 | 18:00
61 | Gollamari | 72 | 18:30 | 127 | Narinda | 64 | 13:00
62 | Gopalganj | 79 | 19:30 | 128 | Narshingdi | 178 | 18:00
63 | Gulshan | 96 | 13:00 | 129 | Natore | 111 | 18:00
64 | Halishahar | 64 | 14:00 | 130 | Nawabganj | 36.8 | 00:00
65 | HaripurSBU | 137 | 01:00 | 131 | Netrakona | 114 | 20:00
66 | Hasnabad | 84 | 11:00 | 132 | New | 52 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11963.34 | 46 |  | 12011.41
1:00 | 11355.28 | 30 |  | 11386.63
2:00 | 10925.57 | 0 |  | 10925.57
3:00 | 10433.51 | 0 |  | 10433.51
4:00 | 10069.53 | 0 |  | 10069.53
5:00 | 9874.95 | 0 |  | 9874.95
6:00 | 9646.19 | 0 |  | 9646.19
7:00 | 10022.25 | 0 |  | 10022.25
8:00 | 9941.3 | 11 |  | 9952.8
9:00 | 9561.02 | 11 |  | 9572.52
10:00 | 9447.41 | 11 |  | 9458.91
11:00 | 10146.9 | 11 |  | 10158.4
12:00 | 10691.03 | 12 |  | 10703.57
13:00 | 11332.37 | 15 |  | 11348.05
14:00 | 11438.09 | 14 |  | 11452.72
15:00 | 11512.95 | 19 |  | 11532.81
16:00 | 11337.92 | 20 |  | 11358.82
17:00 | 11564.1 | 20 |  | 11585
18:00 | 12675.69 | 120 |  | 12800.69
19:00 | 12776.98 | 72 |  | 12851.98
19:30 | 12686.69 | 61 |  | 12750.69
20:00 | 12571.68 | 48 |  | 12621.68
21:00 | 12208.8 | 31 |  | 12240.8
22:00 | 12039 | 31 |  | 12071.4
23:00 | 11532 | 28 |  | 11561.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5910.7 | 6052.64 | 11963.34 | DAILY GENERATION CURVE
00:30 | 5872.7 | 5786.61 | 11659.31
01:00 | 5834.7 | 5520.58 | 11355.28 | 08-11-2025
01:30 | 5655.6 | 5484.825 | 11140.425
02:00 | 5476.5 | 5449.07 | 10925.57
02:30 | 5317.75 | 5361.79 | 10679.54
03:00 | 5159 | 5274.51 | 10433.51
03:30 | 4985.5 | 5266.02 | 10251.52
04:00 | 4812 | 5257.53 | 10069.53
04:30 | 4723.5 | 5248.74 | 9972.24
05:00 | 4635 | 5239.95 | 9874.95
05:30 | 4543 | 5217.57 | 9760.57
06:00 | 4451 | 5195.19 | 9646.19
06:30 | 4611.14 | 5223.08 | 9834.22
07:00 | 4771.28 | 5250.97 | 10022.25
07:30 | 4733.89 | 5247.885 | 9981.775
08:00 | 4696.5 | 5244.8 | 9941.3
08:30 | 4655.38 | 5095.78 | 9751.16
09:00 | 4614.26 | 4946.76 | 9561.02
09:30 | 4586.46 | 4917.755 | 9504.215
10:00 | 4558.66 | 4888.75 | 9447.41
10:30 | 4855.435 | 4941.72 | 9797.155
11:00 | 5152.21 | 4994.69 | 10146.9
11:30 | 5253.67 | 5165.295 | 10418.965
12:00 | 5355.13 | 5335.9 | 10691.03
12:30 | 5564.675 | 5447.025 | 11011.7
13:00 | 5774.22 | 5558.15 | 11332.37
13:30 | 5838.68 | 5546.55 | 11385.23
14:00 | 5903.14 | 5534.95 | 11438.09
14:30 | 5949.385 | 5526.135 | 11475.52
15:00 | 5995.63 | 5517.32 | 11512.95
15:30 | 6015.62 | 5409.815 | 11425.435
16:00 | 6035.61 | 5302.31 | 11337.92
16:30 | 6139.655 | 5311.355 | 11451.01
17:00 | 6243.7 | 5320.4 | 11564.1
17:30 | 6547.45 | 5572.445 | 12119.895
18:00 | 6851.2 | 5824.49 | 12675.69
18:30 | 6865.2 | 5861.135 | 12726.335
19:00 | 6879.2 | 5897.78 | 12776.98
19:30 | 6811.5 | 5875.19 | 12686.69
20:00 | 6743.8 | 5827.88 | 12571.68
20:30 | 6561.3 | 5828.94 | 12390.24 |  | Executive Engineer
21:00 | 6378.8 | 5830 | 12208.8 |  | Network Operation Division
21:30 | 6334.4 | 5789.5 | 12123.9
22:00 | 6290 | 5749 | 12039
22:30 | 6083.5 | 5702 | 11785.5
23:00 | 5877 | 5655 | 11532

## En-Curve
QF-LDC-12
Date | 08-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3347 | 1230 | 916 | 38 | 66 | 1228.44 | 86 | 3062 | 0 | 480 | 1503.9 | 0 | 0 | 6 | 46 | DAILY ENERGY CURVE
00:30 | 3367.5 | 1252 | 915.5 | 38 | 66 | 1224.01 | 86 | 2944.5 | 0 | 327.5 | 1424.3 | 0 | 0 | 14 | 38 | 08-11-2025
01:00 | 3388 | 1274 | 915 | 38 | 66 | 1219.58 | 86 | 2827 | 0 | 175 | 1344.7 | 0 | 0 | 22 | 30
01:30 | 3388 | 1273 | 915 | 38 | 64 | 1220.825 | 86 | 2794.5 | 0 | 137 | 1201.1 | 0 | 0 | 23 | 15 | Energy Generated | 267.544 |  | MKWHr
02:00 | 3388 | 1272 | 915 | 38 | 62 | 1222.07 | 86 | 2762 | 0 | 99 | 1057.5 | 0 | 0 | 24 | 0 | Energy not Served | 0.55 |  | MKWHr
02:30 | 3389.5 | 1280 | 915 | 38 | 60 | 1213.79 | 86 | 2774.5 | 0 | 68.5 | 831.75 | 0 | 0 | 22.5 | 0 | Total Energy Requirement | 268.094 |  | MKWHr
03:00 | 3391 | 1288 | 915 | 38 | 58 | 1205.51 | 86 | 2787 | 0 | 38 | 606 | 0 | 0 | 21 | 0
03:30 | 3397.5 | 1284.5 | 915.5 | 38 | 61 | 1208.02 | 86 | 2780.5 | 0 | 27.5 | 430.5 | 0 | 0 | 22.5 | 0
04:00 | 3404 | 1281 | 916 | 38 | 64 | 1210.53 | 86 | 2774 | 0 | 17 | 255 | 0 | 0 | 24 | 0
04:30 | 3413.5 | 1280.5 | 916 | 38 | 63 | 1196.74 | 86 | 2771.5 | 0 | 8.5 | 167 | 0 | 0 | 31.5 | 0
05:00 | 3423 | 1280 | 916 | 38 | 62 | 1182.95 | 86 | 2769 | 0 | 0 | 79 | 0 | 0 | 39 | 0
05:30 | 3366.5 | 1235.5 | 916 | 38 | 60 | 1180.07 | 86 | 2765 | 0 | 0 | 79 | 0 | 0 | 34.5 | 0
06:00 | 3310 | 1191 | 916 | 38 | 58 | 1177.19 | 86 | 2761 | 0 | 0 | 79 | 0 | 0 | 30 | 0
06:30 | 3407.5 | 1211 | 915.5 | 38 | 55 | 1167.38 | 86 | 2764.5 | 36.34 | 22.5 | 105.5 | 0 | 0 | 25 | 0
07:00 | 3505 | 1231 | 915 | 38 | 52 | 1157.57 | 86 | 2768 | 72.68 | 45 | 132 | 0 | 0 | 20 | 0
07:30 | 3319 | 1155.5 | 915.5 | 38 | 49 | 1136.785 | 86 | 2724.5 | 178.99 | 91 | 268 | 0 | 0 | 19.5 | 5.5
08:00 | 3133 | 1080 | 916 | 38 | 46 | 1116 | 86 | 2681 | 285.3 | 137 | 404 | 0 | 0 | 19 | 11
08:30 | 3118 | 1060.9 | 890.5 | 38 | 49 | 1068.5 | 86 | 2560 | 383.26 | 109.5 | 372 | 0 | 0 | 15.5 | 11
09:00 | 3103 | 1041.8 | 865 | 38 | 52 | 1021 | 86 | 2439 | 481.22 | 82 | 340 | 0 | 0 | 12 | 11
09:30 | 3144.5 | 1049.65 | 890.5 | 38 | 53 | 952.5 | 86 | 2399.5 | 550.065 | 66 | 263.5 | 0 | 0 | 11 | 11
10:00 | 3186 | 1057.5 | 916 | 38 | 54 | 884 | 86 | 2360 | 618.91 | 50 | 187 | 0 | 0 | 10 | 11
10:30 | 3345.5 | 1148 | 916 | 38 | 57 | 868.5 | 86 | 2458.5 | 648.655 | 50 | 172 | 0 | 0 | 9 | 11
11:00 | 3505 | 1238.5 | 916 | 38 | 60 | 853 | 86 | 2557 | 678.4 | 50 | 157 | 0 | 0 | 8 | 11
11:30 | 3513.5 | 1262.5 | 915.5 | 38 | 59 | 864 | 86 | 2721 | 686.465 | 68 | 195 | 0 | 0 | 10 | 11.5
12:00 | 3522 | 1286.5 | 915 | 38 | 58 | 875 | 86 | 2885 | 694.53 | 86 | 233 | 0 | 0 | 12 | 12
12:30 | 3500.5 | 1289.35 | 915 | 38 | 59 | 963.5 | 86 | 2971.5 | 648.35 | 113.5 | 412 | 0 | 0 | 15 | 13.5
13:00 | 3479 | 1292.2 | 915 | 38 | 60 | 1052 | 86 | 3058 | 602.17 | 141 | 591 | 0 | 0 | 18 | 15
13:30 | 3450 | 1261.2 | 915 | 38 | 63 | 1084.17 | 86 | 3052.5 | 576.86 | 160 | 681.5 | 0 | 0 | 17 | 14.5
14:00 | 3421 | 1230.2 | 915 | 38 | 66 | 1116.34 | 86 | 3047 | 551.55 | 179 | 772 | 0 | 0 | 16 | 14
14:30 | 3462 | 1252.1 | 915 | 38 | 65 | 1120.795 | 86 | 3061 | 469.125 | 182.5 | 807 | 0 | 0 | 17 | 16.5
15:00 | 3503 | 1274 | 915 | 38 | 64 | 1125.25 | 86 | 3075 | 386.7 | 186 | 842 | 0 | 0 | 18 | 19
15:30 | 3488 | 1279.5 | 915 | 38 | 66 | 1123.62 | 86 | 3061 | 273.315 | 209 | 868 | 0 | 0 | 18 | 19.5
16:00 | 3473 | 1285 | 915 | 38 | 68 | 1121.99 | 86 | 3047 | 159.93 | 232 | 894 | 0 | 0 | 18 | 20
16:30 | 3469 | 1271.25 | 915 | 38 | 66 | 1119.985 | 86 | 3047 | 87.025 | 326.5 | 1007.25 | 0 | 0 | 18 | 20
17:00 | 3465 | 1257.5 | 915 | 38 | 64 | 1117.98 | 86 | 3047 | 14.12 | 421 | 1120.5 | 0 | 0 | 18 | 20
17:30 | 3501.5 | 1274.5 | 916 | 38 | 69 | 1149.235 | 86 | 3064.5 | 7.06 | 603 | 1391.1 | 0 | 0 | 20 | 70
18:00 | 3538 | 1291.5 | 917 | 38 | 74 | 1180.49 | 86 | 3082 | 0 | 785 | 1661.7 | 0 | 0 | 22 | 120
18:30 | 3452 | 1267 | 916.5 | 38 | 70 | 1198.535 | 86 | 3096.5 | 0 | 794.5 | 1789.8 | 0 | 0 | 17.5 | 96
19:00 | 3366 | 1242.5 | 916 | 38 | 66 | 1216.58 | 86 | 3111 | 0 | 804 | 1917.9 | 0 | 0 | 13 | 72
19:30 | 3379 | 1248.5 | 917 | 38 | 66 | 1223.19 | 86 | 3111 | 0 | 785 | 1820 | 0 | 0 | 13 | 61
20:00 | 3358 | 1272.8 | 916 | 38 | 64 | 1211.88 | 86 | 3113 | 0 | 761 | 1740 | 0 | 0 | 11 | 48
20:30 | 3327 | 1275.8 | 916 | 38 | 65 | 1214.94 | 86 | 3096 | 0 | 735 | 1625 | 0 | 0 | 11.5 | 39.5
21:00 | 3296 | 1278.8 | 916 | 38 | 66 | 1218 | 86 | 3079 | 0 | 709 | 1510 | 0 | 0 | 12 | 31
21:30 | 3237.5 | 1284.8 | 915.5 | 38 | 69 | 1225.5 | 86 | 3082.5 | 0 | 710 | 1463.6 | 0 | 0 | 11.5 | 31
22:00 | 3179 | 1290.8 | 915 | 38 | 72 | 1233 | 86 | 3086 | 0 | 711 | 1417.2 | 0 | 0 | 11 | 31
22:30 | 3098 | 1288.8 | 915.5 | 38 | 73 | 1230.5 | 86 | 3071.5 | 0 | 605.5 | 1367.2 | 0 | 0 | 11.5 | 29.5
23:00 | 3017 | 1286.8 | 916 | 38 | 74 | 1228 | 86 | 3057 | 0 | 500 | 1317.2 | 0 | 0 | 12 | 28
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 08:00 | 372 | 12:00 | Meghnaghat | 388 | 08:00 | 374 | 12:00
Ashuganj | 400 | 09:00 | 390 | 12:00 | Payra | 413 | 09:00 | 407 | 14:00
Bhulta | 392 | 07:00 | 374 | 12:00 | Rahanpur | 411 | 10:00 | 403 | 15:00
Bibiana | 391 | 08:00 | 382 | 14:00 | Rampal | 408 | 09:00 | 397 | 15:00
BIPTC | 407 | 03:00 | 397 | 18:00
Bogura | 404 | 10:00 | 392 | 15:00
Gopalganj | 400 | 09:00 | 390 | 12:00
Kaliakoir | 379 | 08:00 | 364 | 15:00
Korerhat | 393 | 18:30 | 390 | 16:00
Madunaghat | 399 | 01:00 | 388 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 09:00 | 221 | 12:00 | Kaliakoir | 234 | 07:00 | 225 | 12:00
AKSML | 236 | 18:30 | 228 | 12:00 | Keranigonj | 229 | 08:00 | 218 | 12:00
Aminbazar | 232 | 07:00 | 222 | 12:00 | Khulna(S) | 237 | 06:00 | 229 | 14:00
Ashuganj | 233 | 08:00 | 224 | 15:00 | Korerhat | 235 | 18:30 | 233 | 16:00
Ashuganj-400 | 233 | 08:00 | 224 | 15:00 | Madunaghat | 237 | 01:00 | 229 | 11:00
Baghabari | 235 | 08:00 | 229 | 15:00 | Madunaghat-400 | 238 | 19:00 | 230 | 12:00
Barapukuria | 224 | 20:00 | 212 | 07:00 | Maniknagar | 225 | 08:00 | 216 | 12:00
Barapukuria-230 | 235 | 08:00 | 229 | 15:00 | Meghnaghat | 231 | 23:00 | 223 | 15:00
Barishal | 236 | 08:00 | 232 | 12:00 | Meghnaghat-400 | 227 | 08:00 | 218 | 12:00
Bheramara | 234 | 06:00 | 225 | 14:00 | Mirsorai | 235 | 18:30 | 224 | 16:00
Bhulta | 227 | 07:00 | 216 | 12:00 | Rajshahi | 234 | 04:00 | 225 | 13:00
Bibiana | 232 | 07:00 | 225 | 12:00 | Rampal | 235 | 09:00 | 227 | 13:00
BIPTC | 237 | 05:00 | 226 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bogura | 234 | 09:00 | 227 | 15:00 | Rampura | 225 | 08:00 | 214 | 12:00
Bogura-400 | 234 | 10:00 | 227 | 15:00 | Shikalbaha | 237 | 18:00 | 228 | 12:00
Borhanuddin | 238 | 07:00 | 234 | 00:00 | Shyampur | 228 | 08:00 | 218 | 12:00
BSRM | 233 | 18:30 | 224 | 05:00 | Siddhirganj | 226 | 05:00 | 218 | 12:00
Cumilla(N) | 228 | 08:00 | 221 | 12:00 | Sirajgonj | 240 | 09:00 | 234 | 15:00
Faridpur | 234 | 08:00 | 228 | 12:00 | Sreepur | 230 | 09:00 | 222 | 15:00
Fenchuganj | 234 | 08:00 | 228 | 15:00 | Tongi | 228 | 23:00 | 215 | 15:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 227 | 08:00 | 217 | 12:00
Gopalganj | 234 | 06:00 | 229 | 12:00
GPH | 235 | 01:00 | 228 | 05:00
Haripur | 226 | 08:00 | 217 | 12:00
Hasnabad | 228 | 07:00 | 218 | 12:00
Hathazari | 235 | 18:00 | 227 | 15:00
Ishurdi | 237 | 06:00 | 229 | 13:00
Jhenaidah | 233 | 06:00 | 224 | 13:00
Kachua | 233 | 18:00 | 221 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 131 | 07:00 | 124 | 12:00 | Lalmonirhat | 132 | 21:00 | 125 | 07:00
Agargaon | 136 | 07:00 | 129 | 12:00 | Madanganj | 131 | 13:00 | 128 | 10:00
Agrabad | 135 | 00:00 | 130 | 11:00 | Madaripur | 136 | 07:00 | 35 | 10:00
AKS | 133 | 00:00 | 130 | 12:00 | Madartek | 134 | 07:00 | 123 | 12:00
Aminbazar | 137 | 07:00 | 130 | 12:00 | Madunaghat | 137 | 01:00 | 133 | 11:00
Amnura | 141 | 10:00 | 130 | 13:00 | Magura | 137 | 06:00 | 129 | 14:00
Ashuganj | 142 | 08:00 | 136 | 12:00 | Mahasthangarh | 133 | 19:00 | 128 | 13:00
Bagerhat | 136 | 07:00 | 127 | 18:00 | Maijdee | 133 | 06:00 | 129 | 15:00
Bajitpur | 135 | 08:00 | 130 | 05:00 | Manikganj | 134 | 07:00 | 128 | 15:00
Bakulia | 139 | 18:30 | 131 | 12:00 | Maniknagar | 136 | 07:00 | 129 | 12:00
Banani | 131 | 07:00 | 124 | 12:00 | Matarbari | 125 | 09:00 | 115 | 18:00
Bangabhaban | 136 | 08:00 | 129 | 12:00 | Matuail | 131 | 08:00 | 126 | 12:00
Barapukuria | 138 | 20:00 | 127 | 07:00 | Metrorail_Motijheel | 136 | 07:00 | 129 | 12:00
Barguna | 137 | 08:00 | 134 | 14:00 | Metrorail_Uttara | 137 | 01:00 | 130 | 15:00
Barishal | 136 | 07:00 | 132 | 12:00 | Millgate | 139 | 07:00 | 131 | 12:00
Barishal-230 | 136 | 08:00 | 133 | 00:00 | Mirpur | 136 | 20:00 | 128 | 12:00
Baroaulia | 137 | 18:00 | 131 | 12:00 | Mirzapur | 132 | 08:00 | 127 | 16:00
Baroirhat | 134 | 00:00 | 129 | 15:00 | Mithapukur | 135 | 20:00 | 127 | 15:00
Bashundhara | 132 | 22:00 | 124 | 12:00 | MI_Cement | 134.7 | 08:00 | 125 | 12:00
BashundharaCement | 131 | 13:00 | 128 | 10:00 | Modern | 0 | 00:00 | 0 | 00:00
Beanibazar | 132 | 07:00 | 127 | 18:00 | Mogbazar | 133 | 07:00 | 125 | 12:00
Benapole | 133 | 05:00 | 123 | 14:00 | Mongla | 134 | 08:00 | 127 | 18:00
Bhaluka | 133 | 20:00 | 128 | 06:00 | Motijheel | 136 | 08:00 | 129 | 12:00
Bhandaria | 134 | 08:00 | 127 | 00:00 | Muktagacha | 136 | 09:00 | 123 | 18:00
Bhangura | 135 | 09:00 | 130 | 14:00 | Munshiganj | 130 | 08:00 | 125 | 12:00
Bheramara | 139 | 04:00 | 135 | 15:00 | Muradnagar | 130 | 07:00 | 124 | 15:00
Bheramara(GK) | 139 | 04:00 | 135 | 13:00 | Mymensingh | 135 | 09:00 | 121 | 18:00
Bhulta | 129 | 06:00 | 126 | 00:00 | Naogaon | 131 | 20:00 | 126 | 13:00
Bog-Sherpur | 134 | 09:00 | 129 | 16:00 | Narail | 136 | 05:00 | 128 | 14:00
Bogura | 135 | 22:00 | 129 | 13:00 | Narinda | 134 | 07:00 | 128 | 15:00
Bogura-230 | 134 | 00:00 | 129 | 15:00 | Narshingdi | 135 | 06:00 | 121 | 18:00
Brahmanbaria | 134 | 08:00 | 127 | 15:00 | Natore | 135 | 09:00 | 130 | 16:00
Cantonment | 136 | 07:00 | 129 | 12:00 | Nawabganj | 137 | 07:00 | 128 | 12:00
Chandina | 134 | 07:00 | 129 | 12:00 | Netrakona | 127 | 10:00 | 122 | 00:00
Chandpur | 140 | 18:00 | 133 | 12:00 | New | 140 | 05:00 | 132 | 12:00
Chandraghona | 137 | 00:00 | 133 | 12:00 | Niamatpur | 141 | 09:00 | 138 | 13:00
Chapai | 141 | 11:00 | 137 | 00:00 | Noapara | 137 | 08:00 | 130 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 08:00 | 125 | 12:00 | Pabna | 137 | 06:00 | 133 | 12:00
Chauddagram | 133 | 01:00 | 129 | 12:00 | Palashbari | 132 | 20:00 | 125 | 06:00
Chhatak | 129 | 08:00 | 124 | 00:00 | Panchagarh | 141 | 18:30 | 125 | 07:00
Chowmuhani | 133 | 13:00 | 130 | 01:00 | Patiya | 135 | 08:00 | 130 | 05:00
Chuadanga | 135 | 05:00 | 126 | 13:00 | Patuakhali | 137 | 09:00 | 134 | 07:00
Coxsbazar | 124 | 08:00 | 114 | 21:00 | Payra | 138 | 08:00 | 136 | 00:00
Cumilla(N) | 134 | 07:00 | 129 | 12:00 | PHP | 134 | 01:00 | 129 | 12:00
Cumilla(S) | 134 | 08:00 | 128 | 13:00 | Postogola | 135 | 07:00 | 127 | 12:00
Daganbhuiyan | 134 | 01:00 | 130 | 11:00 | Purbachal | 133 | 07:00 | 124 | 12:00
Daudkandi | 129 | 08:00 | 123 | 12:00 | Purbasadipur | 136 | 19:00 | 125 | 07:00
DhakaUniversity | 132 | 07:00 | 124 | 12:00 | Rahanpur | 141 | 20:00 | 139 | 13:00
Dhamrai | 134 | 08:00 | 127 | 12:00 | Rahanpur-400 | 142 | 10:00 | 139 | 14:00
Dhanmondi | 132 | 07:00 | 127 | 12:00 | Rahim | 132 | 08:00 | 126 | 12:00
Dohazari | 133 | 18:00 | 125 | 00:00 | Rajbari | 138 | 09:00 | 132 | 15:00
Faridpur | 137 | 06:00 | 133 | 12:00 | Rajendrapur | 133 | 09:00 | 127 | 14:00
Fatullah | 139 | 08:00 | 126 | 13:00 | Rajshahi | 135 | 06:00 | 130 | 13:00
Fenchuganj | 138 | 08:00 | 134 | 15:00 | Rajshahi-230 | 134 | 00:00 | 129 | 13:00
Feni | 133 | 01:00 | 128 | 12:00 | Ramganj | 135 | 08:00 | 130 | 04:00
Ghatail | 132 | 09:00 | 121 | 18:00 | Rampur | 135 | 19:00 | 130 | 12:00
Ghorashal | 139 | 07:00 | 132 | 12:00 | Rampura | 132 | 22:00 | 124 | 12:00
Goalpara | 137 | 08:00 | 131 | 15:00 | Rangamati | 136 | 00:00 | 131 | 12:00
Gollamari | 137 | 06:00 | 132 | 13:00 | Rangpur | 136 | 22:00 | 127 | 16:00
Gopalganj | 136 | 06:00 | 132 | 00:00 | Ruppur | 138 | 00:00 | 135 | 13:00
Gopalganj-400 | 137 | 06:00 | 134 | 12:00 | Saidpur | 135 | 20:00 | 126 | 07:00
Gulshan | 131 | 07:00 | 124 | 12:00 | Satkhira | 135 | 06:00 | 127 | 18:00
Halishahar | 136 | 00:00 | 132 | 05:00 | Satmasjid | 136 | 08:00 | 129 | 12:00
Haripur | 132 | 08:00 | 127 | 12:00 | Savar | 136 | 19:00 | 128 | 12:00
HaripurSBU | 132 | 08:00 | 127 | 12:00 | SevenRings | 140 | 08:00 | 130 | 15:00
Hasnabad | 136 | 07:00 | 128 | 12:00 | ShahCement | 131 | 08:00 | 125 | 12:00
Hathazari | 137 | 17:00 | 132 | 12:00 | Shahjadpur | 138 | 00:00 | 132 | 12:00
Ishurdi | 140 | 06:00 | 135 | 16:00 | Shahjibazar | 135 | 07:00 | 129 | 15:00
Jaldhaka | 133 | 20:00 | 122 | 07:00 | Shahmirpur | 136 | 02:00 | 132 | 12:00
Jamalpur | 134 | 09:00 | 117 | 18:00 | Shariatpur | 136 | 09:00 | 131 | 00:00
Jashore | 134 | 05:00 | 125 | 13:00 | Sherpur | 132 | 09:00 | 114 | 18:00
Jhenaidah | 138 | 06:00 | 130 | 18:00 | Shikalbaha | 125 | 09:00 | 121 | 04:00
Jhenaidah-230 | 139 | 06:00 | 131 | 13:00 | Shikalbaha-230 | 138 | 19:00 | 133 | 06:00
Joydebpur | 134 | 02:00 | 124 | 15:00 | Shitalakhya | 134.7 | 08:00 | 125 | 12:00
Joypurhat | 131 | 10:00 | 121 | 11:00 | Sholosohor | 137 | 00:00 | 132 | 12:00
Juldah | 136 | 00:00 | 133 | 11:00 | Shyampur | 137 | 21:00 | 132 | 12:00
Kabirpur | 136 | 07:00 | 127 | 06:00 | Shyampur-230 | 139 | 08:00 | 132 | 12:00
Kachua | 138 | 07:00 | 131 | 05:00 | Siddhirganj | 131 | 07:00 | 126 | 12:00
Kaliakoir | 137 | 07:00 | 130 | 12:00 | Sirajganj | 134 | 09:00 | 128 | 16:00
Kallyanpur | 137 | 08:00 | 130 | 12:00 | Sonargaon | 129 | 07:00 | 124 | 12:00
Kalurghat | 137 | 00:00 | 132 | 12:00 | Sreemongol | 134 | 07:00 | 130 | 15:00
Kamrangirchar | 135 | 06:00 | 129 | 12:00 | Sreepur | 134 | 09:00 | 130 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 136 | 07:00 | 129 | 12:00
Kasba | 131 | 08:00 | 124 | 15:00 | SSM | 140 | 00:00 | 134 | 13:00
Kazla | 136 | 09:00 | 129 | 13:00 | Sunamganj | 129 | 07:00 | 123 | 00:00
Keranigonj | 137 | 08:00 | 129 | 12:00 | Sylhet | 132 | 08:00 | 128 | 00:00
Khagrachori | 135 | 01:00 | 130 | 12:00 | Sylhet-132 | 132 | 08:00 | 129 | 00:00
Khulna | 136 | 05:00 | 131 | 18:00 | Tangail | 131 | 09:00 | 125 | 17:00
Khulna(S) | 137 | 05:00 | 132 | 18:00 | Taraganj | 134 | 00:00 | 126 | 12:00
Khulshi | 134 | 00:00 | 130 | 04:00 | Thakurgaon | 140 | 18:30 | 123 | 07:00
Kishoreganj | 134 | 07:00 | 128 | 18:00 | TK | 137 | 00:00 | 133 | 11:00
Kodda | 134 | 18:30 | 124 | 11:00 | Tongi | 139 | 04:00 | 130 | 23:00
KSRM | 136 | 00:00 | 131 | 12:00 | Ullahpara | 135 | 09:00 | 130 | 16:00
Kulaura | 137 | 08:00 | 133 | 15:00 | Ullon | 132 | 22:00 | 124 | 12:00
Kurigram | 133 | 22:00 | 123 | 07:00 | Uttara | 136 | 07:00 | 128 | 12:00
Kushtia | 138 | 03:00 | 132 | 18:00 | UttaraNew | 137 | 01:00 | 130 | 15:00
Laksam | 137 | 01:00 | 130 | 05:00 | Zigatola | 136 | 08:00 | 128 | 13:00
Lakshmipur | 134 | 06:00 | 130 | 15:00
Lalbag | 135 | 06:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division