## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-11-2025 | during | 10-11-2025 | during | 10-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 367 | 353 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 52 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 125 | 149.36 | 149.36 | 122 | 122 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 19 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 31 | 47 | 300 | 300 | 30 | 30 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 33 | 149 | 149 | 17 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 88 | 88 | 88 | 88 | 88 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 71 | 141 | 162 | 162 | 72 | 72 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1461 | 1871 | 5910.1 | 5876.1 | 1836.75 | 1891.75
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 221 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 86 | 97 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 0 | 0 | 60 | 60 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 25 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 7 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 80 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.65 | 0 | 3.31 | 0 | 3.31 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 100 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 71 | 107 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 7 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 16 | 91 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 126 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 605 | 580 | 612 | 612 | 582 | 582 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 9 | 4 | 6 | 7 | 6 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 315 | 315 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1800.65 | 2259 | 2894.03 | 2876.72 | 2053.81 | 2036.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 221 | 221 | 0 | 0 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 220 | 250 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 295 | 275 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 35 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 41 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 85 | 135 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 104 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 96 | 160 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 56 | 66 | 160 | 160 | 80 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 18.5 | 24.5 | 18.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 80 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1062 | 1354.2 | 2836.56 | 2772.56 | 2099.56 | 2035.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-11-2025 | during | 10-11-2025 | during | 10-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 29 | 33 | 157.5 | 157.5 | 108 | 108 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 18.5 | 18.5 | 18.5 | 18.5 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.62 | 0 | 47.32 | 0 | 47.32 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 154.62 | 127 | 361.92 | 312.5 | 258.92 | 209.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 68 | 68 | 68 | 68 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 15 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 376 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1178 | 1159 | 1212 | 1212 | 1168 | 1168
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 916 | 916 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 36 | 36 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 15 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 18 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1115 | 1116 | 0 | 0 | 1140 | 1140 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2403 | 2389 | 2386 | 2306 | 2771 | 2691
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 507 | 503 | 0 | 0 | 374 | 434 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 262 | 343 | 622 | 622 | 592 | 592 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1099.6 | 1209 | 1218 | 1218 | 1335 | 1395
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 55.14 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 183 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 404 | 406 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 27 | 27 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 40 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Engine Problem
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.65 | 0 | 5.65 | 0 | Low irradiation
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1067 | 1221.7 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.63 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1844.77 | 2079.9 | 3184.52 | 3017.87 | 2571.74 | 2405.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 84 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 109 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 170 | 0 | 182.71 | 0 | 182.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 209.8 | 193 | 480.51 | 262 | 368.51 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 11213.44 | 12641.1 | 20483.64 | 19853.75 | 14463.29 | 14060.4
Forecast Scenario (10-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11440 |  | 0 |  | 11440
|  |  |  | 1:00 | 10890 |  | 0 |  | 10890
|  |  |  | 2:00 | 10430 |  | 0 |  | 10430
|  |  |  | 3:00 | 10040 |  | 0 |  | 10040
|  |  |  | 4:00 | 9690 |  | 0 |  | 9690
|  |  |  | 5:00 | 9600 |  | 0 |  | 9600
|  |  |  | 6:00 | 9550 |  | 0 |  | 9550
|  |  |  | 7:00 | 10180 |  | 0 |  | 10180
|  |  |  | 8:00 | 9980 |  | 0 |  | 9980
|  |  |  | 9:00 | 9980 |  | 0 |  | 9980
|  |  |  | 10:00 | 9980 |  | 0 |  | 9980
|  |  |  | 11:00 | 10480 |  | 0 |  | 10480
|  |  |  | 12:00 | 11110 |  | 0 |  | 11110
|  |  |  | 13:00 | 11630 |  | 0 |  | 11630
|  |  |  | 14:00 | 11460 |  | 0 |  | 11460
|  |  |  | 15:00 | 11350 |  | 0 |  | 11350
|  |  |  | 16:00 | 11180 |  | 0 |  | 11180
|  |  |  | 17:00 | 11490 |  | 0 |  | 11490
|  |  |  | 18:00 | 12750 |  | 0 |  | 12750
|  |  |  | 18:30 | 12600 |  | 0 |  | 12600
|  |  |  | 19:00 | 12530 |  | 0 |  | 12530
|  |  |  | 19:30 | 12290 |  | 0 |  | 12290
|  |  |  | 20:00 | 12120 |  | 0 |  | 12120
|  |  |  | 21:00 | 11820 |  | 0 |  | 11820
|  |  |  | 22:00 | 11650 |  | 0 |  | 11650
|  |  |  | 23:00 | 11500 |  | 0 |  | 11500
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 11110.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12750.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12750.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 262.83 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:25 hrs on 10-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-11-2025 | [28 empty] | Date: | 09-11-2025 | [28 empty] | Date: | 09-11-2025 | [28 empty] | Date: | 09-11-2025 | [28 empty] | Date: | 09-11-2025 | [14 empty] | Date: | 09-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 19 | 15 | 31 | 0 | 0 | 54 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 20.8 | 21 | 0 | 0 | 91 | 0 | 0 | 0 | 16 | 65 | 0 | 0 | 12 | 12 | 0 | 86 | 107 | 37 | 650 | 0 | 0 | 24 | 8 | 99 | 226 | 0 | 0 | 0 | 577 | 0 | 0 | 145 | 0 | 285 | 0 | 250 | 42 | 0 | 38 | 33 | 104 | 200 | 0 | 20 | 0 | 70 | 0 | 0 | 22 | 310 | 0 | 350 | 0 | 67 | 150 | 23 | 0 | 82 | 30 | 0 | 17 | 99 | 0 | 19 | 58 | 74 | 0 | 0 | 0 | 5785.8 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 1221 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 260 | 17 | 5400 | 11185.8 | 101.74
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 17 | 0 | 31 | 0 | 0 | 54 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 30 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 104 | 30 | 650 | 0 | 0 | 25 | 0 | 97 | 227 | 0 | 0 | 0 | 570 | 0 | 0 | 145 | 0 | 285 | 0 | 250 | 42 | 0 | 38 | 51 | 104 | 97 | 0 | 20 | 0 | 66 | 0 | 0 | 22 | 310 | 0 | 314 | 0 | 67 | 144 | 23 | 0 | 82 | 30 | 0 | 17 | 99 | 0 | 19 | 58 | 74 | 0 | 0 | 0 | 5459 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 1225 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 502 | 260 | 17 | 5206 | 10665 | 101.74
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 54 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 34 | 32 | 650 | 0 | 0 | 0 | 0 | 97 | 226 | 0 | 0 | 0 | 577 | 0 | 0 | 100 | 0 | 300 | 0 | 250 | 43 | 0 | 38 | 69 | 108 | 52 | 0 | 20 | 0 | 58 | 0 | 0 | 0 | 300 | 0 | 336 | 0 | 67 | 145 | 23 | 0 | 82 | 30 | 0 | 17 | 99 | 0 | 19 | 58 | 74 | 0 | 0 | 0 | 5227 | 731 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 260 | 0 | 4975 | 10202 | 101.74
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 54 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 0 | 33 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 579 | 0 | 0 | 0 | 0 | 295 | 0 | 250 | 42 | 0 | 38 | 25 | 106 | 34 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 300 | 0 | 314 | 0 | 67 | 143 | 23 | 0 | 82 | 30 | 0 | 17 | 99 | 0 | 19 | 24 | 74 | 0 | 0 | 0 | 4899 | 731 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 503 | 260 | 0 | 4920 | 9819 | 101.74
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 577 | 0 | 0 | 0 | 0 | 275 | 0 | 250 | 43 | 0 | 38 | 0 | 106 | 0 | 0 | 20 | 0 | 58 | 0 | 0 | 0 | 300 | 0 | 333 | 0 | 67 | 145 | 0 | 0 | 82 | 30 | 0 | 17 | 99 | 0 | 8 | 9 | 74 | 0 | 0 | 0 | 4666 | 894 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1039 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 353 | 260 | 0 | 4804 | 9470 | 101.74
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 290 | 0 | 250 | 43 | 0 | 35 | 0 | 106 | 0 | 0 | 20 | 0 | 60 | 0 | 0 | 0 | 310 | 0 | 333 | 0 | 67 | 149 | 16 | 0 | 82 | 30 | 0 | 17 | 99 | 0 | 8 | 8 | 74 | 0 | 0 | 0 | 4713 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 991 | 0 | 1037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 310 | 260 | 0 | 4661 | 9374 | 101.74
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 38 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 295 | 0 | 250 | 43 | 0 | 35 | 0 | 106 | 0 | 0 | 20 | 0 | 54 | 0 | 0 | 0 | 315 | 0 | 333 | 0 | 67 | 158 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 0 | 8 | 8 | 74 | 0 | 0 | 0 | 4739 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 0 | 1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 310 | 260 | 0 | 4597 | 9336 | 101.74
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 17 | 19.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 10 | 10 | 0.2 | 86 | 0 | 39 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 590 | 2 | 0 | 0 | 0 | 280 | 0 | 250 | 42 | 0 | 35 | 0 | 105 | 1 | 0 | 20 | 0 | 54 | 0 | 10 | 0 | 320 | 0 | 386 | 0 | 67 | 160 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 0 | 19 | 22 | 74 | 0 | 5.42 | 0 | 4883.12 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 1044 | 0 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.89 | 9 | 0 | 0 | 5.37 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.41 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.7 | 20 | 0.06 | 0 | 0 | 110 | 220 | 0 | 408 | 260 | 0 | 5082.43 | 9965.55 | 101.74
08:00 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17.5 | 0 | 13 | 0 | 0 | 0 | 3 | 54 | 0 | 300 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 11 | 17 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.67 | 86 | 0 | 10 | 590 | 0 | 0 | 7 | 0 | 37 | 227 | 0 | 0 | 0 | 587 | 9 | 0 | 0 | 0 | 280 | 0 | 220 | 43 | 0 | 39 | 24 | 104 | 44 | 0 | 20 | 0 | 50 | 0 | 32 | 0 | 310 | 0 | 386 | 0 | 67 | 152 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 0 | 19 | 56 | 61 | 1 | 20.17 | 0 | 4863.34 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1104 | 0 | 1226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.25 | 37 | 0 | 0 | 18.02 | 181 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 1.72 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 2 | 67 | 0.2 | 0 | 0 | 110 | 180 | 0 | 407 | 260 | 0 | 5216.19 | 10079.53 | 101.74
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17.5 | 0 | 17 | 0 | 0 | 0 | 17 | 17 | 0 | 340 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 19 | 17 | 20.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.88 | 86 | 0 | 5 | 590 | 0 | 0 | 32 | 0 | 14 | 226 | 0 | 0 | 0 | 562 | 15 | 0 | 0 | 0 | 295 | 0 | 220 | 42 | 0 | 39 | 16 | 104 | 17 | 0 | 20 | 0 | 50 | 0 | 50 | 0 | 310 | 0 | 364 | 0 | 67 | 149 | 21 | 0 | 79 | 30 | 0 | 17 | 100 | 0 | 19 | 56 | 61 | 1 | 34.22 | 0 | 4863.4 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 1076 | 0 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.07 | 64 | 0 | 0 | 38.27 | 172 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 2.98 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 3.7 | 78 | 0.37 | 0 | 0 | 110 | 180 | 0 | 358 | 260 | 0 | 5219.39 | 10082.79 | 101.73
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 0 | 17 | 0 | 0 | 0 | 35 | 14 | 0 | 340 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 25 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.85 | 86 | 0 | 5 | 590 | 0 | 0 | 32 | 0 | 0 | 223 | 0 | 0 | 0 | 530 | 15 | 0 | 0 | 0 | 300 | 0 | 220 | 42 | 0 | 39 | 0 | 103 | 16 | 0 | 14 | 0 | 50 | 0 | 63 | 0 | 310 | 0 | 396 | 0 | 67 | 149 | 8 | 0 | 79 | 30 | 0 | 17 | 100 | 0 | 19 | 56 | 61 | 2 | 41.72 | 0 | 4906.07 | 915 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 1050 | 0 | 1038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.9 | 76 | 0 | 0 | 49.16 | 171 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 4.62 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5 | 143 | 0.51 | 0 | 0 | 110 | 180 | 0 | 360 | 262 | 0 | 5180.19 | 10086.26 | 101.72
11:00 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17.5 | 0 | 17 | 15 | 31 | 0 | 35 | 25 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 29 | 17 | 20.5 | 22 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.79 | 86 | 10 | 3 | 650 | 0 | 0 | 33 | 0 | 24 | 221 | 0 | 0 | 0 | 583 | 18 | 0 | 18 | 0 | 300 | 0 | 220 | 39 | 0 | 39 | 19 | 103 | 24 | 0 | 14 | 0 | 56 | 0 | 69 | 0 | 315 | 0 | 387 | 0 | 67 | 158 | 21 | 0 | 79 | 30 | 0 | 17 | 100 | 0 | 19 | 58 | 29 | 2 | 45.52 | 0 | 5209.31 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 1078 | 0 | 1046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.59 | 98 | 0 | 0 | 55.32 | 179 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 4.96 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5.8 | 175 | 0.67 | 0 | 0 | 110 | 220 | 0 | 458 | 262 | 0 | 5370.34 | 10579.65 | 101.72
12:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17.5 | 0 | 17 | 30 | 31 | 0 | 35 | 71 | 0 | 380 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 30 | 52 | 20.5 | 22 | 0 | 0 | 16 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 1.65 | 86 | 71 | 4 | 650 | 0 | 0 | 33 | 0 | 86 | 220 | 0 | 0 | 0 | 605 | 19 | 0 | 85 | 0 | 295 | 0 | 220 | 40 | 0 | 38 | 48 | 100 | 96 | 0 | 14 | 0 | 56 | 0 | 70 | 0 | 325 | 0 | 385 | 0 | 67 | 153 | 21 | 0 | 81 | 30 | 0 | 16 | 100 | 0 | 19 | 58 | 29 | 2 | 46.62 | 0 | 5656.27 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 1115 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.14 | 99 | 0 | 0 | 59.63 | 160 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 5.8 | 170 | 0.6 | 0 | 0 | 110 | 220 | 0 | 507 | 262 | 0 | 5557.17 | 11213.44 | 101.72
13:00 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17.5 | 0 | 17 | 60 | 31 | 4 | 35 | 89 | 0 | 400 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 28 | 90 | 20.5 | 21 | 0 | 0 | 74 | 45 | 4 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2.14 | 86 | 92 | 14 | 650 | 17 | 0 | 39 | 11 | 99 | 219 | 0 | 0 | 0 | 580 | 12 | 0 | 115 | 0 | 280 | 0 | 220 | 42 | 0 | 38 | 66 | 100 | 152 | 0 | 14 | 70 | 66 | 26 | 63 | 0 | 320 | 0 | 376 | 0 | 67 | 157 | 21 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 32 | 2 | 44.78 | 0 | 6114.92 | 916 | 280 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 1125 | 0 | 1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.26 | 93 | 0 | 0 | 55.47 | 175 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5.3 | 161 | 0.52 | 1 | 0 | 110 | 220 | 0 | 502 | 262 | 0 | 5620.55 | 11735.47 | 101.71
14:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17.5 | 0 | 17 | 60 | 31 | 15 | 35 | 83 | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 24 | 70 | 19.5 | 21 | 0 | 0 | 89 | 45 | 24 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2.45 | 86 | 107 | 4 | 650 | 17 | 0 | 48 | 25 | 103 | 219 | 0 | 0 | 0 | 580 | 13 | 0 | 128 | 0 | 270 | 0 | 220 | 41 | 0 | 35 | 68 | 102 | 145 | 0 | 14 | 67 | 68 | 34 | 52 | 0 | 310 | 0 | 386 | 0 | 67 | 155 | 21 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 33 | 1 | 37.17 | 0 | 6088.62 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 1113 | 2 | 1120.57 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 40.97 | 75 | 0 | 0 | 42.65 | 174 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 27 | 21 | 0 | 0 | 0 | 4.4 | 127 | 0.45 | 16 | 0 | 110 | 180 | 0 | 501 | 262 | 17 | 5479.04 | 11567.66 | 101.71
15:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 0 | 17 | 60 | 31 | 15 | 35 | 78 | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 16 | 70 | 19.5 | 21 | 0 | 0 | 89 | 45 | 24 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 1.55 | 86 | 106 | 5 | 650 | 17 | 0 | 50 | 25 | 96 | 217 | 0 | 0 | 0 | 581 | 9 | 0 | 122 | 0 | 275 | 0 | 220 | 41 | 0 | 35 | 67 | 100 | 145 | 0 | 14 | 67 | 64 | 34 | 33 | 0 | 310 | 0 | 386 | 0 | 67 | 154 | 21 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 31 | 0 | 25.87 | 0 | 6005.42 | 915 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 1110 | 8 | 1228.01 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 28.75 | 51 | 0 | 0 | 9.13 | 173 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0.84 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 106 | 0.29 | 16 | 0 | 110 | 180 | 0 | 502 | 263 | 17 | 5448.02 | 11453.44 | 101.7
16:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17.5 | 0 | 17 | 60 | 31 | 15 | 35 | 85 | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 8 | 35 | 19.5 | 21 | 0 | 0 | 91 | 45 | 24 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.64 | 86 | 98 | 3 | 650 | 17 | 0 | 50 | 25 | 95 | 218 | 0 | 0 | 0 | 582 | 5 | 0 | 128 | 0 | 275 | 0 | 220 | 40 | 0 | 35 | 69 | 100 | 147 | 0 | 14 | 68 | 64 | 34 | 14 | 1 | 315 | 0 | 387 | 0 | 67 | 156 | 21 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 33 | 0 | 10.39 | 0 | 5944.03 | 916 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 1119 | 17 | 1218.08 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 10.92 | 23 | 0 | 0 | 4.12 | 176 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0.6 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.2 | 41 | 0.12 | 16 | 0 | 110 | 180 | 0 | 502 | 263 | 17 | 5340.04 | 11284.07 | 101.7
17:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 37 | 7 | 17 | 121 | 31 | 15 | 35 | 86 | 0 | 380 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 1 | 35 | 19 | 21 | 0 | 0 | 99 | 35 | 33 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0.01 | 86 | 106 | 9 | 650 | 17 | 0 | 50 | 25 | 102 | 218 | 0 | 0 | 0 | 581 | 0 | 0 | 137 | 0 | 275 | 0 | 220 | 40 | 0 | 36 | 70 | 100 | 155 | 0 | 14 | 90 | 64 | 37 | 1 | 22 | 315 | 0 | 386 | 0 | 67 | 156 | 21 | 0 | 81 | 30 | 0 | 15 | 100 | 1 | 19 | 58 | 33 | 0 | 0.48 | 0 | 6135.49 | 916 | 250 | 0 | 2 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.95 | 1128 | 17 | 1217.97 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 12 | 25 | 1.07 | 1 | 0 | 0 | 0.54 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.07 | 0 | 0 | 43 | 1 | 5 | 0 | 0 | 0 | 0.1 | 2 | 0.01 | 16 | 0 | 110 | 220 | 0 | 502 | 265 | 17 | 5461.71 | 11597.2 | 101.7
18:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 52 | 17 | 33 | 125 | 47 | 15 | 35 | 141 | 0 | 420 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 0 | 91 | 30 | 80 | 0 | 4 | 49 | 24 | 0 | 25 | 7 | 0 | 86 | 107 | 7 | 650 | 126 | 0 | 50 | 25 | 97 | 221 | 0 | 0 | 0 | 580 | 0 | 0 | 135 | 0 | 275 | 0 | 250 | 41 | 0 | 35 | 80 | 104 | 160 | 0 | 14 | 114 | 66 | 52.2 | 0 | 28 | 310 | 0 | 376 | 0 | 67 | 156 | 24 | 0 | 81 | 30 | 0 | 15 | 100 | 17 | 19 | 58 | 33 | 0 | 0 | 0 | 6770.2 | 916 | 250 | 0 | 36 | 15 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 18 | 1221.7 | 0 | 35 | 0 | 0 | 40 | 0 | 98 | 22 | 52.2 | 0 | 0 | 22 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 109 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 503 | 343 | 17 | 5870.9 | 12641.1 | 101.69
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 48.8 | 17 | 35 | 125 | 47 | 15 | 35 | 138 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 0 | 84 | 16 | 82 | 0 | 6 | 49 | 32 | 0 | 25 | 12 | 0 | 86 | 106 | 9 | 650 | 126 | 0 | 50 | 25 | 92 | 220 | 0 | 0 | 0 | 580 | 0 | 0 | 135 | 0 | 236 | 0 | 240 | 42 | 0 | 35 | 93 | 104 | 172 | 0 | 14 | 114 | 60 | 52.2 | 0 | 28 | 305 | 0 | 349 | 0 | 67 | 145 | 24 | 0 | 81 | 30 | 0 | 18 | 100 | 17 | 19 | 58 | 34 | 0 | 0 | 0 | 6662 | 915 | 250 | 0 | 31 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 25 | 1221.36 | 0 | 47 | 0 | 0 | 50 | 0 | 98 | 30 | 52.2 | 0 | 0 | 22 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 111 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 503 | 430 | 17 | 5924.56 | 12586.56 | 101.69
19:30 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 48.4 | 17 | 35 | 90 | 47 | 15 | 35 | 138 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 0 | 82 | 16 | 50 | 0 | 8 | 66 | 38 | 0 | 25 | 24 | 0 | 86 | 106 | 5 | 650 | 90 | 0 | 50 | 25 | 90 | 222 | 0 | 0 | 0 | 570 | 0 | 0 | 143 | 0 | 243 | 0 | 240 | 42 | 0 | 35 | 61 | 104 | 121 | 0 | 14 | 15 | 68 | 52.2 | 0 | 28 | 305 | 0 | 364 | 0 | 67 | 141 | 24 | 0 | 81 | 30 | 0 | 12 | 100 | 17 | 19 | 58 | 34 | 0 | 0 | 0 | 6437.6 | 915 | 247 | 0 | 31 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 30 | 1219.85 | 0 | 48 | 0 | 0 | 50 | 0 | 98 | 30 | 16 | 0 | 0 | 22 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 115 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 502 | 470 | 17 | 5918.85 | 12356.45 | 101.69
20:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 47.5 | 17 | 35 | 90 | 47 | 15 | 35 | 139 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 0 | 82 | 16 | 38 | 0 | 10 | 65 | 31 | 0 | 25 | 24 | 0 | 86 | 102 | 13 | 650 | 35 | 0 | 50 | 8 | 90 | 221 | 0 | 0 | 0 | 564 | 0 | 0 | 142 | 0 | 250 | 0 | 240 | 42 | 0 | 38 | 64 | 104 | 135 | 0 | 20 | 0 | 64 | 16 | 0 | 28 | 300 | 0 | 356 | 0 | 67 | 140 | 24 | 0 | 81 | 30 | 0 | 18 | 100 | 17 | 19 | 58 | 34 | 0 | 0 | 0 | 6311.5 | 915 | 246 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 34 | 1237.06 | 0 | 48 | 0 | 0 | 50 | 0 | 98 | 32 | 0 | 0 | 0 | 22 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 115 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 503 | 460 | 17 | 5884.06 | 12195.56 | 101.69
21:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 50 | 17 | 34 | 90 | 47 | 15 | 35 | 138 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 19 | 21 | 0 | 0 | 30 | 16 | 0 | 0 | 12 | 65 | 31 | 8 | 25 | 24 | 0 | 86 | 34 | 2 | 650 | 0 | 0 | 50 | 0 | 96 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 145 | 0 | 250 | 0 | 240 | 42 | 0 | 38 | 65 | 104 | 128 | 0 | 20 | 0 | 64 | 0 | 0 | 29 | 310 | 0 | 386 | 0 | 67 | 150 | 24 | 0 | 81 | 30 | 0 | 18 | 100 | 17 | 19 | 58 | 34 | 0 | 0 | 0 | 6150 | 915 | 244 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 34 | 1217.46 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 50 | 50 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 488 | 17 | 5750.46 | 11900.46 | 101.69
22:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 48.8 | 17 | 35 | 90 | 47 | 15 | 35 | 81 | 0 | 380 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 70 | 13 | 21 | 0 | 0 | 30 | 16 | 0 | 0 | 8 | 65 | 31 | 17 | 25 | 24 | 0 | 86 | 34 | 26 | 650 | 0 | 0 | 50 | 0 | 96 | 226 | 0 | 0 | 0 | 574 | 0 | 0 | 145 | 0 | 245 | 0 | 240 | 42 | 0 | 38 | 62 | 105 | 128 | 0 | 20 | 0 | 62 | 0 | 0 | 7 | 305 | 0 | 360 | 0 | 67 | 145 | 24 | 0 | 81 | 30 | 0 | 15 | 100 | 17 | 19 | 58 | 34 | 0 | 0 | 0 | 5955.8 | 915 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1111 | 34 | 1219.77 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 53 | 50 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 500 | 500 | 17 | 5696.77 | 11652.57 | 101.68
23:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 48.4 | 0 | 35 | 30 | 47 | 0 | 35 | 54 | 0 | 380 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 17 | 18 | 21 | 0 | 0 | 28 | 0 | 0 | 0 | 18 | 50 | 31 | 0 | 25 | 12 | 0 | 86 | 34 | 23 | 650 | 0 | 0 | 26 | 0 | 91 | 225 | 0 | 0 | 0 | 579 | 0 | 0 | 145 | 0 | 245 | 0 | 240 | 42 | 0 | 38 | 60 | 105 | 136 | 0 | 20 | 0 | 62 | 0 | 0 | 0 | 305 | 0 | 311 | 0 | 67 | 143 | 24 | 0 | 81 | 30 | 0 | 15 | 100 | 17 | 19 | 58 | 34 | 0 | 0 | 0 | 5600.4 | 916 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 21 | 1226.92 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 52 | 35 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 520 | 17 | 5693.92 | 11294.32 | 101.68
Total KWH | 0 | 1032960 | 277440 | 0 | 0 | 0 | 0 | 0 | 8611200 | 0 | 0 | 519120 | 100080 | 459072 | 981600 | 597916 | 160797 | 532092 | 1562400 | 0 | 9276300 | 0 | 0 | 0 | 141781 | 7827531 | 0 | 0 | 189610 | 1134000 | 457200 | 514080 | 0 | 0 | 939655 | 321164 | 312000 | 0 | 273120 | 390367 | 193392 | 36992 | 203520 | 169920 | 12523 | 2080860 | 1252036 | 414720 | 15483636.36 | 373018 | 0 | 733440 | 188181 | 1568181 | 5242548 | 0 | 0 | 0 | 13865453 | 117990 | 0 | 2064145 | 0 | 6680500 | 0 | 5790000 | 998400 | 0 | 896184 | 1126080 | 2487465 | 2147520 | 0 | 407370 | 576840 | 1435200 | 290424 | 460000 | 174088 | 7566000 | 0 | 9067000 | 0 | 1585320 | 3622500 | 500664 | 0 | 1943040 | 715104 | 0 | 392000 | 2401500 | 110160 | 432600 | 1178400 | 1124160 | 12300 | 313530 | 0 | 135046389.36 | 21813090 | 6313824 | 0 | 68260 | 47868 | 912000 | 0 | 0 | 0 | 0 | 0 | 557280 | 25956360 | 216340 | 28178645 | 0 | 103737 | 0 | 0 | 543360 | 0 | 382144 | 70910 | 119203 | 347836 | 652130 | 155117 | 0 | 345744 | 4282182 | 0 | 0 | 0 | 0 | 0 | 8659709 | 0 | 16860 | 0 | 210763 | 658885 | 209538 | 646713 | 0 | 0 | 0 | 36340.92 | 1064160 | 3682 | 120096 | 0 | 2644000 | 5311240 | 0 | 11032727 | 8094545.46 | 213600 | 129988889.38 | 265035278.74

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11213.44 | MW | 12:00 Hr. | Energy Generated |  |  | 265.0353 |  | MKWHr.
| Day Peak Demand |  |  | 11213.44 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.566 |  | MKWHr.
| Evening Peak Generation |  |  | 12641.1 | MW | 18:00 Hr. | Energy Demand |  |  | 265.6013 |  | MKWHr.
| Evening Peak Demand |  |  | 12851.15 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29 |  | °C
| Minimum Generation of the Day |  |  | 9336 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 784.9 |  | MMCFD
| Maximum Generation of the Day |  |  | 12641.1 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 6.4222 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.6863 | 0 | 7.4993 | 0 | 0 | 0.18961 | 0 | 0 | 34.3752 | Gas | 105.7317 | Gas | 377388013.67
| Chattogram Zone |  |  | 5.6573 | 29.3491 | 6.6819 | 0 | 2.0809 | 0.13051 | 0 | 0.27312 | 44.1727 | Coal | 74.6435 | Coal | 486963720.5084
| Cumilla Zone |  |  | 17.2599 | 0 | 6.3791 | 0 | 0 | 0.46 | 1.4352 | 0 | 25.5342 | HFO | 25.6276 | HFO | 453531740.37
| Mymensingh Zone |  |  | 1.1242 | 0 | 1.7212 | 0 | 0 | 0.32583 | 0 | 0 | 3.1711 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.7931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7931 | Hydro | 2.0809 | Hydro | 208086
| Khulna Zone |  |  | 6.3138 | 25.9564 | 0.33247 | 0 | 0 | 0.55728 | 22.7251 | 0 | 55.885 | Solar | 4.3395 | Solar | 69436933.0672
| Barishal Zone |  |  | 7.9552 | 19.1273 | 0.3337 | 0 | 0 | 0.003682 | 0 | 0 | 27.4199 | Import | 52.3389 | Import | 310567355.1
| Rajshahi Zone |  |  | 12.9419 | 0 | 1.3745 | 0 | 0 | 1.3626 | 28.1786 | 0 | 43.8576 | Wind | 0.27312 | Wind | 4017595.2
| Rangpur Zone |  |  | 0 | 0.21076 | 1.3056 | 0 | 0 | 1.31 | 0 | 0 | 2.8264
| Total |  |  | 105.7317 | 74.6435 | 25.6276 | 0 | 2.0809 | 4.3395 | 52.3389 | 0.27312 | 265.0353
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 377388013.67 |  | Hydro | 208086
|  |  |  | Coal | 486963720.5084 |  | Solar | 69436933.0672
|  |  |  | HFO | 453531740.37 |  | Import | 310567355.1
|  |  |  | HSD | 0 |  | Wind | 4017595.2
[5 empty] | Total: | 170,21,13,443 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8131 | Peak Hr Flow | 916.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52228026.26 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.1786 | Peak Hr Flow | 1221.70 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2392 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4352 | Peak Hr Flow | 66.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2739 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.4269 | Peak Hr Flow | 2203.70 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 28 |  | 4825
|  |  |  | Chattogram |  | 31 |  | 1490
|  |  |  | Cumilla |  | 9 |  | 1103
|  |  |  | Mymensingh |  | 52 |  | 939
|  |  |  | Sylhet |  | 10 |  | 517
|  |  |  | Khulna |  | 46 |  | 1277
|  |  |  | Barishal |  | 7 |  | 342
|  |  |  | Rajshahi |  | 8 |  | 1037
|  |  |  | Rangpur |  | 10 |  | 744
|  |  |  | Total |  | 201 |  | 12274
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 10:31 | KSRM 132/33kV S/S Transformer-01 HT Forced S/D Due to For 33 KV Incoming CT Oil Leakage
Check
| 08:23 | 16:04 | Amnura 132/33kV S/S T-1 (406T) LT Scheduled S/D Due to Annual maintenance.
| 08:23 | 16:01 | Amnura 132/33kV S/S T-1 (406T) HT Scheduled S/D Due to Annual maintenance
| 08:24 | 15:20 | Sreemongol 132/33kV S/S 132/33kv T-1AB HT Scheduled S/D Due to Annual Maintanance Works.
| 08:24 | 15:20 | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Scheduled S/D Due to Annual Maintanance Works.
| 08:33 | 16:29 | Bheramara-HVDC Bheramara 230 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to
Annual maintenance and from BIPTC end Due to Annual Maintenance
| 08:33 | 13:13 | Noapara 132/33kV S/S BUS A Scheduled S/D Due to Due to annual maintenance.
| 08:34 | 16:31 | Juldah-Shahmirpur 132kV Ckt-1 Scheduled S/D from Shahmirpur 132/33kV end Due to Juldha
BUS Shutdown
| 08:34 | 16:31 | Juldah-Shahmirpur 132kV Ckt-2 Scheduled S/D from Shahmirpur 132/33kV end Due to Juldha
Grid BUS Shutdown
| 08:35 | 16:51 | Faridpur 132/33kV S/S ATR-1 LT Scheduled S/D Due to Annual Maintenance
| 08:36 | 13:13 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Scheduled S/D from Bog-Sherpur 132/33kV end Due
to Annual maintenance and from Bogura 230/132kV end Due to Annual Maintenance
| 08:36 | 16:50 | Faridpur 132/33kV S/S ATR-1 HT Scheduled S/D Due to Annual Maintenance
| 08:38 | 16:38 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end Due to Annual
maintenance
| 08:48 | 18:13 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 Scheduled S/D from Rangpur 132/33kV end
Due to Annual Maintenance work
| 08:51 | 15:51 | Gollamari 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annual Maintenance 2025
| 08:52 | 15:50 | Gollamari 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual Maintenance 2025
| 09:01 | 22:49 | Gopalganj 400/132kV S/S ATR-02 LT Scheduled S/D Due to Annual Maintenance
| 09:03 | 22:48 | Gopalganj 400/132kV S/S ATR-02 HT Scheduled S/D Due to Annual Maintenance
| 09:18 | 20:26 | Meghnaghat 400/230kV S/S 230kV BUS Section 01 Scheduled S/D Due to 230 kV Bus- 01
shutdown instructed by NLDC.
| 09:24 | 20:33 | Meghnaghat 230/132kV S/S Bus1 Project Work S/D Due to Project work.
| 09:35 | 15:58 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance work
| 09:35 | 15:58 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance work
| 09:47 | 15:39 | Barapukuria 230/132/33kV S/S 132 KV Bus Coupler Scheduled S/D Due to Annual maintenance
work
| 09:55 | 16:10 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to Annual Maintenance of Syl-Fen T line 2 Bay
| 10:09 | 16:50 | Tongi 230/132/33kV S/S Tongi-Mill Gate Ckt-2 Scheduled S/D Due to Annual maintenance work
| 10:33 | 16:45 | KSRM 132/33kV S/S Transformer-03 HT Forced S/D Due to for 33 KV Incoming CT Oil Leakage
Check
| 10:34 | 16:23 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end Due to
Annual Maintenance
| 10:40 | 16:30 | Shahjadpur 132/33kV S/S T-2(415T) HT Scheduled S/D Due to Annual Maintenance
| 10:46 | 14:45 | Mithapukur 132/33kV S/S BUS-2 (132KV) Scheduled S/D Due to Annual Maintenance.
| 10:57 | 16:56 | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to Project Work;
S/D taken by Feni 230kv GSS
| 11:44 | 12:02 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Due to OFF Load Tap Changing.
| 11:55 | 12:09 | Fatullah-Shyampur(New) 132 kV Ckt-1 Tripped from Fatullah 132/33kV end showing Zone-1 &
21-Trip relays.
| 14:38 | 15:28 | Lakshmipur 132/33kV S/S Transformer-1 HT Project Work S/D Due to 33 KV CB maintenance of
TR-01
| 14:38 | 15:28 | Lakshmipur 132/33kV S/S Transformer-1 LT Project Work S/D Due to 33 kv CB Maintenance .
|  | 15:53 | Khagrachori 132/33kV S/S TR-2 LT is restored.
|  | 15:58 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 is restored.
|  | 16:45 | Savar 132/33kV S/S Bus-B is restored.
| 16:45 |  | Payra 1320 MW PP U-2 Synchronized with remarks:- None
| 16:45 |  | Payra 1320 MW Synchronized with remarks:- unit-2
|  | 16:51 | Khagrachori 132/33kV S/S TR-2 HT is restored.
|  | 17:01 | Savar 132/33kV S/S Main Bus-I is restored.
|  | 17:05 | Savar 132/33kV S/S T-1 HT is restored.
|  | 17:05 | Savar 132/33kV S/S T-1 LT is restored.
|  | 17:15 | Keraniganj-Nawabganj 132kV Ckt-1 is restored.
| 18:00 |  | Evening peak Generation is 12640 MW
| 18:00 |  | Evening Peak Generation: 12640 MW.
|  | 20:06 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT is restored.
|  | 20:06 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT is restored.
| 03:35 |  | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing N/A relays.
| 03:35 |  | Mahasthangarh 132/33kV S/S 406T MTR1 HT Tripped showing F1- Differential Protection P632
relays.
| 05:37 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to Due to Sylhet - | [7 empty] | 46.0MW load
|  |  | Chatak CKT-1 & 2 Parallel | [7 empty] | interrup. Sylhet
132/33kV end
| 06:00 |  | Minimum Generation: 9163 MW.
| 06:00 |  | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to Due to annual maintenance | [7 empty] | 45.0MW load
interrup.
| 06:02 |  | Sunamganj 132/33kV S/S Tr-1 LT Scheduled S/D Due to Due to annual maintenance | [7 empty] | 45.0MW load
interrup.
| 07:23 |  | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
| 07:26 |  | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance
| 07:27 |  | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance
| 07:33 |  | Keraniganj-Nawabganj 132kV Ckt-2 Scheduled S/D from Nawabganj 132/33kV end Due to Due to
annual maintenance and from Keranigonj 230/132/33kV end Due to Annual maintenance work
completed.
| 07:48 |  | Gopalganj 400/132kV S/S 400kV Bus-01 Scheduled S/D Due to Annual Maintenance
| 07:56 |  | Amnura 132/33kV S/S T-2 (416T) LT Scheduled S/D Due to Annual Maintenance, Clearance from
ALDC, Bogura
| 07:57 |  | Amnura 132/33kV S/S T-2 (416T) HT Scheduled S/D Due to Annual Maintenance, Clearance
ALDC, Bogura.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 353 | 8611200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9276300 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 160797 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7827531 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 52 | 519120 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 981600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 532092 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 141781 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 457200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 514080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 277440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 47 | 597916 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 33 | 459072 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1032960 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 141 | 1562400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 189610 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 100080 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1134000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1871 | 34375179
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25 | 188181 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117990 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 733440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2080860 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5242548 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 1568181 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 193392 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 390367 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 203520 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 414720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 312000 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 12523 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 321164 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 36992 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 107 | 1252036 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 7 | 169920 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 91 | 939655 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 126 | 373018 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 13865453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 4 | 273120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15483636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2259 | 44172716.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 250 | 5790000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 275 | 6680500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 896184 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 41 | 998400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 135 | 2064145 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 174088 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2487465 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 160 | 2147520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1435200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 290424 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 407370 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 576840 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 80 | 1126080 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 460000 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1354.2 | 25534216
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 1124160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1178400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 432600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 313530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 110160 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 127 | 3171150
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1585320 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3622500 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715104 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1943040 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2401500 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 500664 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7566000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 376 | 9067000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 1159 | 27793128
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 916 | 21813090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 36 | 68260 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 15 | 47868 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6313824 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 18 | 216340 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 557280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1116 | 25956360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2389 | 55885022
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 11032727 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 120096 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2644000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 343 | 8094545.46 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5311240 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 213600 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3682 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1209 | 27419890.46
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 347836 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 103737 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 70910 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 183 | 4282182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 406 | 8659709 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 155117 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 119203 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 382144 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 40 | 543360 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Engine Problem
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16860 | Low irradiation
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1221.7 | 28178645 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 345744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 652130 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2079.9 | 43857577
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 210763 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 84 | 646713 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36340.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 109 | 658885 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 209538 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1064160 | -
Rangpur Area Total |  |  |  |  | 950 | 193 | 2826399.92
Eastern Grid Total |  |  |  |  | 17383.855 | 6770.2 | 135046389.36
Western Grid Total |  |  |  |  | 10821.56 | 5870.9 | 129988889.38
National Grid Total |  |  |  |  | 28205.415 | 12641.1 | 265035278.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8744.25 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3328.6 | MW
i) Dhaka area |  |  | 4797.24 |  | MW | i) Khulna area |  |  |  | 1231 | MW
ii) Chattogram area |  |  | 1459 |  | MW | ii) Barishal area |  |  |  | 335 | MW
iii) Cumilla area |  |  | 1094.01 |  | MW | iii) Rajshahi area |  |  |  | 1028.6 | MW
iv) Mymensingh area |  |  | 887 |  | MW | iv) Rangpur area |  |  |  | 734 | MW
v) Sylhet area |  |  | 507 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12072.85 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 79 | 19:00 | 133 | Niamatpur | 41 | 21:00
2 | AKSML | 163 | 17:00 | 68 | Ishurdi | 65 | 18:00 | 134 | Noapara | 36 | 19:00
3 | Aftabnagar | 32 | 00:00 | 69 | Jaldhaka | 61 | 18:30 | 135 | PHP | 9 | 02:00
4 | Agargaon | 109 | 13:00 | 70 | Jamalpur | 86 | 18:30 | 136 | Pabna | 78 | 18:00
5 | Agrabad | 96 | 18:00 | 71 | Jashore | 105 | 13:00 | 137 | Palashbari | 81 | 19:00
6 | Amnura | 16 | 18:00 | 72 | Jhenaidah | 94 | 18:30 | 138 | Panchagarh | 48 | 18:00
7 | Ashuganj | 68 | 14:00 | 73 | Joydebpur | 135 | 16:00 | 139 | Patiya | 9 | 00:00
8 | BSRM | 205 | 17:00 | 74 | Joypurhat | 42 | 15:00 | 140 | Patuakhali | 47 | 21:00
9 | Bagerhat | 65 | 18:00 | 75 | Juldah | 7.5 | 03:00 | 141 | Payra | 24 | 18:30
10 | Bajitpur | 65 | 18:00 | 76 | KSRM | 21 | 00:00 | 142 | Postogola | 58 | 18:00
11 | Bakulia | 94 | 15:00 | 77 | Kabirpur | 232 | 16:00 | 143 | Purbachal | 15 | 13:00
12 | Banani | 48 | 13:00 | 78 | Kachua | 68 | 18:00 | 144 | Purbasadipur | 87 | 18:30
13 | Bangabhaban | 22 | 11:00 | 79 | Kallyanpur | 90 | 18:00 | 145 | Rahanpur | 20 | 18:00
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 50 | 18:00 | 146 | Rahim | 34 | 12:00
15 | Barguna | 16 | 21:00 | 81 | Kamrangirchar | 73 | 18:00 | 147 | Rajbari | 56 | 19:00
16 | Barishal | 95 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 119 | 18:30
17 | Barishal-230 | 72 | 18:00 | 83 | Kasba | 29 | 00:00 | 149 | Rajshahi | 83 | 19:00
18 | Baroaulia | 56 | 01:00 | 84 | Kazla | 85 | 00:00 | 150 | Rajshahi-230 | 53 | 13:00
19 | Baroirhat | 52 | 18:30 | 85 | Keranigonj | 73 | 18:00 | 151 | Ramganj | 76 | 18:00
20 | Bashundhara | 165 | 13:00 | 86 | Khagrachori | 28 | 18:00 | 152 | Rampur | 40 | 18:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 77 | 13:00 | 153 | Rangamati | 16 | 18:00
22 | Beanibazar | 64 | 18:00 | 88 | Khulshi | 158 | 13:00 | 154 | Rangpur | 119 | 18:00
23 | Benapole | 44 | 18:30 | 89 | Kishoreganj | 96 | 19:00 | 155 | Ruppur | 6.4 | 15:00
24 | Bhaluka | 115 | 19:00 | 90 | Kodda | 301 | 16:00 | 156 | SSM | 5 | 23:00
25 | Bhandaria | 40 | 21:00 | 91 | Kulaura | 43 | 18:00 | 157 | Saidpur | 85 | 18:30
26 | Bhangura | 28 | 18:00 | 92 | Kurigram | 50 | 18:00 | 158 | Satkhira | 85 | 18:30
27 | Bheramara(GK) | 43 | 18:00 | 93 | Kushtia | 117 | 19:00 | 159 | Satmasjid | 91 | 14:00
28 | Bhulta | 213 | 16:00 | 94 | Laksam | 26 | 00:00 | 160 | Savar | 200 | 18:00
29 | Bog-Sherpur | 46 | 19:00 | 95 | Lakshmipur | 22 | 19:00 | 161 | SevenRings | 13.55 | 10:00
30 | Bogura | 126 | 19:00 | 96 | Lalbag | 62 | 18:30 | 162 | ShahCement | 32 | 23:00
31 | Borhanuddin | 72 | 00:00 | 97 | Lalmonirhat | 46 | 18:00 | 163 | Shahjadpur | 65 | 18:00
32 | Brahmanbaria | 110 | 00:00 | 98 | MI_Cement | 13.7 | 17:00 | 164 | Shahjibazar | 115 | 19:30
33 | Cantonment | 112 | 13:00 | 99 | Madanganj | 35 | 13:00 | 165 | Shahmirpur | 45 | 18:30
34 | Chandina | 14.01 | 18:00 | 100 | Madaripur | 74 | 18:30 | 166 | Shariatpur | 61 | 21:00
35 | Chandpur | 60 | 18:00 | 101 | Madartek | 74 | 18:30 | 167 | Sherpur | 102 | 19:30
36 | Chandraghona | 33 | 18:30 | 102 | Madunaghat | 47 | 16:00 | 168 | Shikalbaha | 30.5 | 12:00
37 | Chapai | 41 | 20:00 | 103 | Magura | 44 | 18:30 | 169 | Shitalakhya | 73.1 | 13:00
38 | Charsaidpur | 36 | 00:00 | 104 | Mahasthangarh | 52 | 18:00 | 170 | Sholosohor | 45 | 15:00
39 | Chauddagram | 50 | 18:30 | 105 | Maijdee | 26 | 00:00 | 171 | Shyampur | 118 | 12:00
40 | Chhatak | 21 | 22:00 | 106 | Manikganj | 105 | 18:30 | 172 | Siddhirganj | 109 | 18:00
41 | Chowmuhani | 129 | 21:00 | 107 | Maniknagar | 62 | 13:00 | 173 | Sirajganj | 92 | 18:30
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 46 | 00:00 | 174 | Sonargaon | 113 | 07:00
43 | Coxsbazar | 131 | 18:30 | 109 | Matuail | 72 | 12:00 | 175 | Sreemongol | 67 | 22:00
44 | Cumilla(N) | 105 | 00:00 | 110 | Metrorail_Motijheel | 18 | 09:00 | 176 | Sreepur | 95 | 15:00
45 | Cumilla(S) | 137 | 14:00 | 111 | Metrorail_Uttara | 8 | 10:00 | 177 | Srinagar | 35.4 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 122 | 12:00 | 178 | Sunamganj | 32 | 02:00
47 | Daudkandi | 126 | 19:00 | 113 | Mirpur | 120 | 15:00 | 179 | Sylhet | 49 | 18:00
48 | DhakaUniversity | 78 | 13:00 | 114 | Mirsorai | 10 | 14:00 | 180 | Sylhet-132 | 127 | 18:00
49 | Dhamrai | 122 | 18:00 | 115 | Mirzapur | 39 | 20:00 | 181 | TK | 19 | 00:00
50 | Dhanmondi | 117 | 13:00 | 116 | Mithapukur | 43 | 18:00 | 182 | Tangail | 138 | 18:00
51 | Dohazari | 86 | 00:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 19 | 18:00
52 | Faridpur | 122 | 18:00 | 118 | Mogbazar | 86.4 | 13:00 | 184 | Thakurgaon | 76 | 18:30
53 | Fatullah | 100 | 12:00 | 119 | Mongla | 40 | 12:00 | 185 | Tongi | 111 | 15:00
54 | Fenchuganj | 38 | 18:00 | 120 | Motijheel | 37 | 13:00 | 186 | Ullahpara | 30 | 18:00
55 | Feni | 101 | 18:00 | 121 | Muktagacha | 29 | 20:00 | 187 | Ullon | 55 | 18:00
56 | GPH | 76 | 22:00 | 122 | Munshiganj | 85 | 15:00 | 188 | Uttara | 75 | 13:00
57 | Ghatail | 62 | 18:00 | 123 | Muradnagar | 31 | 18:00 | 189 | UttaraNew | 27 | 18:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 177 | 18:00 | 190 | Zigatola | 60 | 13:00
59 | Ghorashal-230 | 86 | 00:00 | 125 | Naogaon | 83 | 18:00
60 | Goalpara | 30 | 18:00 | 126 | Narail | 42 | 18:00
61 | Gollamari | 70 | 18:30 | 127 | Narinda | 64 | 13:00
62 | Gopalganj | 76 | 19:30 | 128 | Narshingdi | 150 | 21:00
63 | Gulshan | 108 | 13:00 | 129 | Natore | 109 | 18:00
64 | Halishahar | 69.5 | 15:00 | 130 | Nawabganj | 33.8 | 21:00
65 | HaripurSBU | 156 | 15:00 | 131 | Netrakona | 109 | 18:30
66 | Hasnabad | 83 | 13:00 | 132 | New | 75 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11185.8 | 53 |  | 11241.19
1:00 | 10665 | 33 |  | 10699.49
2:00 | 10202 | 27 |  | 10230.22
3:00 | 9819 | 25 |  | 9845.13
4:00 | 9470 | 24 |  | 9495.08
5:00 | 9374 | 25 |  | 9400.13
6:00 | 9336 | 19 |  | 9355.86
7:00 | 9965.55 | 19 |  | 9985.41
8:00 | 10079.53 | 0 |  | 10079.53
9:00 | 10082.79 | 0 |  | 10082.79
10:00 | 10086.26 | 0 |  | 10086.26
11:00 | 10579.65 | 0 |  | 10579.65
12:00 | 11213.44 | 0 |  | 11213.44
13:00 | 11735.47 | 0 |  | 11735.47
14:00 | 11567.66 | 0 |  | 11567.66
15:00 | 11453.44 | 0 |  | 11453.44
16:00 | 11284.07 | 0 |  | 11284.07
17:00 | 11597.2 | 0 |  | 11597.2
18:00 | 12641.1 | 201 |  | 12851.15
19:00 | 12586.56 | 43 |  | 12631.5
19:30 | 12356.45 | 33 |  | 12390.94
20:00 | 12195.56 | 29 |  | 12225.87
21:00 | 11900.46 | 24 |  | 11925.54
22:00 | 11652.57 | 23 |  | 11676.57
23:00 | 11294.32 | 21 |  | 11316.32
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5785.8 | 5400 | 11185.8 | DAILY GENERATION CURVE
00:30 | 5622.4 | 5303 | 10925.4
01:00 | 5459 | 5206 | 10665 | 09-11-2025
01:30 | 5343 | 5090.5 | 10433.5
02:00 | 5227 | 4975 | 10202
02:30 | 5063 | 4947.5 | 10010.5
03:00 | 4899 | 4920 | 9819
03:30 | 4782.5 | 4862 | 9644.5
04:00 | 4666 | 4804 | 9470
04:30 | 4689.5 | 4732.5 | 9422
05:00 | 4713 | 4661 | 9374
05:30 | 4726 | 4629 | 9355
06:00 | 4739 | 4597 | 9336
06:30 | 4811.06 | 4839.715 | 9650.775
07:00 | 4883.12 | 5082.43 | 9965.55
07:30 | 4873.23 | 5149.31 | 10022.54
08:00 | 4863.34 | 5216.19 | 10079.53
08:30 | 4863.37 | 5217.79 | 10081.16
09:00 | 4863.4 | 5219.39 | 10082.79
09:30 | 4884.735 | 5199.79 | 10084.525
10:00 | 4906.07 | 5180.19 | 10086.26
10:30 | 5057.69 | 5275.265 | 10332.955
11:00 | 5209.31 | 5370.34 | 10579.65
11:30 | 5432.79 | 5463.755 | 10896.545
12:00 | 5656.27 | 5557.17 | 11213.44
12:30 | 5885.595 | 5588.86 | 11474.455
13:00 | 6114.92 | 5620.55 | 11735.47
13:30 | 6101.77 | 5549.795 | 11651.565
14:00 | 6088.62 | 5479.04 | 11567.66
14:30 | 6047.02 | 5463.53 | 11510.55
15:00 | 6005.42 | 5448.02 | 11453.44
15:30 | 5974.725 | 5394.03 | 11368.755
16:00 | 5944.03 | 5340.04 | 11284.07
16:30 | 6039.76 | 5400.875 | 11440.635
17:00 | 6135.49 | 5461.71 | 11597.2
17:30 | 6452.845 | 5666.305 | 12119.15
18:00 | 6770.2 | 5870.9 | 12641.1
18:30 | 6716.1 | 5897.73 | 12613.83
19:00 | 6662 | 5924.56 | 12586.56
19:30 | 6437.6 | 5918.85 | 12356.45
20:00 | 6311.5 | 5884.06 | 12195.56
20:30 | 6230.75 | 5817.26 | 12048.01 |  | Executive Engineer
21:00 | 6150 | 5750.46 | 11900.46 |  | Network Operation Division
21:30 | 6052.9 | 5723.615 | 11776.515
22:00 | 5955.8 | 5696.77 | 11652.57
22:30 | 5778.1 | 5695.345 | 11473.445
23:00 | 5600.4 | 5693.92 | 11294.32

## En-Curve
QF-LDC-12
Date | 09-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3106 | 1305.8 | 916 | 38 | 70 | 1221 | 86 | 3090 | 0 | 224 | 1113 | 0 | 0 | 16 | 53 | DAILY ENERGY CURVE
00:30 | 3075 | 1278.9 | 916 | 38 | 68 | 1223 | 86 | 3080 | 0 | 144 | 1000.5 | 0 | 0 | 16 | 43 | 09-11-2025
01:00 | 3044 | 1252 | 916 | 38 | 66 | 1225 | 86 | 3070 | 0 | 64 | 888 | 0 | 0 | 16 | 33
01:30 | 3072 | 1269 | 823.5 | 38 | 62 | 1223.5 | 86 | 3075 | 0 | 36 | 723 | 0 | 0 | 25.5 | 30 | Energy Generated | 265.0353 |  | MKWHr
02:00 | 3100 | 1286 | 731 | 38 | 58 | 1222 | 86 | 3080 | 0 | 8 | 558 | 0 | 0 | 35 | 27 | Energy not Served | 0.566 |  | MKWHr
02:30 | 3080 | 1285 | 731 | 38 | 61 | 1217 | 86 | 3081 | 0 | 16.5 | 377.5 | 0 | 0 | 37.5 | 26 | Total Energy Requirement | 265.6013 |  | MKWHr
03:00 | 3060 | 1284 | 731 | 38 | 64 | 1212 | 86 | 3082 | 0 | 25 | 197 | 0 | 0 | 40 | 25
03:30 | 3067 | 1275.5 | 812.5 | 38 | 61 | 1164 | 86 | 2980.5 | 0 | 21 | 107 | 0 | 0 | 32 | 24.5
04:00 | 3074 | 1267 | 894 | 38 | 58 | 1116 | 86 | 2879 | 0 | 17 | 17 | 0 | 0 | 24 | 24
04:30 | 3085.5 | 1282.5 | 905 | 38 | 59 | 1076.5 | 86 | 2835 | 0 | 17 | 16.5 | 0 | 0 | 21 | 24.5
05:00 | 3097 | 1298 | 916 | 38 | 60 | 1037 | 86 | 2791 | 0 | 17 | 16 | 0 | 0 | 18 | 25
05:30 | 3116.5 | 1305.5 | 916 | 38 | 57 | 1032.5 | 86 | 2756 | 0 | 17 | 16 | 0 | 0 | 14.5 | 22
06:00 | 3136 | 1313 | 916 | 38 | 54 | 1028 | 86 | 2721 | 0 | 17 | 16 | 0 | 0 | 11 | 19
06:30 | 3190.5 | 1315.75 | 916 | 38 | 54 | 1106 | 86 | 2836.5 | 36.525 | 17 | 47 | 0 | 0 | 7.5 | 19
07:00 | 3245 | 1318.5 | 916 | 38 | 54 | 1184 | 86 | 2952 | 73.05 | 17 | 78 | 0 | 0 | 4 | 19
07:30 | 3156.5 | 1237.25 | 916 | 38 | 52 | 1205 | 86 | 2950 | 169.04 | 24 | 184.75 | 0 | 0 | 4 | 9.5
08:00 | 3068 | 1156 | 916 | 38 | 50 | 1226 | 86 | 2948 | 265.03 | 31 | 291.5 | 0 | 0 | 4 | 0
08:30 | 3047 | 1172.4 | 916 | 38 | 50 | 1221 | 86 | 2897 | 344.26 | 40.5 | 265.5 | 0 | 0 | 3.5 | 0
09:00 | 3026 | 1188.8 | 916 | 38 | 50 | 1216 | 86 | 2846 | 423.49 | 50 | 239.5 | 0 | 0 | 3 | 0
09:30 | 3085.5 | 1178.9 | 915.5 | 38 | 50 | 1127 | 86 | 2819 | 499.625 | 50 | 231.5 | 0 | 0 | 3.5 | 0
10:00 | 3145 | 1169 | 915 | 38 | 50 | 1038 | 86 | 2792 | 575.76 | 50 | 223.5 | 0 | 0 | 4 | 0
10:30 | 3101 | 1220.25 | 915.5 | 38 | 53 | 1042 | 86 | 2911.5 | 624.705 | 59.5 | 277.5 | 0 | 0 | 4 | 0
11:00 | 3057 | 1271.5 | 916 | 38 | 56 | 1046 | 86 | 3031 | 673.65 | 69 | 331.5 | 0 | 0 | 4 | 0
11:30 | 3085 | 1276 | 916 | 38 | 56 | 1056.5 | 86 | 3085 | 675.545 | 108.5 | 507.5 | 0 | 0 | 6.5 | 0
12:00 | 3113 | 1280.5 | 916 | 38 | 56 | 1067 | 86 | 3139 | 677.44 | 148 | 683.5 | 0 | 0 | 9 | 0
12:30 | 3108.5 | 1295.5 | 916 | 38 | 61 | 1109.5 | 86 | 3129 | 652.955 | 187 | 882.5 | 0 | 0 | 8.5 | 0
13:00 | 3104 | 1310.5 | 916 | 38 | 66 | 1152 | 86 | 3119 | 628.47 | 226 | 1081.5 | 0 | 0 | 8 | 0
13:30 | 3064 | 1268.5 | 916 | 38 | 67 | 1136.285 | 86 | 3112.5 | 571.28 | 221 | 1163.5 | 0 | 0 | 7.5 | 0
14:00 | 3024 | 1226.5 | 916 | 38 | 68 | 1120.57 | 86 | 3106 | 514.09 | 216 | 1245.5 | 0 | 0 | 7 | 0
14:30 | 3013.5 | 1226.5 | 915.5 | 38 | 66 | 1174.29 | 86 | 3106 | 429.26 | 207 | 1239.5 | 0 | 0 | 9 | 0
15:00 | 3003 | 1226.5 | 915 | 38 | 64 | 1228.01 | 86 | 3106 | 344.43 | 198 | 1233.5 | 0 | 0 | 11 | 0
15:30 | 3025.5 | 1228.5 | 915.5 | 38 | 64 | 1223.045 | 86 | 3111 | 245.21 | 181 | 1243.5 | 0 | 0 | 7.5 | 0
16:00 | 3048 | 1230.5 | 916 | 38 | 64 | 1218.08 | 86 | 3116 | 145.99 | 164 | 1253.5 | 0 | 0 | 4 | 0
16:30 | 3094 | 1253.25 | 916 | 38 | 64 | 1218.025 | 86 | 3121 | 78.61 | 232.5 | 1336.75 | 0 | 0 | 2.5 | 0
17:00 | 3140 | 1276 | 916 | 38 | 64 | 1217.97 | 86 | 3126 | 11.23 | 301 | 1420 | 0 | 0 | 1 | 0
17:30 | 3139 | 1294.5 | 916 | 38 | 65 | 1219.835 | 86 | 3159 | 5.615 | 500.5 | 1693.2 | 0 | 0 | 2.5 | 100.5
18:00 | 3138 | 1313 | 916 | 38 | 66 | 1221.7 | 86 | 3192 | 0 | 700 | 1966.4 | 0 | 0 | 4 | 201
18:30 | 3049 | 1306.5 | 915.5 | 38 | 63 | 1221.53 | 86 | 3230 | 0 | 721.5 | 1977.8 | 0 | 0 | 5 | 122
19:00 | 2960 | 1300 | 915 | 38 | 60 | 1221.36 | 86 | 3268 | 0 | 743 | 1989.2 | 0 | 0 | 6 | 43
19:30 | 2986 | 1292 | 915 | 38 | 68 | 1219.85 | 86 | 3279 | 0 | 737 | 1727.6 | 0 | 0 | 8 | 33
20:00 | 2981 | 1300 | 915 | 38 | 64 | 1237.06 | 86 | 3312 | 0 | 660 | 1592.5 | 0 | 0 | 10 | 29
20:30 | 3028.5 | 1304.5 | 915 | 38 | 64 | 1227.26 | 86 | 3348.5 | 0 | 574.5 | 1450.75 | 0 | 0 | 11 | 26.5
21:00 | 3076 | 1309 | 915 | 38 | 64 | 1217.46 | 86 | 3385 | 0 | 489 | 1309 | 0 | 0 | 12 | 24
21:30 | 3050 | 1293 | 915 | 38 | 63 | 1218.615 | 86 | 3386.5 | 0 | 435 | 1281.4 | 0 | 0 | 10 | 23.5
22:00 | 3024 | 1277 | 915 | 38 | 62 | 1219.77 | 86 | 3388 | 0 | 381 | 1253.8 | 0 | 0 | 8 | 23
22:30 | 2998 | 1277 | 915.5 | 38 | 62 | 1223.345 | 86 | 3398 | 0 | 290.5 | 1172.1 | 0 | 0 | 13 | 22
23:00 | 2972 | 1277 | 916 | 38 | 62 | 1226.92 | 86 | 3408 | 0 | 200 | 1090.4 | 0 | 0 | 18 | 21
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 06:00 | 373 | 12:00 | Meghnaghat | 387 | 05:00 | 374 | 12:00
Ashuganj | 403 | 05:00 | 393 | 13:00 | Payra | 414 | 22:00 | 407 | 12:00
Bhulta | 390 | 06:00 | 373 | 12:00 | Rahanpur | 411 | 05:00 | 403 | 13:00
Bibiana | 391 | 06:00 | 382 | 12:00 | Rampal | 408 | 04:00 | 398 | 12:00
BIPTC | 409 | 02:00 | 399 | 18:00
Bogura | 403 | 05:00 | 393 | 13:00
Gopalganj | 401 | 05:00 | 390 | 12:00
Kaliakoir | 378 | 22:00 | 365 | 12:00
Korerhat | 396 | 19:00 | 387 | 11:00
Madunaghat | 398 | 19:00 | 390 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 06:00 | 222 | 12:00 | Kaliakoir | 235 | 04:00 | 226 | 12:00
AKSML | 236 | 18:00 | 228 | 10:00 | Keranigonj | 230 | 06:00 | 219 | 12:00
Aminbazar | 233 | 06:00 | 224 | 12:00 | Khulna(S) | 239 | 05:00 | 230 | 12:00
Ashuganj | 232 | 18:00 | 223 | 12:00 | Korerhat | 237 | 07:00 | 231 | 11:00
Ashuganj-400 | 232 | 18:00 | 223 | 12:00 | Madunaghat | 237 | 18:00 | 230 | 10:00
Baghabari | 235 | 22:00 | 229 | 13:00 | Madunaghat-400 | 238 | 19:00 | 231 | 04:00
Barapukuria | 223 | 00:00 | 209 | 07:00 | Maniknagar | 225 | 07:00 | 215 | 12:00
Barapukuria-230 | 223 | 00:00 | 209 | 07:00 | Meghnaghat | 231 | 08:00 | 223 | 12:00
Barishal | 237 | 05:00 | 233 | 10:00 | Meghnaghat-400 | 228 | 06:00 | 218 | 12:00
Bheramara | 233 | 02:00 | 226 | 12:00 | Mirsorai | 238 | 19:00 | 225 | 04:00
Bhulta | 227 | 06:00 | 215 | 12:00 | Rajshahi | 234 | 05:00 | 225 | 13:00
Bibiana | 232 | 02:00 | 226 | 11:00 | Rampal | 236 | 03:00 | 227 | 12:00
BIPTC | 237 | 05:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bogura | 234 | 05:00 | 228 | 13:00 | Rampura | 226 | 05:00 | 214 | 12:00
Bogura-400 | 233 | 00:00 | 227 | 13:00 | Shikalbaha | 237 | 17:00 | 228 | 10:00
Borhanuddin | 239 | 04:00 | 236 | 00:00 | Shyampur | 228 | 05:00 | 218 | 12:00
BSRM | 237 | 19:30 | 224 | 12:00 | Siddhirganj | 226 | 04:00 | 219 | 11:00
Cumilla(N) | 228 | 08:00 | 221 | 12:00 | Sirajgonj | 239 | 05:00 | 234 | 12:00
Faridpur | 235 | 06:00 | 228 | 12:00 | Sreepur | 230 | 18:00 | 222 | 16:00
Fenchuganj | 233 | 06:00 | 229 | 10:00 | Tongi | 230 | 06:00 | 221 | 11:00
Ghorashal | 234 | 23:00 | 225 | 14:00
Ghorashal-230 | 227 | 05:00 | 217 | 12:00
Gopalganj | 236 | 06:00 | 229 | 12:00
GPH | 236 | 18:00 | 227 | 12:00
Haripur | 226 | 06:00 | 216 | 12:00
Hasnabad | 229 | 04:00 | 219 | 12:00
Hathazari | 236 | 18:00 | 223 | 16:00
Ishurdi | 237 | 05:00 | 229 | 12:00
Jhenaidah | 235 | 03:00 | 225 | 13:00
Kachua | 231 | 07:00 | 225 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 125 | 12:00 | Lalmonirhat | 131 | 00:00 | 124 | 07:00
Agargaon | 137 | 06:00 | 130 | 12:00 | Madanganj | 132 | 18:30 | 127 | 12:00
Agrabad | 136 | 18:00 | 130 | 02:00 | Madaripur | 137 | 06:00 | 130 | 08:00
AKS | 133 | 18:00 | 130 | 00:00 | Madartek | 133 | 05:00 | 124 | 12:00
Aminbazar | 138 | 18:30 | 132 | 12:00 | Madunaghat | 138 | 19:30 | 133 | 04:00
Amnura | 140 | 02:00 | 130 | 13:00 | Magura | 137 | 06:00 | 130 | 12:00
Ashuganj | 140 | 02:00 | 135 | 12:00 | Mahasthangarh | 133 | 20:00 | 128 | 12:00
Bagerhat | 134 | 04:00 | 129 | 13:00 | Maijdee | 135 | 18:30 | 130 | 04:00
Bajitpur | 136 | 20:00 | 130 | 12:00 | Manikganj | 135 | 07:00 | 128 | 16:00
Bakulia | 137 | 18:00 | 131 | 03:00 | Maniknagar | 137 | 05:00 | 130 | 12:00
Banani | 134 | 07:00 | 124 | 12:00 | Matarbari | 127 | 09:00 | 114 | 01:00
Bangabhaban | 137 | 05:00 | 130 | 12:00 | Matuail | 132 | 22:00 | 125 | 12:00
Barapukuria | 137 | 00:00 | 126 | 07:00 | Metrorail_Motijheel | 137 | 05:00 | 130 | 12:00
Barguna | 137 | 04:00 | 134 | 12:00 | Metrorail_Uttara | 138 | 03:00 | 130 | 12:00
Barishal | 136 | 00:00 | 132 | 12:00 | Millgate | 139 | 04:00 | 131 | 12:00
Barishal-230 | 137 | 03:00 | 133 | 10:00 | Mirpur | 137 | 08:00 | 130 | 12:00
Baroaulia | 137 | 19:30 | 132 | 10:00 | Mirzapur | 131 | 00:00 | 127 | 12:00
Baroirhat | 136 | 19:00 | 130 | 01:00 | Mithapukur | 134 | 20:00 | 126 | 13:00
Bashundhara | 133 | 02:00 | 125 | 12:00 | MI_Cement | 135 | 05:00 | 126 | 13:00
BashundharaCement | 132 | 18:30 | 127 | 09:00 | Modern | 0 | 00:00 | 0 | 00:00
Beanibazar | 131 | 06:00 | 126 | 12:00 | Mogbazar | 135 | 03:00 | 125 | 12:00
Benapole | 135 | 02:00 | 125 | 13:00 | Mongla | 135 | 03:00 | 129 | 12:00
Bhaluka | 134 | 18:00 | 128 | 16:00 | Motijheel | 137 | 05:00 | 130 | 12:00
Bhandaria | 135 | 05:00 | 131 | 00:00 | Muktagacha | 134 | 09:00 | 123 | 17:00
Bhangura | 135 | 00:00 | 131 | 12:00 | Munshiganj | 131 | 20:00 | 123 | 12:00
Bheramara | 139 | 01:00 | 136 | 12:00 | Muradnagar | 131 | 18:00 | 126 | 11:00
Bheramara(GK) | 139 | 03:00 | 135 | 16:00 | Mymensingh | 135 | 10:00 | 121 | 17:00
Bhulta | 130 | 07:00 | 122 | 12:00 | Naogaon | 131 | 00:00 | 126 | 13:00
Bog-Sherpur | 134 | 00:00 | 129 | 12:00 | Narail | 138 | 05:00 | 130 | 13:00
Bogura | 134 | 00:00 | 130 | 12:00 | Narinda | 137 | 05:00 | 130 | 12:00
Bogura-230 | 134 | 00:00 | 130 | 07:00 | Narshingdi | 133 | 05:00 | 119 | 12:00
Brahmanbaria | 132 | 05:00 | 128 | 12:00 | Natore | 135 | 02:00 | 131 | 12:00
Cantonment | 137 | 03:00 | 130 | 12:00 | Nawabganj | 137 | 06:00 | 129 | 12:00
Chandina | 134 | 06:00 | 129 | 12:00 | Netrakona | 128 | 18:00 | 122 | 01:00
Chandpur | 140 | 17:00 | 134 | 07:00 | New | 139 | 05:00 | 131 | 16:00
Chandraghona | 138 | 18:00 | 133 | 03:00 | Niamatpur | 141 | 05:00 | 138 | 08:00
Chapai | 140 | 05:00 | 137 | 14:00 | Noapara | 137 | 05:00 | 131 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 22:00 | 125 | 12:00 | Pabna | 138 | 06:00 | 133 | 12:00
Chauddagram | 135 | 18:00 | 128 | 12:00 | Palashbari | 131 | 00:00 | 124 | 13:00
Chhatak | 129 | 06:00 | 126 | 12:00 | Panchagarh | 140 | 19:30 | 122 | 07:00
Chowmuhani | 134 | 18:30 | 130 | 00:00 | Patiya | 136 | 18:00 | 130 | 02:00
Chuadanga | 138 | 05:00 | 127 | 03:00 | Patuakhali | 138 | 17:00 | 134 | 11:00
Coxsbazar | 121 | 06:00 | 116 | 00:00 | Payra | 138 | 18:30 | 135 | 12:00
Cumilla(N) | 134 | 07:00 | 129 | 12:00 | PHP | 135 | 19:00 | 129 | 12:00
Cumilla(S) | 134 | 08:00 | 129 | 12:00 | Postogola | 136 | 04:00 | 128 | 12:00
Daganbhuiyan | 136 | 18:30 | 129 | 12:00 | Purbachal | 134 | 04:00 | 125 | 12:00
Daudkandi | 129 | 18:00 | 123 | 12:00 | Purbasadipur | 135 | 00:00 | 121 | 07:00
DhakaUniversity | 134 | 04:00 | 126 | 12:00 | Rahanpur | 141 | 20:00 | 139 | 13:00
Dhamrai | 135 | 05:00 | 128 | 12:00 | Rahanpur-400 | 144 | 21:00 | 139 | 12:00
Dhanmondi | 134.5 | 05:00 | 125 | 12:00 | Rahim | 132 | 22:00 | 126 | 12:00
Dohazari | 132 | 18:00 | 125 | 12:00 | Rajbari | 138 | 04:00 | 133 | 12:00
Faridpur | 138 | 04:00 | 133 | 13:00 | Rajendrapur | 133 | 18:00 | 127 | 11:00
Fatullah | 139 | 05:00 | 128 | 12:00 | Rajshahi | 135 | 03:00 | 130 | 12:00
Fenchuganj | 138 | 08:00 | 135 | 11:00 | Rajshahi-230 | 134 | 00:00 | 129 | 13:00
Feni | 135 | 18:00 | 129 | 12:00 | Ramganj | 136 | 19:00 | 131 | 05:00
Ghatail | 132 | 09:00 | 123 | 18:00 | Rampur | 136 | 19:00 | 130 | 03:00
Ghorashal | 138 | 17:00 | 132 | 12:00 | Rampura | 134 | 05:00 | 125 | 12:00
Goalpara | 139 | 05:00 | 133 | 12:00 | Rangamati | 136 | 18:00 | 132 | 10:00
Gollamari | 138 | 04:00 | 132 | 11:00 | Rangpur | 134 | 00:00 | 127 | 13:00
Gopalganj | 137 | 03:00 | 132 | 12:00 | Ruppur | 139 | 05:00 | 135 | 13:00
Gopalganj-400 | 138 | 03:00 | 133 | 12:00 | Saidpur | 135 | 19:00 | 124 | 13:00
Gulshan | 134 | 04:00 | 125 | 12:00 | Satkhira | 136 | 04:00 | 130 | 12:00
Halishahar | 137 | 19:00 | 129 | 12:00 | Satmasjid | 137 | 03:00 | 130 | 12:00
Haripur | 132 | 22:00 | 126 | 12:00 | Savar | 138 | 20:00 | 130 | 12:00
HaripurSBU | 132 | 22:00 | 126 | 12:00 | SevenRings | 138 | 06:00 | 131 | 12:00
Hasnabad | 137 | 07:00 | 127 | 11:00 | ShahCement | 132 | 22:00 | 125 | 12:00
Hathazari | 138 | 18:00 | 133 | 11:00 | Shahjadpur | 138 | 23:00 | 135 | 10:00
Ishurdi | 140 | 03:00 | 135 | 13:00 | Shahjibazar | 135 | 07:00 | 130 | 12:00
Jaldhaka | 134 | 19:30 | 123 | 13:00 | Shahmirpur | 137 | 18:00 | 132 | 01:00
Jamalpur | 132 | 09:00 | 117 | 17:00 | Shariatpur | 137 | 06:00 | 132 | 12:00
Jashore | 136 | 05:00 | 126 | 13:00 | Sherpur | 130 | 09:00 | 113 | 17:00
Jhenaidah | 139 | 06:00 | 131 | 13:00 | Shikalbaha | 127 | 18:00 | 120 | 03:00
Jhenaidah-230 | 140 | 05:00 | 132 | 13:00 | Shikalbaha-230 | 138 | 17:00 | 133 | 03:00
Joydebpur | 139 | 18:00 | 123 | 12:00 | Shitalakhya | 135 | 05:00 | 126.5 | 11:00
Joypurhat | 130 | 00:00 | 125 | 13:00 | Sholosohor | 137 | 18:00 | 132 | 12:00
Juldah | 137 | 19:00 | 132 | 03:00 | Shyampur | 136 | 00:00 | 130 | 13:00
Kabirpur | 136 | 06:00 | 128 | 10:00 | Shyampur-230 | 139 | 05:00 | 132 | 12:00
Kachua | 139 | 19:00 | 133 | 04:00 | Siddhirganj | 132 | 06:00 | 126 | 12:00
Kaliakoir | 137 | 05:00 | 130 | 16:00 | Sirajganj | 134 | 01:00 | 128 | 15:00
Kallyanpur | 138 | 19:30 | 132 | 12:00 | Sonargaon | 129 | 07:00 | 125 | 11:00
Kalurghat | 138 | 18:00 | 133 | 10:00 | Sreemongol | 135 | 08:00 | 130 | 12:00
Kamrangirchar | 136 | 22:00 | 129 | 12:00 | Sreepur | 134 | 05:00 | 129 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 06:00 | 129 | 12:00
Kasba | 131 | 06:00 | 125 | 12:00 | SSM | 140 | 09:00 | 132 | 12:00
Kazla | 137 | 05:00 | 129 | 13:00 | Sunamganj | 128 | 03:00 | 125 | 12:00
Keranigonj | 137 | 06:00 | 130 | 12:00 | Sylhet | 133 | 08:00 | 129 | 13:00
Khagrachori | 136 | 19:00 | 131 | 12:00 | Sylhet-132 | 132 | 08:00 | 130 | 00:00
Khulna | 138 | 04:00 | 132 | 12:00 | Tangail | 130 | 09:00 | 124 | 18:00
Khulna(S) | 139 | 05:00 | 133 | 12:00 | Taraganj | 134 | 00:00 | 125 | 13:00
Khulshi | 135 | 19:00 | 129 | 10:00 | Thakurgaon | 139 | 19:30 | 120 | 07:00
Kishoreganj | 135 | 22:00 | 128 | 12:00 | TK | 137 | 00:00 | 133 | 10:00
Kodda | 135 | 19:00 | 124 | 11:00 | Tongi | 139 | 07:00 | 134 | 11:00
KSRM | 136 | 17:00 | 130 | 10:00 | Ullahpara | 136 | 04:00 | 130 | 16:00
Kulaura | 136 | 03:00 | 134 | 00:00 | Ullon | 134 | 05:00 | 124 | 12:00
Kurigram | 132 | 00:00 | 123 | 07:00 | Uttara | 138 | 08:00 | 131 | 12:00
Kushtia | 138 | 05:00 | 133 | 13:00 | UttaraNew | 138 | 03:00 | 130 | 12:00
Laksam | 137 | 08:00 | 133 | 04:00 | Zigatola | 137 | 05:00 | 130 | 13:00
Lakshmipur | 135 | 18:00 | 131 | 00:00
Lalbag | 137 | 05:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division