## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-11-2025 | during | 11-11-2025 | during | 11-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 383 | 373 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 4 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 44.5 | 53.97 | 53.97 | 53.97 | 53.97 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 105 | 149.36 | 149.36 | 122 | 122 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 19 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 30 | 64 | 300 | 300 | 30 | 47 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 16 | 33 | 149 | 149 | 17 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 19 | 88 | 88 | 88 | 88 | 88 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 123 | 162 | 162 | 56 | 146 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0.01 | 0.01 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 30 | 142 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1417.5 | 1894.5 | 5909.1 | 5876.1 | 3134.43 | 3225.43
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 217 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 29 | 90 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 68 | 60 | 60 | 60 | 60 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 5 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.19 | 0 | 1.64 | 0 | 1.64 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 20 | 92 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 85 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 126 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 582 | 580 | 612 | 612 | 582 | 582 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 12 | 12 | 15 | 12 | 15 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 315 | 315 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1693.19 | 2229 | 2957.36 | 2944.72 | 2007.14 | 1994.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 240 | 240 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 255 | 245 | 393 | 393 | 300 | 300 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 41 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 51 | 122 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 21 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 101 | 102 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 61 | 153 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 64 | 160 | 160 | 70 | 70 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 26 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 20.84 | 24.5 | 20.84 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 67 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 20 | 73 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 951 | 1212 | 2838.9 | 2772.56 | 2203.9 | 2137.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-11-2025 | during | 11-11-2025 | during | 11-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 28 | 19 | 157.5 | 157.5 | 108 | 108 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 18 | 18 | 18.5 | 18.5 | 18.5 | 18.5 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.77 | 0 | 46.62 | 0 | 46.62 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 8 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 152.77 | 103 | 361.12 | 312.5 | 252.12 | 203.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 68 | 68 | 68 | 68 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 157 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 79 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 386 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1056 | 1077 | 1114 | 1114 | 1136 | 1136
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 909 | 909 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 42 | 42 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 42 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 208 | 190 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 16 | 105 | 105 | 0 | 34 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1040 | 1120 | 0 | 0 | 1140 | 1140 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2274 | 2351 | 2397 | 2312 | 2646 | 2595
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 404 | 501 | 0 | 0 | 374 | 434 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 27 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 820 | 830 | 1085.32 | 1085.32 | 1025 | 1025 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1554.58 | 1705 | 1681.32 | 1681.32 | 1768 | 1828
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 58.66 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 10 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 135 | 180 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 342 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 27 | 27 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 25 | 113 | 113 | 90 | 90 | Engine Problem
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Under Maintenance
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.1 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 832.03 | 1112 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.72 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1535.51 | 1827 | 3086.46 | 2919.87 | 2855.68 | 2689.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 52 | 50 | 50 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 109 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 162 | 0 | 179.13 | 0 | 179.13 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 251.6 | 259 | 526.93 | 312 | 364.93 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 10886.15 | 12657.5 | 20872.19 | 20245.07 | 16368.2 | 16037.08
Forecast Scenario (11-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11080 |  | 0 |  | 11080
|  |  |  | 1:00 | 10290 |  | 0 |  | 10290
|  |  |  | 2:00 | 9950 |  | 0 |  | 9950
|  |  |  | 3:00 | 9640 |  | 0 |  | 9640
|  |  |  | 4:00 | 9260 |  | 0 |  | 9260
|  |  |  | 5:00 | 9210 |  | 0 |  | 9210
|  |  |  | 6:00 | 9180 |  | 0 |  | 9180
|  |  |  | 7:00 | 9790 |  | 0 |  | 9790
|  |  |  | 8:00 | 10130 |  | 0 |  | 10130
|  |  |  | 9:00 | 10100 |  | 0 |  | 10100
|  |  |  | 10:00 | 10080 |  | 0 |  | 10080
|  |  |  | 11:00 | 10250 |  | 0 |  | 10250
|  |  |  | 12:00 | 10880 |  | 0 |  | 10880
|  |  |  | 13:00 | 11160 |  | 0 |  | 11160
|  |  |  | 14:00 | 11210 |  | 0 |  | 11210
|  |  |  | 15:00 | 11340 |  | 0 |  | 11340
|  |  |  | 16:00 | 10990 |  | 0 |  | 10990
|  |  |  | 17:00 | 11370 |  | 0 |  | 11370
|  |  |  | 18:00 | 12720 |  | 0 |  | 12720
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 12350 |  | 0 |  | 12350
|  |  |  | 19:30 | 11940 |  | 0 |  | 11940
|  |  |  | 20:00 | 11820 |  | 0 |  | 11820
|  |  |  | 21:00 | 11580 |  | 0 |  | 11580
|  |  |  | 22:00 | 11270 |  | 0 |  | 11270
|  |  |  | 23:00 | 12100 |  | 0 |  | 12100
Probable Maximum Temperature: |  |  | 29.00°C
Probable Maximum Demand at Day Peak: |  |  | 10880.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12720.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12720.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 257.75 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:26 hrs on 11-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-11-2025 | [28 empty] | Date: | 10-11-2025 | [28 empty] | Date: | 10-11-2025 | [28 empty] | Date: | 10-11-2025 | [28 empty] | Date: | 10-11-2025 | [14 empty] | Date: | 10-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 18 | 30 | 47 | 0 | 35 | 54 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 28 | 0 | 0 | 0 | 7 | 34 | 31 | 0 | 12 | 12 | 0 | 86 | 34 | 24 | 650 | 0 | 0 | 26 | 0 | 96 | 225 | 0 | 0 | 0 | 560 | 0 | 0 | 145 | 0 | 245 | 0 | 240 | 42 | 0 | 38 | 58 | 106 | 115 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 311 | 0 | 67 | 149 | 24 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 34 | 0 | 0 | 0 | 5424 | 916 | 234 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1111 | 17 | 1224.85 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 52 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 503 | 530 | 17 | 5634.85 | 11058.85 | 101.67
01:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 0 | 28 | 650 | 0 | 0 | 19 | 0 | 51 | 225 | 0 | 0 | 0 | 560 | 0 | 0 | 50 | 0 | 245 | 0 | 240 | 42 | 0 | 38 | 60 | 105 | 68 | 0 | 20 | 0 | 62 | 0 | 0 | 0 | 300 | 0 | 308 | 0 | 67 | 144 | 24 | 0 | 81 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 34 | 0 | 0 | 0 | 4900 | 909 | 234 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 1150.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 503 | 550 | 0 | 5376.36 | 10276.36 | 101.67
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 0 | 27 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 0 | 260 | 0 | 240 | 42 | 0 | 38 | 17 | 105 | 51 | 0 | 20 | 0 | 56 | 0 | 0 | 0 | 305 | 0 | 329 | 0 | 67 | 143 | 21 | 0 | 79 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 34 | 0 | 0 | 0 | 4728.5 | 909 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 0 | 1046.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 403 | 580 | 0 | 5203.61 | 9932.11 | 101.67
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 0 | 27 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 578 | 0 | 0 | 0 | 0 | 265 | 0 | 240 | 42 | 0 | 38 | 14 | 105 | 17 | 0 | 20 | 0 | 54 | 0 | 0 | 0 | 315 | 0 | 322 | 0 | 67 | 152 | 21 | 0 | 79 | 30 | 0 | 15 | 100 | 0 | 19 | 58 | 34 | 0 | 0 | 0 | 4723 | 909 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 938 | 0 | 923.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 300 | 640 | 0 | 4903.3 | 9626.3 | 101.66
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 28 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 525 | 0 | 0 | 0 | 0 | 280 | 0 | 240 | 43 | 0 | 38 | 0 | 105 | 0 | 0 | 20 | 0 | 50 | 0 | 0 | 0 | 310 | 0 | 313 | 0 | 67 | 143 | 21 | 0 | 11 | 30 | 0 | 15 | 100 | 0 | 19 | 8 | 34 | 0 | 0 | 0 | 4467 | 909 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 851 | 0 | 832.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 302 | 710 | 0 | 4780.37 | 9247.37 | 101.66
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 280 | 0 | 240 | 43 | 0 | 38 | 0 | 105 | 0 | 0 | 20 | 0 | 50 | 0 | 0 | 0 | 305 | 0 | 333 | 0 | 67 | 147 | 21 | 0 | 11 | 30 | 0 | 15 | 100 | 0 | 8 | 8 | 34 | 0 | 0 | 0 | 4474 | 909 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 844.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 304 | 700 | 0 | 4721.28 | 9195.28 | 101.65
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 0 | 285 | 0 | 240 | 43 | 0 | 38 | 0 | 104 | 0 | 0 | 20 | 0 | 54 | 0 | 0 | 0 | 310 | 0 | 360 | 0 | 67 | 152 | 21 | 0 | 11 | 30 | 0 | 15 | 0 | 0 | 8 | 8 | 44 | 0 | 0 | 0 | 4445 | 909 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 838.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 302 | 655 | 0 | 4718.4 | 9163.4 | 101.65
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.25 | 86 | 0 | 32 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 585 | 3 | 0 | 0 | 0 | 280 | 0 | 240 | 42 | 0 | 36 | 0 | 104 | 0 | 0 | 17 | 0 | 44 | 0 | 8 | 0 | 320 | 0 | 380 | 0 | 67 | 164 | 21 | 0 | 76 | 30 | 0 | 15 | 0 | 0 | 19 | 26 | 44 | 0 | 4.59 | 0 | 4704.84 | 909 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 881 | 0 | 898.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.81 | 9 | 0 | 0 | 4.93 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.36 | 0 | 52 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 16 | 0.06 | 0 | 0 | 110 | 220 | 0 | 404 | 675 | 0 | 5075.98 | 9780.82 | 101.65
08:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 7 | 45 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 11 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.87 | 86 | 0 | 10 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 527 | 9 | 0 | 0 | 0 | 275 | 0 | 240 | 43 | 0 | 36 | 0 | 104 | 0 | 0 | 20 | 0 | 52 | 0 | 28 | 0 | 310 | 0 | 340 | 0 | 67 | 152 | 21 | 0 | 76 | 30 | 0 | 15 | 0 | 0 | 19 | 56 | 30 | 1 | 17.32 | 0 | 4549.19 | 908 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 1085 | 0 | 1028.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.28 | 36 | 0 | 0 | 21.82 | 189 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 1.69 | 0 | 52 | 0 | 10 | 0 | 0 | 0 | 0 | 1.9 | 60 | 0.17 | 0 | 0 | 110 | 220 | 0 | 435 | 760 | 0 | 5569.17 | 10118.36 | 101.64
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 20 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2.1 | 86 | 0 | 7 | 650 | 0 | 0 | 1 | 0 | 0 | 221 | 0 | 0 | 0 | 530 | 14 | 0 | 0 | 0 | 265 | 0 | 240 | 43 | 0 | 39 | 0 | 104 | 0 | 0 | 20 | 0 | 42 | 0 | 46 | 0 | 315 | 0 | 356 | 0 | 67 | 146 | 21 | 0 | 79 | 30 | 0 | 15 | 0 | 0 | 19 | 56 | 28 | 1 | 30.38 | 0 | 4587.48 | 909 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 986 | 0 | 935.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.64 | 64 | 0 | 0 | 39.1 | 186 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 3.18 | 0 | 52 | 0 | 20 | 0 | 0 | 0 | 0 | 3.7 | 112 | 0.33 | 0 | 0 | 110 | 180 | 0 | 404 | 779 | 0 | 5500.81 | 10088.29 | 101.64
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 27 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 2.47 | 86 | 0 | 7 | 650 | 0 | 0 | 33 | 0 | 0 | 223 | 0 | 0 | 0 | 532 | 17 | 0 | 0 | 0 | 255 | 0 | 240 | 43 | 0 | 39 | 0 | 104 | 0 | 0 | 17 | 0 | 40 | 0 | 60 | 0 | 310 | 0 | 328 | 0 | 67 | 149 | 21 | 0 | 79 | 30 | 0 | 15 | 0 | 0 | 19 | 58 | 28 | 2 | 39.73 | 0 | 4638.2 | 909 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68 | 900 | 0 | 841.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.98 | 86 | 0 | 0 | 51.9 | 181 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 4.45 | 0 | 52 | 0 | 27 | 0 | 0 | 0 | 0 | 5 | 144 | 0.46 | 0 | 0 | 110 | 180 | 0 | 405 | 780 | 0 | 5430.17 | 10068.37 | 101.63
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 3 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 30 | 0 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 3.1 | 86 | 0 | 6 | 650 | 0 | 0 | 45 | 0 | 0 | 222 | 0 | 0 | 0 | 595 | 18 | 0 | 0 | 0 | 255 | 0 | 240 | 42 | 0 | 39 | 0 | 103 | 1 | 0 | 17 | 0 | 48 | 0 | 68 | 0 | 320 | 0 | 376 | 0 | 67 | 155 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 19 | 58 | 28 | 2 | 46.82 | 0 | 4848.42 | 909 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 933 | 0 | 842.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.86 | 99 | 0 | 0 | 59.71 | 135 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 5.16 | 0 | 52 | 0 | 31 | 0 | 0 | 0 | 0 | 5.7 | 164 | 0.54 | 0 | 0 | 110 | 180 | 0 | 404 | 785 | 0 | 5409.31 | 10257.73 | 101.63
12:00 | 0 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 0 | 16 | 45 | 30 | 4 | 17 | 90 | 0 | 350 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 31 | 30 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 12 | 12 | 3.19 | 86 | 20 | 7 | 650 | 0 | 0 | 46 | 0 | 29 | 221 | 0 | 0 | 0 | 582 | 19 | 0 | 51 | 0 | 255 | 0 | 240 | 40 | 0 | 38 | 20 | 101 | 61 | 1 | 17 | 0 | 58 | 0 | 69 | 0 | 320 | 0 | 365 | 0 | 67 | 157 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 18 | 58 | 28 | 2 | 46.77 | 0 | 5270.46 | 909 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 1040 | 0 | 832.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.66 | 102 | 0 | 0 | 60.72 | 135 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 5.1 | 0 | 53 | 0 | 31 | 0 | 0 | 0 | 0 | 5.6 | 162 | 0.58 | 0 | 0 | 110 | 220 | 0 | 404 | 820 | 0 | 5615.69 | 10886.15 | 101.62
13:00 | 0 | 48 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 17.5 | 0 | 22 | 75 | 47 | 15 | 35 | 108 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 30 | 90 | 19.5 | 22 | 0 | 0 | 35 | 5 | 0 | 0 | 6 | 0 | 31 | 0 | 24 | 12 | 2.89 | 86 | 91 | 15 | 650 | 0 | 0 | 46 | 0 | 96 | 218 | 0 | 0 | 0 | 520 | 17 | 0 | 120 | 0 | 255 | 0 | 240 | 40 | 0 | 34 | 49 | 100 | 123 | 8 | 17 | 52 | 66 | 25 | 60 | 0 | 310 | 0 | 302 | 0 | 67 | 152 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5502.89 | 909 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 1102 | 0 | 880.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 96 | 0 | 0 | 55.88 | 150 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 4.9 | 0 | 53 | 0 | 31 | 0 | 0 | 0 | 0 | 5.6 | 154 | 0.36 | 0 | 0 | 110 | 180 | 0 | 401 | 830 | 0 | 5657.59 | 11160.48 | 101.62
14:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17.5 | 2 | 15 | 75 | 47 | 15 | 35 | 108 | 0 | 300 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 25 | 52 | 19.5 | 22 | 0 | 0 | 90 | 16 | 0 | 0 | 9 | 0 | 38 | 0 | 24 | 12 | 2.32 | 86 | 88 | 11 | 650 | 0 | 0 | 46 | 0 | 96 | 218 | 0 | 0 | 0 | 533 | 14 | 0 | 127 | 0 | 245 | 0 | 240 | 41 | 0 | 37 | 48 | 100 | 85 | 0 | 17 | 16 | 66 | 25 | 51 | 21 | 315 | 0 | 343 | 0 | 67 | 150 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 18 | 15 | 18 | 2 | 10.54 | 0 | 5659.86 | 909 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 65 | 1000 | 0 | 884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.92 | 80 | 0 | 0 | 49.19 | 169 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 4.32 | 0 | 51 | 0 | 25 | 0 | 0 | 0 | 0 | 4.5 | 128 | 0.41 | 0 | 0 | 110 | 180 | 0 | 403 | 830 | 0 | 5550.34 | 11210.2 | 101.61
15:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17.5 | 17 | 15 | 75 | 47 | 15 | 35 | 104 | 0 | 380 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 18 | 52 | 19.5 | 22 | 0 | 0 | 99 | 16 | 0 | 0 | 7 | 0 | 48 | 0 | 24 | 12 | 1.56 | 86 | 92 | 3 | 650 | 0 | 0 | 50 | 0 | 102 | 218 | 0 | 0 | 0 | 560 | 10 | 0 | 120 | 0 | 245 | 0 | 240 | 41 | 0 | 37 | 50 | 102 | 84 | 0 | 17 | 17 | 60 | 25 | 34 | 22 | 320 | 0 | 386 | 0 | 67 | 154 | 21 | 0 | 78 | 30 | 0 | 17 | 0 | 0 | 18 | 55 | 18 | 1 | 22.65 | 0 | 5888.21 | 908 | 199 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1001 | 0 | 887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.74 | 56 | 0 | 0 | 34.62 | 176 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 2.9 | 87 | 0.26 | 0 | 0 | 110 | 220 | 0 | 405 | 830 | 0 | 5451.52 | 11339.73 | 101.61
16:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 28.4 | 17 | 15 | 75 | 47 | 15 | 35 | 102 | 0 | 380 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 8 | 52 | 19.5 | 22 | 0 | 0 | 60 | 16 | 0 | 0 | 4 | 0 | 62 | 0 | 12 | 12 | 0.64 | 86 | 68 | 5 | 650 | 0 | 0 | 50 | 0 | 80 | 218 | 0 | 0 | 0 | 560 | 4 | 0 | 80 | 0 | 245 | 0 | 240 | 41 | 0 | 37 | 48 | 100 | 82 | 0 | 17 | 16 | 60 | 25 | 14 | 21 | 310 | 0 | 390 | 0 | 67 | 152 | 21 | 0 | 78 | 30 | 0 | 17 | 0 | 0 | 18 | 57 | 18 | 1 | 8.83 | 0 | 5697.37 | 909 | 192 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 990 | 3 | 885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.09 | 23 | 0 | 0 | 12.04 | 172 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 1.33 | 0 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 1.1 | 42 | 0.12 | 1 | 0 | 110 | 220 | 0 | 405 | 830 | 0 | 5298.68 | 10996.05 | 101.61
17:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 35 | 17 | 15 | 105 | 47 | 15 | 35 | 107 | 0 | 420 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 1 | 52 | 19 | 22 | 0 | 0 | 66 | 16 | 24 | 0 | 4 | 0 | 61 | 0 | 24 | 12 | 0.01 | 86 | 66 | 5 | 650 | 50 | 0 | 50 | 1 | 63 | 217 | 0 | 0 | 0 | 560 | 0 | 0 | 85 | 0 | 245 | 0 | 240 | 42 | 0 | 37 | 52 | 100 | 92 | 0 | 17 | 16 | 60 | 25 | 1 | 21 | 315 | 0 | 396 | 0 | 67 | 156 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 1 | 18 | 58 | 19 | 0 | 0.5 | 0 | 5876.51 | 909 | 194 | 0 | 28 | 10 | 38 | 0 | 0 | 0 | 0 | 0 | 2.57 | 1042 | 9 | 1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 3 | 10 | 0 | 0.94 | 178 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0.08 | 0 | 52 | 35 | 1 | 30 | 0 | 0 | 0 | 0.1 | 2 | 0.02 | 16 | 0 | 110 | 220 | 0 | 405 | 830 | 0 | 5496.62 | 11373.13 | 101.6
18:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 44.5 | 17 | 33 | 105 | 64 | 15 | 35 | 123 | 0 | 450 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 0 | 85 | 16 | 50 | 0 | 12 | 49 | 68 | 0 | 24 | 12 | 0 | 86 | 92 | 5 | 650 | 126 | 0 | 50 | 17 | 90 | 217 | 0 | 0 | 0 | 580 | 0 | 0 | 122 | 0 | 245 | 0 | 240 | 41 | 0 | 38 | 73 | 102 | 153 | 0 | 20 | 67 | 64 | 26 | 0 | 21 | 320 | 0 | 386 | 0 | 67 | 157 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 8 | 18 | 58 | 19 | 0 | 0 | 0 | 6515.5 | 909 | 190 | 0 | 36 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 16 | 1112 | 0 | 48 | 0 | 0 | 25 | 0 | 0 | 10 | 8 | 0 | 0 | 30 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 109 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 110 | 220 | 0 | 501 | 830 | 17 | 6142 | 12657.5 | 101.6
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 51 | 18 | 33 | 105 | 64 | 15 | 35 | 107 | 0 | 450 | 0 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 108 | 19 | 22 | 0 | 0 | 30 | 16 | 31 | 0 | 19 | 49 | 61 | 0 | 24 | 12 | 0 | 86 | 65 | 10 | 650 | 30 | 0 | 40 | 25.5 | 91 | 222 | 0 | 0 | 0 | 570 | 0 | 0 | 110 | 0 | 245 | 0 | 240 | 41 | 0 | 38 | 87 | 102 | 120 | 0 | 20 | 17 | 58 | 25 | 0 | 18 | 310 | 0 | 370 | 0 | 67 | 149 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 17 | 18 | 58 | 19 | 0 | 0 | 0 | 6144.5 | 909 | 188 | 0 | 31 | 71 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 17 | 1230 | 0 | 48 | 0 | 0 | 65 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 52 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 501 | 835 | 17 | 6175 | 12319.5 | 101.6
19:30 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 43 | 35 | 33 | 105 | 64 | 15 | 35 | 105 | 0 | 450 | 0 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 70 | 19.5 | 22 | 0 | 0 | 30 | 16 | 24 | 0 | 17 | 49 | 61 | 0 | 24 | 12 | 0 | 86 | 34 | 13 | 650 | 21 | 0 | 33 | 8 | 65 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 70 | 0 | 245 | 0 | 240 | 42 | 0 | 38 | 50 | 103 | 84 | 0 | 20 | 17 | 58 | 0 | 0 | 22 | 315 | 0 | 386 | 0 | 67 | 142 | 22 | 0 | 79 | 30 | 0 | 17 | 0 | 17 | 18 | 68 | 19 | 0 | 0 | 0 | 5950.5 | 909 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 17 | 1238 | 0 | 48 | 0 | 0 | 35 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 35 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 110 | 220 | 0 | 451 | 835 | 17 | 5997 | 11947.5
20:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 43.5 | 35 | 33 | 105 | 64 | 15 | 35 | 103 | 0 | 450 | 0 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 70 | 19.5 | 22 | 0 | 0 | 28 | 16 | 22 | 0 | 17 | 34 | 61 | 0 | 24 | 24 | 0 | 86 | 33 | 18 | 650 | 0 | 0 | 33 | 8 | 64 | 221 | 0 | 0 | 0 | 580 | 0 | 0 | 70 | 0 | 255 | 0 | 240 | 42 | 0 | 38 | 53 | 103 | 85 | 0 | 17 | 0 | 56 | 0 | 0 | 22 | 310 | 0 | 386 | 0 | 67 | 147 | 22 | 0 | 79 | 30 | 0 | 17 | 0 | 17 | 18 | 58 | 21 | 0 | 0 | 0 | 5892 | 910 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 17 | 1221 | 0 | 48 | 0 | 0 | 35 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 51 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 452 | 840 | 17 | 5928 | 11820 | 101.59
21:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 34 | 19 | 33 | 90 | 64 | 15 | 35 | 107 | 0 | 450 | 0 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 52 | 20.3 | 22 | 0 | 0 | 30 | 16 | 0 | 0 | 12 | 34 | 68 | 11 | 24 | 24 | 0 | 86 | 32 | 23 | 580 | 0 | 0 | 33 | 0 | 65 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 70 | 0 | 250 | 0 | 240 | 42 | 0 | 39 | 48 | 103 | 81 | 0 | 20 | 0 | 62 | 0 | 0 | 22 | 310 | 0 | 386 | 0 | 67 | 149 | 16 | 0 | 79 | 30 | 0 | 17 | 0 | 17 | 18 | 58 | 22 | 0 | 0 | 0 | 5742.3 | 909 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 17 | 1211 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 51 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 450 | 852 | 17 | 5842 | 11584.3 | 101.59
22:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 33.7 | 0 | 33 | 60 | 64 | 15 | 22 | 90 | 0 | 450 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 52 | 19 | 22 | 0 | 0 | 30 | 16 | 0 | 0 | 2 | 17 | 67 | 17 | 24 | 24 | 0 | 86 | 33 | 27 | 570 | 0 | 0 | 33 | 0 | 63 | 222 | 0 | 0 | 0 | 561 | 0 | 0 | 70 | 0 | 250 | 0 | 240 | 0 | 76 | 5 | 47 | 103 | 81 | 0 | 20 | 0 | 60 | 0 | 0 | 23 | 305 | 0 | 386 | 0 | 67 | 147 | 16 | 0 | 79 | 30 | 0 | 17 | 0 | 17 | 18 | 58 | 22 | 0 | 0 | 0 | 5584.7 | 908 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 17 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 452 | 852 | 17 | 5721 | 11305.7 | 101.59
23:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 33.7 | 0 | 33 | 30 | 64 | 0 | 17 | 88 | 0 | 450 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 12 | 0 | 86 | 0 | 30 | 590 | 0 | 0 | 33 | 0 | 63 | 227 | 0 | 0 | 0 | 580 | 0 | 0 | 70 | 0 | 210 | 0 | 220 | 0 | 98 | 0 | 48 | 104 | 79 | 0 | 20 | 0 | 62 | 0 | 0 | 0 | 305 | 0 | 386 | 0 | 67 | 147 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 18 | 58 | 22 | 0 | 0 | 0 | 5253.7 | 909 | 178 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 0 | 1192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 355 | 852 | 0 | 5478 | 10731.7 | 101.58
Total KWH | 0 | 1195200 | 262560 | 0 | 0 | 0 | 0 | 0 | 8751600 | 0 | 0 | 416160 | 151560 | 394992 | 1069440 | 708065 | 166495 | 407621 | 1375200 | 0 | 9364800 | 0 | 0 | 0 | 143569 | 7881058 | 0 | 0 | 203816 | 770400 | 443400 | 514080 | 0 | 0 | 626018 | 155564 | 135360 | 0 | 233760 | 188623 | 531744 | 35378 | 312000 | 233280 | 19680 | 2082220 | 787855 | 408960 | 15469090.91 | 189018 | 0 | 671520 | 50841 | 1135781 | 5228080 | 0 | 0 | 0 | 13445453 | 120420 | 0 | 1391709 | 0 | 6221900 | 0 | 5852000 | 896640 | 199000 | 851976 | 792960 | 2435797 | 1470240 | 14280 | 437740 | 216600 | 1320960 | 189230 | 442645 | 188856 | 7583000 | 0 | 8992000 | 0 | 1584120 | 3628145 | 532608 | 0 | 1680000 | 719328 | 0 | 391000 | 583280 | 91800 | 406800 | 1183200 | 603840 | 11450 | 260780 | 0 | 127454545.91 | 22009454 | 5115168 | 0 | 73920 | 88964 | 912000 | 0 | 0 | 0 | 0 | 0 | 507600 | 24036360 | 5760 | 24053368 | 0 | 167165 | 0 | 0 | 211104 | 0 | 0 | 74444 | 15490 | 377966 | 666250 | 159941 | 0 | 392256 | 4328182 | 0 | 0 | 0 | 0 | 0 | 8852072 | 0 | 32580 | 0 | 923345 | 298312 | 201000 | 373689 | 0 | 0 | 0 | 35197.32 | 1073520 | 3439 | 106656 | 0 | 2640000 | 5301300 | 0 | 9751752 | 18794181.82 | 94800 | 131677236.14 | 259131782.05

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10886.15 | MW | 12:00 Hr. | Energy Generated |  |  | 259.1318 |  | MKWHr.
| Day Peak Demand |  |  | 10886.15 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.293 |  | MKWHr.
| Evening Peak Generation |  |  | 12657.5 | MW | 18:00 Hr. | Energy Demand |  |  | 259.4248 |  | MKWHr.
| Evening Peak Demand |  |  | 12725.43 | MW | 18:00 Hr. | Maximum Temperature |  |  | 31.4 |  | °C
| Minimum Generation of the Day |  |  | 9163.4 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 752.14 |  | MMCFD
| Maximum Generation of the Day |  |  | 12657.5 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 6.1627 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.9549 | 0 | 7.0613 | 0 | 0 | 0.20382 | 0 | 0 | 34.22 | Gas | 102.0211 | Gas | 363110875.59
| Chattogram Zone |  |  | 5.637 | 28.9145 | 5.053 | 0 | 2.0822 | 0.1401 | 0 | 0.23376 | 42.0606 | Coal | 82.4202 | Coal | 531288313.2891
| Cumilla Zone |  |  | 16.8951 | 0 | 4.2639 | 0 | 0 | 0.44265 | 1.321 | 0 | 22.9225 | HFO | 19.7302 | HFO | 348143424.22
| Mymensingh Zone |  |  | 0.60384 | 0 | 1.6818 | 0 | 0 | 0.27223 | 0 | 0 | 2.5579 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.6935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.6935 | Hydro | 2.0822 | Hydro | 208222
| Khulna Zone |  |  | 5.1152 | 24.0364 | 0.16864 | 0 | 0 | 0.5076 | 22.9215 | 0 | 52.7492 | Solar | 4.3486 | Solar | 69114363.4012
| Barishal Zone |  |  | 7.9413 | 28.5459 | 0.20146 | 0 | 0 | 0.003439 | 0 | 0 | 36.6921 | Import | 48.2958 | Import | 281646178.42
| Rajshahi Zone |  |  | 13.1803 | 0 | 0.62814 | 0 | 0 | 1.4691 | 24.0534 | 0 | 39.3308 | Wind | 0.23376 | Wind | 3438609.6
| Rangpur Zone |  |  | 0 | 0.92334 | 0.672 | 0 | 0 | 1.3097 | 0 | 0 | 2.9051
| Total |  |  | 102.0211 | 82.4202 | 19.7302 | 0 | 2.0822 | 4.3486 | 48.2958 | 0.23376 | 259.1318
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 363110875.59 |  | Hydro | 208222
|  |  |  | Coal | 531288313.2891 |  | Solar | 69114363.4012
|  |  |  | HFO | 348143424.22 |  | Import | 281646178.42
|  |  |  | HSD | 0 |  | Wind | 3438609.6
[5 empty] | Total: | 159,69,49,986 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0095 | Peak Hr Flow | 909.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 55950173.89 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.0534 | Peak Hr Flow | 1112.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2535 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.321 | Peak Hr Flow | 64.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2967 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.3838 | Peak Hr Flow | 2085.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4942
|  |  |  | Chattogram |  | 0 |  | 1368
|  |  |  | Cumilla |  | 0 |  | 1133
|  |  |  | Mymensingh |  | 65 |  | 923
|  |  |  | Sylhet |  | 0 |  | 534
|  |  |  | Khulna |  | 0 |  | 1340
|  |  |  | Barishal |  | 0 |  | 343
|  |  |  | Rajshahi |  | 0 |  | 1025
|  |  |  | Rangpur |  | 0 |  | 786
|  |  |  | Total |  | 65 |  | 12394
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 |  | Shahjadpur 132/33kV S/S T-3(425T) LT Scheduled S/D Due to Annual Maintenance
| 08:03 | 19:01 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to annual maintence
| 08:03 | 19:01 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to annual maintence
| 08:10 | 16:23 | Benapole 132/33kV S/S Transformer-1(406T) LT Scheduled S/D Due to Annual Maintenance
| 08:11 | 16:19 | Benapole 132/33kV S/S Transformer-1(406T) HT Scheduled S/D Due to Annual Maintenance
| 08:22 | 16:13 | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Scheduled S/D
| 08:23 | 16:13 | Sreemongol 132/33kV S/S 132/33kv T-1AB HT Scheduled S/D
| 08:25 | 11:40 | Khagrachori 132/33kV S/S MAIN BUS-1 Scheduled S/D Due to Annual Maintenance
| 08:27 | 17:46 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to Kulaura -
Fenchuganj circuit -1 Annual maintenance and from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 08:28 | 16:12 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Deadline
checking and Annual maintenance.
| 08:29 | 15:45 | Palashbari 132/33kV S/S TR1-414T LT Scheduled S/D Due to Annual Maintenance
| 08:30 | 15:43 | Palashbari 132/33kV S/S TR1-414T HT Scheduled S/D Due to Annual Maintenance
| 08:30 | 15:42 | Madunaghat 400/230kV S/S Madunaghat-Banskhali 400kV Ckt.-1 Scheduled S/D Due to Annual
maintenance
| 08:32 | 17:04 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 Scheduled S/D from Rangpur 132/33kV end
Due to Annual maintenance
| 08:32 | 14:02 | Gollamari 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annual Maintenance
| 08:34 | 14:00 | Gollamari 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual Maintenance
| 08:42 | 17:22 | Bheramara-HVDC Bheramara 230 kV Ckt-2 Scheduled S/D from Bheramara 230/132kV end Due to
Annual Maintaince
| 08:43 | 16:39 | Joydebpur-Kodda B 132 kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to Annual
Maintenance
| 08:49 | 14:33 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to
Annual Maintenance Work and from Bog-Sherpur 132/33kV end Due to Annual Maintenance
| 08:57 | 16:36 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end Due to
Annual maintenance
| 08:58 | 16:35 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to Annul
Maintainance of Kishoreganj Grid Side
| 09:08 | 18:01 | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end.
| 09:11 |  | Bheramara-HVDC Bheramara 230 kV Ckt-2 Scheduled S/D from BIPTC end Due to shutdown is
taken with bay 20D04B &C for annual maintenance work
| 09:11 | 16:48 | Mymensingh-Netrokona 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end. and from
Netrakona 132/33kV end Due to Maintenance
| 09:12 | 15:44 | Barapukuria 230/132/33kV S/S 132 KV Bus A Scheduled S/D Due to annual maintenance
| 09:16 | 20:06 | Faridpur 132/33kV S/S ATR-2 LT Scheduled S/D Due to annual maintenance
| 09:17 | 20:06 | Faridpur 132/33kV S/S ATR-2 HT Scheduled S/D Due to Annual Maintenance
| 09:17 | 18:14 | Rajendrapur 132/33kV S/S MTR-1 LT Scheduled S/D Due to Annual Maintenance 2025
| 09:18 | 18:14 | Rajendrapur 132/33kV S/S MTR-1 HT Scheduled S/D Due to Annual Maintenance 2025
| 09:20 | 16:56 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Annual
Maintenance Work.
| 09:25 | 15:50 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to Annual
Maintenance
| 09:30 | 16:10 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to Annual
Maintenance
| 09:40 | 16:56 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end Due to Annual
bay maintenance at julda grid end.
| 09:45 | 15:47 | New Tongi S/S T1(403T) HT Scheduled S/D Due to Annual Maintenance.
| 10:00 | 15:22 | Shyampur-Shyampur(New) 132kV Ckt-2 Tripped from Shyampur 230/132kV end showing Busbar
Protection relays Due to GIS SF6 Circuit Breaker Chamber Explosion of 132KV
fatullah-1(E06)
| 10:00 |  | Full interruption (122 MW) is occurring under Shyampur Old 132/33kV grid S/S (DPDC) from
10:00 hrs. due to a problem in 132kV bus of Shyampur New 230/132kV grid S/S.
| 10:00 | 19:37 | Shyampur 230/132kV S/S Auto TR-2 LT Tripped showing Busbar Protection. relays Due to GIS
SF6 Circuit Breaker Chamber Explosion of 132KV fatullah-1(E06)
| 10:00 | 15:18 | Fatullah-Shyampur(New) 132 kV Ckt-2 Tripped from Shyampur 230/132kV end showing F21 &
Busbar Relay. relays Due to GIS SF6 Circuit Breaker Chamber Explosion of 132KV
fatullah-1(E06)
| 10:00 | 15:12 | Shyampur 230/132kV S/S Bus-2 (132kV) Tripped showing F21 & Busbar Relay. relays Due to
GIS SF6 Circuit Breaker Chamber Explosion of 132KV fatullah-1(E06).
| 10:00 | 11:16 | Fatullah-Shyampur(New) 132 kV Ckt-1 Tripped from Shyampur 230/132kV end showing F21 &
Busbar Relay. relays Due to GIS SF6 Circuit Breaker Chamber Explosion of 132KV
fatullah-1(E06)
| 10:00 | 15:12 | Shyampur 230/132kV S/S Auto TR-1 LT Tripped showing Busbar protection relays Due to GIS
SF6 Circuit Breaker Chamber Explosion of 132KV fatullah-1(E06)
| 10:01 | 10:01 | Shyampur-Shyampur(New) 132kV Ckt-1 Forced S/D from Shyampur 230/132kV end Due to CB
chamber gas quality poor.
| 10:01 | 10:01 | Shyampur 230/132kV S/S Bus-1 (132kV) Forced S/D Due to Shyampur-1 CB gas quality poor and
132kV BFP operated.
|  | 10:22 | Chattak-Sylhet 132 kV Ckt-1 is restored.
| 10:24 | 12:02 | Maijdee 132/33kV S/S TR-01 LT Scheduled S/D Due to 33kv BREB Red Hot maintanance work
| 10:28 | 12:05 | Maijdee 132/33kV S/S Tr-02 LT Scheduled S/D Due to 33kv BREB Red Hot maintanance work
|  | 10:30 | Sunamganj 132/33kV S/S Tr-1 HT is restored.
|  | 10:32 | Sunamganj 132/33kV S/S Tr-1 LT is restored.
| 11:16 | 11:16 | Fatullah-Shyampur(New) 132 kV Ckt-1 Forced S/D from Shyampur 230/132kV end Due to CB | [7 empty] | 22.0MW load
|  |  | chamber blusted. | [7 empty] | interrup. Shyampur
230/132kV end
| 11:47 | 15:50 | Khagrachori 132/33kV S/S MAIN BUS-2 Scheduled S/D Due to Annual Maintenance
| 12:00 |  | Day peak Generation is 10882 MW
| 12:10 | 13:28 | Brahmanbaria 132/33kV S/S 403T HT Forced S/D Due to 33 KV Circuit Breaker Maintenance by
BPDB
| 12:46 | 13:02 | Full interruption (about 324MW) occurred under Mirzapur, Tangail, Ghatail, Muktagacha,
Jamalpur, and Sherpur grid substations, and a partial interruption (30MW) occurred under
the Mymensingh grid substation from 12:46 hrs to 13:02 hrs due to the tripping of the
Kaliakoir–Mirzapur and Kaliakoir–Tangail 132 kV circuits.
| 13:38 | 16:52 | Tongi 230/132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to Annual maintenance
|  | 14:25 | Mahasthangarh 132/33kV S/S 406T MTR1 HT is restored.
|  | 14:26 | Mahasthangarh 132/33kV S/S 406T MTR1 LT is restored.
|  | 14:46 | Keraniganj-Nawabganj 132kV Ckt-2 is restored.
|  | 14:46 | Keraniganj-Nawabganj 132kV Ckt-2 is restored.
|  | 15:02 | Savar 132/33kV S/S T-1 HT is restored.
|  | 15:03 | Savar 132/33kV S/S T-1 LT is restored.
|  | 15:07 | Savar 132/33kV S/S Bus-B is restored.
|  | 15:35 | Amnura 132/33kV S/S T-2 (416T) HT is restored.
|  | 15:37 | Amnura 132/33kV S/S T-2 (416T) LT is restored.
| 15:43 | 16:57 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to 33 kv bus section 1 | [7 empty] | 23.0MW load
|  |  | shutdown by pbs for 33 kv Morelganj feeder red hot maintenance. | [7 empty] | interrup.
| 15:44 | 16:57 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to 33 kv bus section 1 | [7 empty] | 23.0MW load
|  |  | shutdown by pbs for 33 kv Morelganj feeder red hot maintenance. | [7 empty] | interrup.
|  | 17:27 | Gopalganj 400/132kV S/S 230 kV Bus-01 is restored.
| 21:39 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 00:08 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 07:07 |  | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to Annual maintenance
| 07:25 |  | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenance
| 07:25 |  | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance
| 07:35 |  | Savar 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 373 | 8751600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9364800 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 166495 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7881058 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44.5 | 416160 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 105 | 1069440 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 407621 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 143569 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 443400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 514080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 262560 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 64 | 708065 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 33 | 394992 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1195200 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 123 | 1375200 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 203816 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 151560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 770400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1894.5 | 34220016
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 50841 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 120420 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 671520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2082220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5228080 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 1135781 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 531744 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 188623 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 312000 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 408960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 135360 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 155564 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 35378 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 787855 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 233280 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 85 | 626018 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 126 | 189018 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 13445453 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 12 | 233760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15469090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2229 | 42060645.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 199000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 240 | 5852000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 245 | 6221900 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 851976 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 41 | 896640 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 122 | 1391709 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 188856 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 2435797 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 153 | 1470240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 64 | 1320960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 26 | 189230 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 437740 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 67 | 216600 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 14280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 792960 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 442645 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1212 | 22922533
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 19 | 603840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1183200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 18 | 406800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 260780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 8 | 91800 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 103 | 2557870
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1584120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3628145 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719328 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1680000 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 583280 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 391000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 532608 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7583000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 8992000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 1077 | 25693481
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 909 | 22009454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 36 | 73920 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 88964 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 190 | 5115168 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 16 | 5760 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 507600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1120 | 24036360 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2351 | 52749226
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 501 | 9751752 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 27 | 106656 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2640000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 830 | 18794181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5301300 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 94800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3439 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1705 | 36692128.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 377966 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 167165 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 10 | 74444 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 4328182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8852072 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 159941 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 15490 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 25 | 211104 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Engine Problem
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32580 | Low irradiation
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1112 | 24053368 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 392256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 666250 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1827 | 39330818
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 923345 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 373689 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35197.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 109 | 298312 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201000 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1073520 | -
Rangpur Area Total |  |  |  |  | 950 | 259 | 2905063.32
Eastern Grid Total |  |  |  |  | 17383.855 | 6515.5 | 127454545.91
Western Grid Total |  |  |  |  | 10821.56 | 6142 | 131677236.14
National Grid Total |  |  |  |  | 28205.415 | 12657.5 | 259131782.05
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8835.5 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3493.6 | MW
i) Dhaka area |  |  | 4942.19 |  | MW | i) Khulna area |  |  |  | 1340 | MW
ii) Chattogram area |  |  | 1368.4 |  | MW | ii) Barishal area |  |  |  | 343 | MW
iii) Cumilla area |  |  | 1132.91 |  | MW | iii) Rajshahi area |  |  |  | 1024.6 | MW
iv) Mymensingh area |  |  | 858 |  | MW | iv) Rangpur area |  |  |  | 786 | MW
v) Sylhet area |  |  | 534 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12329.1 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 71 | 18:00 | 133 | Niamatpur | 40 | 20:00
2 | AKSML | 129 | 06:00 | 68 | Ishurdi | 60 | 18:30 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 32 | 13:00 | 69 | Jaldhaka | 66 | 18:00 | 135 | PHP | 8 | 00:00
4 | Agargaon | 112 | 13:00 | 70 | Jamalpur | 96 | 14:00 | 136 | Pabna | 74 | 18:00
5 | Agrabad | 92 | 18:00 | 71 | Jashore | 110 | 18:30 | 137 | Palashbari | 78 | 18:00
6 | Amnura | 16 | 00:00 | 72 | Jhenaidah | 98 | 18:00 | 138 | Panchagarh | 45 | 18:00
7 | Ashuganj | 66 | 23:00 | 73 | Joydebpur | 142 | 18:30 | 139 | Patiya | 9 | 18:00
8 | BSRM | 180 | 00:00 | 74 | Joypurhat | 42 | 18:00 | 140 | Patuakhali | 45.4 | 20:00
9 | Bagerhat | 68 | 18:00 | 75 | Juldah | 7 | 02:00 | 141 | Payra | 30 | 19:30
10 | Bajitpur | 68 | 18:00 | 76 | KSRM | 32 | 06:00 | 142 | Postogola | 55 | 18:00
11 | Bakulia | 80 | 18:30 | 77 | Kabirpur | 234 | 18:00 | 143 | Purbachal | 15 | 13:00
12 | Banani | 47 | 13:00 | 78 | Kachua | 66 | 18:00 | 144 | Purbasadipur | 93 | 18:00
13 | Bangabhaban | 21 | 10:00 | 79 | Kallyanpur | 93 | 13:00 | 145 | Rahanpur | 20 | 18:00
14 | Barapukuria | 48 | 18:00 | 80 | Kalurghat | 48 | 12:00 | 146 | Rahim | 36 | 14:00
15 | Barguna | 16 | 22:00 | 81 | Kamrangirchar | 73 | 18:00 | 147 | Rajbari | 60 | 18:00
16 | Barishal | 95 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 114 | 18:00
17 | Barishal-230 | 68 | 18:00 | 83 | Kasba | 27 | 18:30 | 149 | Rajshahi | 80 | 18:00
18 | Baroaulia | 61 | 15:00 | 84 | Kazla | 94 | 13:00 | 150 | Rajshahi-230 | 56 | 13:00
19 | Baroirhat | 48 | 18:00 | 85 | Keranigonj | 71 | 13:00 | 151 | Ramganj | 78 | 18:30
20 | Bashundhara | 164 | 18:00 | 86 | Khagrachori | 30 | 18:00 | 152 | Rampur | 38 | 18:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulna | 62 | 13:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 58 | 18:00 | 88 | Khulshi | 175 | 12:00 | 154 | Rangpur | 115 | 18:00
23 | Benapole | 48 | 18:00 | 89 | Kishoreganj | 94 | 19:30 | 155 | Ruppur | 5.8 | 10:00
24 | Bhaluka | 134 | 18:00 | 90 | Kodda | 285 | 15:00 | 156 | SSM | 14 | 00:00
25 | Bhandaria | 37 | 18:00 | 91 | Kulaura | 42 | 18:00 | 157 | Saidpur | 87 | 18:00
26 | Bhangura | 26 | 18:00 | 92 | Kurigram | 56 | 18:00 | 158 | Satkhira | 82 | 18:00
27 | Bheramara(GK) | 44 | 18:00 | 93 | Kushtia | 118 | 18:00 | 159 | Satmasjid | 91 | 13:00
28 | Bhulta | 202 | 11:00 | 94 | Laksam | 25 | 18:00 | 160 | Savar | 188 | 12:00
29 | Bog-Sherpur | 48 | 18:00 | 95 | Lakshmipur | 22 | 18:00 | 161 | SevenRings | 14.73 | 02:00
30 | Bogura | 124 | 18:00 | 96 | Lalbag | 61 | 17:00 | 162 | ShahCement | 32 | 00:00
31 | Borhanuddin | 69 | 21:00 | 97 | Lalmonirhat | 49 | 18:00 | 163 | Shahjadpur | 61 | 18:00
32 | Brahmanbaria | 111 | 20:00 | 98 | MI_Cement | 13.4 | 01:00 | 164 | Shahjibazar | 101 | 18:00
33 | Cantonment | 118 | 13:00 | 99 | Madanganj | 39 | 23:00 | 165 | Shahmirpur | 47 | 18:00
34 | Chandina | 7.91 | 18:00 | 100 | Madaripur | 68 | 21:00 | 166 | Shariatpur | 60 | 21:00
35 | Chandpur | 60 | 18:00 | 101 | Madartek | 72 | 18:00 | 167 | Sherpur | 100 | 07:00
36 | Chandraghona | 33 | 18:00 | 102 | Madunaghat | 49 | 17:00 | 168 | Shikalbaha | 30 | 18:00
37 | Chapai | 40 | 13:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 73.8 | 12:00
38 | Charsaidpur | 35 | 01:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 45 | 16:00
39 | Chauddagram | 49 | 18:00 | 105 | Maijdee | 22 | 03:00 | 171 | Shyampur | 116 | 02:00
40 | Chhatak | 28 | 11:00 | 106 | Manikganj | 102 | 18:00 | 172 | Siddhirganj | 114 | 15:00
41 | Chowmuhani | 130 | 18:00 | 107 | Maniknagar | 58 | 18:00 | 173 | Sirajganj | 88 | 18:30
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 46 | 18:00 | 174 | Sonargaon | 127 | 19:00
43 | Coxsbazar | 122 | 19:30 | 109 | Matuail | 72 | 12:00 | 175 | Sreemongol | 67 | 18:00
44 | Cumilla(N) | 119 | 12:00 | 110 | Metrorail_Motijheel | 30 | 18:00 | 176 | Sreepur | 89 | 19:00
45 | Cumilla(S) | 125 | 18:00 | 111 | Metrorail_Uttara | 6 | 14:00 | 177 | Srinagar | 34.14 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 101 | 12:00 | 178 | Sunamganj | 55 | 11:00
47 | Daudkandi | 130 | 18:00 | 113 | Mirpur | 123 | 18:00 | 179 | Sylhet | 45 | 00:00
48 | DhakaUniversity | 76 | 12:00 | 114 | Mirsorai | 11 | 15:00 | 180 | Sylhet-132 | 114 | 18:00
49 | Dhamrai | 120 | 18:00 | 115 | Mirzapur | 37 | 14:00 | 181 | TK | 20 | 18:30
50 | Dhanmondi | 111.2 | 13:00 | 116 | Mithapukur | 52 | 18:00 | 182 | Tangail | 133 | 18:30
51 | Dohazari | 84 | 00:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 19 | 18:00
52 | Faridpur | 121 | 18:00 | 118 | Mogbazar | 84.3 | 13:00 | 184 | Thakurgaon | 78 | 18:00
53 | Fatullah | 97 | 15:00 | 119 | Mongla | 43 | 12:00 | 185 | Tongi | 118 | 12:00
54 | Fenchuganj | 35 | 14:00 | 120 | Motijheel | 37 | 12:00 | 186 | Ullahpara | 27 | 18:00
55 | Feni | 105 | 17:00 | 121 | Muktagacha | 27 | 14:00 | 187 | Ullon | 56 | 13:00
56 | GPH | 84 | 10:00 | 122 | Munshiganj | 87 | 19:30 | 188 | Uttara | 74 | 13:00
57 | Ghatail | 60 | 07:00 | 123 | Muradnagar | 30 | 18:00 | 189 | UttaraNew | 32 | 15:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 148 | 19:30 | 190 | Zigatola | 52 | 18:00
59 | Ghorashal-230 | 83 | 15:00 | 125 | Naogaon | 82 | 18:00
60 | Goalpara | 30 | 13:00 | 126 | Narail | 39 | 18:00
61 | Gollamari | 72 | 18:00 | 127 | Narinda | 64 | 13:00
62 | Gopalganj | 79 | 18:00 | 128 | Narshingdi | 147 | 19:00
63 | Gulshan | 110 | 13:00 | 129 | Natore | 103 | 18:00
64 | Halishahar | 68 | 15:00 | 130 | Nawabganj | 32 | 13:00
65 | HaripurSBU | 156 | 11:00 | 131 | Netrakona | 106 | 19:00
66 | Hasnabad | 83 | 19:30 | 132 | New | 68 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11058.85 | 21 |  | 11080.8
1:00 | 10276.36 | 18 |  | 10295.17
2:00 | 9932.11 | 18 |  | 9950.92
3:00 | 9626.3 | 18 |  | 9645.11
4:00 | 9247.37 | 17 |  | 9265.14
5:00 | 9195.28 | 19 |  | 9215.14
6:00 | 9163.4 | 16 |  | 9180.12
7:00 | 9780.82 | 17 |  | 9798.59
8:00 | 10118.36 | 15 |  | 10134.04
9:00 | 10088.29 | 19 |  | 10108.15
10:00 | 10068.37 | 20 |  | 10089.27
11:00 | 10257.73 | 0 |  | 10257.73
12:00 | 10886.15 | 0 |  | 10886.15
13:00 | 11160.48 | 0 |  | 11160.48
14:00 | 11210.2 | 0 |  | 11210.2
15:00 | 11339.73 | 0 |  | 11339.73
16:00 | 10996.05 | 0 |  | 10996.05
17:00 | 11373.13 | 0 |  | 11373.13
18:00 | 12657.5 | 65 |  | 12725.43
19:00 | 12319.5 | 30 |  | 12350.5
19:30 | 11947.5 | 0 |  | 11947.5
20:00 | 11820 | 0 |  | 11820
21:00 | 11584.3 | 0 |  | 11584.3
22:00 | 11305.7 | 0 |  | 11305.7
23:00 | 10731.7 | 0 |  | 10731.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5424 | 5634.85 | 11058.85 | DAILY GENERATION CURVE
00:30 | 5162 | 5505.605 | 10667.605
01:00 | 4900 | 5376.36 | 10276.36 | 10-11-2025
01:30 | 4814.25 | 5289.985 | 10104.235
02:00 | 4728.5 | 5203.61 | 9932.11
02:30 | 4725.75 | 5053.455 | 9779.205
03:00 | 4723 | 4903.3 | 9626.3
03:30 | 4595 | 4841.835 | 9436.835
04:00 | 4467 | 4780.37 | 9247.37
04:30 | 4470.5 | 4750.825 | 9221.325
05:00 | 4474 | 4721.28 | 9195.28
05:30 | 4459.5 | 4719.84 | 9179.34
06:00 | 4445 | 4718.4 | 9163.4
06:30 | 4574.92 | 4897.19 | 9472.11
07:00 | 4704.84 | 5075.98 | 9780.82
07:30 | 4627.015 | 5322.575 | 9949.59
08:00 | 4549.19 | 5569.17 | 10118.36
08:30 | 4568.335 | 5534.99 | 10103.325
09:00 | 4587.48 | 5500.81 | 10088.29
09:30 | 4612.84 | 5465.49 | 10078.33
10:00 | 4638.2 | 5430.17 | 10068.37
10:30 | 4743.31 | 5419.74 | 10163.05
11:00 | 4848.42 | 5409.31 | 10257.73
11:30 | 5059.44 | 5512.5 | 10571.94
12:00 | 5270.46 | 5615.69 | 10886.15
12:30 | 5386.675 | 5636.64 | 11023.315
13:00 | 5502.89 | 5657.59 | 11160.48
13:30 | 5581.375 | 5603.965 | 11185.34
14:00 | 5659.86 | 5550.34 | 11210.2
14:30 | 5774.035 | 5500.93 | 11274.965
15:00 | 5888.21 | 5451.52 | 11339.73
15:30 | 5792.79 | 5375.1 | 11167.89
16:00 | 5697.37 | 5298.68 | 10996.05
16:30 | 5786.94 | 5397.65 | 11184.59
17:00 | 5876.51 | 5496.62 | 11373.13
17:30 | 6196.005 | 5819.31 | 12015.315
18:00 | 6515.5 | 6142 | 12657.5
18:30 | 6330 | 6158.5 | 12488.5
19:00 | 6144.5 | 6175 | 12319.5
19:30 | 5950.5 | 5997 | 11947.5
20:00 | 5892 | 5928 | 11820
20:30 | 5817.15 | 5885 | 11702.15 |  | Executive Engineer
21:00 | 5742.3 | 5842 | 11584.3 |  | Network Operation Division
21:30 | 5663.5 | 5781.5 | 11445
22:00 | 5584.7 | 5721 | 11305.7
22:30 | 5419.2 | 5599.5 | 11018.7
23:00 | 5253.7 | 5478 | 10731.7

## En-Curve
QF-LDC-12
Date | 10-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2971 | 1284 | 916 | 38 | 64 | 1224.85 | 86 | 3406 | 0 | 167 | 895 | 0 | 0 | 7 | 21 | DAILY ENERGY CURVE
00:30 | 2953 | 1281.5 | 912.5 | 38 | 63 | 1187.605 | 86 | 3407 | 0 | 108 | 622 | 0 | 0 | 9 | 19.5 | 10-11-2025
01:00 | 2935 | 1279 | 909 | 38 | 62 | 1150.36 | 86 | 3408 | 0 | 49 | 349 | 0 | 0 | 11 | 18
01:30 | 2958.5 | 1277.75 | 909 | 38 | 59 | 1098.485 | 86 | 3376 | 0 | 33 | 259 | 0 | 0 | 9.5 | 18 | Energy Generated | 259.1318 |  | MKWHr
02:00 | 2982 | 1276.5 | 909 | 38 | 56 | 1046.61 | 86 | 3344 | 0 | 17 | 169 | 0 | 0 | 8 | 18 | Energy not Served | 0.293 |  | MKWHr
02:30 | 2998 | 1285.75 | 909 | 38 | 55 | 984.955 | 86 | 3251 | 0 | 8.5 | 150.5 | 0 | 0 | 12.5 | 18 | Total Energy Requirement | 259.4248 |  | MKWHr
03:00 | 3014 | 1295 | 909 | 38 | 54 | 923.3 | 86 | 3158 | 0 | 0 | 132 | 0 | 0 | 17 | 18
03:30 | 3003 | 1255 | 909 | 38 | 52 | 877.835 | 86 | 3123.5 | 0 | 0 | 79.5 | 0 | 0 | 13 | 17.5
04:00 | 2992 | 1215 | 909 | 38 | 50 | 832.37 | 86 | 3089 | 0 | 0 | 27 | 0 | 0 | 9 | 17
04:30 | 3017 | 1216 | 909 | 38 | 50 | 838.325 | 86 | 3029.5 | 0 | 0 | 21.5 | 0 | 0 | 16 | 18
05:00 | 3042 | 1217 | 909 | 38 | 50 | 844.28 | 86 | 2970 | 0 | 0 | 16 | 0 | 0 | 23 | 19
05:30 | 3037 | 1224 | 909 | 38 | 52 | 841.34 | 86 | 2956 | 0 | 0 | 16 | 0 | 0 | 20 | 17.5
06:00 | 3032 | 1231 | 909 | 38 | 54 | 838.4 | 86 | 2942 | 0 | 0 | 16 | 0 | 0 | 17 | 16
06:30 | 3059 | 1272 | 909 | 38 | 49 | 868.46 | 86 | 3094.5 | 31.65 | 19.5 | 30.5 | 0 | 0 | 14.5 | 16.5
07:00 | 3086 | 1313 | 909 | 38 | 44 | 898.52 | 86 | 3247 | 63.3 | 39 | 45 | 0 | 0 | 12 | 17
07:30 | 2971 | 1263.5 | 908.5 | 38 | 48 | 963.415 | 86 | 3378 | 155.175 | 63 | 63.5 | 0 | 0 | 11.5 | 16
08:00 | 2856 | 1214 | 908 | 38 | 52 | 1028.31 | 86 | 3509 | 247.05 | 87 | 82 | 0 | 0 | 11 | 15
08:30 | 2868 | 1193 | 908.5 | 38 | 47 | 982.085 | 86 | 3455 | 344.74 | 83.5 | 87 | 0 | 0 | 10.5 | 17
09:00 | 2880 | 1172 | 909 | 38 | 42 | 935.86 | 86 | 3401 | 442.43 | 80 | 92 | 0 | 0 | 10 | 19
09:30 | 2890.5 | 1169 | 909 | 38 | 41 | 888.62 | 86 | 3360 | 513.71 | 64 | 109 | 0 | 0 | 9.5 | 19.5
10:00 | 2901 | 1166 | 909 | 38 | 40 | 841.38 | 86 | 3319 | 584.99 | 48 | 126 | 0 | 0 | 9 | 20
10:30 | 2871.5 | 1187.75 | 909 | 38 | 44 | 841.86 | 86 | 3369 | 625.94 | 48 | 135.5 | 0 | 0 | 6.5 | 10
11:00 | 2842 | 1209.5 | 909 | 38 | 48 | 842.34 | 86 | 3419 | 666.89 | 48 | 145 | 0 | 0 | 4 | 0
11:30 | 2856 | 1230 | 909 | 38 | 53 | 837.185 | 86 | 3484 | 671.255 | 79 | 323.5 | 0 | 0 | 5 | 0
12:00 | 2870 | 1250.5 | 909 | 38 | 58 | 832.03 | 86 | 3549 | 675.62 | 110 | 502 | 0 | 0 | 6 | 0
12:30 | 2778.5 | 1203 | 909 | 38 | 62 | 856.44 | 86 | 3552.5 | 630.625 | 185 | 716.25 | 0 | 0 | 6 | 0
13:00 | 2687 | 1155.5 | 909 | 38 | 66 | 880.85 | 86 | 3556 | 585.63 | 260 | 930.5 | 0 | 0 | 6 | 0
13:30 | 2769.5 | 1155.5 | 909 | 38 | 66 | 882.425 | 86 | 3511.5 | 546.915 | 275 | 938 | 0 | 0 | 7.5 | 0
14:00 | 2852 | 1155.5 | 909 | 38 | 66 | 884 | 86 | 3467 | 508.2 | 290 | 945.5 | 0 | 0 | 9 | 0
14:30 | 2881.5 | 1215.5 | 908.5 | 38 | 63 | 885.5 | 86 | 3481.5 | 431.965 | 295.5 | 980 | 0 | 0 | 8 | 0
15:00 | 2911 | 1275.5 | 908 | 38 | 60 | 887 | 86 | 3496 | 355.73 | 301 | 1014.5 | 0 | 0 | 7 | 0
15:30 | 2909 | 1270.5 | 908.5 | 38 | 60 | 886 | 86 | 3491 | 253.94 | 308.5 | 950.95 | 0 | 0 | 5.5 | 0
16:00 | 2907 | 1265.5 | 909 | 38 | 60 | 885 | 86 | 3486 | 152.15 | 316 | 887.4 | 0 | 0 | 4 | 0
16:30 | 2913.5 | 1290.75 | 909 | 38 | 60 | 951 | 86 | 3512.5 | 82.64 | 353.5 | 983.7 | 0 | 0 | 4 | 0
17:00 | 2920 | 1316 | 909 | 38 | 60 | 1017 | 86 | 3539 | 13.13 | 391 | 1080 | 0 | 0 | 4 | 0
17:30 | 2939.5 | 1335 | 909 | 38 | 62 | 1064.5 | 86 | 3636 | 6.565 | 523 | 1407.75 | 0 | 0 | 8 | 32.5
18:00 | 2959 | 1354 | 909 | 38 | 64 | 1112 | 86 | 3733 | 0 | 655 | 1735.5 | 0 | 0 | 12 | 65
18:30 | 2924 | 1347.5 | 909 | 38 | 61 | 1171 | 86 | 3715.5 | 0 | 656 | 1565 | 0 | 0 | 15.5 | 47.5
19:00 | 2889 | 1341 | 909 | 38 | 58 | 1230 | 86 | 3698 | 0 | 657 | 1394.5 | 0 | 0 | 19 | 30
19:30 | 2947 | 1344.5 | 909 | 38 | 58 | 1238 | 86 | 3661 | 0 | 521 | 1128 | 0 | 0 | 17 | 0
20:00 | 2904 | 1346.5 | 910 | 38 | 56 | 1221 | 86 | 3681 | 0 | 506 | 1054.5 | 0 | 0 | 17 | 0
20:30 | 2903.5 | 1348.9 | 909.5 | 38 | 59 | 1216 | 86 | 3652 | 0 | 444 | 1030.75 | 0 | 0 | 14.5 | 0
21:00 | 2903 | 1351.3 | 909 | 38 | 62 | 1211 | 86 | 3623 | 0 | 382 | 1007 | 0 | 0 | 12 | 0
21:30 | 2910 | 1328.15 | 908.5 | 38 | 61 | 1213 | 86 | 3578 | 0 | 357.5 | 957.85 | 0 | 0 | 7 | 0
22:00 | 2917 | 1305 | 908 | 38 | 60 | 1215 | 86 | 3533 | 0 | 333 | 908.7 | 0 | 0 | 2 | 0
22:30 | 2908 | 1289 | 908.5 | 38 | 61 | 1203.5 | 86 | 3499.5 | 0 | 229 | 791.7 | 0 | 0 | 4.5 | 0
23:00 | 2899 | 1273 | 909 | 38 | 62 | 1192 | 86 | 3466 | 0 | 125 | 674.7 | 0 | 0 | 7 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 06:00 | 373 | 11:00 | Meghnaghat | 389 | 06:00 | 283 | 23:00
Ashuganj | 397 | 4:00 | 379 | 11:00 | Payra | 416 | 05:00 | 409 | 10:00
Bhulta | 395 | 19:00 | 376 | 11:00 | Rahanpur | 414 | 04:00 | 406 | 19:30
Bibiana | 391 | 05:00 | 384 | 11:00 | Rampal | 411 | 05:00 | 400 | 10:00
BIPTC | 408 | 03:00 | 395 | 18:00
Bogura | 408 | 04:00 | 397 | 23:00
Gopalganj | 402 | 04:00 | 391 | 11:00
Kaliakoir | 378 | 05:00 | 366 | 11:00
Korerhat | 395 | 06:00 | 380 | 11:00
Madunaghat | 397 | 18:00 | 381 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 04:00 | 223 | 11:00 | Kaliakoir | 236 | 05:00 | 226 | 11:00
AKSML | 237 | 17:00 | 226 | 10:00 | Keranigonj | 231 | 05:00 | 220 | 11:00
Aminbazar | 234 | 06:00 | 224 | 11:00 | Khulna(S) | 240 | 04:00 | 230 | 18:00
Ashuganj | 234 | 06:00 | 223 | 11:00 | Korerhat | 236 | 06:00 | 228 | 10:00
Ashuganj-400 | 234 | 06:00 | 223 | 11:00 | Madunaghat | 236 | 17:00 | 227 | 10:00
Baghabari | 237 | 03:00 | 231 | 11:00 | Madunaghat-400 | 236 | 18:00 | 227 | 11:00
Barapukuria | 227 | 10:00 | 216 | 23:00 | Maniknagar | 227 | 06:00 | 217 | 11:00
Barapukuria-230 | 227 | 10:00 | 216 | 23:00 | Meghnaghat | 230 | 20:00 | 222 | 11:00
Barishal | 238 | 06:00 | 233 | 12:00 | Meghnaghat-400 | 229 | 06:00 | 220 | 11:00
Bheramara | 235 | 04:00 | 228 | 11:00 | Mirsorai | 237 | 18:00 | 223 | 10:00
Bhulta | 228 | 04:00 | 218 | 11:00 | Rajshahi | 235 | 04:00 | 227 | 13:00
Bibiana | 234 | 06:00 | 225 | 11:00 | Rampal | 237 | 03:00 | 228 | 10:00
BIPTC | 239 | 04:00 | 227 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura | 236 | 04:00 | 230 | 23:00 | Rampura | 228 | 05:00 | 217 | 11:00
Bogura-400 | 236 | 05:00 | 230 | 23:00 | Shikalbaha | 237 | 18:00 | 225 | 09:00
Borhanuddin | 238 | 00:00 | 235 | 10:00 | Shyampur | 229 | 05:00 | 219 | 11:00
BSRM | 236 | 18:00 | 223 | 10:00 | Siddhirganj | 225 | 03:00 | 220 | 15:00
Cumilla(N) | 229 | 22:00 | 221 | 11:00 | Sirajgonj | 240 | 04:00 | 236 | 11:00
Faridpur | 236 | 05:00 | 230 | 12:00 | Sreepur | 230 | 05:00 | 222 | 10:00
Fenchuganj | 234 | 05:00 | 228 | 12:00 | Tongi | 230 | 00:00 | 219 | 15:00
Ghorashal | 234 | 00:00 | 228 | 10:00
Ghorashal-230 | 228 | 04:00 | 217 | 11:00
Gopalganj | 237 | 06:00 | 230 | 11:00
GPH | 236 | 18:00 | 225 | 10:00
Haripur | 228 | 06:00 | 218 | 11:00
Hasnabad | 229 | 06:00 | 220 | 11:00
Hathazari | 235 | 18:00 | 223 | 12:00
Ishurdi | 239 | 04:00 | 231 | 11:00
Jhenaidah | 237 | 04:00 | 226 | 18:00
Kachua | 233 | 17:00 | 226 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 127 | 11:00 | Lalmonirhat | 130 | 00:00 | 123 | 07:00
Agargaon | 138 | 04:00 | 130 | 11:00 | Madanganj | 131 | 22:00 | 121 | 16:00
Agrabad | 135 | 18:00 | 128 | 11:00 | Madaripur | 138 | 05:00 | 134 | 11:00
AKS | 134 | 18:30 | 126 | 10:00 | Madartek | 134 | 01:00 | 126 | 11:00
Aminbazar | 138 | 05:00 | 131 | 11:00 | Madunaghat | 137 | 17:00 | 131 | 10:00
Amnura | 140 | 05:00 | 131 | 13:00 | Magura | 137 | 01:00 | 131 | 14:00
Ashuganj | 141 | 04:00 | 137 | 11:00 | Mahasthangarh | 133 | 03:00 | 129 | 07:00
Bagerhat | 135 | 03:00 | 129 | 18:00 | Maijdee | 135 | 06:00 | 129 | 11:00
Bajitpur | 137 | 04:00 | 132 | 11:00 | Manikganj | 135 | 22:00 | 130 | 10:00
Bakulia | 135 | 05:00 | 130 | 11:00 | Maniknagar | 138 | 05:00 | 130 | 11:00
Banani | 135 | 05:00 | 126 | 11:00 | Matarbari | 125 | 11:00 | 115 | 00:00
Bangabhaban | 137 | 05:00 | 130 | 11:00 | Matuail | 132.5 | 05:00 | 126 | 12:00
Barapukuria | 137 | 18:30 | 127 | 12:00 | Metrorail_Motijheel | 138 | 05:00 | 131 | 12:00
Barguna | 137 | 00:00 | 135 | 12:00 | Metrorail_Uttara | 139 | 04:00 | 130 | 15:00
Barishal | 137 | 03:00 | 133 | 11:00 | Millgate | 139 | 03:00 | 132 | 11:00
Barishal-230 | 138 | 05:00 | 134 | 11:00 | Mirpur | 138 | 22:00 | 128 | 11:00
Baroaulia | 136 | 17:00 | 130 | 10:00 | Mirzapur | 132 | 04:00 | 125 | 14:00
Baroirhat | 135 | 18:00 | 129 | 11:00 | Mithapukur | 134 | 18:30 | 128 | 07:00
Bashundhara | 136 | 23:00 | 126 | 12:00 | MI_Cement | 136 | 05:00 | 126 | 11:00
BashundharaCement | 131 | 22:00 | 127 | 01:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 133 | 08:00 | 126 | 18:00 | Mogbazar | 135 | 02:00 | 128 | 11:00
Benapole | 136 | 03:00 | 125 | 13:00 | Mongla | 135 | 05:00 | 130 | 12:00
Bhaluka | 133 | 18:30 | 126 | 11:00 | Motijheel | 137 | 05:00 | 130 | 11:00
Bhandaria | 135 | 07:00 | 132 | 02:00 | Muktagacha | 131 | 09:00 | 118 | 19:00
Bhangura | 137 | 04:00 | 133 | 12:00 | Munshiganj | 131 | 22:00 | 126 | 10:00
Bheramara | 141 | 04:00 | 136 | 12:00 | Muradnagar | 132 | 06:00 | 126 | 11:00
Bheramara(GK) | 139 | 00:00 | 136 | 12:00 | Mymensingh | 131 | 08:00 | 118 | 18:00
Bhulta | 130 | 00:00 | 124 | 11:00 | Naogaon | 132 | 04:00 | 128 | 07:00
Bog-Sherpur | 135 | 04:00 | 131 | 16:00 | Narail | 139 | 06:00 | 131 | 13:00
Bogura | 135 | 05:00 | 131 | 07:00 | Narinda | 138 | 05:00 | 130 | 11:00
Bogura-230 | 135 | 04:00 | 132 | 01:00 | Narshingdi | 133 | 08:00 | 121 | 11:00
Brahmanbaria | 133 | 06:00 | 128 | 04:00 | Natore | 135 | 04:00 | 132 | 17:00
Cantonment | 138 | 04:00 | 130 | 11:00 | Nawabganj | 137 | 04:00 | 130 | 11:00
Chandina | 135 | 06:00 | 129 | 11:00 | Netrakona | 130 | 04:00 | 121 | 13:00
Chandpur | 140 | 18:00 | 133 | 10:00 | New | 140 | 05:00 | 133 | 10:00
Chandraghona | 137 | 18:00 | 132 | 10:00 | Niamatpur | 142 | 04:00 | 139 | 18:00
Chapai | 141 | 09:00 | 139 | 00:00 | Noapara | 138 | 04:00 | 132 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 06:00 | 126 | 11:00 | Pabna | 139 | 04:00 | 134 | 13:00
Chauddagram | 134 | 05:00 | 127 | 11:00 | Palashbari | 132 | 02:00 | 127 | 07:00
Chhatak | 130 | 05:00 | 122 | 11:00 | Panchagarh | 141 | 18:30 | 125 | 07:00
Chowmuhani | 134 | 17:00 | 130 | 10:00 | Patiya | 135 | 18:00 | 130 | 05:00
Chuadanga | 138 | 05:00 | 130 | 13:00 | Patuakhali | 137 | 00:00 | 135 | 15:00
Coxsbazar | 121 | 07:00 | 115 | 00:00 | Payra | 138 | 06:00 | 136 | 14:00
Cumilla(N) | 134 | 22:00 | 130 | 10:00 | PHP | 134 | 18:00 | 128 | 11:00
Cumilla(S) | 134 | 06:00 | 124 | 21:00 | Postogola | 137 | 05:00 | 128 | 11:00
Daganbhuiyan | 135 | 18:00 | 129 | 11:00 | Purbachal | 134 | 03:00 | 126 | 11:00
Daudkandi | 130 | 04:00 | 125 | 11:00 | Purbasadipur | 134 | 18:30 | 124 | 12:00
DhakaUniversity | 135 | 04:00 | 126 | 11:00 | Rahanpur | 142 | 09:00 | 140 | 00:00
Dhamrai | 134 | 04:00 | 129 | 10:00 | Rahanpur-400 | 143 | 04:00 | 140 | 18:00
Dhanmondi | 135 | 05:00 | 127 | 11:00 | Rahim | 132 | 06:00 | 127 | 10:00
Dohazari | 131 | 17:00 | 126 | 02:00 | Rajbari | 139 | 04:00 | 134 | 11:00
Faridpur | 139 | 05:00 | 135 | 11:00 | Rajendrapur | 133 | 03:00 | 127 | 11:00
Fatullah | 139 | 03:00 | 127 | 11:00 | Rajshahi | 135 | 05:00 | 131 | 13:00
Fenchuganj | 139 | 07:00 | 134 | 12:00 | Rajshahi-230 | 135 | 04:00 | 131 | 13:00
Feni | 133 | 22:00 | 129 | 10:00 | Ramganj | 135 | 03:00 | 131 | 10:00
Ghatail | 130 | 09:00 | 118 | 14:00 | Rampur | 135 | 18:00 | 129 | 10:00
Ghorashal | 138 | 01:00 | 133 | 12:00 | Rampura | 135 | 05:00 | 127 | 11:00
Goalpara | 138 | 04:00 | 133 | 11:00 | Rangamati | 136 | 18:00 | 131 | 10:00
Gollamari | 138 | 03:00 | 134 | 11:00 | Rangpur | 135 | 04:00 | 125 | 09:00
Gopalganj | 138 | 04:00 | 133 | 11:00 | Ruppur | 139 | 03:00 | 136 | 11:00
Gopalganj-400 | 139 | 06:00 | 134 | 11:00 | Saidpur | 134 | 18:30 | 124 | 07:00
Gulshan | 134 | 05:00 | 126 | 11:00 | Satkhira | 138 | 05:00 | 131 | 13:00
Halishahar | 136 | 17:00 | 127 | 11:00 | Satmasjid | 138 | 05:00 | 130 | 11:00
Haripur | 133 | 03:00 | 127 | 11:00 | Savar | 137 | 20:00 | 128 | 10:00
HaripurSBU | 133 | 04:00 | 127 | 11:00 | SevenRings | 139 | 05:00 | 132 | 11:00
Hasnabad | 137 | 04:00 | 129 | 11:00 | ShahCement | 132 | 06:00 | 126 | 11:00
Hathazari | 137 | 17:00 | 132 | 11:00 | Shahjadpur | 140 | 04:00 | 135 | 09:00
Ishurdi | 141 | 04:00 | 136 | 16:00 | Shahjibazar | 135 | 08:00 | 131 | 04:00
Jaldhaka | 131 | 09:00 | 123 | 07:00 | Shahmirpur | 136 | 17:00 | 132 | 07:00
Jamalpur | 130 | 09:00 | 114 | 19:00 | Shariatpur | 137 | 03:00 | 133 | 13:00
Jashore | 137 | 04:00 | 126 | 18:00 | Sherpur | 129 | 09:00 | 114 | 19:00
Jhenaidah | 139 | 04:00 | 130 | 18:30 | Shikalbaha | 125 | 17:00 | 120 | 10:00
Jhenaidah-230 | 141 | 04:00 | 133 | 18:00 | Shikalbaha-230 | 138 | 18:00 | 132 | 09:00
Joydebpur | 136 | 06:00 | 125 | 15:00 | Shitalakhya | 136 | 05:00 | 126 | 11:00
Joypurhat | 131 | 05:00 | 128 | 12:00 | Sholosohor | 137 | 18:00 | 131 | 10:00
Juldah | 136 | 17:00 | 131 | 09:00 | Shyampur | 137 | 22:00 | 132 | 16:00
Kabirpur | 136 | 04:00 | 128 | 10:00 | Shyampur-230 | 139 | 03:00 | 133 | 10:00
Kachua | 138 | 17:00 | 133 | 10:00 | Siddhirganj | 133 | 03:00 | 127 | 11:00
Kaliakoir | 137 | 04:00 | 131 | 11:00 | Sirajganj | 134 | 05:00 | 130 | 16:00
Kallyanpur | 138 | 00:00 | 130 | 11:00 | Sonargaon | 130 | 21:00 | 125 | 12:00
Kalurghat | 137 | 18:00 | 132 | 10:00 | Sreemongol | 136 | 08:00 | 130 | 17:00
Kamrangirchar | 137 | 04:00 | 130 | 11:00 | Sreepur | 133 | 05:00 | 129 | 10:00
Kaptai | 134 | 19:00 | 128 | 11:00 | Srinagar | 137 | 05:00 | 130 | 11:00
Kasba | 131 | 05:00 | 126 | 11:00 | SSM | 138 | 01:00 | 132 | 10:00
Kazla | 138 | 05:00 | 130 | 12:00 | Sunamganj | 128 | 03:00 | 120 | 11:00
Keranigonj | 138 | 05:00 | 130 | 11:00 | Sylhet | 135 | 07:00 | 127 | 12:00
Khagrachori | 135 | 18:00 | 130 | 10:00 | Sylhet-132 | 135 | 06:00 | 127 | 11:00
Khulna | 138 | 04:00 | 133 | 14:00 | Tangail | 130 | 09:00 | 120 | 16:00
Khulna(S) | 139 | 03:00 | 134 | 12:00 | Taraganj | 133 | 18:30 | 126 | 11:00
Khulshi | 134 | 07:00 | 128 | 10:00 | Thakurgaon | 140 | 18:30 | 122 | 07:00
Kishoreganj | 136 | 05:00 | 129 | 14:00 | TK | 137 | 18:00 | 132 | 09:00
Kodda | 135 | 21:00 | 123 | 15:00 | Tongi | 139 | 00:00 | 132 | 15:00
KSRM | 136 | 17:00 | 129 | 10:00 | Ullahpara | 136 | 04:00 | 132 | 11:00
Kulaura | 137 | 06:00 | 133 | 11:00 | Ullon | 135 | 04:00 | 126 | 11:00
Kurigram | 132 | 05:00 | 122 | 07:00 | Uttara | 138 | 05:00 | 128 | 11:00
Kushtia | 140 | 03:00 | 133 | 18:00 | UttaraNew | 139 | 04:00 | 132 | 10:00
Laksam | 137 | 17:00 | 132 | 11:00 | Zigatola | 138 | 05:00 | 124 | 12:00
Lakshmipur | 135 | 06:00 | 130 | 10:00
Lalbag | 137 | 04:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division