## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-11-2025 | [28 empty] | Date: | 13-11-2025 | [28 empty] | Date: | 13-11-2025 | [28 empty] | Date: | 13-11-2025 | [28 empty] | Date: | 13-11-2025 | [14 empty] | Date: | 13-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 20 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 502 | 0 | 0 | 0 | 0 | 240 | 0 | 280 | 0 | 42 | 0 | 0 | 106 | 0 | 0 | 20 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 311 | 0 | 67 | 147 | 23 | 0 | 78 | 30 | 0 | 13 | 98 | 17 | 19 | 58 | 23 | 0 | 0 | 0 | 4623 | 896 | 111 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 1183.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 307 | 750 | 0 | 5146.73 | 9769.73 | 101.35
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 23 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 43 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 66 | 0 | 0 | 0 | 305 | 0 | 328 | 0 | 67 | 145 | 21 | 0 | 78 | 30 | 0 | 15 | 98 | 0 | 19 | 16 | 24 | 0 | 0 | 0 | 4139 | 896 | 116 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1016 | 0 | 1040.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 308 | 650 | 0 | 4837.76 | 8976.76 | 101.35
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 25 | 638 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 43 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 334 | 0 | 67 | 150 | 21 | 0 | 78 | 30 | 0 | 15 | 98 | 0 | 19 | 8 | 24 | 0 | 0 | 0 | 4067 | 896 | 120 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 935.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 308 | 618 | 0 | 4606.79 | 8673.79 | 101.34
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 20 | 586 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 42 | 0 | 0 | 106 | 0 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 313 | 0 | 67 | 151 | 21 | 0 | 78 | 30 | 0 | 15 | 98 | 0 | 8 | 8 | 24 | 0 | 0 | 0 | 3936 | 896 | 125 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 868 | 0 | 847.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 308 | 530 | 0 | 4377.21 | 8313.21 | 101.33
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 20 | 590 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 30 | 0 | 0 | 106 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 300 | 0 | 363 | 0 | 67 | 148 | 21 | 0 | 41 | 30 | 0 | 15 | 99 | 0 | 8 | 8 | 24 | 0 | 0 | 0 | 3931 | 896 | 130 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 819.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 307 | 510 | 0 | 4332.08 | 8263.08 | 101.33
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 590 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 40 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 315 | 0 | 386 | 0 | 67 | 157 | 21 | 0 | 11 | 30 | 0 | 15 | 98 | 0 | 8 | 8 | 24 | 0 | 0 | 0 | 3975 | 896 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 788.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 307 | 500 | 0 | 4249.32 | 8224.32 | 101.32
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 590 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 40 | 20 | 0 | 107 | 0 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 315 | 0 | 400 | 0 | 67 | 154 | 21 | 0 | 41 | 30 | 0 | 15 | 99 | 0 | 8 | 8 | 24 | 0 | 0 | 0 | 4169 | 896 | 137 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 804 | 0 | 777.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 307 | 532 | 0 | 4259.48 | 8428.48 | 101.32
07:00 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.44 | 86 | 0 | 28 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 580 | 4 | 0 | 0 | 0 | 345 | 0 | 44 | 0 | 131 | 20 | 0 | 107 | 0 | 0 | 20 | 0 | 64 | 0 | 11 | 0 | 310 | 0 | 397 | 0 | 67 | 160 | 21 | 0 | 78 | 30 | 0 | 15 | 98 | 0 | 19 | 35 | 24 | 0 | 3.38 | 0 | 4755.82 | 897 | 145 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 882 | 0 | 665.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.37 | 7 | 0 | 0 | 4.51 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.34 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 14 | 0.05 | 0 | 0 | 110 | 220 | 0 | 310 | 628 | 0 | 4479.67 | 9235.49 | 101.32
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 11 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.44 | 86 | 0 | 10 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 11 | 0 | 0 | 0 | 350 | 0 | 80 | 0 | 128 | 0 | 0 | 107 | 0 | 0 | 14 | 0 | 74 | 0 | 35 | 0 | 310 | 0 | 383 | 0 | 67 | 159 | 21 | 0 | 79 | 30 | 0 | 15 | 98 | 0 | 19 | 56 | 20 | 1 | 16.35 | 0 | 4867.79 | 896 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27.99 | 1062 | 0 | 545.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1 | 33 | 0 | 0 | 20.78 | 130 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 1.66 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1.9 | 56 | 0.18 | 0 | 0 | 110 | 220 | 0 | 309 | 750 | 0 | 4738.63 | 9606.42 | 101.31
09:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 19 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.43 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 612 | 15 | 0 | 0 | 0 | 335 | 0 | 84 | 0 | 128 | 0 | 0 | 105 | 0 | 0 | 14 | 0 | 74 | 0 | 54 | 0 | 305 | 0 | 336 | 0 | 67 | 155 | 21 | 0 | 76 | 30 | 0 | 15 | 98 | 0 | 19 | 55 | 18 | 1 | 29.54 | 0 | 4729.97 | 896 | 149 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 1090 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.43 | 60 | 0 | 0 | 37.04 | 130 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 2.99 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 3.5 | 101 | 0.23 | 0 | 0 | 110 | 220 | 0 | 311 | 782 | 0 | 4867.19 | 9597.16 | 101.31
10:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 25 | 0 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.06 | 86 | 0 | 7 | 650 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 612 | 18 | 0 | 0 | 0 | 255 | 0 | 44 | 0 | 125 | 0 | 0 | 104 | 0 | 0 | 14 | 0 | 84 | 0 | 66 | 0 | 315 | 0 | 336 | 0 | 67 | 153 | 21 | 0 | 78 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 18 | 1 | 37.79 | 0 | 4744.85 | 896 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 1010 | 0 | 466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.86 | 83 | 0 | 0 | 49.3 | 130 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 4.27 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 5.3 | 137 | 0.48 | 0 | 0 | 110 | 220 | 0 | 308 | 784 | 0 | 4886.21 | 9631.06 | 101.3
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 17 | 62 | 0 | 420 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 28 | 0 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 3.37 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 4 | 222 | 0 | 0 | 0 | 612 | 19 | 0 | 2 | 0 | 250 | 0 | 29 | 0 | 129 | 0 | 0 | 102 | 39 | 0 | 14 | 0 | 80 | 0 | 71 | 0 | 320 | 0 | 390 | 0 | 67 | 159 | 10 | 0 | 78 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 18 | 2 | 43.23 | 0 | 5012.6 | 896 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 995 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.5 | 94 | 0 | 0 | 56.02 | 130 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 4.96 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.6 | 158 | 0.56 | 0 | 0 | 110 | 220 | 0 | 308 | 790 | 0 | 4965.64 | 9978.24 | 101.3
12:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 35 | 0 | 17 | 0 | 134 | 0 | 17 | 145 | 0 | 420 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 29 | 0 | 23 | 21 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 12 | 3.39 | 86 | 17 | 7 | 650 | 0 | 0 | 20 | 0 | 83 | 220 | 0 | 0 | 0 | 612 | 20 | 0 | 71 | 0 | 250 | 0 | 18 | 0 | 128 | 0 | 15 | 101 | 79 | 0 | 14 | 0 | 88 | 0 | 71 | 0 | 320 | 0 | 390 | 0 | 67 | 162 | 21 | 0 | 81 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 15 | 2 | 43.69 | 0 | 5523.08 | 896 | 144 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82 | 981 | 0 | 468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.19 | 97 | 0 | 0 | 57.86 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.21 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5.7 | 162 | 0.52 | 0 | 0 | 110 | 220 | 0 | 310 | 790 | 0 | 4994.48 | 10517.56 | 101.3
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 50 | 0 | 17 | 0 | 210 | 5 | 35 | 140 | 0 | 420 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 27 | 52 | 19 | 21 | 0 | 0 | 74 | 16 | 0 | 0 | 0 | 0 | 33 | 0 | 37 | 24 | 3.1 | 86 | 89 | 14 | 650 | 60 | 0 | 43 | 5 | 90 | 217 | 0 | 0 | 0 | 612 | 18 | 0 | 122 | 0 | 240 | 0 | 69 | 0 | 125 | 0 | 69 | 101 | 17 | 0 | 14 | 0 | 78 | 0 | 65 | 1 | 310 | 0 | 353 | 0 | 67 | 156 | 21 | 0 | 81 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 12 | 2 | 41.77 | 0 | 6007.87 | 895 | 144 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 76 | 1077 | 0 | 468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 93 | 0 | 0 | 52.28 | 130 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 4.47 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.4 | 149 | 0.51 | 0 | 0 | 110 | 220 | 0 | 307 | 790 | 0 | 4997.66 | 11005.53 | 101.29
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 51.6 | 0 | 17 | 0 | 210 | 15 | 35 | 141 | 0 | 350 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 22 | 17 | 19 | 21 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 50 | 24 | 2.53 | 86 | 90 | 9 | 650 | 15 | 0 | 33 | 8 | 97 | 219 | 0 | 0 | 0 | 612 | 16 | 0 | 122 | 0 | 220 | 0 | 69 | 0 | 121 | 0 | 94 | 102 | 17 | 6 | 20 | 0 | 84 | 0 | 53 | 25 | 310 | 0 | 386 | 0 | 67 | 147 | 21 | 0 | 81 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 12 | 1 | 35.31 | 0 | 5849.44 | 896 | 135 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64 | 1072 | 0 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.73 | 77 | 0 | 0 | 41.48 | 130 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 3.73 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.3 | 130 | 0.43 | 0 | 0 | 110 | 180 | 0 | 307 | 790 | 0 | 4856.67 | 10706.11 | 101.29
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 49 | 0 | 17 | 0 | 195 | 0 | 35 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 15 | 0 | 19 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 24 | 1.7 | 86 | 68 | 4 | 650 | 0 | 0 | 33 | 0 | 94 | 216 | 0 | 0 | 0 | 612 | 11 | 0 | 80 | 0 | 225 | 0 | 95 | 0 | 127 | 0 | 95 | 102 | 17 | 9 | 20 | 0 | 90 | 0 | 38 | 28 | 305 | 0 | 386 | 0 | 67 | 144 | 21 | 0 | 81 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 12 | 1 | 22.98 | 0 | 5644.68 | 897 | 132 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43 | 1085 | 0 | 466.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.96 | 52 | 0 | 0 | 30.01 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.6 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.9 | 85 | 0.28 | 0 | 0 | 110 | 180 | 0 | 310 | 784 | 0 | 4691.63 | 10336.31 | 101.28
16:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 43.7 | 0 | 17 | 0 | 145 | 0 | 35 | 126 | 0 | 350 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 7 | 0 | 19 | 21 | 0 | 0 | 58 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 38 | 24 | 0.78 | 86 | 68 | 6 | 650 | 0 | 0 | 33 | 0 | 68 | 217 | 0 | 0 | 0 | 612 | 6 | 0 | 80 | 0 | 225 | 0 | 154 | 0 | 132 | 0 | 65 | 102 | 24 | 8 | 14 | 0 | 90 | 0 | 16 | 27 | 315 | 0 | 392 | 0 | 67 | 151 | 21 | 0 | 81 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 12 | 0 | 8.39 | 0 | 5636.87 | 896 | 132 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 1112 | 0 | 493.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.05 | 21 | 0 | 0 | 11.14 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.06 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.1 | 32 | 0.13 | 0 | 0 | 110 | 180 | 0 | 308 | 788 | 0 | 4590.3 | 10227.17 | 101.28
17:00 | 0 | 41 | 25 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 32.7 | 2 | 17 | 60 | 188 | 0 | 35 | 120 | 0 | 400 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 1 | 70 | 19 | 21 | 0 | 0 | 62 | 15 | 0 | 0 | 5 | 0 | 40 | 0 | 38 | 24 | 0.01 | 86 | 68 | 12 | 590 | 15 | 0 | 33 | 0 | 66 | 219 | 0 | 0 | 0 | 612 | 0 | 0 | 80 | 0 | 230 | 0 | 184 | 0 | 125 | 0 | 66 | 103 | 63 | 8 | 14 | 0 | 88 | 0 | 1 | 35 | 315 | 0 | 384 | 0 | 67 | 157 | 21 | 0 | 81 | 30 | 0 | 12 | 98 | 0 | 19 | 58 | 12 | 0 | 0.31 | 0 | 5873.02 | 895 | 132 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1106 | 0 | 701.67 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 10 | 0 | 0.92 | 1 | 16 | 0 | 0.85 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.08 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0.1 | 2 | 0 | 0 | 0 | 110 | 220 | 0 | 311 | 790 | 0 | 4885.62 | 10758.64 | 101.27
18:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 38.2 | 17 | 30 | 76 | 240 | 16 | 35 | 141 | 0 | 420 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 90 | 14.5 | 14 | 0 | 0 | 76 | 45 | 0 | 0 | 10 | 66 | 40 | 3 | 50 | 24 | 0 | 86 | 76 | 17 | 570 | 75 | 0 | 36 | 0 | 80 | 218 | 0 | 0 | 0 | 612 | 0 | 0 | 103 | 0 | 215 | 0 | 224 | 3 | 100 | 0 | 70 | 104 | 105 | 0 | 14 | 0 | 94 | 0 | 0 | 35 | 320 | 0 | 384 | 0 | 67 | 158 | 21 | 0 | 81 | 30 | 0 | 12 | 98 | 17 | 19 | 58 | 12 | 0 | 0 | 0 | 6385.7 | 896 | 132 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 5 | 749.13 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 28 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 105 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 311 | 798 | 17 | 5192.13 | 11577.83 | 101.27
19:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 47 | 17 | 34 | 90 | 290 | 36 | 35 | 140 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 16.5 | 21 | 0 | 0 | 34 | 15 | 0 | 0 | 13 | 19 | 70 | 0 | 50 | 24 | 0 | 86 | 106 | 20 | 595 | 110 | 0 | 50 | 0 | 96 | 218 | 0 | 0 | 0 | 612 | 0 | 0 | 133 | 0 | 215 | 0 | 230 | 0 | 30 | 0 | 45 | 105 | 120 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 353 | 0 | 67 | 149 | 22 | 0 | 81 | 30 | 0 | 12 | 98 | 17 | 19 | 58 | 12 | 0 | 0 | 0 | 6372.5 | 896 | 131 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1079 | 10 | 735.85 | 0 | 25 | 0 | 0 | 105 | 0 | 0 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 310 | 830 | 17 | 5165.85 | 11538.35 | 101.26
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 46.2 | 17 | 34 | 30 | 292 | 0 | 17 | 142 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 17 | 16.5 | 21 | 0 | 0 | 30 | 15 | 0 | 0 | 9 | 17 | 70 | 0 | 50 | 24 | 0 | 86 | 104 | 22 | 570 | 49 | 0 | 32 | 0 | 94 | 221 | 0 | 0 | 0 | 612 | 0 | 0 | 139 | 0 | 230 | 0 | 230 | 0 | 36 | 0 | 15 | 105 | 33 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 386 | 0 | 67 | 148 | 23 | 0 | 81 | 30 | 0 | 12 | 98 | 17 | 19 | 58 | 12 | 0 | 0 | 0 | 6019.7 | 896 | 132 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 0 | 735.28 | 0 | 40 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 790 | 0 | 5112.28 | 11131.98
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 46 | 17 | 34 | 15 | 293 | 0 | 17 | 141 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 16.5 | 21 | 0 | 0 | 33 | 0 | 0 | 0 | 3 | 8 | 70 | 0 | 50 | 24 | 0 | 86 | 105 | 27 | 570 | 0 | 0 | 33 | 0 | 93 | 221 | 0 | 0 | 0 | 612 | 0 | 0 | 138 | 0 | 240 | 0 | 230 | 0 | 39 | 0 | 16 | 105 | 34 | 0 | 20 | 0 | 78 | 0 | 0 | 0 | 300 | 0 | 381 | 0 | 67 | 152 | 23 | 0 | 81 | 30 | 0 | 15 | 98 | 0 | 19 | 58 | 20 | 0 | 0 | 0 | 5899.5 | 896 | 131 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 741.82 | 0 | 40 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 788 | 0 | 5141.82 | 11041.32 | 101.26
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 45.6 | 0 | 33 | 15 | 293 | 0 | 17 | 136 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 16.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 50 | 24 | 0 | 86 | 85 | 31 | 570 | 0 | 0 | 33 | 0 | 95 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 90 | 0 | 270 | 0 | 230 | 0 | 42 | 0 | 15 | 105 | 31 | 0 | 20 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 390 | 0 | 67 | 154 | 23 | 0 | 81 | 30 | 0 | 18 | 25 | 0 | 19 | 58 | 20 | 0 | 0 | 0 | 5687.1 | 896 | 131 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 741.92 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 309 | 780 | 0 | 5056.92 | 10744.02 | 101.25
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 50 | 0 | 33 | 15 | 195 | 0 | 17 | 108 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 50 | 24 | 0 | 86 | 34 | 32 | 570 | 0 | 0 | 33 | 0 | 96 | 225 | 0 | 0 | 0 | 612 | 0 | 0 | 90 | 0 | 285 | 0 | 230 | 0 | 32 | 16 | 14 | 106 | 32 | 0 | 20 | 0 | 78 | 0 | 0 | 0 | 310 | 0 | 376 | 0 | 67 | 157 | 23 | 0 | 81 | 30 | 0 | 18 | 25 | 0 | 19 | 58 | 20 | 0 | 0 | 0 | 5491 | 897 | 135 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 748.73 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 778 | 0 | 4969.73 | 10460.73 | 101.25
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 38.5 | 0 | 33 | 0 | 45 | 0 | 17 | 72 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 12 | 0 | 86 | 0 | 28 | 570 | 0 | 0 | 0 | 0 | 96 | 225 | 0 | 0 | 0 | 612 | 0 | 0 | 80 | 0 | 280 | 0 | 230 | 0 | 34 | 20 | 16 | 105 | 31 | 0 | 20 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 392 | 0 | 67 | 154 | 23 | 0 | 81 | 30 | 0 | 18 | 25 | 0 | 19 | 58 | 20 | 0 | 0 | 0 | 5116.5 | 896 | 135 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 738.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 306 | 785 | 0 | 4834.84 | 9951.34 | 101.24
Total KWH | 0 | 618240 | 360000 | 0 | 0 | 0 | 0 | 0 | 8737200 | 0 | 0 | 518400 | 73080 | 417312 | 229920 | 2471455 | 96105 | 349743 | 1588320 | 0 | 9311000 | 0 | 0 | 0 | 116730 | 7672594 | 0 | 0 | 186576 | 265200 | 425400 | 505080 | 0 | 0 | 588382 | 122945 | 0 | 0 | 114240 | 113313 | 507456 | 18893 | 562560 | 296640 | 22082 | 2085600 | 888218 | 421920 | 14836363.64 | 240873 | 0 | 425280 | 28368 | 1189309 | 5228061 | 0 | 0 | 0 | 13221817 | 135945 | 0 | 1373309 | 0 | 6526000 | 0 | 3318000 | 6240 | 2026000 | 68608 | 624000 | 2499307 | 654720 | 33600 | 425940 | 0 | 1829760 | 0 | 484255 | 159376 | 7585500 | 0 | 9229000 | 0 | 1585440 | 3705300 | 521280 | 0 | 1752960 | 709920 | 0 | 355000 | 2096220 | 56520 | 409200 | 1082400 | 422400 | 12250 | 285780 | 0 | 124828905.64 | 21710545 | 3381696 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 523440 | 24421820 | 20640 | 28853091 | 0 | 80983 | 0 | 0 | 561216 | 0 | 0 | 34524 | 0 | 338192 | 627850 | 155225 | 0 | 360752 | 3230455 | 0 | 0 | 0 | 0 | 0 | 8423018 | 0 | 31320 | 0 | 0 | 347955 | 191617 | 703497 | 0 | 0 | 0 | 35758.32 | 1031040 | 3510 | 0 | 0 | 2641000 | 5204510 | 0 | 7410168 | 17956363.64 | 30000 | 129222185.96 | 254051091.6

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-11-2025 | during | 14-11-2025 | during | 14-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 382 | 363 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 16 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 38.2 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 76 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 14.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 134 | 240 | 300 | 300 | 100 | 100 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 30 | 149 | 149 | 17 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 88 | 88 | 88 | 88 | 88 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 145 | 141 | 162 | 162 | 146 | 146 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 90 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1596 | 1957.7 | 5917.1 | 5885.1 | 3155.85 | 3140.85
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 36 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 83 | 80 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 17 | 35 | 35 | 35 | 35 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.39 | 0 | 3.4 | 0 | 3.4 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 5 | 45 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 3 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 76 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 1 | 76 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 75 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 10 | 1 | 8 | 1 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 570 | 315 | 315 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1773.39 | 2084 | 2640.12 | 2632.72 | 2415.9 | 2408.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 128 | 100 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Planned Shutdown
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 18 | 224 | 318.81 | 318.81 | 318.81 | 318.81 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 215 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 3 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 0.01 | 0.01 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 71 | 103 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 35 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 101 | 104 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 79 | 105 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 88 | 94 | 160 | 160 | 94 | 94 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 15 | 70 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 835 | 1067 | 2484.21 | 2419.21 | 1915.22 | 1850.22
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-11-2025 | during | 14-11-2025 | during | 14-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 15 | 12 | 157.5 | 157.5 | 30 | 30 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 18.5 | 18.5 | 18.5 | 18.5 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.69 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 137.69 | 106 | 362.5 | 312.5 | 175.5 | 125.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 162 | 158 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 98 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 12 | 12 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 384 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1181 | 1171 | 1217 | 1217 | 1139 | 1139
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 896 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 144 | 132 | 410 | 410 | 167 | 167 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 5 | 105 | 105 | 0 | 34 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 84 | 0 | 84 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 981 | 1130 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2141 | 2201 | 2402 | 2318 | 2546 | 2496
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 310 | 311 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 790 | 798 | 857 | 857 | 857 | 857 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1430.52 | 1456 | 1453 | 1452 | 1320 | 1319
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 52.19 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 49 | 49 | 49 | 49 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 130 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 350 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 27 | 27 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 45 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Under Maintenance
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.21 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 468 | 749.13 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.86 | 0 | 59 | 0 | 59 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1224.26 | 1330.13 | 2398.58 | 2233.99 | 1694.2 | 1529.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 105 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 162 | 0 | 166.59 | 0 | 166.59 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 198.7 | 205 | 464.39 | 262 | 352.39 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 10517.56 | 11577.83 | 19338.9 | 18732.52 | 14714.06 | 14236.68
Forecast Scenario (14-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10200 |  | 0 |  | 10200
|  |  |  | 1:00 | 9820 |  | 0 |  | 9820
|  |  |  | 2:00 | 9520 |  | 0 |  | 9520
|  |  |  | 3:00 | 8980 |  | 0 |  | 8980
|  |  |  | 4:00 | 8630 |  | 0 |  | 8630
|  |  |  | 5:00 | 8500 |  | 0 |  | 8500
|  |  |  | 6:00 | 8210 |  | 0 |  | 8210
|  |  |  | 7:00 | 8200 |  | 0 |  | 8200
|  |  |  | 8:00 | 8200 |  | 0 |  | 8200
|  |  |  | 9:00 | 8040 |  | 0 |  | 8040
|  |  |  | 10:00 | 8050 |  | 0 |  | 8050
|  |  |  | 11:00 | 8390 |  | 0 |  | 8390
|  |  |  | 12:00 | 8980 |  | 0 |  | 8980
|  |  |  | 13:00 | 10000 |  | 0 |  | 10000
|  |  |  | 14:00 | 9550 |  | 0 |  | 9550
|  |  |  | 15:00 | 9300 |  | 0 |  | 9300
|  |  |  | 16:00 | 8840 |  | 0 |  | 8840
|  |  |  | 17:00 | 8690 |  | 0 |  | 8690
|  |  |  | 18:00 | 10670 |  | 0 |  | 10670
|  |  |  | 18:30 | 10750 |  | 0 |  | 10750
|  |  |  | 19:00 | 10800 |  | 0 |  | 10800
|  |  |  | 19:30 | 10770 |  | 0 |  | 10770
|  |  |  | 20:00 | 10742 |  | 0 |  | 10742
|  |  |  | 21:00 | 10785 |  | 0 |  | 10785
|  |  |  | 22:00 | 10750 |  | 0 |  | 10750
|  |  |  | 23:00 | 10490 |  | 0 |  | 10490
Probable Maximum Temperature: |  |  | 30.20°C
Probable Maximum Demand at Day Peak: |  |  | 8980.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 224.337 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:33 hrs on 14-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10517.56 | MW | 12:00 Hr. | Energy Generated |  |  | 254.0511 |  | MKWHr.
| Day Peak Demand |  |  | 10517.56 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11577.83 | MW | 18:00 Hr. | Energy Demand |  |  | 254.0511 |  | MKWHr.
| Evening Peak Demand |  |  | 11577.83 | MW | 18:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 8224.32 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 759.33 |  | MMCFD
| Maximum Generation of the Day |  |  | 11577.83 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 6.1044 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.6513 | 0 | 7.1045 | 0 | 0 | 0.18658 | 0 | 0 | 33.9424 | Gas | 98.015 | Gas | 346509192.67
| Chattogram Zone |  |  | 5.65 | 28.0582 | 4.9822 | 0 | 2.0856 | 0.15803 | 0 | 0.11424 | 41.0483 | Coal | 77.8465 | Coal | 498155133.5936
| Cumilla Zone |  |  | 14.8701 | 0 | 2.845 | 0 | 0 | 0.48425 | 1.8298 | 0 | 20.0291 | HFO | 18.4139 | HFO | 317893930
| Mymensingh Zone |  |  | 0.4224 | 0 | 1.5481 | 0 | 0 | 0.29803 | 0 | 0 | 2.2685 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5406 | Hydro | 2.0856 | Hydro | 208560
| Khulna Zone |  |  | 3.3817 | 24.4218 | 0.02064 | 0 | 0 | 0.52344 | 22.6225 | 0 | 50.9701 | Solar | 4.2704 | Solar | 67924101.3112
| Barishal Zone |  |  | 7.8455 | 25.3665 | 0.03 | 0 | 0 | 0.00351 | 0 | 0 | 33.2456 | Import | 53.3054 | Import | 318465264.71
| Rajshahi Zone |  |  | 11.6535 | 0 | 0.83195 | 0 | 0 | 1.3581 | 28.8531 | 0 | 42.6966 | Wind | 0.11424 | Wind | 1680470.4
| Rangpur Zone |  |  | 0 | 0 | 1.0515 | 0 | 0 | 1.2584 | 0 | 0 | 2.3099
| Total |  |  | 98.015 | 77.8465 | 18.4139 | 0 | 2.0856 | 4.2704 | 53.3054 | 0.11424 | 254.0511
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 346509192.67 |  | Hydro | 208560
|  |  |  | Coal | 498155133.5936 |  | Solar | 67924101.3112
|  |  |  | HFO | 317893930 |  | Import | 318465264.71
|  |  |  | HSD | 0 |  | Wind | 1680470.4
[5 empty] | Total: | 155,08,36,652 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7105 | Peak Hr Flow | 896.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45760472.74 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.8531 | Peak Hr Flow | 749.13 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1870 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.8298 | Peak Hr Flow | 94.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2478 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.3934 | Peak Hr Flow | 1739.13 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4538
|  |  |  | Chattogram |  | 0 |  | 1436
|  |  |  | Cumilla |  | 0 |  | 1057
|  |  |  | Mymensingh |  | 0 |  | 866
|  |  |  | Sylhet |  | 0 |  | 479
|  |  |  | Khulna |  | 0 |  | 1227
|  |  |  | Barishal |  | 0 |  | 298
|  |  |  | Rajshahi |  | 0 |  | 936
|  |  |  | Rangpur |  | 0 |  | 712
|  |  |  | Total |  | 0 |  | 11549
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 12:58 | Bhaluka 132/33kV S/S Capacitor Bank- 01 Scheduled S/D Due to Annual maintenance
| 08:01 | 12:58 | Bhaluka 132/33kV S/S Capacitor Bank- 02 Scheduled S/D Due to Annual maintenance
| 08:10 | 17:10 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Annual Maintenance Work.
| 08:10 | 17:09 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Annual Maintenance Work.
| 08:16 | 14:31 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to 132/33 kv TR-02 bay annual
maintenance.
| 08:16 | 14:31 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to 132/33 kv TR-02 bay annual
maintenance.
| 08:20 | 16:11 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance
| 08:22 | 16:05 | Palashbari 132/33kV S/S TR2-404T LT Scheduled S/D Due to Annual Maintenance
| 08:23 | 16:04 | Palashbari 132/33kV S/S TR2-404T HT Scheduled S/D Due to Annual Maintenance
| 08:23 | 15:14 | Panchagarh 132/33kV S/S Thakurgaon- 2 Scheduled S/D Due to Annual maintenance work
| 08:25 | 15:12 | Thakurgaon 132/33kV S/S Panchagar CKT-2 Scheduled S/D Due to Annual maintenance
| 08:30 | 16:25 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to annual
maintenance by kaliakoir grid SS. and from Kaliakoir 400/230/132kV end Due to Annual
maintenance.
| 08:31 |  | Jhenaidah 132/33kV S/S Jhenaidah-Kushtia 132kV Circuit-1(L1) Scheduled S/D Due to
Upgradation work
| 08:32 |  | Jhenaidah-Kushtia 132kV Ckt-1 Project Work S/D from Kushtia 132/33kV end Due to 132 kV
Circuit Breaker Replacement Work
| 08:34 | 16:52 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end
Due to Annual Maintenance Work
| 08:34 |  | Bheramara P/S-Kustia 132 kV Ckt-1 Project Work S/D from Kushtia 132/33kV end Due to 132
kV Circuit Breaker Replacement Work and from Bheramara 230/132kV end Due to A/M
| 08:38 | 15:46 | Amnura 132/33kV S/S T-3 (426T) HT Scheduled S/D Due to Annual Maintenance
| 08:42 | 15:56 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to
Maintenance work
| 08:47 | 12:59 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Scheduled S/D from Bog-Sherpur 132/33kV end Due to
Anual Maintenance work and from Sirajganj 132/33kV end Due to Annual Maintance Purpose
(Work Place: Sherpur Sub-Station end). all operation has been conducted by the
instruction of ALDC, Bogura.
| 08:47 | 15:28 | Ghorasal- Ishwardi 230 kV Ckt-1 Project Work S/D from Ishurdi 230/132kV end. and from
Ghorashal 230kV end Due to G2G project works
| 08:55 | 17:21 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Annual maintenance
| 08:55 | 12:58 | Tangail 132/33kV S/S Tr-2 LT Scheduled S/D Due to Annaual Maintenance.
| 08:55 | 12:58 | Tangail 132/33kV S/S Tr-2 HT Scheduled S/D Due to Annaual Maintenance.
| 08:56 | 17:18 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Annual maintenance
| 09:35 | 17:08 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to Annual
Maintenance
| 09:35 | 17:07 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to Annual
Maintenance
| 09:36 | 15:47 | BIPTC S/S 20DF21 Scheduled S/D Due to For Annual Maintenance
| 10:10 | 15:36 | Tongi 230/132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to Annual maintenance
| 10:28 |  | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Transformer Oil leakage test.
| 11:13 |  | Monakasha-Rahanpur 400kV Ckt-1 Scheduled S/D from Rahanpur 400/132kV end Due to As per
instruction of ALDC Bogura
| 11:15 | 13:15 | New Tongi S/S Tr-1 (4061-3) Scheduled S/D Due to Annual Maintanance.
| 11:27 |  | 400/230 kV, 750 MVA ATR-03 transformer was charged at Meghnaghat 400/230 kV grid s/s from
400 kV side for the first time.
|  | 11:51 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
| 12:01 | 13:09 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-01 Project Work S/D Due to SCADA
OPERATION
| 12:09 | 13:26 | Rangamati 132/33kV S/S Main Bus 02 Scheduled S/D Due to Annual Maintenance.
| 12:20 | 13:10 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-1 Scheduled S/D Due to Test perform at Muradnagar
end.
|  | 12:57 | Siddhirganj 132/33kV S/S T-2 HT is restored.
|  | 12:58 | Siddhirganj 132/33kV S/S T-2 LT is restored.
| 13:00 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Solar aviation
light, and ball setting
| 13:00 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Scheduled S/D Due to Solar aviation
light, and ball setting
| 13:06 | 15:17 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to
Annual Maintenance
|  | 13:31 | Juldah-Shahmirpur 132kV Ckt-2 is restored.
|  | 13:34 | Ishurdi-Pabna 132kV ckt is restored.
| 13:54 |  | 400/230 kV, 750 MVA ATR-03 transformer of Meghnaghat was switched ON with load.
| 13:55 | 14:10 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing DIR O/C & E/F RELAY relays Due to Due to | [7 empty] | 42.0MW load
|  |  | salam steel cable fault | [7 empty] | interrup.
|  | 14:21 | Chhatak 132/33kV S/S T-1 HT is restored.
| 14:43 | 15:20 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-01 Project Work S/D Due to SCADA
| 14:47 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 14:50 | 17:33 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to
Maintenance at Muradnagar Substation
|  | 15:13 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT is restored.
| 15:28 | 15:51 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 Project Work S/D Due to
SCADA Work
|  | 15:45 | Savar 132/33kV S/S Bus-B is restored.
|  | 15:53 | Savar 132/33kV S/S Main Bus-II is restored.
|  | 15:54 | Amnura 132/33kV S/S T-3 (426T) LT is restored.
|  | 15:55 | Savar 132/33kV S/S T-2 LT is restored.
|  | 15:55 | Savar 132/33kV S/S T-2 HT is restored.
| 16:08 | 17:13 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Project Work S/D Due to SCADA Work. | [7 empty] | 10.0MW load
interrup.
| 17:26 | 21:45 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to project work shutdown
| 18:00 |  | Evening Peak Generation: 11577 MW.
|  | 18:05 | Barishal 230/132kV S/S Gopalgonj CKT-2 is restored.
|  | 18:06 | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 is restored.
|  | 20:45 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT is restored.
|  | 20:45 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT is restored.
| 21:18 | 21:36 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Over current protection p142, lockout | [7 empty] | 14.7MW load
|  |  | relay1 &2. relays Due to For 33 kv pbs sholla feeder fault. | [7 empty] | interrup.
| 21:18 | 21:33 | Nawabganj 132/33kV S/S TR-1 LT Tripped showing Over current protection P142, lockout | [7 empty] | 14.7MW load
|  |  | Relay -1 &2. relays Due to For 33 kv pbs sholla feeder fault. | [7 empty] | interrup.
| 23:48 |  | Sylhet 225MW CCPP ST was sync.
| 06:00 |  | Min. Gen. 7954 MW
| 06:00 |  | Minimum Generation: 7954 MW.
| 06:18 |  | Fenchuganj GT-3 tripped.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 363 | 8737200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9311000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 16 | 96105 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7672594 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 38.2 | 518400 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 76 | 229920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 349743 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 116730 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14.5 | 425400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 505080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 360000 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 240 | 2471455 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 30 | 417312 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 618240 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 141 | 1588320 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 186576 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 73080 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | under maint.
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 90 | 265200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1957.7 | 33942355
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 28368 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 135945 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 36 | 425280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2085600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5228061 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 80 | 1189309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 507456 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 113313 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 562560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 421920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22082 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 122945 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 3 | 18893 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 76 | 888218 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 296640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 76 | 588382 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 75 | 240873 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13221817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 114240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 570 | 14836363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2084 | 41048265.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 100 | 2026000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Depending on fuel availability
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 224 | 3318000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 6526000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 68608 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 3 | 6240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 103 | 1373309 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 159376 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2499307 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 105 | 654720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 94 | 1829760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 425940 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 33600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 70 | 624000 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 484255 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1067 | 20029115
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 12 | 422400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1082400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 409200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 285780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 56520 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 106 | 2268550
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1585440 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 158 | 3705300 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 709920 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1752960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2096220 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 355000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 521280 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7585500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 384 | 9229000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1171 | 27540620
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 896 | 21710545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 132 | 3381696 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 5 | 20640 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 523440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1130 | 24421820 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2201 | 50970141
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 311 | 7410168 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2641000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 798 | 17956363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5204510 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 30000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3510 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1456 | 33245551.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 338192 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 80983 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 34524 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 130 | 3230455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 8423018 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 155225 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Under Maintenance
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 45 | 561216 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Under Maintenance
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 749.13 | 28853091 | Unit #1 Under Maintenance.
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 360752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 627850 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1330.13 | 42696626
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 703497 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35758.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 105 | 347955 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 191617 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1031040 | -
Rangpur Area Total |  |  |  |  | 950 | 205 | 2309867.32
Eastern Grid Total |  |  |  |  | 17383.855 | 6385.7 | 124828905.64
Western Grid Total |  |  |  |  | 10821.56 | 5192.13 | 129222185.96
National Grid Total |  |  |  |  | 28205.415 | 11577.83 | 254051091.6
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8375.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3173 | MW
i) Dhaka area |  |  | 4538.04 |  | MW | i) Khulna area |  |  |  | 1227 | MW
ii) Chattogram area |  |  | 1436 |  | MW | ii) Barishal area |  |  |  | 298.2 | MW
iii) Cumilla area |  |  | 1056.55 |  | MW | iii) Rajshahi area |  |  |  | 935.8 | MW
iv) Mymensingh area |  |  | 866 |  | MW | iv) Rangpur area |  |  |  | 712 | MW
v) Sylhet area |  |  | 479 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11548.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 63 | 19:30 | 133 | Niamatpur | 38 | 18:00
2 | AKSML | 141.3 | 03:00 | 68 | Ishurdi | 57 | 18:30 | 134 | Noapara | 35 | 18:30
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 63 | 18:00 | 135 | PHP | 9 | 17:00
4 | Agargaon | 99 | 14:00 | 70 | Jamalpur | 83 | 18:30 | 136 | Pabna | 67 | 18:00
5 | Agrabad | 82 | 18:00 | 71 | Jashore | 95 | 18:30 | 137 | Palashbari | 80 | 15:00
6 | Amnura | 15 | 19:00 | 72 | Jhenaidah | 92 | 18:00 | 138 | Panchagarh | 42 | 18:30
7 | Ashuganj | 75 | 00:00 | 73 | Joydebpur | 128 | 18:00 | 139 | Patiya | 8 | 18:00
8 | BSRM | 206 | 18:00 | 74 | Joypurhat | 40 | 18:30 | 140 | Patuakhali | 54 | 21:00
9 | Bagerhat | 61 | 19:00 | 75 | Juldah | 17 | 12:00 | 141 | Payra | 22 | 19:00
10 | Bajitpur | 60 | 18:00 | 76 | KSRM | 31 | 18:30 | 142 | Postogola | 55 | 13:00
11 | Bakulia | 71 | 18:00 | 77 | Kabirpur | 200 | 16:00 | 143 | Purbachal | 15 | 13:00
12 | Banani | 37.2 | 13:00 | 78 | Kachua | 58 | 18:00 | 144 | Purbasadipur | 93 | 18:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 78 | 11:00 | 145 | Rahanpur | 18 | 21:00
14 | Barapukuria | 48 | 18:30 | 80 | Kalurghat | 46 | 15:00 | 146 | Rahim | 46 | 13:00
15 | Barguna | 0 | 00:00 | 81 | Kamrangirchar | 65 | 13:00 | 147 | Rajbari | 56 | 18:00
16 | Barishal | 91 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 104 | 18:00
17 | Barishal-230 | 66 | 18:00 | 83 | Kasba | 24 | 13:00 | 149 | Rajshahi | 80 | 13:00
18 | Baroaulia | 62 | 13:00 | 84 | Kazla | 89 | 13:00 | 150 | Rajshahi-230 | 52 | 13:00
19 | Baroirhat | 44 | 18:00 | 85 | Keranigonj | 72 | 12:00 | 151 | Ramganj | 72 | 18:00
20 | Bashundhara | 160 | 18:00 | 86 | Khagrachori | 26 | 18:00 | 152 | Rampur | 36 | 18:30
21 | BashundharaCement | 12 | 12:00 | 87 | Khulna | 53 | 13:00 | 153 | Rangamati | 14 | 18:00
22 | Beanibazar | 52 | 18:00 | 88 | Khulshi | 173 | 18:00 | 154 | Rangpur | 117 | 18:00
23 | Benapole | 48 | 12:00 | 89 | Kishoreganj | 90 | 18:00 | 155 | Ruppur | 6 | 11:00
24 | Bhaluka | 116 | 18:00 | 90 | Kodda | 281 | 15:00 | 156 | SSM | 3 | 01:00
25 | Bhandaria | 42 | 21:00 | 91 | Kulaura | 36 | 18:30 | 157 | Saidpur | 84 | 18:00
26 | Bhangura | 23 | 18:00 | 92 | Kurigram | 48 | 18:30 | 158 | Satkhira | 82 | 18:30
27 | Bheramara(GK) | 41 | 18:00 | 93 | Kushtia | 105 | 18:30 | 159 | Satmasjid | 87 | 13:00
28 | Bhulta | 198 | 12:00 | 94 | Laksam | 22 | 18:00 | 160 | Savar | 186 | 16:00
29 | Bog-Sherpur | 54 | 18:00 | 95 | Lakshmipur | 20 | 18:00 | 161 | SevenRings | 17.99 | 00:00
30 | Bogura | 122 | 19:00 | 96 | Lalbag | 61 | 17:00 | 162 | ShahCement | 16 | 00:00
31 | Borhanuddin | 64 | 21:00 | 97 | Lalmonirhat | 42 | 18:00 | 163 | Shahjadpur | 57 | 18:30
32 | Brahmanbaria | 100 | 18:00 | 98 | MI_Cement | 14.4 | 09:00 | 164 | Shahjibazar | 93 | 18:00
33 | Cantonment | 110 | 13:00 | 99 | Madanganj | 36 | 08:00 | 165 | Shahmirpur | 48 | 17:00
34 | Chandina | 11.55 | 18:00 | 100 | Madaripur | 66 | 20:00 | 166 | Shariatpur | 55 | 21:00
35 | Chandpur | 54 | 18:00 | 101 | Madartek | 70 | 18:00 | 167 | Sherpur | 100 | 18:00
36 | Chandraghona | 29 | 18:00 | 102 | Madunaghat | 43 | 18:00 | 168 | Shikalbaha | 22 | 13:00
37 | Chapai | 40 | 21:00 | 103 | Magura | 44 | 18:30 | 169 | Shitalakhya | 60.7 | 16:00
38 | Charsaidpur | 38 | 00:00 | 104 | Mahasthangarh | 48 | 18:00 | 170 | Sholosohor | 41 | 12:00
39 | Chauddagram | 45 | 13:00 | 105 | Maijdee | 21 | 21:00 | 171 | Shyampur | 124 | 12:00
40 | Chhatak | 27 | 01:00 | 106 | Manikganj | 97 | 18:30 | 172 | Siddhirganj | 103 | 18:30
41 | Chowmuhani | 120 | 18:00 | 107 | Maniknagar | 56 | 13:00 | 173 | Sirajganj | 76 | 18:30
42 | Chuadanga | 71 | 18:00 | 108 | Matarbari | 44 | 18:30 | 174 | Sonargaon | 114 | 17:00
43 | Coxsbazar | 123 | 18:00 | 109 | Matuail | 64 | 12:00 | 175 | Sreemongol | 62 | 18:00
44 | Cumilla(N) | 102 | 18:00 | 110 | Metrorail_Motijheel | 27 | 18:30 | 176 | Sreepur | 80 | 18:00
45 | Cumilla(S) | 119 | 18:00 | 111 | Metrorail_Uttara | 8 | 19:00 | 177 | Srinagar | 31.8 | 20:00
46 | Daganbhuiyan | 0 | 06:00 | 112 | Millgate | 92 | 12:00 | 178 | Sunamganj | 44 | 18:00
47 | Daudkandi | 114 | 20:00 | 113 | Mirpur | 112 | 18:00 | 179 | Sylhet | 39 | 14:00
48 | DhakaUniversity | 66 | 13:00 | 114 | Mirsorai | 8 | 10:00 | 180 | Sylhet-132 | 97 | 18:00
49 | Dhamrai | 114 | 18:00 | 115 | Mirzapur | 37 | 18:00 | 181 | TK | 18 | 18:00
50 | Dhanmondi | 99.2 | 13:00 | 116 | Mithapukur | 46 | 18:00 | 182 | Tangail | 124 | 18:30
51 | Dohazari | 80 | 17:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 16 | 18:00
52 | Faridpur | 112 | 18:00 | 118 | Mogbazar | 72.1 | 13:00 | 184 | Thakurgaon | 76 | 18:30
53 | Fatullah | 107 | 12:00 | 119 | Mongla | 44 | 18:00 | 185 | Tongi | 106 | 12:00
54 | Fenchuganj | 31 | 18:00 | 120 | Motijheel | 29 | 12:00 | 186 | Ullahpara | 25 | 19:00
55 | Feni | 88 | 18:00 | 121 | Muktagacha | 24 | 07:00 | 187 | Ullon | 56 | 13:00
56 | GPH | 18 | 00:00 | 122 | Munshiganj | 81 | 14:00 | 188 | Uttara | 68 | 13:00
57 | Ghatail | 58 | 17:00 | 123 | Muradnagar | 29 | 18:00 | 189 | UttaraNew | 22 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 150 | 18:00 | 190 | Zigatola | 54 | 13:00
59 | Ghorashal-230 | 81 | 19:00 | 125 | Naogaon | 78 | 18:00
60 | Goalpara | 24 | 13:00 | 126 | Narail | 41 | 18:00
61 | Gollamari | 76 | 13:00 | 127 | Narinda | 56 | 13:00
62 | Gopalganj | 76 | 18:00 | 128 | Narshingdi | 140 | 19:00
63 | Gulshan | 90 | 13:00 | 129 | Natore | 99 | 18:00
64 | Halishahar | 66 | 15:00 | 130 | Nawabganj | 31 | 22:00
65 | HaripurSBU | 146 | 17:00 | 131 | Netrakona | 100 | 18:00
66 | Hasnabad | 70 | 12:00 | 132 | New | 65 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9769.73 | 0 |  | 9769.73
1:00 | 8976.76 | 0 |  | 8976.76
2:00 | 8673.79 | 0 |  | 8673.79
3:00 | 8313.21 | 0 |  | 8313.21
4:00 | 8263.08 | 0 |  | 8263.08
5:00 | 8224.32 | 0 |  | 8224.32
6:00 | 8428.48 | 0 |  | 8428.48
7:00 | 9235.49 | 0 |  | 9235.49
8:00 | 9606.42 | 0 |  | 9606.42
9:00 | 9597.16 | 0 |  | 9597.16
10:00 | 9631.06 | 0 |  | 9631.06
11:00 | 9978.24 | 0 |  | 9978.24
12:00 | 10517.56 | 0 |  | 10517.56
13:00 | 11005.53 | 0 |  | 11005.53
14:00 | 10706.11 | 0 |  | 10706.11
15:00 | 10336.31 | 0 |  | 10336.31
16:00 | 10227.17 | 0 |  | 10227.17
17:00 | 10758.64 | 0 |  | 10758.64
18:00 | 11577.83 | 0 |  | 11577.83
19:00 | 11538.35 | 0 |  | 11538.35
19:30 | 11131.98 | 0 |  | 11131.98
20:00 | 11041.32 | 0 |  | 11041.32
21:00 | 10744.02 | 0 |  | 10744.02
22:00 | 10460.73 | 0 |  | 10460.73
23:00 | 9951.34 | 0 |  | 9951.34
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4623 | 5146.73 | 9769.73 | DAILY GENERATION CURVE
00:30 | 4381 | 4992.245 | 9373.245
01:00 | 4139 | 4837.76 | 8976.76 | 13-11-2025
01:30 | 4103 | 4722.275 | 8825.275
02:00 | 4067 | 4606.79 | 8673.79
02:30 | 4001.5 | 4492 | 8493.5
03:00 | 3936 | 4377.21 | 8313.21
03:30 | 3933.5 | 4354.645 | 8288.145
04:00 | 3931 | 4332.08 | 8263.08
04:30 | 3953 | 4290.7 | 8243.7
05:00 | 3975 | 4249.32 | 8224.32
05:30 | 4072 | 4254.4 | 8326.4
06:00 | 4169 | 4259.48 | 8428.48
06:30 | 4462.41 | 4369.575 | 8831.985
07:00 | 4755.82 | 4479.67 | 9235.49
07:30 | 4811.805 | 4609.15 | 9420.955
08:00 | 4867.79 | 4738.63 | 9606.42
08:30 | 4798.88 | 4802.91 | 9601.79
09:00 | 4729.97 | 4867.19 | 9597.16
09:30 | 4737.41 | 4876.7 | 9614.11
10:00 | 4744.85 | 4886.21 | 9631.06
10:30 | 4878.725 | 4925.925 | 9804.65
11:00 | 5012.6 | 4965.64 | 9978.24
11:30 | 5267.84 | 4980.06 | 10247.9
12:00 | 5523.08 | 4994.48 | 10517.56
12:30 | 5765.475 | 4996.07 | 10761.545
13:00 | 6007.87 | 4997.66 | 11005.53
13:30 | 5928.655 | 4927.165 | 10855.82
14:00 | 5849.44 | 4856.67 | 10706.11
14:30 | 5747.06 | 4774.15 | 10521.21
15:00 | 5644.68 | 4691.63 | 10336.31
15:30 | 5640.775 | 4640.965 | 10281.74
16:00 | 5636.87 | 4590.3 | 10227.17
16:30 | 5754.945 | 4737.96 | 10492.905
17:00 | 5873.02 | 4885.62 | 10758.64
17:30 | 6129.36 | 5038.875 | 11168.235
18:00 | 6385.7 | 5192.13 | 11577.83
18:30 | 6379.1 | 5178.99 | 11558.09
19:00 | 6372.5 | 5165.85 | 11538.35
19:30 | 6019.7 | 5112.28 | 11131.98
20:00 | 5899.5 | 5141.82 | 11041.32
20:30 | 5793.3 | 5099.37 | 10892.67 |  | Executive Engineer
21:00 | 5687.1 | 5056.92 | 10744.02 |  | Network Operation Division
21:30 | 5589.05 | 5013.325 | 10602.375
22:00 | 5491 | 4969.73 | 10460.73
22:30 | 5303.75 | 4902.285 | 10206.035
23:00 | 5116.5 | 4834.84 | 9951.34

## En-Curve
QF-LDC-12
Date | 13-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2807 | 1215 | 896 | 38 | 74 | 1183.73 | 86 | 3313 | 0 | 8 | 138 | 0 | 0 | 11 | 0 | DAILY ENERGY CURVE
00:30 | 2668 | 1212 | 896 | 38 | 70 | 1112.245 | 86 | 3183.5 | 0 | 4 | 91.5 | 0 | 0 | 12 | 0 | 13-11-2025
01:00 | 2529 | 1209 | 896 | 38 | 66 | 1040.76 | 86 | 3054 | 0 | 0 | 45 | 0 | 0 | 13 | 0
01:30 | 2547 | 1189 | 896 | 38 | 68 | 988.275 | 86 | 2966.5 | 0 | 0 | 36 | 0 | 0 | 10.5 | 0 | Energy Generated | 254.0511 |  | MKWHr
02:00 | 2565 | 1169 | 896 | 38 | 70 | 935.79 | 86 | 2879 | 0 | 0 | 27 | 0 | 0 | 8 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2547.5 | 1164.5 | 896 | 38 | 67 | 891.5 | 86 | 2771.5 | 0 | 0 | 21.5 | 0 | 0 | 10 | 0 | Total Energy Requirement | 254.0511 |  | MKWHr
03:00 | 2530 | 1160 | 896 | 38 | 64 | 847.21 | 86 | 2664 | 0 | 0 | 16 | 0 | 0 | 12 | 0
03:30 | 2600 | 1112.5 | 896 | 38 | 66 | 833.145 | 86 | 2628 | 0 | 0 | 16 | 0 | 0 | 12.5 | 0
04:00 | 2670 | 1065 | 896 | 38 | 68 | 819.08 | 86 | 2592 | 0 | 0 | 16 | 0 | 0 | 13 | 0
04:30 | 2693 | 1067.5 | 896 | 38 | 68 | 803.7 | 86 | 2565 | 0 | 0 | 16 | 0 | 0 | 10.5 | 0
05:00 | 2716 | 1070 | 896 | 38 | 68 | 788.32 | 86 | 2538 | 0 | 0 | 16 | 0 | 0 | 8 | 0
05:30 | 2743 | 1102 | 896 | 38 | 66 | 782.9 | 86 | 2588.5 | 0 | 0 | 16 | 0 | 0 | 8 | 0
06:00 | 2770 | 1134 | 896 | 38 | 64 | 777.48 | 86 | 2639 | 0 | 0 | 16 | 0 | 0 | 8 | 0
06:30 | 2887 | 1213 | 896.5 | 38 | 64 | 721.64 | 86 | 2844.5 | 30.845 | 6.5 | 38.5 | 0 | 0 | 5.5 | 0
07:00 | 3004 | 1292 | 897 | 38 | 64 | 665.8 | 86 | 3050 | 61.69 | 13 | 61 | 0 | 0 | 3 | 0
07:30 | 2976 | 1282 | 896.5 | 38 | 69 | 605.41 | 86 | 3216.5 | 154.545 | 19 | 76.5 | 0 | 0 | 1.5 | 0
08:00 | 2948 | 1272 | 896 | 38 | 74 | 545.02 | 86 | 3383 | 247.4 | 25 | 92 | 0 | 0 | 0 | 0
08:30 | 2883 | 1234.5 | 896 | 38 | 74 | 512.51 | 86 | 3414 | 338.78 | 33.5 | 91.5 | 0 | 0 | 0 | 0
09:00 | 2818 | 1197 | 896 | 38 | 74 | 480 | 86 | 3445 | 430.16 | 42 | 91 | 0 | 0 | 0 | 0
09:30 | 2788 | 1214.5 | 896 | 38 | 79 | 473 | 86 | 3404.5 | 500.61 | 42 | 92.5 | 0 | 0 | 0 | 0
10:00 | 2758 | 1232 | 896 | 38 | 84 | 466 | 86 | 3364 | 571.06 | 42 | 94 | 0 | 0 | 0 | 0
10:30 | 2789.5 | 1251.5 | 896 | 38 | 82 | 468 | 86 | 3359.5 | 609.15 | 42 | 183 | 0 | 0 | 0 | 0
11:00 | 2821 | 1271 | 896 | 38 | 80 | 470 | 86 | 3355 | 647.24 | 42 | 272 | 0 | 0 | 0 | 0
11:30 | 2830.5 | 1280 | 896 | 38 | 84 | 469 | 86 | 3349 | 654.9 | 42 | 518.5 | 0 | 0 | 0 | 0
12:00 | 2840 | 1289 | 896 | 38 | 88 | 468 | 86 | 3343 | 662.56 | 42 | 765 | 0 | 0 | 0 | 0
12:30 | 2808 | 1282.5 | 895.5 | 38 | 83 | 468 | 86 | 3389.5 | 637.045 | 101.5 | 972.5 | 0 | 0 | 0 | 0
13:00 | 2776 | 1276 | 895 | 38 | 78 | 468 | 86 | 3436 | 611.53 | 161 | 1180 | 0 | 0 | 0 | 0
13:30 | 2731 | 1217 | 895.5 | 38 | 81 | 468.5 | 86 | 3433.5 | 563.02 | 157.5 | 1184.8 | 0 | 0 | 0 | 0
14:00 | 2686 | 1158 | 896 | 38 | 84 | 469 | 86 | 3431 | 514.51 | 154 | 1189.6 | 0 | 0 | 0 | 0
14:30 | 2676 | 1151.5 | 896.5 | 38 | 87 | 467.94 | 86 | 3436 | 431.47 | 140.5 | 1110.3 | 0 | 0 | 0 | 0
15:00 | 2666 | 1145 | 897 | 38 | 90 | 466.88 | 86 | 3441 | 348.43 | 127 | 1031 | 0 | 0 | 0 | 0
15:30 | 2738 | 1151.5 | 896.5 | 38 | 90 | 480.35 | 86 | 3455.5 | 244.54 | 126.5 | 970.35 | 0 | 0 | 4.5 | 0
16:00 | 2810 | 1158 | 896 | 38 | 90 | 493.82 | 86 | 3470 | 140.65 | 126 | 909.7 | 0 | 0 | 9 | 0
16:30 | 2825.5 | 1209 | 895.5 | 38 | 89 | 597.745 | 86 | 3439.5 | 74.96 | 211.5 | 1019.2 | 0 | 0 | 7 | 0
17:00 | 2841 | 1260 | 895 | 38 | 88 | 701.67 | 86 | 3409 | 9.27 | 297 | 1128.7 | 0 | 0 | 5 | 0
17:30 | 2861.5 | 1271.25 | 895.5 | 38 | 91 | 725.4 | 86 | 3415 | 4.635 | 386.5 | 1385.95 | 0 | 0 | 7.5 | 0
18:00 | 2882 | 1282.5 | 896 | 38 | 94 | 749.13 | 86 | 3421 | 0 | 476 | 1643.2 | 0 | 0 | 10 | 0
18:30 | 2794 | 1278.5 | 896 | 38 | 89 | 742.49 | 86 | 3423.5 | 0 | 473.5 | 1725.6 | 0 | 0 | 11.5 | 0
19:00 | 2706 | 1274.5 | 896 | 38 | 84 | 735.85 | 86 | 3426 | 0 | 471 | 1808 | 0 | 0 | 13 | 0
19:30 | 2796 | 1281.5 | 896 | 38 | 84 | 735.28 | 86 | 3369 | 0 | 297 | 1540.2 | 0 | 0 | 9 | 0
20:00 | 2805 | 1280.5 | 896 | 38 | 78 | 741.82 | 86 | 3393 | 0 | 256 | 1464 | 0 | 0 | 3 | 0
20:30 | 2792.5 | 1288.5 | 896 | 38 | 80 | 741.87 | 86 | 3388 | 0 | 197 | 1383.3 | 0 | 0 | 1.5 | 0
21:00 | 2780 | 1296.5 | 896 | 38 | 82 | 741.92 | 86 | 3383 | 0 | 138 | 1302.6 | 0 | 0 | 0 | 0
21:30 | 2778 | 1299.25 | 896.5 | 38 | 80 | 745.325 | 86 | 3382.5 | 0 | 119 | 1177.8 | 0 | 0 | 0 | 0
22:00 | 2776 | 1302 | 897 | 38 | 78 | 748.73 | 86 | 3382 | 0 | 100 | 1053 | 0 | 0 | 0 | 0
22:30 | 2781.5 | 1294 | 896.5 | 38 | 79 | 743.785 | 86 | 3380.5 | 0 | 50 | 856.75 | 0 | 0 | 0 | 0
23:00 | 2787 | 1286 | 896 | 38 | 80 | 738.84 | 86 | 3379 | 0 | 0 | 660.5 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 06:00 | 379 | 13:00 | Meghnaghat | 393 | 05:00 | 381 | 11:00
Ashuganj | 402 | 22:00 | 384 | 11:00 | Payra | 415 | 05:00 | 410 | 10:00
Bhulta | 397 | 22:00 | 380 | 11:00 | Rahanpur | 416 | 04:00 | 400 | 13:00
Bibiana | 394 | 18:30 | 387 | 11:00 | Rampal | 412 | 05:00 | 401 | 10:00
BIPTC | 405 | 00:00 | 396 | 08:00
Bogura | 409 | 03:00 | 395 | 16:00
Gopalganj | 404 | 05:00 | 394 | 12:00
Kaliakoir | 384 | 19:00 | 372 | 10:00
Korerhat | 399 | 18:30 | 390 | 10:00
Madunaghat | 400 | 19:00 | 392 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 05:00 | 228 | 11:00 | Kaliakoir | 241 | 20:00 | 230 | 10:00
AKSML | 237 | 03:00 | 230 | 10:00 | Keranigonj | 234 | 03:00 | 225 | 11:00
Aminbazar | 238 | 20:00 | 228 | 10:00 | Khulna(S) | 238 | 05:00 | 232 | 12:00
Ashuganj | 236 | 20:00 | 224 | 11:00 | Korerhat | 239 | 05:00 | 233 | 10:00
Ashuganj-400 | 236 | 20:00 | 224 | 11:00 | Madunaghat | 238 | 18:00 | 232 | 09:00
Baghabari | 238 | 03:00 | 230 | 13:00 | Madunaghat-400 | 240 | 19:00 | 233 | 10:00
Barapukuria | 224 | 20:00 | 214 | 13:00 | Maniknagar | 228 | 19:00 | 221 | 11:00
Barapukuria-230 | 224 | 20:00 | 214 | 13:00 | Meghnaghat | 235 | 05:00 | 228 | 12:00
Barishal | 239 | 05:00 | 234 | 12:00 | Meghnaghat-400 | 232 | 19:30 | 223 | 11:00
Bheramara | 234 | 01:00 | 229 | 07:00 | Mirsorai | 239 | 19:00 | 223 | 20:00
Bhulta | 230 | 03:00 | 221 | 11:00 | Rajshahi | 234 | 05:00 | 228 | 13:00
Bibiana | 234 | 02:00 | 228 | 10:00 | Rampal | 238 | 05:00 | 230 | 12:00
BIPTC | 237 | 03:00 | 232 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Bogura | 237 | 03:00 | 230 | 16:00 | Rampura | 229 | 03:00 | 219 | 12:00
Bogura-400 | 236 | 03:00 | 229 | 16:00 | Shikalbaha | 238 | 18:00 | 230 | 10:00
Borhanuddin | 240 | 05:00 | 236 | 18:00 | Shyampur | 232 | 03:00 | 223 | 12:00
BSRM | 236 | 19:00 | 227 | 10:00 | Siddhirganj | 231 | 22:00 | 222 | 10:00
Cumilla(N) | 233 | 18:30 | 223 | 12:00 | Sirajgonj | 241 | 05:00 | 237 | 11:00
Faridpur | 238 | 04:00 | 231 | 12:00 | Sreepur | 232 | 18:30 | 223 | 11:00
Fenchuganj | 236 | 06:00 | 231 | 11:00 | Tongi | 237 | 19:30 | 225 | 11:00
Ghorashal | 235 | 01:00 | 230 | 00:00
Ghorashal-230 | 233 | 22:00 | 222 | 11:00
Gopalganj | 238 | 05:00 | 232 | 11:00
GPH | 232 | 10:00 | 230 | 00:00
Haripur | 230 | 03:00 | 222 | 11:00
Hasnabad | 232 | 02:00 | 224 | 12:00
Hathazari | 238 | 18:30 | 228 | 07:00
Ishurdi | 237 | 01:00 | 233 | 07:00
Jhenaidah | 236 | 03:00 | 228 | 13:00
Kachua | 236 | 18:30 | 228 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 02:00 | 128 | 11:00 | Lalmonirhat | 132 | 05:00 | 125 | 16:00
Agargaon | 140 | 02:00 | 134 | 12:00 | Madanganj | 134 | 19:00 | 128 | 10:00
Agrabad | 136 | 18:00 | 131 | 10:00 | Madaripur | 138 | 05:00 | 135 | 11:00
AKS | 135 | 18:00 | 130 | 10:00 | Madartek | 134 | 04:00 | 127 | 11:00
Aminbazar | 141 | 18:30 | 134 | 10:00 | Madunaghat | 138 | 18:00 | 134 | 11:00
Amnura | 141 | 04:00 | 132 | 13:00 | Magura | 139 | 04:00 | 132 | 13:00
Ashuganj | 141 | 19:30 | 138 | 12:00 | Mahasthangarh | 135 | 04:00 | 129 | 13:00
Bagerhat | 135 | 04:00 | 128 | 18:00 | Maijdee | 139 | 19:30 | 133 | 00:00
Bajitpur | 137 | 18:30 | 132 | 12:00 | Manikganj | 136 | 04:00 | 128 | 10:00
Bakulia | 139 | 23:00 | 133 | 10:00 | Maniknagar | 139 | 03:00 | 133 | 11:00
Banani | 135 | 03:00 | 127 | 12:00 | Matarbari | 129 | 12:00 | 121 | 21:00
Bangabhaban | 139 | 02:00 | 133 | 11:00 | Matuail | 134.1 | 21:00 | 129 | 11:00
Barapukuria | 138 | 20:00 | 130 | 07:00 | Metrorail_Motijheel | 139 | 03:00 | 133 | 11:00
Barguna | 0 | 00:00 | 0 | 0 | Metrorail_Uttara | 140 | 01:00 | 131 | 11:00
Barishal | 138 | 04:00 | 135 | 11:00 | Millgate | 141 | 02:00 | 131 | 10:00
Barishal-230 | 139 | 02:00 | 134 | 13:00 | Mirpur | 140 | 03:00 | 133 | 10:00
Baroaulia | 137 | 14:00 | 133 | 00:00 | Mirzapur | 133 | 04:00 | 129 | 08:00
Baroirhat | 136 | 18:00 | 132 | 11:00 | Mithapukur | 135 | 18:30 | 129 | 13:00
Bashundhara | 135 | 04:00 | 127 | 11:00 | MI_Cement | 138 | 05:00 | 130 | 10:00
BashundharaCement | 134 | 19:00 | 128 | 10:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 133 | 02:00 | 130 | 11:00 | Mogbazar | 136 | 22:00 | 30 | 13:00
Benapole | 136 | 05:00 | 127 | 13:00 | Mongla | 134 | 06:00 | 129 | 18:00
Bhaluka | 135 | 19:00 | 127 | 12:00 | Motijheel | 140 | 03:00 | 133 | 11:00
Bhandaria | 136 | 05:00 | 130 | 15:00 | Muktagacha | 131 | 09:00 | 122 | 18:00
Bhangura | 136 | 01:00 | 131 | 13:00 | Munshiganj | 134 | 19:00 | 128 | 10:00
Bheramara | 139 | 01:00 | 137 | 07:00 | Muradnagar | 133 | 00:00 | 129 | 12:00
Bheramara(GK) | 139 | 04:00 | 137 | 07:00 | Mymensingh | 132 | 17:00 | 117 | 18:00
Bhulta | 132 | 22:00 | 125 | 12:00 | Naogaon | 133 | 05:00 | 127 | 13:00
Bog-Sherpur | 136 | 03:00 | 130 | 13:00 | Narail | 140 | 05:00 | 132 | 13:00
Bogura | 136 | 04:00 | 130 | 13:00 | Narinda | 139 | 03:00 | 133 | 11:00
Bogura-230 | 136 | 04:00 | 131 | 13:00 | Narshingdi | 135 | 19:00 | 124 | 12:00
Brahmanbaria | 135 | 22:00 | 130 | 11:00 | Natore | 135 | 01:00 | 132 | 05:00
Cantonment | 140 | 03:00 | 134 | 11:00 | Nawabganj | 140 | 03:00 | 133 | 12:00
Chandina | 137 | 19:00 | 132 | 11:00 | Netrakona | 132 | 17:00 | 126 | 06:00
Chandpur | 141 | 18:30 | 136 | 10:00 | New | 142 | 05:00 | 132 | 10:00
Chandraghona | 138 | 18:00 | 135 | 00:00 | Niamatpur | 141 | 01:00 | 134 | 13:00
Chapai | 140 | 00:00 | 134 | 16:00 | Noapara | 137 | 05:00 | 132 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 18:30 | 129 | 10:00 | Pabna | 139 | 06:00 | 126 | 13:00
Chauddagram | 136 | 05:00 | 132 | 10:00 | Palashbari | 133 | 18:30 | 127 | 16:00
Chhatak | 132 | 03:00 | 128 | 11:00 | Panchagarh | 140 | 18:30 | 126 | 23:00
Chowmuhani | 137 | 18:30 | 132 | 00:00 | Patiya | 138 | 18:00 | 133 | 00:00
Chuadanga | 138 | 04:00 | 131 | 13:00 | Patuakhali | 135 | 07:00 | 134 | 00:00
Coxsbazar | 126 | 12:00 | 121 | 11:00 | Payra | 136 | 01:00 | 134 | 10:00
Cumilla(N) | 136 | 04:00 | 131 | 10:00 | PHP | 136 | 18:30 | 121 | 10:00
Cumilla(S) | 138 | 06:00 | 126 | 12:00 | Postogola | 139 | 21:00 | 132 | 10:00
Daganbhuiyan | 136 | 18:00 | 133 | 10:00 | Purbachal | 135 | 02:00 | 127 | 12:00
Daudkandi | 132 | 02:00 | 126 | 11:00 | Purbasadipur | 136 | 18:30 | 125 | 13:00
DhakaUniversity | 135 | 03:00 | 127 | 12:00 | Rahanpur | 140 | 00:00 | 135 | 14:00
Dhamrai | 138 | 20:00 | 129 | 10:00 | Rahanpur-400 | 143 | 02:00 | 135 | 13:00
Dhanmondi | 135.5 | 03:00 | 128 | 11:00 | Rahim | 134 | 05:00 | 129 | 12:00
Dohazari | 135 | 17:00 | 129 | 00:00 | Rajbari | 140 | 04:00 | 135 | 12:00
Faridpur | 140 | 05:00 | 136 | 12:00 | Rajendrapur | 135 | 03:00 | 128 | 11:00
Fatullah | 141 | 02:00 | 131 | 12:00 | Rajshahi | 136 | 03:00 | 132 | 13:00
Fenchuganj | 139 | 06:00 | 136 | 12:00 | Rajshahi-230 | 135 | 01:00 | 132 | 07:00
Feni | 135 | 19:00 | 132 | 01:00 | Ramganj | 137 | 18:30 | 135 | 00:00
Ghatail | 130 | 10:00 | 122 | 18:00 | Rampur | 136 | 05:00 | 126 | 18:30
Ghorashal | 141 | 19:30 | 135 | 09:00 | Rampura | 134 | 02:00 | 128 | 12:00
Goalpara | 137 | 05:00 | 132 | 18:00 | Rangamati | 137 | 18:00 | 134 | 10:00
Gollamari | 138 | 02:00 | 133 | 13:00 | Rangpur | 136 | 21:00 | 129 | 8:00
Gopalganj | 138 | 02:00 | 134 | 11:00 | Ruppur | 140 | 10:00 | 136 | 06:00
Gopalganj-400 | 139 | 03:00 | 136 | 10:00 | Saidpur | 135 | 18:30 | 127 | 23:00
Gulshan | 134 | 04:00 | 127 | 12:00 | Satkhira | 137 | 06:00 | 131 | 13:00
Halishahar | 138 | 18:00 | 133 | 00:00 | Satmasjid | 140 | 05:00 | 134 | 10:00
Haripur | 135 | 22:00 | 130 | 11:00 | Savar | 141 | 19:00 | 132 | 10:00
HaripurSBU | 135 | 22:00 | 130 | 11:00 | SevenRings | 141 | 19:00 | 134 | 11:00
Hasnabad | 140 | 21:00 | 133 | 10:00 | ShahCement | 134 | 18:30 | 129 | 10:00
Hathazari | 140 | 18:00 | 132 | 02:00 | Shahjadpur | 139 | 20:00 | 134 | 12:00
Ishurdi | 140 | 03:00 | 137 | 07:00 | Shahjibazar | 136 | 00:00 | 132 | 02:00
Jaldhaka | 134 | 18:30 | 126 | 00:00 | Shahmirpur | 138 | 18:00 | 132 | 04:00
Jamalpur | 131 | 10:00 | 118 | 18:00 | Shariatpur | 138 | 04:00 | 134 | 12:00
Jashore | 137 | 02:00 | 128 | 13:00 | Sherpur | 129 | 09:00 | 114 | 18:00
Jhenaidah | 140 | 05:00 | 123 | 18:00 | Shikalbaha | 126 | 03:00 | 123 | 00:00
Jhenaidah-230 | 141 | 03:00 | 134 | 13:00 | Shikalbaha-230 | 139 | 19:00 | 134 | 10:00
Joydebpur | 140 | 18:30 | 128 | 12:00 | Shitalakhya | 138 | 05:00 | 130 | 10:00
Joypurhat | 133 | 04:00 | 127 | 13:00 | Sholosohor | 138 | 18:00 | 134 | 10:00
Juldah | 137 | 13:00 | 133 | 10:00 | Shyampur | 139 | 03:00 | 135 | 14:00
Kabirpur | 138 | 06:00 | 130 | 10:00 | Shyampur-230 | 141 | 03:00 | 135 | 11:00
Kachua | 140 | 18:30 | 136 | 10:00 | Siddhirganj | 135 | 05:00 | 130 | 10:00
Kaliakoir | 140 | 18:30 | 133 | 11:00 | Sirajganj | 135 | 05:00 | 131 | 12:00
Kallyanpur | 142 | 19:00 | 135 | 09:00 | Sonargaon | 133 | 19:00 | 128 | 12:00
Kalurghat | 139 | 18:00 | 130 | 21:00 | Sreemongol | 136 | 02:00 | 132 | 11:00
Kamrangirchar | 140 | 05:00 | 133 | 10:00 | Sreepur | 136 | 17:00 | 130 | 11:00
Kaptai | 139 | 14:00 | 135 | 9:00 | Srinagar | 139 | 02:00 | 133 | 10:00
Kasba | 134 | 03:00 | 129 | 11:00 | SSM | 141 | 19:00 | 138 | 05:00
Kazla | 139 | 03:00 | 133 | 11:00 | Sunamganj | 131 | 06:00 | 127 | 12:00
Keranigonj | 140 | 06:00 | 133 | 12:00 | Sylhet | 134 | 06:00 | 131 | 11:00
Khagrachori | 137 | 19:00 | 133 | 11:00 | Sylhet-132 | 133 | 02:00 | 130 | 17:00
Khulna | 138 | 03:00 | 132 | 18:00 | Tangail | 129 | 09:00 | 125 | 07:00
Khulna(S) | 138 | 03:00 | 134 | 12:00 | Taraganj | 135 | 18:30 | 128 | 16:00
Khulshi | 136 | 18:00 | 131 | 10:00 | Thakurgaon | 139 | 18:30 | 125 | 23:00
Kishoreganj | 136 | 19:00 | 130 | 12:00 | TK | 138 | 18:00 | 134 | 05:00
Kodda | 137 | 20:00 | 127 | 10:00 | Tongi | 141 | 04:00 | 133 | 11:00
KSRM | 137 | 05:00 | 132 | 03:00 | Ullahpara | 137 | 02:00 | 132 | 12:00
Kulaura | 138 | 05:00 | 136 | 12:00 | Ullon | 134 | 03:00 | 127 | 12:00
Kurigram | 134 | 04:00 | 125 | 13:00 | Uttara | 140 | 05:00 | 134 | 10:00
Kushtia | 138 | 04:00 | 131 | 13:00 | UttaraNew | 140 | 01:00 | 131 | 11:00
Laksam | 139 | 18:00 | 135 | 10:00 | Zigatola | 140 | 06:00 | 133 | 12:00
Lakshmipur | 136 | 03:00 | 133 | 12:00
Lalbag | 140 | 06:00 | 133 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division