## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-11-2025 | during | 15-11-2025 | during | 15-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 367 | 363 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 15 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 9 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13 | 13 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 8 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 100 | 100 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 11 | 149 | 149 | 17 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 88 | 88 | 88 | 88 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 102 | 162 | 162 | 146 | 146 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1165 | 1413 | 5728.1 | 5695.1 | 2048.11 | 2032.11
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 14 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 220 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 60 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 70 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 0 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 26 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 16 | 36 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.37 | 0 | 3.39 | 0 | 3.39 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 400 | 570 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 4 | 0 | 4 | 0 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 320 | 315 | 650 | 650 | 650 | 650 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1064.37 | 1393 | 2879.11 | 2881.72 | 2379.89 | 2376.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 142 | 143 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 230 | 230 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 400 | 230 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 32 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 103 | 103 | 0 | 0 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 48 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 68 | 160 | 160 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 21 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1026 | 889 | 2326.21 | 2256.21 | 1802.21 | 1732.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-11-2025 | during | 15-11-2025 | during | 15-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 24 | 28 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 37 | 55 | 58 | 58 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 18.5 | 18.5 | 18.5 | 18.5 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.89 | 0 | 47 | 0 | 47 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 129.89 | 119 | 359.5 | 310.5 | 324 | 275
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 130 | 157 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 12 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 379 | 335 | 365 | 365 | 337 | 337 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1159 | 1121 | 1155 | 1155 | 1077 | 1077
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 896 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 198 | 212 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 0 | 105 | 105 | 0 | 150 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82.99 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 892 | 1045 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2123.99 | 2191 | 2397 | 2312 | 1642 | 1707
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 312 | 307 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 550 | 610 | 857 | 857 | 857 | 857 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.26 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1192.26 | 1247 | 1453 | 1452 | 1320 | 1319
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 60.16 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 49 | 49 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 175 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 347 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 27 | 27 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 8 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.78 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 520.2 | 751 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.75 | 0 | 59 | 0 | 59 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1215.89 | 1348 | 2396.29 | 2231.99 | 1806.91 | 1642.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 166 | 0 | 166.41 | 0 | 166.41 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 203.6 | 105 | 464.21 | 262 | 352.21 | 228
System Total |  |  |  |  | 28823.2 | 28205.415 | 9280 | 9826 | 19158.42 | 18556.52 | 12752.33 | 12389.43
Forecast Scenario (15-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9100 |  | 0 |  | 9100
|  |  |  | 1:00 | 8580 |  | 0 |  | 8580
|  |  |  | 2:00 | 8230 |  | 0 |  | 8230
|  |  |  | 3:00 | 7840 |  | 0 |  | 7840
|  |  |  | 4:00 | 7580 |  | 0 |  | 7580
|  |  |  | 5:00 | 7490 |  | 0 |  | 7490
|  |  |  | 6:00 | 7370 |  | 0 |  | 7370
|  |  |  | 7:00 | 7840 |  | 0 |  | 7840
|  |  |  | 8:00 | 7880 |  | 0 |  | 7880
|  |  |  | 9:00 | 7600 |  | 0 |  | 7600
|  |  |  | 10:00 | 7800 |  | 0 |  | 7800
|  |  |  | 11:00 | 8400 |  | 0 |  | 8400
|  |  |  | 12:00 | 9050 |  | 0 |  | 9050
|  |  |  | 13:00 | 9800 |  | 0 |  | 9800
|  |  |  | 14:00 | 10000 |  | 0 |  | 10000
|  |  |  | 15:00 | 9860 |  | 0 |  | 9860
|  |  |  | 16:00 | 9470 |  | 0 |  | 9470
|  |  |  | 17:00 | 9550 |  | 0 |  | 9550
|  |  |  | 18:00 | 10250 |  | 0 |  | 10250
|  |  |  | 18:30 | 10280 |  | 0 |  | 10280
|  |  |  | 19:00 | 10300 |  | 0 |  | 10300
|  |  |  | 19:30 | 10200 |  | 0 |  | 10200
|  |  |  | 20:00 | 10070 |  | 0 |  | 10070
|  |  |  | 21:00 | 9690 |  | 0 |  | 9690
|  |  |  | 22:00 | 9520 |  | 0 |  | 9520
|  |  |  | 23:00 | 9010 |  | 0 |  | 9010
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 9050.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 212.28 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:35 hrs on 15-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-11-2025 | [28 empty] | Date: | 14-11-2025 | [28 empty] | Date: | 14-11-2025 | [28 empty] | Date: | 14-11-2025 | [28 empty] | Date: | 14-11-2025 | [14 empty] | Date: | 14-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [14 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 35 | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 86 | 0 | 36 | 570 | 0 | 0 | 0 | 0 | 95 | 225 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 275 | 0 | 230 | 0 | 34 | 20 | 0 | 106 | 32 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 310 | 0 | 360 | 0 | 67 | 158 | 23 | 0 | 81 | 30 | 0 | 18 | 54 | 0 | 19 | 58 | 21 | 0 | 0 | 0 | 4839 | 896 | 140 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 724.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 852 | 0 | 4806.19 | 9645.19 | 101.24
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 570 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 585 | 0 | 0 | 0 | 0 | 265 | 0 | 230 | 0 | 40 | 20 | 0 | 105 | 0 | 0 | 20 | 0 | 72 | 0 | 0 | 0 | 305 | 0 | 334 | 0 | 67 | 149 | 23 | 0 | 81 | 30 | 0 | 18 | 68 | 0 | 19 | 0 | 23 | 0 | 0 | 0 | 4445.2 | 896 | 144 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 664.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 4.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 307 | 750 | 0 | 4596.28 | 9041.48 | 101.23
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 570 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 505 | 0 | 0 | 0 | 0 | 265 | 0 | 230 | 0 | 40 | 0 | 0 | 106 | 0 | 0 | 20 | 0 | 60 | 0 | 0 | 0 | 315 | 0 | 325 | 0 | 67 | 153 | 21 | 0 | 81 | 30 | 0 | 18 | 69 | 0 | 19 | 0 | 24 | 0 | 0 | 0 | 4264 | 896 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1029 | 0 | 573.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 308 | 750 | 0 | 4444.78 | 8708.78 | 101.23
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 37 | 570 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 280 | 0 | 230 | 0 | 40 | 0 | 0 | 106 | 0 | 0 | 18 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 346 | 0 | 67 | 147 | 21 | 0 | 81 | 30 | 0 | 18 | 69 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4213 | 896 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 896 | 0 | 484.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 308 | 700 | 0 | 4177.67 | 8390.67 | 101.23
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 37 | 570 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 300 | 0 | 230 | 0 | 40 | 0 | 0 | 107 | 0 | 0 | 18 | 0 | 66 | 0 | 0 | 0 | 315 | 0 | 333 | 0 | 67 | 159 | 21 | 0 | 81 | 30 | 0 | 18 | 75 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4218 | 896 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 418.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 307 | 600 | 0 | 3911.92 | 8129.92 | 101.22
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 38 | 570 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 300 | 0 | 230 | 0 | 40 | 0 | 0 | 107 | 0 | 0 | 18 | 0 | 62 | 0 | 0 | 0 | 300 | 0 | 336 | 0 | 67 | 152 | 21 | 0 | 81 | 30 | 0 | 18 | 76 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4103 | 897 | 170 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 424.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 308 | 595 | 0 | 3900.28 | 8003.28 | 101.22
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 26 | 570 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 375 | 4 | 0 | 0 | 0 | 310 | 0 | 230 | 0 | 40 | 0 | 0 | 107 | 0 | 0 | 18 | 0 | 56 | 0 | 0 | 0 | 300 | 0 | 331 | 0 | 67 | 154 | 21 | 0 | 55 | 30 | 0 | 18 | 78 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 4066.5 | 897 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 423.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 180 | 0 | 307 | 595 | 0 | 3892.09 | 7958.59 | 101.22
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 3 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 27 | 570 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 355 | 4 | 0 | 0 | 0 | 335 | 0 | 230 | 0 | 40 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 58 | 0 | 12 | 0 | 325 | 0 | 358 | 0 | 30 | 160 | 21 | 0 | 53 | 30 | 0 | 18 | 77 | 0 | 0 | 0 | 24 | 0 | 3.9 | 0 | 4221.9 | 896 | 190 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 793 | 0 | 432.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.06 | 7 | 0 | 0 | 3.69 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.34 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.4 | 11 | 0.03 | 0 | 0 | 110 | 220 | 0 | 310 | 570 | 0 | 4006.33 | 8228.23 | 101.21
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 11 | 0 | 12 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.45 | 86 | 0 | 29 | 570 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 400 | 11 | 0 | 0 | 0 | 320 | 0 | 230 | 0 | 28 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 56 | 0 | 35 | 0 | 315 | 0 | 395 | 0 | 30 | 157 | 21 | 0 | 53 | 30 | 0 | 18 | 78 | 0 | 18 | 22 | 24 | 0 | 19.22 | 0 | 4395.67 | 896 | 192 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 820 | 0 | 428.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.43 | 33 | 0 | 0 | 19.35 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 1.65 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1.8 | 56 | 0.1 | 0 | 0 | 110 | 220 | 0 | 311 | 570 | 0 | 4164.37 | 8560.04 | 101.21
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 21 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.39 | 86 | 0 | 30 | 570 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 345 | 15 | 0 | 0 | 0 | 280 | 0 | 230 | 0 | 28 | 0 | 0 | 105 | 0 | 0 | 14 | 0 | 56 | 0 | 53 | 0 | 300 | 0 | 314 | 0 | 30 | 143 | 21 | 0 | 11 | 17 | 0 | 18 | 86 | 0 | 18 | 56 | 24 | 1 | 31.45 | 0 | 4041.84 | 896 | 192 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52 | 789 | 17 | 430.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.07 | 59 | 0 | 0 | 34.85 | 130 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 2.97 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 3.4 | 90 | 0.17 | 0 | 0 | 100 | 180 | 0 | 310 | 530 | 0 | 4234.87 | 8276.71 | 101.21
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 27 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.05 | 86 | 0 | 31 | 380 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 300 | 18 | 0 | 0 | 0 | 250 | 0 | 230 | 0 | 34 | 0 | 0 | 104 | 0 | 0 | 14 | 0 | 62 | 0 | 64 | 0 | 300 | 0 | 339 | 0 | 30 | 144 | 21 | 0 | 11 | 20 | 0 | 18 | 87 | 0 | 19 | 16 | 24 | 2 | 41.21 | 0 | 3798.26 | 896 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 791 | 17 | 434.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3 | 83 | 0 | 0 | 49.23 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 4.2 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 4.7 | 136 | 0.22 | 0 | 0 | 100 | 180 | 0 | 310 | 480 | 0 | 4275.68 | 8073.94 | 101.21
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 28 | 0 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.34 | 86 | 0 | 23 | 390 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 300 | 20 | 0 | 0 | 0 | 250 | 0 | 230 | 0 | 74 | 0 | 0 | 103 | 0 | 0 | 14 | 0 | 68 | 0 | 70 | 0 | 310 | 0 | 377 | 0 | 30 | 149 | 16 | 0 | 11 | 20 | 0 | 18 | 103 | 0 | 19 | 16 | 24 | 2 | 48.01 | 0 | 3982.35 | 896 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79.38 | 805 | 17 | 428.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.9 | 97 | 0 | 0 | 55.74 | 130 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 4.69 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5.4 | 160 | 0.25 | 0 | 0 | 100 | 180 | 0 | 308 | 490 | 0 | 4439.55 | 8421.9 | 101.2
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 30 | 0 | 13 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 86 | 0 | 16 | 320 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 400 | 20 | 0 | 0 | 0 | 400 | 0 | 230 | 0 | 142 | 0 | 0 | 103 | 0 | 0 | 14 | 0 | 70 | 0 | 67 | 0 | 320 | 0 | 379 | 0 | 30 | 155 | 16 | 0 | 81 | 30 | 0 | 18 | 130 | 0 | 19 | 37 | 24 | 2 | 47.89 | 0 | 4544.26 | 896 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82.99 | 892 | 17 | 520.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.16 | 97 | 0 | 0 | 56.75 | 130 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 4.78 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5.6 | 166 | 0.26 | 0 | 0 | 110 | 220 | 0 | 312 | 550 | 0 | 4735.74 | 9280 | 101.2
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 30 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 86 | 0 | 29 | 315 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 530 | 12 | 0 | 0 | 0 | 260 | 0 | 230 | 0 | 160 | 0 | 0 | 103 | 0 | 0 | 14 | 0 | 74 | 0 | 67 | 0 | 315 | 0 | 359 | 0 | 30 | 157 | 22 | 0 | 81 | 30 | 0 | 18 | 103 | 0 | 19 | 56 | 23 | 2 | 45.06 | 0 | 4607.16 | 896 | 199 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 1103 | 17 | 724.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.49 | 81 | 0 | 0 | 56.25 | 155 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 4.64 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.4 | 144 | 0.42 | 0 | 0 | 110 | 220 | 0 | 310 | 660 | 0 | 5283.58 | 9890.74 | 101.19
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 24 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 86 | 0 | 29 | 315 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 450 | 16 | 0 | 0 | 0 | 230 | 0 | 230 | 0 | 142 | 0 | 0 | 102 | 0 | 0 | 14 | 0 | 64 | 0 | 53 | 0 | 305 | 0 | 320 | 0 | 30 | 143 | 22 | 0 | 41 | 30 | 0 | 18 | 161 | 0 | 19 | 16 | 24 | 1 | 38.11 | 0 | 4062.62 | 896 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 986 | 0 | 650.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.33 | 64 | 0 | 0 | 39.12 | 192 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 3.79 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.4 | 124 | 0.33 | 0 | 0 | 110 | 180 | 0 | 310 | 650 | 0 | 4949.35 | 9011.97 | 101.19
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 16 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 86 | 0 | 29 | 315 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 400 | 12 | 0 | 0 | 0 | 230 | 0 | 230 | 0 | 142 | 0 | 0 | 102 | 0 | 0 | 14 | 0 | 60 | 0 | 37 | 0 | 300 | 0 | 320 | 0 | 30 | 144 | 22 | 0 | 42 | 30 | 0 | 12 | 160 | 0 | 19 | 16 | 23 | 1 | 26.43 | 0 | 3960.11 | 896 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42.1 | 827 | 0 | 543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.46 | 52 | 0 | 0 | 22.71 | 173 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 1.12 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.8 | 79 | 0.22 | 0 | 0 | 110 | 180 | 0 | 307 | 580 | 0 | 4439.41 | 8399.52 | 101.18
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 7 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 86 | 0 | 25 | 315 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 355 | 6 | 0 | 0 | 0 | 230 | 0 | 230 | 0 | 143 | 0 | 0 | 103 | 0 | 0 | 14 | 0 | 58 | 0 | 16 | 0 | 310 | 0 | 327 | 0 | 30 | 148 | 22 | 0 | 42 | 30 | 0 | 12 | 160 | 0 | 19 | 16 | 23 | 0 | 10.41 | 0 | 3849.17 | 896 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.21 | 801 | 0 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.25 | 18 | 0 | 0 | 9.47 | 175 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0.66 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.1 | 34 | 0.09 | 0 | 0 | 110 | 180 | 0 | 308 | 530 | 0 | 4190.78 | 8039.95 | 101.18
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 10 | 12 | 0 | 86 | 0 | 33 | 315 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 230 | 0 | 230 | 0 | 142 | 0 | 0 | 104 | 0 | 0 | 14 | 0 | 64 | 0 | 1 | 0 | 320 | 0 | 366 | 0 | 30 | 157 | 22 | 0 | 42 | 30 | 0 | 12 | 160 | 1 | 19 | 20 | 22 | 0 | 0.36 | 0 | 4157.36 | 896 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.4 | 851 | 0 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0 | 0 | 0 | 0.7 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.05 | 0 | 0 | 10 | 0 | 8 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 0 | 110 | 220 | 0 | 308 | 535 | 0 | 4340.07 | 8497.43 | 101.17
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 35 | 0 | 11 | 15 | 45 | 0 | 9 | 102 | 0 | 420 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 17 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 0 | 26 | 12 | 0 | 86 | 0 | 36 | 315 | 0 | 0 | 14 | 0 | 60 | 220 | 0 | 0 | 0 | 570 | 0 | 0 | 32 | 0 | 230 | 0 | 230 | 0 | 143 | 0 | 21 | 103 | 48 | 0 | 14 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 335 | 0 | 30 | 148 | 23 | 0 | 81 | 30 | 0 | 12 | 157 | 17 | 19 | 55 | 28 | 0 | 0 | 0 | 4935 | 896 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1045 | 0 | 751 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 307 | 610 | 0 | 4891 | 9826 | 101.17
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 36 | 0 | 16 | 0 | 15 | 0 | 17 | 17 | 0 | 420 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 40 | 36 | 0 | 86 | 0 | 36 | 315 | 0 | 0 | 0 | 0 | 50 | 223 | 0 | 0 | 0 | 612 | 0 | 0 | 10 | 0 | 230 | 0 | 230 | 0 | 80 | 0 | 16 | 104 | 34 | 0 | 16 | 0 | 66 | 0 | 0 | 0 | 305 | 0 | 324 | 0 | 30 | 142 | 23 | 0 | 81 | 30 | 0 | 12 | 157 | 17 | 19 | 56 | 28 | 0 | 0 | 0 | 4714 | 897 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1071 | 0 | 757 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 730 | 0 | 4990 | 9704 | 101.16
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 36 | 0 | 16 | 0 | 15 | 0 | 17 | 17 | 0 | 420 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 0 | 0 | 40 | 36 | 0 | 86 | 0 | 36 | 315 | 0 | 0 | 0 | 0 | 34 | 224 | 0 | 0 | 0 | 612 | 0 | 0 | 10 | 0 | 230 | 0 | 230 | 0 | 84 | 0 | 15 | 104 | 33 | 0 | 20 | 0 | 66 | 0 | 0 | 0 | 305 | 0 | 331 | 0 | 30 | 146 | 23 | 0 | 81 | 30 | 0 | 12 | 157 | 17 | 19 | 56 | 28 | 0 | 0 | 0 | 4718 | 896 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 751 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 780 | 0 | 5045 | 9763
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 36 | 0 | 16 | 0 | 15 | 0 | 17 | 15 | 0 | 420 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 56 | 36 | 0 | 86 | 0 | 36 | 315 | 0 | 0 | 0 | 0 | 16 | 224 | 0 | 0 | 0 | 612 | 0 | 0 | 10 | 0 | 230 | 0 | 230 | 0 | 119 | 0 | 15 | 106 | 34 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 310 | 0 | 335 | 0 | 30 | 147 | 23 | 0 | 81 | 30 | 0 | 14 | 157 | 17 | 19 | 56 | 28 | 0 | 0 | 0 | 4757 | 897 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 0 | 752 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 775 | 0 | 5046 | 9803 | 101.16
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 0 | 0 | 59 | 36 | 0 | 86 | 0 | 36 | 315 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 230 | 0 | 230 | 0 | 121 | 0 | 0 | 105 | 31 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 335 | 0 | 30 | 147 | 23 | 0 | 81 | 30 | 0 | 14 | 157 | 0 | 19 | 56 | 46 | 0 | 0 | 0 | 4652 | 896 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 757.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 778 | 0 | 4992.26 | 9644.26 | 101.15
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 60 | 38 | 0 | 86 | 0 | 42 | 315 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 0 | 113 | 0 | 0 | 106 | 32 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 315 | 0 | 315 | 0 | 30 | 151 | 23 | 0 | 81 | 30 | 0 | 14 | 157 | 0 | 19 | 35 | 35 | 0 | 0 | 0 | 4558 | 896 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 752.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 308 | 790 | 0 | 4995.51 | 9553.51 | 101.15
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 315 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 0 | 108 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 326 | 0 | 30 | 145 | 22 | 0 | 81 | 30 | 0 | 12 | 157 | 0 | 19 | 35 | 48 | 0 | 0 | 0 | 4375 | 896 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 752.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 307 | 790 | 0 | 4918.35 | 9293.35 | 101.14
Total KWH | 0 | 86400 | 25440 | 0 | 0 | 0 | 0 | 0 | 8593200 | 0 | 0 | 130320 | 0 | 201024 | 10560 | 81545 | 0 | 88706 | 228960 | 0 | 8801500 | 0 | 0 | 0 | 114940 | 7023367 | 0 | 0 | 198492 | 54000 | 329400 | 352800 | 0 | 0 | 0 | 0 | 0 | 0 | 55200 | 113519 | 0 | 0 | 251520 | 170880 | 22199 | 2078220 | 0 | 813120 | 10210909.09 | 0 | 0 | 32640 | 0 | 219964 | 5105101 | 0 | 0 | 0 | 11241817 | 134865 | 0 | 93672 | 0 | 6363500 | 0 | 5608000 | 0 | 2177000 | 37728 | 70080 | 2481016 | 228480 | 0 | 374950 | 0 | 1543680 | 0 | 469200 | 0 | 7536000 | 0 | 8464000 | 0 | 966480 | 3609327.27 | 524256 | 0 | 1493760 | 689856 | 0 | 375000 | 2682900 | 58680 | 355200 | 676800 | 620160 | 11300 | 308530 | 14400 | 104604563.36 | 21653818 | 4838112 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 522720 | 22072728 | 6000 | 13909910 | 0 | 0 | 0 | 0 | 103680 | 0 | 0 | 0 | 0 | 356228 | 613010 | 0 | 0 | 346512 | 3728091 | 0 | 0 | 0 | 0 | 0 | 8049164 | 0 | 29040 | 0 | 0 | 134718 | 198423 | 240633 | 0 | 0 | 0 | 34715.76 | 1002960 | 2136 | 0 | 0 | 2609000 | 5094300 | 0 | 7410168 | 16283636.36 | 0 | 110151703.12 | 214756266.48

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9280 | MW | 12:00 Hr. | Energy Generated |  |  | 214.7563 |  | MKWHr.
| Day Peak Demand |  |  | 9280 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9826 | MW | 18:00 Hr. | Energy Demand |  |  | 214.7563 |  | MKWHr.
| Evening Peak Demand |  |  | 9826 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29.2 |  | °C
| Minimum Generation of the Day |  |  | 7958.59 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 749 |  | MMCFD
| Maximum Generation of the Day |  |  | 9890.74 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.2612 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.1003 | 0 | 1.0219 | 0 | 0 | 0.19849 | 0 | 0 | 26.3207 | Gas | 99.3411 | Gas | 352376820.1557
| Chattogram Zone |  |  | 5.9182 | 21.4527 | 0.78852 | 0 | 2.0782 | 0.15706 | 0 | 0.0552 | 30.45 | Coal | 67.2193 | Coal | 432995071.5045
| Cumilla Zone |  |  | 17.0422 | 0 | 0.39223 | 0 | 0 | 0.4692 | 1.5437 | 0 | 19.4473 | HFO | 3.7928 | HFO | 64131051.79
| Mymensingh Zone |  |  | 0.62016 | 0 | 1.1051 | 0 | 0 | 0.31983 | 0 | 0 | 2.0451 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.3416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3416 | Hydro | 2.0782 | Hydro | 207822
| Khulna Zone |  |  | 4.8381 | 22.0727 | 0.006 | 0 | 0 | 0.52272 | 22.5658 | 0 | 50.0054 | Solar | 4.2503 | Solar | 67777532.1416
| Barishal Zone |  |  | 7.7033 | 23.6938 | 0 | 0 | 0 | 0.002136 | 0 | 0 | 31.3992 | Import | 38.0194 | Import | 211572852.38
| Rajshahi Zone |  |  | 11.7773 | 0 | 0.10368 | 0 | 0 | 1.3448 | 13.9099 | 0 | 27.1356 | Wind | 0.0552 | Wind | 811992
| Rangpur Zone |  |  | 0 | 0 | 0.37535 | 0 | 0 | 1.2361 | 0 | 0 | 1.6114
| Total |  |  | 99.3411 | 67.2193 | 3.7928 | 0 | 2.0782 | 4.2503 | 38.0194 | 0.0552 | 214.7563
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 352376820.1557 |  | Hydro | 207822
|  |  |  | Coal | 432995071.5045 |  | Solar | 67777532.1416
|  |  |  | HFO | 64131051.79 |  | Import | 211572852.38
|  |  |  | HSD | 0 |  | Wind | 811992
[5 empty] | Total: | 112,98,73,141 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6538 | Peak Hr Flow | 896.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43976618.2 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 13.9099 | Peak Hr Flow | 751.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1977 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5437 | Peak Hr Flow | 68.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2558 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.1074 | Peak Hr Flow | 1715.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3394
|  |  |  | Chattogram |  | 0 |  | 1206
|  |  |  | Cumilla |  | 0 |  | 926
|  |  |  | Mymensingh |  | 0 |  | 825
|  |  |  | Sylhet |  | 0 |  | 421
|  |  |  | Khulna |  | 0 |  | 1093
|  |  |  | Barishal |  | 0 |  | 284
|  |  |  | Rajshahi |  | 0 |  | 878
|  |  |  | Rangpur |  | 0 |  | 641
|  |  |  | Total |  | 0 |  | 9668
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 16:49 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Scheduled S/D Due to Annual maintenance
| 08:25 | 16:49 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT Scheduled S/D Due to Annual maintenance.
| 08:30 |  | Niamotpur 132 kV Bus-01 S/D for Annual Maintenance [No Load Shed. Double Bus Scheme]
| 08:40 | 09:10 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Maintenance of pbs Barpa 33kv feeder | [7 empty] | 45.0MW load
|  |  | heat shrink. | [7 empty] | interrup.
| 08:41 | 09:08 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to Maintenance of PBS Barpa 33kv feeder | [7 empty] | 45.0MW load
|  |  | Heat shrink | [7 empty] | interrup.
| 08:42 | 13:27 | Bhaluka-Mymensingh 132 kV Ckt-2 Scheduled S/D from Bhaluka 132/33kV end Due to Work at
Mymensingh end.
| 08:43 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to G2G
| 08:43 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to G2G project work
|  | 08:44 | Jashore-Noapara 132kV Ckt-2 is restored.
|  | 08:44 | Jashore-Noapara 132kV Ckt-1 is restored.
| 08:45 | 15:47 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end. and from Khulna
(C) end Due to 132KV South - 1, R-phase jack Bus Maintenance.
| 08:45 | 15:38 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end. and from Khulna
(C) end Due to 132KV South - 1, R-phase jack Bus Maintenance
| 08:56 | 13:29 | Khulna (C) S/S North- West Ckt-2 Scheduled S/D Due to 132KV South - 1, R-phase jack Bus
Maintenance.
| 08:56 | 13:29 | Khulna (C) S/S North-WestCkt-1 Scheduled S/D Due to 132KV South - 1, R-phase jack Bus
Maintenance.
| 09:07 | 13:28 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to 132KV South - 1, R-phase jack Bus
Maintenance.
| 09:07 | 13:28 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to 132KV South - 1, R-phase jack Bus
Maintenance.
| 09:17 | 13:59 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to 132KV South -
1, R-phase jack Bus Maintenance. and from Khulna(S) 230/132kVend.
| 09:18 | 13:22 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to 132KV South -
1, R-phase jack Bus Maintenance. and from Khulna(S) 230/132kVend.
| 10:41 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 14:49 | 16:20 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Pbs 33KV Borpa feeder maintenance | [7 empty] | 25.0MW load
|  |  | works | [7 empty] | interrup.
| 14:50 | 16:18 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to Maintenance works on PBS 33KV Borpa | [7 empty] | 25.0MW load
|  |  | feeder | [7 empty] | interrup.
| 15:48 |  | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end.
| 15:49 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Project Work S/D from Purbasadipur 132/33kV end
Due to Reconductoring of EPVL to Purbasadipur CKT-1.
| 15:49 |  | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end.
| 18:18 |  | Goalpara- Khulna (C) 132kV Ckt-1 Tripped from Khulna (C) end showing No relay operate
relays Due to Not identify
| 18:32 |  | Niamotpur 132 kV Bus-01 Sync.
| 18:50 |  | Ashuganj 225 MW ST tripped.
| 20:39 |  | Goalpara- Khulna (C) 132kV Ckt-1 Forced S/D from Goalpara 132/33kV end Due to Shutdoun
for maintenence works. order by Aldc khulna.
| 21:56 |  | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Tripped showing FBCPU-1 relays Due to
B-phase gas pressure low.
| 22:01 | 23:32 | Noapara 132/33kV S/S T-1 HT Scheduled S/D | [7 empty] | 13.0MW load
interrup.
| 22:01 | 23:32 | Noapara 132/33kV S/S T-1 LT Scheduled S/D | [7 empty] | 13.0MW load
interrup.
| 22:03 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:-
| 05:00 |  | Minimum Generation: 7355 MW.
| 05:15 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 06:45 |  | Bhulta-Rampura 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Annual
Maintenance and from Rampura 230/132kV end Due to Annual Maintenance of Bhulta-Rampura
230Kv Ckt-1 Bay.
| 07:00 |  | Chandpur 132/33kV S/S 200KVA Aux. T-1 LT Forced S/D Due to Auxiliary Power alternate from
ST-1 to ST-2
|  | 07:00 | Chandpur 132/33kV S/S 200KVA Aux. T-2 LT is restored.
| 07:07 |  | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance work
| 07:14 |  | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance work
| 07:14 |  | Chandpur 132/33kV S/S 33 kV T-1 Section Scheduled S/D Due to Maintenance | [7 empty] | 10.0MW load
interrup.
| 07:16 |  | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance
| 07:16 |  | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance
| 07:22 |  | BIPTC S/S 10CF16 Tripped showing 60/61 Instant L1 tripped relays Due to No birds or such
abnormalities were noticed.
| 07:28 |  | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to Annual maintenance
| 07:35 |  | Brahmanbaria 132/33kV S/S 402T LT Scheduled S/D Due to Isolator Maintenance | [7 empty] | 20.0MW load
interrup.
| 07:35 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled S/D Due to Annual Maintenance.
| 07:35 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled S/D Due to Annual Maintenance
| 07:36 |  | Brahmanbaria 132/33kV S/S 402T HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 07:40 |  | Savar 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance
| 07:49 |  | Mymensingh 132/33kV S/S 50 MW Solar Plant Scheduled S/D
| 07:53 |  | AKSML-Khulshi 132kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual
Maintenance(Bay Equioment) and from AKS 132/33kV end Due to Khulshi line shutdown due to
khulshi sub -station annual maintenance.
| 08:00 |  | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D Due to Maintenance
| 08:00 |  | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D Due to Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 363 | 8593200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8801500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7023367 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 130320 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 10560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 9 | 88706 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 114940 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 329400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 352800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 25440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 81545 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 11 | 201024 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 86400 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 102 | 228960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 198492 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 54000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1413 | 26320654
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134865 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 14 | 32640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2078220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5105101 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 60 | 219964 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 113519 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 26 | 251520 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 36 | 813120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 170880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 570 | 11241817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 4 | 55200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 315 | 10210909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 1393 | 30449954.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 143 | 2177000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Planned Shutdown
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 230 | 5608000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 6363500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 37728 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 32 | 93672 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2481016 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 48 | 228480 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 68 | 1543680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 374950 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 21 | 70080 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 469200 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 889 | 19447306
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 28 | 620160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 55 | 676800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 355200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 308530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 14400 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 58680 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 119 | 2045070
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 966480 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3609327.27 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 689856 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1493760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 2682900 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 375000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 524256 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7536000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 8464000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 1121 | 26341579.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 896 | 21653818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 212 | 4838112 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 6000 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 522720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1045 | 22072728 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2191 | 50005378
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 307 | 7410168 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2609000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 610 | 16283636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5094300 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2136 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1247 | 31399240.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 356228 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 175 | 3728091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8049164 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Under Maintenance
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 8 | 103680 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29040 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 751 | 13909910 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 346512 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 613010 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1348 | 27135635
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 240633 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34715.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 134718 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 198423 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1002960 | -
Rangpur Area Total |  |  |  |  | 950 | 105 | 1611449.76
Eastern Grid Total |  |  |  |  | 17383.855 | 4935 | 104604563.36
Western Grid Total |  |  |  |  | 10821.56 | 4891 | 110151703.12
National Grid Total |  |  |  |  | 28205.415 | 9826 | 214756266.48
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6771.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 2895.6 | MW
i) Dhaka area |  |  | 3394.08 |  | MW | i) Khulna area |  |  |  | 1093 | MW
ii) Chattogram area |  |  | 1205.5 |  | MW | ii) Barishal area |  |  |  | 283.6 | MW
iii) Cumilla area |  |  | 926.41 |  | MW | iii) Rajshahi area |  |  |  | 878 | MW
iv) Mymensingh area |  |  | 825 |  | MW | iv) Rangpur area |  |  |  | 641 | MW
v) Sylhet area |  |  | 421 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9667.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 59 | 18:00 | 133 | Niamatpur | 38 | 18:00
2 | AKSML | 165 | 04:00 | 68 | Ishurdi | 51 | 18:00 | 134 | Noapara | 27 | 19:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 54 | 18:00 | 135 | PHP | 8 | 03:00
4 | Agargaon | 91 | 13:00 | 70 | Jamalpur | 84 | 18:30 | 136 | Pabna | 57 | 18:00
5 | Agrabad | 68 | 18:00 | 71 | Jashore | 95 | 13:00 | 137 | Palashbari | 70 | 18:00
6 | Amnura | 15 | 07:00 | 72 | Jhenaidah | 84 | 18:00 | 138 | Panchagarh | 39 | 18:00
7 | Ashuganj | 65 | 20:00 | 73 | Joydebpur | 98 | 00:00 | 139 | Patiya | 7 | 18:00
8 | BSRM | 205 | 03:00 | 74 | Joypurhat | 37 | 18:00 | 140 | Patuakhali | 53 | 21:00
9 | Bagerhat | 55 | 18:00 | 75 | Juldah | 14 | 00:00 | 141 | Payra | 30 | 18:00
10 | Bajitpur | 57 | 18:00 | 76 | KSRM | 28 | 04:00 | 142 | Postogola | 44 | 00:00
11 | Bakulia | 62 | 15:00 | 77 | Kabirpur | 145 | 00:00 | 143 | Purbachal | 14 | 18:00
12 | Banani | 26.6 | 13:00 | 78 | Kachua | 57 | 18:00 | 144 | Purbasadipur | 90 | 12:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 81 | 13:00 | 145 | Rahanpur | 20 | 18:30
14 | Barapukuria | 40 | 18:00 | 80 | Kalurghat | 34 | 00:00 | 146 | Rahim | 31 | 00:00
15 | Barguna | 0 | 00:00 | 81 | Kamrangirchar | 54 | 00:00 | 147 | Rajbari | 50 | 18:00
16 | Barishal | 85 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 81 | 00:00
17 | Barishal-230 | 62 | 13:00 | 83 | Kasba | 25 | 13:00 | 149 | Rajshahi | 78 | 13:00
18 | Baroaulia | 55 | 11:00 | 84 | Kazla | 78 | 00:00 | 150 | Rajshahi-230 | 52 | 13:00
19 | Baroirhat | 39 | 19:30 | 85 | Keranigonj | 57 | 13:00 | 151 | Ramganj | 68 | 13:00
20 | Bashundhara | 140 | 12:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 31 | 17:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 39 | 14:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 48 | 18:00 | 88 | Khulshi | 154 | 18:30 | 154 | Rangpur | 90 | 18:00
23 | Benapole | 44 | 13:00 | 89 | Kishoreganj | 82 | 18:00 | 155 | Ruppur | 5.6 | 12:00
24 | Bhaluka | 107 | 13:00 | 90 | Kodda | 206 | 00:00 | 156 | SSM | 2 | 08:00
25 | Bhandaria | 40 | 20:00 | 91 | Kulaura | 32 | 18:00 | 157 | Saidpur | 63 | 12:00
26 | Bhangura | 22 | 19:00 | 92 | Kurigram | 40 | 08:00 | 158 | Satkhira | 78 | 07:00
27 | Bheramara(GK) | 38 | 18:00 | 93 | Kushtia | 80 | 00:00 | 159 | Satmasjid | 71 | 12:00
28 | Bhulta | 183 | 00:00 | 94 | Laksam | 21 | 20:00 | 160 | Savar | 120 | 12:00
29 | Bog-Sherpur | 50 | 18:00 | 95 | Lakshmipur | 19 | 19:30 | 161 | SevenRings | 17.87 | 19:00
30 | Bogura | 104 | 18:30 | 96 | Lalbag | 55 | 01:00 | 162 | ShahCement | 13 | 00:00
31 | Borhanuddin | 61 | 21:00 | 97 | Lalmonirhat | 40 | 18:00 | 163 | Shahjadpur | 44 | 18:00
32 | Brahmanbaria | 97 | 13:00 | 98 | MI_Cement | 17 | 05:00 | 164 | Shahjibazar | 77 | 00:00
33 | Cantonment | 104 | 13:00 | 99 | Madanganj | 46 | 17:00 | 165 | Shahmirpur | 31.5 | 00:00
34 | Chandina | 11.41 | 18:00 | 100 | Madaripur | 65 | 13:00 | 166 | Shariatpur | 54 | 21:00
35 | Chandpur | 50 | 13:00 | 101 | Madartek | 69.29 | 13:00 | 167 | Sherpur | 102 | 18:00
36 | Chandraghona | 29 | 18:00 | 102 | Madunaghat | 38 | 18:00 | 168 | Shikalbaha | 22 | 00:00
37 | Chapai | 44 | 12:00 | 103 | Magura | 40 | 18:00 | 169 | Shitalakhya | 40 | 13:00
38 | Charsaidpur | 35 | 11:00 | 104 | Mahasthangarh | 44 | 18:00 | 170 | Sholosohor | 32 | 00:00
39 | Chauddagram | 41 | 13:00 | 105 | Maijdee | 21 | 19:30 | 171 | Shyampur | 108 | 08:00
40 | Chhatak | 27 | 18:00 | 106 | Manikganj | 78 | 00:00 | 172 | Siddhirganj | 79 | 12:00
41 | Chowmuhani | 111 | 18:00 | 107 | Maniknagar | 52 | 13:00 | 173 | Sirajganj | 65 | 18:00
42 | Chuadanga | 93 | 13:00 | 108 | Matarbari | 37 | 18:00 | 174 | Sonargaon | 93 | 01:00
43 | Coxsbazar | 110 | 18:30 | 109 | Matuail | 50 | 00:00 | 175 | Sreemongol | 56 | 18:00
44 | Cumilla(N) | 95 | 19:00 | 110 | Metrorail_Motijheel | 12 | 17:00 | 176 | Sreepur | 66 | 12:00
45 | Cumilla(S) | 93 | 21:00 | 111 | Metrorail_Uttara | 6 | 18:30 | 177 | Srinagar | 35.2 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 66 | 12:00 | 178 | Sunamganj | 41 | 18:00
47 | Daudkandi | 110 | 21:00 | 113 | Mirpur | 107 | 13:00 | 179 | Sylhet | 37 | 13:00
48 | DhakaUniversity | 32 | 13:00 | 114 | Mirsorai | 14 | 17:00 | 180 | Sylhet-132 | 82 | 13:00
49 | Dhamrai | 90 | 00:00 | 115 | Mirzapur | 32 | 07:00 | 181 | TK | 17 | 18:30
50 | Dhanmondi | 84 | 13:00 | 116 | Mithapukur | 43 | 18:00 | 182 | Tangail | 120 | 18:00
51 | Dohazari | 75 | 18:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 13 | 18:00
52 | Faridpur | 95 | 19:00 | 118 | Mogbazar | 57.2 | 13:00 | 184 | Thakurgaon | 68 | 18:00
53 | Fatullah | 85 | 00:00 | 119 | Mongla | 29 | 00:00 | 185 | Tongi | 87 | 12:00
54 | Fenchuganj | 27 | 18:00 | 120 | Motijheel | 28 | 13:00 | 186 | Ullahpara | 26 | 18:00
55 | Feni | 80 | 13:00 | 121 | Muktagacha | 24 | 13:00 | 187 | Ullon | 49 | 13:00
56 | GPH | 20 | 08:00 | 122 | Munshiganj | 74 | 13:00 | 188 | Uttara | 59 | 18:00
57 | Ghatail | 54 | 17:00 | 123 | Muradnagar | 26 | 18:00 | 189 | UttaraNew | 21 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 130 | 18:00 | 190 | Zigatola | 54 | 13:00
59 | Ghorashal-230 | 77 | 00:00 | 125 | Naogaon | 75 | 18:00
60 | Goalpara | 24 | 12:00 | 126 | Narail | 35 | 21:00
61 | Gollamari | 78 | 09:00 | 127 | Narinda | 37 | 13:00
62 | Gopalganj | 72 | 18:00 | 128 | Narshingdi | 129 | 20:00
63 | Gulshan | 66 | 12:00 | 129 | Natore | 87 | 20:00
64 | Halishahar | 37 | 00:00 | 130 | Nawabganj | 34.2 | 00:00
65 | HaripurSBU | 129 | 00:00 | 131 | Netrakona | 99 | 18:00
66 | Hasnabad | 64 | 13:00 | 132 | New | 44 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9645.19 | 0 |  | 9645.19
1:00 | 9041.48 | 0 |  | 9041.48
2:00 | 8708.78 | 0 |  | 8708.78
3:00 | 8390.67 | 0 |  | 8390.67
4:00 | 8129.92 | 0 |  | 8129.92
5:00 | 8003.28 | 0 |  | 8003.28
6:00 | 7958.59 | 0 |  | 7958.59
7:00 | 8228.23 | 0 |  | 8228.23
8:00 | 8560.04 | 0 |  | 8560.04
9:00 | 8276.71 | 0 |  | 8276.71
10:00 | 8073.94 | 0 |  | 8073.94
11:00 | 8421.9 | 0 |  | 8421.9
12:00 | 9280 | 0 |  | 9280
13:00 | 9890.74 | 0 |  | 9890.74
14:00 | 9011.97 | 0 |  | 9011.97
15:00 | 8399.52 | 0 |  | 8399.52
16:00 | 8039.95 | 0 |  | 8039.95
17:00 | 8497.43 | 0 |  | 8497.43
18:00 | 9826 | 0 |  | 9826
19:00 | 9704 | 0 |  | 9704
19:30 | 9763 | 0 |  | 9763
20:00 | 9803 | 0 |  | 9803
21:00 | 9644.26 | 0 |  | 9644.26
22:00 | 9553.51 | 0 |  | 9553.51
23:00 | 9293.35 | 0 |  | 9293.35
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4839 | 4806.19 | 9645.19 | DAILY GENERATION CURVE
00:30 | 4642.1 | 4701.235 | 9343.335
01:00 | 4445.2 | 4596.28 | 9041.48 | 14-11-2025
01:30 | 4354.6 | 4520.53 | 8875.13
02:00 | 4264 | 4444.78 | 8708.78
02:30 | 4238.5 | 4311.225 | 8549.725
03:00 | 4213 | 4177.67 | 8390.67
03:30 | 4215.5 | 4044.795 | 8260.295
04:00 | 4218 | 3911.92 | 8129.92
04:30 | 4160.5 | 3906.1 | 8066.6
05:00 | 4103 | 3900.28 | 8003.28
05:30 | 4084.75 | 3896.185 | 7980.935
06:00 | 4066.5 | 3892.09 | 7958.59
06:30 | 4144.2 | 3949.21 | 8093.41
07:00 | 4221.9 | 4006.33 | 8228.23
07:30 | 4308.785 | 4085.35 | 8394.135
08:00 | 4395.67 | 4164.37 | 8560.04
08:30 | 4218.755 | 4199.62 | 8418.375
09:00 | 4041.84 | 4234.87 | 8276.71
09:30 | 3920.05 | 4255.275 | 8175.325
10:00 | 3798.26 | 4275.68 | 8073.94
10:30 | 3890.305 | 4357.615 | 8247.92
11:00 | 3982.35 | 4439.55 | 8421.9
11:30 | 4263.305 | 4587.645 | 8850.95
12:00 | 4544.26 | 4735.74 | 9280
12:30 | 4575.71 | 5009.66 | 9585.37
13:00 | 4607.16 | 5283.58 | 9890.74
13:30 | 4334.89 | 5116.465 | 9451.355
14:00 | 4062.62 | 4949.35 | 9011.97
14:30 | 4011.365 | 4694.38 | 8705.745
15:00 | 3960.11 | 4439.41 | 8399.52
15:30 | 3904.64 | 4315.095 | 8219.735
16:00 | 3849.17 | 4190.78 | 8039.95
16:30 | 4003.265 | 4265.425 | 8268.69
17:00 | 4157.36 | 4340.07 | 8497.43
17:30 | 4546.18 | 4615.535 | 9161.715
18:00 | 4935 | 4891 | 9826
18:30 | 4824.5 | 4940.5 | 9765
19:00 | 4714 | 4990 | 9704
19:30 | 4718 | 5045 | 9763
20:00 | 4757 | 5046 | 9803
20:30 | 4704.5 | 5019.13 | 9723.63 |  | Executive Engineer
21:00 | 4652 | 4992.26 | 9644.26 |  | Network Operation Division
21:30 | 4605 | 4993.885 | 9598.885
22:00 | 4558 | 4995.51 | 9553.51
22:30 | 4466.5 | 4956.93 | 9423.43
23:00 | 4375 | 4918.35 | 9293.35

## En-Curve
QF-LDC-12
Date | 14-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2793 | 1308 | 896 | 38 | 68 | 724.19 | 86 | 3450 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2769.5 | 1259.1 | 896 | 38 | 70 | 694.415 | 86 | 3377 | 0 | 0 | 150.5 | 0 | 0 | 0.5 | 0 | 14-11-2025
01:00 | 2746 | 1210.2 | 896 | 38 | 72 | 664.64 | 86 | 3304 | 4.64 | 0 | 19 | 0 | 0 | 1 | 0
01:30 | 2717 | 1196.1 | 896 | 38 | 66 | 619.21 | 86 | 3233 | 0 | 0 | 19 | 0 | 0 | 2.5 | 0 | Energy Generated | 214.7563 |  | MKWHr
02:00 | 2688 | 1182 | 896 | 38 | 60 | 573.78 | 86 | 3162 | 0 | 0 | 19 | 0 | 0 | 4 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2701.5 | 1173.5 | 896 | 38 | 62 | 529.225 | 86 | 3050.5 | 0 | 0 | 9.5 | 0 | 0 | 3.5 | 0 | Total Energy Requirement | 214.7563 |  | MKWHr
03:00 | 2715 | 1165 | 896 | 38 | 64 | 484.67 | 86 | 2939 | 0 | 0 | 0 | 0 | 0 | 3 | 0
03:30 | 2734 | 1176 | 896 | 38 | 65 | 451.795 | 86 | 2811.5 | 0 | 0 | 0 | 0 | 0 | 2 | 0
04:00 | 2753 | 1187 | 896 | 38 | 66 | 418.92 | 86 | 2684 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:30 | 2752 | 1156.5 | 896.5 | 38 | 64 | 421.6 | 86 | 2650 | 0 | 0 | 0 | 0 | 0 | 2 | 0
05:00 | 2751 | 1126 | 897 | 38 | 62 | 424.28 | 86 | 2616 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 2746.5 | 1106.75 | 897 | 38 | 59 | 423.685 | 86 | 2617.5 | 2 | 0 | 0 | 0 | 0 | 4.5 | 0
06:00 | 2742 | 1087.5 | 897 | 38 | 56 | 423.09 | 86 | 2619 | 4 | 0 | 0 | 0 | 0 | 6 | 0
06:30 | 2786 | 1154.25 | 896.5 | 38 | 57 | 427.95 | 86 | 2608.5 | 31.71 | 0 | 0 | 0 | 0 | 7.5 | 0
07:00 | 2830 | 1221 | 896 | 38 | 58 | 432.81 | 86 | 2598 | 59.42 | 0 | 0 | 0 | 0 | 9 | 0
07:30 | 2841.5 | 1230 | 896 | 38 | 57 | 430.425 | 86 | 2634.5 | 153.21 | 0 | 22.5 | 0 | 0 | 5 | 0
08:00 | 2853 | 1239 | 896 | 38 | 56 | 428.04 | 86 | 2671 | 247 | 0 | 45 | 0 | 0 | 1 | 0
08:30 | 2749 | 1132.5 | 896 | 38 | 56 | 429.225 | 86 | 2607.5 | 334.15 | 4 | 85 | 0 | 0 | 1 | 0
09:00 | 2645 | 1026 | 896 | 38 | 56 | 430.41 | 86 | 2544 | 421.3 | 8 | 125 | 0 | 0 | 1 | 0
09:30 | 2625.5 | 1019 | 896 | 38 | 59 | 432.22 | 86 | 2402.5 | 500.105 | 8 | 108.5 | 0 | 0 | 0.5 | 0
10:00 | 2606 | 1012 | 896 | 38 | 62 | 434.03 | 86 | 2261 | 578.91 | 8 | 92 | 0 | 0 | 0 | 0
10:30 | 2731 | 1016 | 896 | 38 | 65 | 431.11 | 86 | 2277 | 618.81 | 8 | 80.5 | 0 | 0 | 0.5 | 0
11:00 | 2856 | 1020 | 896 | 38 | 68 | 428.19 | 86 | 2293 | 658.71 | 8 | 69 | 0 | 0 | 1 | 0
11:30 | 3021.5 | 1131.5 | 896 | 38 | 69 | 474.195 | 86 | 2383.5 | 667.255 | 4 | 79.5 | 0 | 0 | 0.5 | 0
12:00 | 3187 | 1243 | 896 | 38 | 70 | 520.2 | 86 | 2474 | 675.8 | 0 | 90 | 0 | 0 | 0 | 0
12:30 | 3146.5 | 1275.5 | 896 | 38 | 72 | 622.29 | 86 | 2696 | 644.08 | 0 | 109 | 0 | 0 | 0 | 0
13:00 | 3106 | 1308 | 896 | 38 | 74 | 724.38 | 86 | 2918 | 612.36 | 0 | 128 | 0 | 0 | 0 | 0
13:30 | 3040 | 1181 | 896 | 38 | 69 | 687.38 | 86 | 2814.5 | 557.975 | 0 | 81.5 | 0 | 0 | 0 | 0
14:00 | 2974 | 1054 | 896 | 38 | 64 | 650.38 | 86 | 2711 | 503.59 | 0 | 35 | 0 | 0 | 0 | 0
14:30 | 2951.5 | 1052.5 | 896 | 38 | 62 | 596.69 | 86 | 2570 | 418.055 | 0 | 35 | 0 | 0 | 0 | 0
15:00 | 2929 | 1051 | 896 | 38 | 60 | 543 | 86 | 2429 | 332.52 | 0 | 35 | 0 | 0 | 0 | 0
15:30 | 2940.5 | 1056 | 896 | 38 | 59 | 505 | 86 | 2369 | 235.235 | 0 | 35 | 0 | 0 | 0 | 0
16:00 | 2952 | 1061 | 896 | 38 | 58 | 467 | 86 | 2309 | 137.95 | 0 | 35 | 0 | 0 | 0 | 0
16:30 | 3037.5 | 1123 | 896 | 38 | 61 | 512 | 86 | 2384 | 72.69 | 0 | 57.5 | 0 | 0 | 1 | 0
17:00 | 3123 | 1185 | 896 | 38 | 64 | 557 | 86 | 2459 | 7.43 | 0 | 80 | 0 | 0 | 2 | 0
17:30 | 3125 | 1229.5 | 896 | 38 | 66 | 654 | 86 | 2653 | 3.715 | 49.5 | 358 | 0 | 0 | 3 | 0
18:00 | 3127 | 1274 | 896 | 38 | 68 | 751 | 86 | 2847 | 0 | 99 | 636 | 0 | 0 | 4 | 0
18:30 | 3060.5 | 1272 | 896.5 | 38 | 67 | 754 | 86 | 2941.5 | 0 | 66.5 | 580 | 0 | 0 | 3 | 0
19:00 | 2994 | 1270 | 897 | 38 | 66 | 757 | 86 | 3036 | 0 | 34 | 524 | 0 | 0 | 2 | 0
19:30 | 2999 | 1278 | 896 | 38 | 66 | 751 | 86 | 3110 | 0 | 34 | 500 | 0 | 0 | 5 | 0
20:00 | 3051 | 1284 | 897 | 38 | 64 | 752 | 86 | 3097 | 0 | 34 | 497 | 0 | 0 | 3 | 0
20:30 | 3063 | 1282 | 896.5 | 38 | 67 | 754.63 | 86 | 3099 | 0 | 34 | 399.5 | 0 | 0 | 4 | 0
21:00 | 3075 | 1280 | 896 | 38 | 70 | 757.26 | 86 | 3101 | 0 | 34 | 302 | 0 | 0 | 5 | 0
21:30 | 3051.5 | 1290 | 896 | 38 | 69 | 754.885 | 86 | 3109.5 | 0 | 25.5 | 274.5 | 0 | 0 | 4 | 0
22:00 | 3028 | 1300 | 896 | 38 | 68 | 752.51 | 86 | 3118 | 0 | 17 | 247 | 0 | 0 | 3 | 0
22:30 | 3035 | 1295 | 896 | 38 | 68 | 752.43 | 86 | 3091 | 0 | 8.5 | 150.5 | 0 | 0 | 3 | 0
23:00 | 3042 | 1290 | 896 | 38 | 68 | 752.35 | 86 | 3064 | 0 | 0 | 54 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 395 | 09:00 | 388 | 12:00 | Meghnaghat | 396 | 05:00 | 383 | 12:00
Ashuganj | 407 | 09:00 | 397 | 13:00 | Payra | 415 | 04:00 | 412 | 00:00
Bhulta | 401 | 06:00 | 388 | 13:00 | Rahanpur | 410 | 06:00 | 400 | 00:00
Bibiana | 400 | 09:00 | 392 | 00:00 | Rampal | 413 | 06:00 | 403 | 13:00
BIPTC | 407 | 01:00 | 396 | 11:00
Bogura | 407 | 06:00 | 394 | 13:00
Gopalganj | 407 | 09:00 | 397 | 13:00
Kaliakoir | 393 | 08:00 | 380 | 00:00
Korerhat | 402 | 06:00 | 391 | 13:00
Madunaghat | 400 | 18:00 | 393 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 06:00 | 231 | 13:00 | Kaliakoir | 241 | 04:00 | 231 | 13:00
AKSML | 236 | 06:00 | 230 | 13:00 | Keranigonj | 237 | 06:00 | 228 | 13:00
Aminbazar | 239 | 05:00 | 231 | 14:00 | Khulna(S) | 240 | 04:00 | 234 | 13:00
Ashuganj | 236 | 04:00 | 228 | 13:00 | Korerhat | 240 | 06:00 | 233 | 13:00
Ashuganj-400 | 236 | 04:00 | 228 | 13:00 | Madunaghat | 237 | 05:00 | 232 | 13:00
Baghabari | 238 | 05:00 | 233 | 18:00 | Madunaghat-400 | 237 | 05:00 | 233 | 01:00
Barapukuria | 223 | 04:00 | 215 | 13:00 | Maniknagar | 231 | 08:00 | 225 | 13:00
Barapukuria-230 | 223 | 04:00 | 215 | 13:00 | Meghnaghat | 238 | 09:00 | 229 | 00:00
Barishal | 240 | 05:00 | 233 | 13:00 | Meghnaghat-400 | 233 | 05:00 | 227 | 12:00
Bheramara | 234 | 01:00 | 230 | 13:00 | Mirsorai | 235 | 09:00 | 229 | 13:00
Bhulta | 233 | 06:00 | 226 | 13:00 | Rajshahi | 234 | 01:00 | 228 | 13:00
Bibiana | 236 | 09:00 | 231 | 00:00 | Rampal | 238 | 06:00 | 231 | 13:00
BIPTC | 238 | 01:00 | 230 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bogura | 235 | 04:00 | 229 | 13:00 | Rampura | 232 | 04:00 | 224 | 13:00
Bogura-400 | 235 | 05:00 | 228 | 13:00 | Shikalbaha | 236 | 18:00 | 230 | 13:00
Borhanuddin | 242 | 08:00 | 237 | 12:00 | Shyampur | 235 | 06:00 | 227 | 13:00
BSRM | 235 | 04:00 | 227 | 14:00 | Siddhirganj | 232 | 07:00 | 229 | 00:00
Cumilla(N) | 233 | 05:00 | 227 | 13:00 | Sirajgonj | 242 | 06:00 | 237 | 13:00
Faridpur | 239 | 06:00 | -238 | 07:00 | Sreepur | 234 | 04:00 | 131 | 03:00
Fenchuganj | 237 | 10:00 | 232 | 03:00 | Tongi | 236 | 04:00 | 229 | 13:00
Ghorashal | 240 | 01:00 | 230 | 00:00
Ghorashal-230 | 233 | 05:00 | 225 | 13:00
Gopalganj | 240 | 06:00 | 233 | 13:00
GPH | 234 | 08:00 | 230 | 00:00
Haripur | 233 | 06:00 | 225 | 14:00
Hasnabad | 235 | 05:00 | 230 | 12:00
Hathazari | 236 | 01:00 | 231 | 13:00
Ishurdi | 238 | 01:00 | 233 | 13:00
Jhenaidah | 237 | 04:00 | 223 | 12:00
Kachua | 236 | 18:00 | 228 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 131 | 13:00 | Lalmonirhat | 130 | 03:00 | 124 | 08:00
Agargaon | 139 | 06:00 | 133 | 13:00 | Madanganj | 135 | 07:00 | 130 | 13:00
Agrabad | 136 | 07:00 | 132 | 12:00 | Madaripur | 139 | 09:00 | 135 | 13:00
AKS | 135 | 13:00 | 132 | 14:00 | Madartek | 136 | 06:00 | 131 | 13:00
Aminbazar | 139 | 05:00 | 134 | 12:00 | Madunaghat | 138 | 05:00 | 134 | 13:00
Amnura | 137 | 03:00 | 132 | 13:00 | Magura | 140 | 05:00 | 133 | 13:00
Ashuganj | 142 | 05:00 | 139 | 13:00 | Mahasthangarh | 134 | 03:00 | 130 | 13:00
Bagerhat | 137 | 05:00 | 118 | 13:00 | Maijdee | 137 | 04:00 | 131 | 13:00
Bajitpur | 138 | 06:00 | 134 | 12:00 | Manikganj | 137 | 03:00 | 134 | 07:00
Bakulia | 139 | 01:00 | 132 | 13:00 | Maniknagar | 141 | 04:00 | 136 | 13:00
Banani | 137 | 04:00 | 130 | 13:00 | Matarbari | 126 | 06:00 | 117 | 13:00
Bangabhaban | 141 | 09:00 | 136 | 13:00 | Matuail | 135 | 06:00 | 132 | 12:00
Barapukuria | 136 | 04:00 | 130 | 13:00 | Metrorail_Motijheel | 141 | 04:00 | 136 | 13:00
Barguna | 0 | 00:00 | N/A | N/A | Metrorail_Uttara | 139 | 05:00 | 134 | 13:00
Barishal | 139 | 05:00 | 133 | 13:00 | Millgate | 139 | 03:00 | 134 | 13:00
Barishal-230 | 139 | 03:00 | 133 | 13:00 | Mirpur | 139 | 05:00 | 132 | 13:00
Baroaulia | 137 | 09:00 | 133 | 13:00 | Mirzapur | 137 | 09:00 | 131 | 01:00
Baroirhat | 137 | 06:00 | 133 | 13:00 | Mithapukur | 133 | 00:00 | 129 | 07:00
Bashundhara | 137 | 06:00 | 131 | 13:00 | MI_Cement | 140.3 | 06:00 | 131 | 13:00
BashundharaCement | 135 | 07:00 | 130 | 13:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 135 | 08:00 | 131 | 13:00 | Mogbazar | 138 | 04:00 | 15 | 15:00
Benapole | 137 | 04:00 | 126 | 13:00 | Mongla | 138 | 09:00 | 120 | 13:00
Bhaluka | 134 | 04:00 | 127 | 13:00 | Motijheel | 141 | 09:00 | 136 | 13:00
Bhandaria | 137 | 04:00 | 125 | 13:00 | Muktagacha | 132 | 09:00 | 123 | 13:00
Bhangura | 136 | 07:00 | 133 | 02:00 | Munshiganj | 134 | 04:00 | 131 | 12:00
Bheramara | 139 | 01:00 | 137 | 13:00 | Muradnagar | 136 | 09:00 | 131 | 13:00
Bheramara(GK) | 139 | 03:00 | 137 | 13:00 | Mymensingh | 133 | 04:00 | 119 | 07:00
Bhulta | 133 | 08:00 | 130 | 00:00 | Naogaon | 133 | 05:00 | 128 | 13:00
Bog-Sherpur | 135 | 04:00 | 132 | 13:00 | Narail | 140 | 05:00 | 132 | 13:00
Bogura | 135 | 05:00 | 131 | 13:00 | Narinda | 141 | 04:00 | 136 | 13:00
Bogura-230 | 135 | 04:00 | 131 | 13:00 | Narshingdi | 136 | 08:00 | 128 | 00:00
Brahmanbaria | 136 | 08:00 | 131 | 13:00 | Natore | 136 | 05:00 | 132 | 13:00
Cantonment | 138 | 03:00 | 132 | 13:00 | Nawabganj | 138 | 04:00 | 133 | 13:00
Chandina | 138 | 05:00 | 133 | 13:00 | Netrakona | 130 | 23:00 | 121 | 13:00
Chandpur | 140 | 18:00 | 130 | 19:00 | New | 139 | 09:00 | 135 | 13:00
Chandraghona | 138 | 05:00 | 134 | 18:00 | Niamatpur | 138 | 06:00 | 133 | 13:00
Chapai | 136 | 03:00 | 133 | 19:00 | Noapara | 138 | 03:00 | 127 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 04:00 | 131 | 13:00 | Pabna | 139 | 06:00 | 136 | 13:00
Chauddagram | 137 | 04:00 | 132 | 13:00 | Palashbari | 131 | 15:00 | 127 | 01:00
Chhatak | 132 | 03:00 | 128 | 13:00 | Panchagarh | 135 | 20:00 | 125 | 21:00
Chowmuhani | 136 | 03:00 | 133 | 12:00 | Patiya | 136 | 06:00 | 132 | 13:00
Chuadanga | 141 | 05:00 | 130 | 13:00 | Patuakhali | 136 | 07:00 | 134 | 00:00
Coxsbazar | 126 | 09:00 | 118 | 13:00 | Payra | 137 | 07:00 | 135 | 00:00
Cumilla(N) | 138 | 05:00 | 133 | 13:00 | PHP | 136 | 05:00 | 132 | 13:00
Cumilla(S) | 138 | 05:00 | 128 | 11:00 | Postogola | 141 | 06:00 | 133 | 13:00
Daganbhuiyan | 137 | 04:00 | 132 | 13:00 | Purbachal | 137 | 03:00 | 131 | 13:00
Daudkandi | 133 | 05:00 | 128 | 13:00 | Purbasadipur | 133 | 04:00 | 124 | 21:00
DhakaUniversity | 136 | 02:00 | 131 | 13:00 | Rahanpur | 138 | 06:00 | 134 | 13:00
Dhamrai | 139 | 05:00 | 129 | 13:00 | Rahanpur-400 | 138 | 04:00 | 135 | 00:00
Dhanmondi | 137 | 05:00 | 131 | 13:00 | Rahim | 135 | 05:00 | 132 | 13:00
Dohazari | 133 | 06:00 | 128 | 12:00 | Rajbari | 142 | 06:00 | 137 | 13:00
Faridpur | 140 | 02:00 | 137 | 13:00 | Rajendrapur | 136 | 05:00 | 130 | 13:00
Fatullah | 140 | 05:00 | 131 | 13:00 | Rajshahi | 136 | 02:00 | 132 | 13:00
Fenchuganj | 140 | 06:00 | 138 | 00:00 | Rajshahi-230 | 136 | 03:00 | 131 | 13:00
Feni | 135 | 07:00 | 131 | 13:00 | Ramganj | 137 | 04:00 | 131 | 13:00
Ghatail | 133 | 09:00 | 125 | 13:00 | Rampur | 136 | 06:00 | 131 | 13:00
Ghorashal | 142 | 06:00 | 137 | 13:00 | Rampura | 136 | 04:00 | 131 | 13:00
Goalpara | 138 | 02:00 | 119 | 13:00 | Rangamati | 137 | 02:00 | 134 | 13:00
Gollamari | 139 | 06:00 | 136 | 00:00 | Rangpur | 134 | 04:00 | 130 | 00:00
Gopalganj | 139 | 04:00 | 135 | 13:00 | Ruppur | 140 | 04:00 | 137 | 02:00
Gopalganj-400 | 140 | 05:00 | 136 | 13:00 | Saidpur | 133 | 04:00 | 126 | 13:00
Gulshan | 136 | 05:00 | 131 | 13:00 | Satkhira | 138 | 06:00 | 133 | 18:00
Halishahar | 137 | 06:00 | 133 | 13:00 | Satmasjid | 137 | 04:00 | 132 | 13:00
Haripur | 136 | 04:00 | 132 | 12:00 | Savar | 137 | 05:00 | 133 | 11:00
HaripurSBU | 136 | 04:00 | 132 | 13:00 | SevenRings | 143 | 09:00 | 136 | 13:00
Hasnabad | 138 | 00:00 | 133 | 12:00 | ShahCement | 135 | 04:00 | 131 | 13:00
Hathazari | 139 | 01:00 | 134 | 17:00 | Shahjadpur | 140 | 03:00 | 137 | 13:00
Ishurdi | 140 | 01:00 | 138 | 13:00 | Shahjibazar | 138 | 04:00 | 133 | 11:00
Jaldhaka | 132 | 05:00 | 124 | 08:00 | Shahmirpur | 138 | 18:00 | 133 | 12:00
Jamalpur | 129 | 09:00 | 113 | 07:00 | Shariatpur | 139 | 04:00 | 136 | 00:00
Jashore | 138 | 05:00 | 128 | 13:00 | Sherpur | 129 | 09:00 | 111 | 07:00
Jhenaidah | 141 | 06:00 | 126 | 14:00 | Shikalbaha | 126 | 09:00 | 121 | 13:00
Jhenaidah-230 | 141 | 01:00 | 134 | 13:00 | Shikalbaha-230 | 138 | 05:00 | 134 | 00:00
Joydebpur | 140 | 04:00 | 130 | 13:00 | Shitalakhya | 140.3 | 06:00 | 131 | 13:00
Joypurhat | 133 | 05:00 | 128 | 13:00 | Sholosohor | 138 | 09:00 | 134 | 13:00
Juldah | 137 | 03:00 | 133 | 13:00 | Shyampur | 137 | 03:00 | 134 | 13:00
Kabirpur | 139 | 06:00 | 133 | 00:00 | Shyampur-230 | 139 | 05:00 | 134 | 23:00
Kachua | 140 | 04:00 | 135 | 13:00 | Siddhirganj | 136 | 04:00 | 132 | 13:00
Kaliakoir | 141 | 04:00 | 131 | 13:00 | Sirajganj | 136 | 09:00 | 132 | 18:00
Kallyanpur | 139 | 05:00 | 134 | 13:00 | Sonargaon | 135 | 02:00 | 132 | 12:00
Kalurghat | 138 | 04:00 | 133 | 14:00 | Sreemongol | 137 | 07:00 | 134 | 11:00
Kamrangirchar | 139 | 06:00 | 133 | 13:00 | Sreepur | 137 | 06:00 | 131 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 138 | 04:00 | 132 | 13:00
Kasba | 135 | 09:00 | 131 | 13:00 | SSM | 140 | 03:00 | 139 | 00:00
Kazla | 141 | 05:00 | 136 | 13:00 | Sunamganj | 132 | 06:00 | 127 | 12:00
Keranigonj | 138 | 04:00 | 133 | 13:00 | Sylhet | 135 | 05:00 | 132 | 13:00
Khagrachori | 137 | 06:00 | 133 | 13:00 | Sylhet-132 | 134 | 05:00 | 131 | 13:00
Khulna | 139 | 09:00 | 118 | 13:00 | Tangail | 134 | 09:00 | 126 | 13:00
Khulna(S) | 139 | 03:00 | 136 | 18:00 | Taraganj | 133 | 06:00 | 126 | 07:00
Khulshi | 135 | 06:00 | 131 | 13:00 | Thakurgaon | 133 | 20:00 | 121 | 21:00
Kishoreganj | 136 | 05:00 | 128 | 13:00 | TK | 138 | 08:00 | 135 | 00:00
Kodda | 138 | 08:00 | 130 | 00:00 | Tongi | 141 | 04:00 | 136 | 13:00
KSRM | 138 | 18:30 | 133 | 12:00 | Ullahpara | 136 | 01:00 | 134 | 13:00
Kulaura | 140 | 05:00 | 137 | 12:00 | Ullon | 137 | 05:00 | 131 | 13:00
Kurigram | 131 | 04:00 | 124 | 00:00 | Uttara | 139 | 04:00 | 133 | 13:00
Kushtia | 138 | 04:00 | 132 | 18:00 | UttaraNew | 139 | 05:00 | 134 | 13:00
Laksam | 139 | 04:00 | 134 | 13:00 | Zigatola | 139 | 06:00 | 133 | 13:00
Lakshmipur | 138 | 09:00 | 132 | 13:00
Lalbag | 138 | 04:00 | 133 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division