## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-11-2025 | during | 17-11-2025 | during | 17-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 370 | 366 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 225 | 225 | 225 | 225 | GT-1 shut down for schedule outage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 90 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 27 | 22 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 34 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 160 | 300 | 300 | 100 | 100 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 16 | 0 | 149 | 149 | 17 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 88 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 90 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 7 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 60 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1238 | 1718 | 5691.6 | 5659.6 | 2970.61 | 2955.61
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 21 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 222 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 81 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 42 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 100 | 37 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 17 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.33 | 0 | 3.37 | 0 | 3.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 10 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 26 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 2 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 40 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 582 | 600 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 4 | 0 | 4 | 0 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1676.33 | 1926 | 2944.09 | 2937.72 | 2379.87 | 2373.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 189 | 190 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 220 | 220 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 215 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 51 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 107 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 103 | 104 | 0 | 0 | 109 | 109 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 64 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 94 | 96 | 160 | 160 | 96 | 96 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 11 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 48 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 904 | 1055 | 2326.21 | 2256.21 | 1890.51 | 1820.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-11-2025 | during | 17-11-2025 | during | 17-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 66 | 39 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 56 | 58 | 58 | 58 | 58 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.83 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 141.83 | 114 | 402 | 352 | 342.5 | 292.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 67 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 157 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 159 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 12 | 12 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 397 | 392 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1232 | 1239 | 1205 | 1205 | 1157 | 1157
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 860 | 859 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 916 | 1136 | 0 | 0 | 892 | 1045 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2105 | 2245 | 2392 | 2310 | 2529.1 | 2600.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 340 | 505 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 740 | 785 | 857 | 857 | 857 | 857 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.56 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1420.56 | 1630 | 1458 | 1458 | 1325 | 1325
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 62.31 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 182 | 186 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 15 | 113 | 113 | 113 | 113 | Under Maintenance
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.89 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 535.92 | 765 | 748 | 748 | 748 | 748 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.17 | 0 | 58 | 0 | 58 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1348.29 | 1458 | 2364.58 | 2200.99 | 1783.8 | 1620.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 75 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 178 | 0 | 179.13 | 0 | 179.13 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 219.6 | 145 | 456.93 | 242 | 344.93 | 208
System Total |  |  |  |  | 28823.2 | 28205.415 | 10285.61 | 11530 | 19240.41 | 18621.52 | 14723.32 | 14352.43
Forecast Scenario (17-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9770 |  | 0 |  | 9770
|  |  |  | 1:00 | 8970 |  | 0 |  | 8970
|  |  |  | 2:00 | 8670 |  | 0 |  | 8670
|  |  |  | 3:00 | 8310 |  | 0 |  | 8310
|  |  |  | 4:00 | 8260 |  | 0 |  | 8260
|  |  |  | 5:00 | 8220 |  | 0 |  | 8220
|  |  |  | 6:00 | 8420 |  | 0 |  | 8420
|  |  |  | 7:00 | 9230 |  | 0 |  | 9230
|  |  |  | 8:00 | 9600 |  | 0 |  | 9600
|  |  |  | 9:00 | 9590 |  | 0 |  | 9590
|  |  |  | 10:00 | 9630 |  | 0 |  | 9630
|  |  |  | 11:00 | 9970 |  | 0 |  | 9970
|  |  |  | 12:00 | 10510 |  | 0 |  | 10510
|  |  |  | 13:00 | 11000 |  | 0 |  | 11000
|  |  |  | 14:00 | 10700 |  | 0 |  | 10700
|  |  |  | 15:00 | 10330 |  | 0 |  | 10330
|  |  |  | 16:00 | 10220 |  | 0 |  | 10220
|  |  |  | 17:00 | 10750 |  | 0 |  | 10750
|  |  |  | 18:00 | 11570 |  | 0 |  | 11570
|  |  |  | 18:30 | 11400 |  | 0 |  | 11400
|  |  |  | 19:00 | 11330 |  | 0 |  | 11330
|  |  |  | 19:30 | 11130 |  | 0 |  | 11130
|  |  |  | 20:00 | 11040 |  | 0 |  | 11040
|  |  |  | 21:00 | 10740 |  | 0 |  | 10740
|  |  |  | 22:00 | 10460 |  | 0 |  | 10460
|  |  |  | 23:00 | 9950 |  | 0 |  | 9950
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 10510.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11570.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11570.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 237.24 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:28 hrs on 17-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-11-2025 | [28 empty] | Date: | 16-11-2025 | [28 empty] | Date: | 16-11-2025 | [28 empty] | Date: | 16-11-2025 | [28 empty] | Date: | 16-11-2025 | [14 empty] | Date: | 16-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 2 | 172 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 349 | 0 | 30 | 151 | 13 | 0 | 79 | 30 | 0 | 15 | 157 | 0 | 19 | 8 | 77 | 0 | 0 | 0 | 4746 | 843 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 307 | 750 | 0 | 4568 | 9314 | 101.02
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 2 | 171 | 0 | 0 | 107 | 0 | 0 | 20 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 382 | 0 | 30 | 159 | 13 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 4722 | 838 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 307 | 600 | 0 | 4166 | 8888 | 101.02
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 2 | 171 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 72 | 0 | 0 | 0 | 305 | 0 | 383 | 0 | 30 | 158 | 13 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 4645 | 837 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 307 | 600 | 0 | 4017 | 8662 | 101.01
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 37 | 590 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 2 | 171 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 318 | 0 | 30 | 149 | 13 | 0 | 79 | 30 | 0 | 15 | 157 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 4377 | 843 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 306 | 500 | 0 | 3930 | 8307 | 101.01
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 37 | 590 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 2 | 171 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 316 | 0 | 30 | 146 | 16 | 0 | 79 | 30 | 0 | 15 | 157 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 4214 | 848 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 307 | 500 | 0 | 3848 | 8062 | 101.01
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 10 | 590 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 225 | 0 | 230 | 2 | 171 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 323 | 0 | 30 | 149 | 16 | 0 | 2 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 4040 | 848 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 307 | 500 | 0 | 3822 | 7862 | 101
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 86 | 0 | 10 | 590 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 225 | 0 | 230 | 2 | 171 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 60 | 0 | 0 | 0 | 315 | 0 | 324 | 0 | 30 | 159 | 16 | 0 | 2 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 4172 | 848 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 791 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 306 | 500 | 0 | 4036 | 8208 | 101
07:00 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 24 | 0 | 0 | 86 | 0 | 38 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 450 | 3 | 0 | 0 | 0 | 225 | 0 | 230 | 2 | 172 | 0 | 0 | 109 | 0 | 0 | 12 | 0 | 68 | 0 | 11 | 0 | 315 | 0 | 324 | 0 | 30 | 166 | 16 | 0 | 78 | 30 | 0 | 15 | 157 | 0 | 19 | 22 | 83 | 0 | 4.17 | 0 | 4710.17 | 848 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 893 | 0 | 521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.93 | 8 | 0 | 0 | 3.25 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.19 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 14 | 0.04 | 0 | 0 | 120 | 220 | 0 | 307 | 550 | 0 | 4349.71 | 9059.88 | 101
08:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 13 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 100 | 0 | 0 | 86 | 0 | 12 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 600 | 11 | 0 | 0 | 0 | 225 | 0 | 230 | 2 | 172 | 0 | 0 | 108 | 0 | 0 | 12 | 0 | 74 | 0 | 38 | 0 | 310 | 0 | 324 | 0 | 30 | 147 | 16 | 0 | 78 | 30 | 0 | 15 | 157 | 0 | 19 | 56 | 69 | 1 | 12.03 | 0 | 4946.03 | 859 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.17 | 894 | 0 | 518.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.47 | 33 | 0 | 0 | 23.78 | 173 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0.72 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1.8 | 64 | 0.18 | 0 | 0 | 120 | 180 | 0 | 306 | 700 | 0 | 4529.27 | 9475.3 | 100.99
09:00 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 21 | 0 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 0 | 2.32 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 574 | 15 | 0 | 0 | 0 | 220 | 0 | 220 | 0 | 193 | 0 | 0 | 105 | 0 | 0 | 12 | 0 | 78 | 0 | 56 | 0 | 300 | 0 | 362 | 0 | 30 | 139 | 16 | 0 | 75 | 30 | 0 | 15 | 157 | 0 | 19 | 35 | 70 | 1 | 32.58 | 0 | 4845.9 | 859 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 845 | 0 | 420.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.83 | 58 | 0 | 0 | 43.97 | 167 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 3.32 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 3.4 | 117 | 0.36 | 0 | 0 | 120 | 180 | 0 | 275 | 700 | 0 | 4504.14 | 9350.04 | 100.99
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 28 | 0 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 100 | 0 | 3 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 520 | 18 | 0 | 0 | 0 | 220 | 0 | 220 | 0 | 193 | 0 | 0 | 104 | 0 | 0 | 12 | 0 | 84 | 0 | 67 | 0 | 310 | 0 | 374 | 0 | 48 | 144 | 17 | 0 | 78 | 30 | 0 | 15 | 157 | 0 | 19 | 16 | 64 | 2 | 29.83 | 0 | 4838.83 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 780 | 0 | 428.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.99 | 79 | 0 | 0 | 53.23 | 171 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 4.19 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 5.3 | 150 | 0.49 | 0 | 0 | 120 | 180 | 0 | 274 | 690 | 0 | 4544.03 | 9382.86 | 100.99
11:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 31 | 0 | 27 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 100 | 0 | 3.32 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 560 | 20 | 0 | 0 | 0 | 215 | 0 | 220 | 0 | 191 | 0 | 0 | 103 | 0 | 0 | 12 | 0 | 96 | 0 | 72 | 0 | 315 | 0 | 388 | 0 | 58 | 152 | 5 | 0 | 78 | 30 | 0 | 15 | 157 | 0 | 19 | 16 | 66 | 2 | 46.22 | 0 | 5091.54 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 780 | 0 | 433.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.41 | 92 | 0 | 0 | 59.27 | 177 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 5.09 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 5.5 | 176 | 0.56 | 0 | 0 | 120 | 220 | 0 | 272 | 690 | 0 | 4670.05 | 9761.59 | 100.98
12:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 32 | 0 | 27 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 100 | 0 | 3.33 | 86 | 0 | 9 | 650 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 582 | 19 | 0 | 0 | 0 | 215 | 0 | 220 | 0 | 189 | 0 | 0 | 103 | 0 | 0 | 11 | 0 | 94 | 0 | 72 | 0 | 320 | 0 | 397 | 0 | 57 | 157 | 21 | 0 | 81 | 30 | 0 | 12 | 157 | 0 | 19 | 19 | 66 | 2 | 35.83 | 0 | 5192.16 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 916 | 0 | 535.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.31 | 94 | 0 | 0 | 58.17 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.89 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 5.6 | 178 | 0.56 | 0 | 0 | 120 | 220 | 0 | 340 | 740 | 0 | 5093.45 | 10285.61 | 100.98
13:00 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 15 | 0 | 16 | 0 | 0 | 0 | 4 | 30 | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 28 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 3.07 | 86 | 0 | 13 | 650 | 0 | 0 | 0 | 0 | 10 | 219 | 0 | 0 | 0 | 570 | 15 | 0 | 0 | 0 | 215 | 0 | 220 | 0 | 190 | 0 | 6 | 103 | 16 | 0 | 11 | 0 | 92 | 0 | 67 | 0 | 320 | 0 | 369 | 0 | 50 | 157 | 21 | 0 | 78 | 30 | 0 | 1 | 157 | 0 | 19 | 56 | 62 | 1 | 18.25 | 0 | 5217.32 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 1086 | 0 | 712.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.37 | 80 | 0 | 0 | 60.53 | 182 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 3.9 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5 | 173 | 0.49 | 0 | 0 | 120 | 220 | 0 | 402 | 780 | 0 | 5458.1 | 10675.42 | 100.98
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 25 | 0 | 27.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 2.48 | 86 | 0 | 10 | 650 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 580 | 15 | 0 | 0 | 0 | 215 | 0 | 220 | 0 | 187 | 0 | 0 | 102 | 0 | 0 | 11 | 0 | 104 | 0 | 57 | 0 | 310 | 0 | 388 | 0 | 50 | 146 | 21 | 0 | 75 | 30 | 0 | 12 | 157 | 0 | 19 | 35 | 40 | 2 | 38.4 | 0 | 5089.38 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1092 | 0 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.47 | 81 | 0 | 0 | 23.66 | 173 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 4.08 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 4.4 | 144 | 0.41 | 0 | 0 | 115 | 180 | 0 | 305 | 780 | 0 | 5225.02 | 10314.4 | 100.97
15:00 | 0 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 0 | 26 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 580 | 11 | 0 | 0 | 0 | 215 | 0 | 220 | 0 | 187 | 0 | 0 | 102 | 0 | 0 | 11 | 0 | 106 | 0 | 41 | 0 | 315 | 0 | 386 | 0 | 67 | 154 | 21 | 0 | 75 | 30 | 0 | 12 | 159 | 0 | 19 | 56 | 39 | 1 | 27.21 | 0 | 4984.87 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1124 | 0 | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.44 | 53 | 0 | 0 | 29.24 | 176 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.58 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3 | 102 | 0.27 | 0 | 0 | 115 | 180 | 0 | 304 | 780 | 0 | 5149.53 | 10134.4 | 100.97
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 7 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 86 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 588 | 5 | 0 | 0 | 0 | 215 | 0 | 220 | 0 | 181 | 0 | 0 | 103 | 0 | 0 | 11 | 0 | 104 | 0 | 20 | 0 | 310 | 0 | 390 | 0 | 67 | 151 | 21 | 0 | 77 | 30 | 0 | 12 | 159 | 0 | 19 | 56 | 39 | 0 | 9.43 | 0 | 4904.7 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1069 | 0 | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21 | 0 | 0 | 7.77 | 172 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0.75 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.2 | 38 | 0.14 | 0 | 0 | 115 | 180 | 0 | 401 | 780 | 0 | 5055.86 | 9960.56 | 100.97
17:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 8 | 60 | 30 | 0 | 17 | 65 | 0 | 350 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 1 | 17 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 35 | 2 | 0 | 37 | 8 | 0 | 86 | 1 | 12 | 650 | 0 | 0 | 9 | 0 | 18 | 222 | 0 | 0 | 0 | 566 | 0 | 0 | 30 | 0 | 215 | 0 | 220 | 0 | 160 | 0 | 12 | 103 | 12 | 0 | 11 | 0 | 94 | 0 | 1 | 0 | 305 | 0 | 400 | 0 | 67 | 147 | 21 | 0 | 80 | 30 | 0 | 12 | 159 | 0 | 19 | 56 | 39 | 0 | 0.22 | 0 | 5144.72 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1043 | 0 | 728 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.76 | 1 | 12 | 0 | 0.63 | 168 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0.05 | 0 | 0 | 56 | 0 | 12 | 0 | 0 | 0 | 0.1 | 1 | 0.02 | 0 | 0 | 115 | 220 | 0 | 505 | 778 | 0 | 5092.56 | 10237.28 | 100.96
18:00 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 7 | 0 | 90 | 160 | 0 | 17 | 90 | 0 | 400 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 60 | 22 | 15 | 0 | 0 | 2 | 10 | 0 | 0 | 4 | 50 | 42 | 0 | 37 | 38 | 0 | 86 | 26 | 17 | 650 | 40 | 0 | 21 | 0 | 81 | 222 | 0 | 0 | 0 | 600 | 0 | 0 | 107 | 0 | 215 | 0 | 220 | 0 | 190 | 0 | 48 | 104 | 64 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 320 | 0 | 392 | 0 | 67 | 157 | 21 | 0 | 81 | 30 | 0 | 12 | 159 | 0 | 19 | 56 | 39 | 0 | 0 | 0 | 6052 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 765 | 0 | 0 | 0 | 15 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 505 | 785 | 0 | 5478 | 11530 | 100.96
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 17 | 0 | 45 | 145 | 0 | 17 | 90 | 0 | 400 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 17 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 55 | 48 | 0 | 37 | 38 | 0 | 86 | 34 | 12 | 650 | 0 | 0 | 32 | 0 | 99 | 224 | 0 | 0 | 0 | 612 | 0 | 0 | 133 | 0 | 215 | 0 | 220 | 0 | 180 | 0 | 49 | 104 | 64 | 0 | 20 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 368 | 0 | 67 | 156 | 21 | 0 | 81 | 30 | 0 | 12 | 159 | 0 | 19 | 58 | 39 | 0 | 0 | 0 | 5928.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 765 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 35 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 785 | 0 | 5401 | 11329.5 | 100.95
19:30 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 17 | 33 | 45 | 95 | 0 | 17 | 90 | 0 | 400 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 17 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17 | 48 | 0 | 37 | 38 | 0 | 86 | 29 | 18 | 650 | 0 | 0 | 32 | 0 | 93 | 224 | 0 | 0 | 0 | 612 | 0 | 0 | 80 | 0 | 215 | 0 | 220 | 0 | 180 | 0 | 47 | 104 | 68 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 366 | 0 | 67 | 152 | 21 | 0 | 81 | 30 | 0 | 12 | 159 | 0 | 19 | 58 | 39 | 0 | 0 | 0 | 5787.5 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 0 | 762 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 35 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 790 | 0 | 5379 | 11166.5 | 100.95
20:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 23 | 15 | 45 | 0 | 17 | 85 | 0 | 400 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 17 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 48 | 0 | 37 | 38 | 0 | 86 | 0 | 20 | 650 | 0 | 0 | 0 | 0 | 97 | 225 | 0 | 0 | 0 | 612 | 0 | 0 | 80 | 0 | 215 | 0 | 220 | 0 | 180 | 0 | 32 | 105 | 64 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 384 | 0 | 68 | 158 | 21 | 0 | 81 | 30 | 0 | 12 | 159 | 0 | 19 | 58 | 39 | 0 | 0 | 0 | 5584.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1133 | 0 | 774 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 780 | 0 | 5376 | 10960.5 | 100.95
21:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 17 | 0 | 35 | 15 | 45 | 0 | 17 | 35 | 0 | 400 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 17 | 21.5 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 37 | 38 | 0 | 86 | 0 | 30 | 650 | 0 | 0 | 0 | 0 | 98 | 227 | 0 | 0 | 0 | 613 | 0 | 0 | 80 | 0 | 215 | 0 | 220 | 0 | 152 | 0 | 16 | 105 | 65 | 0 | 20 | 0 | 88 | 0 | 0 | 0 | 315 | 0 | 386 | 0 | 68 | 162 | 21 | 0 | 81 | 30 | 0 | 12 | 159 | 0 | 19 | 58 | 41 | 0 | 0 | 0 | 5475.5 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129 | 0 | 770.39 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 506 | 778 | 0 | 5313.39 | 10788.89 | 100.94
22:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 0 | 33 | 0 | 15 | 0 | 17 | 17 | 0 | 400 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 38 | 0 | 86 | 0 | 10 | 650 | 0 | 0 | 0 | 0 | 49 | 228 | 0 | 0 | 0 | 612 | 0 | 0 | 60 | 0 | 215 | 0 | 220 | 0 | 151 | 0 | 17 | 105 | 65 | 0 | 20 | 0 | 86 | 0 | 0 | 0 | 315 | 0 | 383 | 0 | 68 | 160 | 21 | 0 | 81 | 30 | 0 | 12 | 159 | 0 | 19 | 58 | 40 | 0 | 0 | 0 | 5279.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 768.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 748 | 0 | 5196.37 | 10475.87 | 100.94
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 16 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 215 | 0 | 220 | 0 | 151 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 403 | 0 | 68 | 157 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 19 | 35 | 40 | 0 | 0 | 0 | 4862 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 750.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 505 | 746 | 0 | 5129.01 | 9991.01 | 100.93
Total KWH | 0 | 437760 | 252480 | 0 | 0 | 0 | 0 | 0 | 8560800 | 0 | 0 | 129600 | 39600 | 229104 | 228960 | 492535 | 0 | 134216 | 404640 | 0 | 9253300 | 0 | 0 | 0 | 142991 | 7768567 | 0 | 0 | 205300 | 133200 | 477000 | 344520 | 0 | 0 | 30109 | 17564 | 0 | 0 | 100320 | 129446 | 112413 | 0 | 974400 | 192000 | 20203 | 2073480 | 124617 | 480000 | 15432727.27 | 30109 | 0 | 87360 | 0 | 552836 | 5153407 | 0 | 0 | 0 | 12643635 | 134865 | 0 | 572072 | 0 | 5294000 | 0 | 5434000 | 21120 | 4312000 | 0 | 216000 | 2520505 | 402720 | 0 | 367630 | 0 | 2024640 | 0 | 506209 | 0 | 7561000 | 0 | 9142000 | 0 | 1139400 | 3705300 | 468408 | 0 | 1662720 | 692928 | 0 | 334000 | 3702960 | 0 | 337200 | 796800 | 1353600 | 12100 | 276500 | 0 | 120379876.27 | 20728000 | 6329088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514080 | 22843640 | 0 | 14524042 | 0 | 0 | 0 | 30720 | 321312 | 0 | 0 | 0 | 0 | 385510 | 600820 | 92715 | 0 | 360752 | 4269636 | 0 | 0 | 0 | 0 | 0 | 8947418 | 0 | 30120 | 0 | 0 | 205044 | 206443 | 499564 | 0 | 0 | 0 | 35767.68 | 1148400 | 3507 | 0 | 0 | 2831000 | 5179170 | 0 | 8959104 | 17265454.55 | 0 | 116311307.23 | 236691183.5

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10285.61 | MW | 12:00 Hr. | Energy Generated |  |  | 236.6912 |  | MKWHr.
| Day Peak Demand |  |  | 10285.61 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11530 | MW | 18:00 Hr. | Energy Demand |  |  | 236.6912 |  | MKWHr.
| Evening Peak Demand |  |  | 11530 | MW | 18:00 Hr. | Maximum Temperature |  |  | 30.6 |  | °C
| Minimum Generation of the Day |  |  | 7862 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 792.25 |  | MMCFD
| Maximum Generation of the Day |  |  | 11530 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.4897 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.4042 | 0 | 2.6251 | 0 | 0 | 0.2053 | 0 | 0 | 29.2346 | Gas | 107.3055 | Gas | 380078510.29
| Chattogram Zone |  |  | 5.6334 | 28.0764 | 2.2509 | 0 | 2.0735 | 0.15507 | 0 | 0.10032 | 38.2895 | Coal | 77.1446 | Coal | 491897909.0984
| Cumilla Zone |  |  | 17.9493 | 0 | 1.1908 | 0 | 0 | 0.50621 | 2.0246 | 0 | 21.6709 | HFO | 8.3501 | HFO | 145041797.93
| Mymensingh Zone |  |  | 1.3536 | 0 | 1.134 | 0 | 0 | 0.2886 | 0 | 0 | 2.7762 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.4087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4087 | Hydro | 2.0735 | Hydro | 207348
| Khulna Zone |  |  | 6.3291 | 22.8436 | 0 | 0 | 0 | 0.51408 | 20.728 | 0 | 50.4148 | Solar | 4.4406 | Solar | 70937413.7228
| Barishal Zone |  |  | 8.0102 | 26.2246 | 0 | 0 | 0 | 0.003507 | 0 | 0 | 34.2382 | Import | 37.2767 | Import | 209734808.86
| Rajshahi Zone |  |  | 13.2171 | 0 | 0.44475 | 0 | 0 | 1.3772 | 14.524 | 0 | 29.563 | Wind | 0.10032 | Wind | 1475707.2
| Rangpur Zone |  |  | 0 | 0 | 0.70461 | 0 | 0 | 1.3906 | 0 | 0 | 2.0952
| Total |  |  | 107.3055 | 77.1446 | 8.3501 | 0 | 2.0735 | 4.4406 | 37.2767 | 0.10032 | 236.6912
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 380078510.29 |  | Hydro | 207348
|  |  |  | Coal | 491897909.0984 |  | Solar | 70937413.7228
|  |  |  | HFO | 145041797.93 |  | Import | 209734808.86
|  |  |  | HSD | 0 |  | Wind | 1475707.2
[5 empty] | Total: | 129,93,73,495 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.728 | Peak Hr Flow | 859.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45016937.51 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.524 | Peak Hr Flow | 765.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2230 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.0246 | Peak Hr Flow | 96.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2610 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.2767 | Peak Hr Flow | 1720.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4531
|  |  |  | Chattogram |  | 0 |  | 1282
|  |  |  | Cumilla |  | 0 |  | 969
|  |  |  | Mymensingh |  | 0 |  | 852
|  |  |  | Sylhet |  | 0 |  | 425
|  |  |  | Khulna |  | 0 |  | 1203
|  |  |  | Barishal |  | 0 |  | 312
|  |  |  | Rajshahi |  | 0 |  | 987
|  |  |  | Rangpur |  | 0 |  | 702
|  |  |  | Total |  | 0 |  | 11263
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 15:39 | Madaripur-Shariatpur 132kV Ckt-1 Scheduled S/D from Shariatpur 132/33kV end Due to
Annual Maintenance(Schedule Shutdown). and from Madaripur 132/33kV end Due to Annual
Maintenance
| 08:18 | 16:18 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Scheduled S/D Due to Annual maintenance
| 08:18 | 16:12 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Scheduled S/D Due to Annual maintenance
| 08:19 | 16:37 | Benapole 132/33kV S/S Transformer-2(416T) LT Scheduled S/D Due to Annual Maintenance
| 08:20 | 16:35 | Benapole 132/33kV S/S Transformer-2(416T) HT Scheduled S/D Due to Annual Maintenance
| 08:20 | 15:34 | Chapainawabganj-Rahanpur 132kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to
Sheduled S/D and from Rahanpur 400/132kVend.
| 08:21 | 16:05 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to QF-
GMD-39 and as the instruction of ALDC Bogura (499264)
| 08:21 | 16:05 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to QF-
GMD-39 and as the instruction of ALDC Bogura (499264)
| 08:22 | 16:01 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to S/D for Annual
maintenance (Deadline Checking) work.
| 08:22 | 16:05 | Barapukuria-Saidpur 132 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual Maintenance work
| 08:27 | 16:11 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to Annual Maintenance
| 08:27 | 16:10 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to Annual Maintenance
|  | 08:28 | Kodda 132/33kV S/S Tr-1 (406T) HT is restored.
|  | 08:29 | Kodda 132/33kV S/S Tr-1 (406T) LT is restored.
| 08:29 |  | Chandpur 132/33kV S/S 200KVA Aux. T-2 LT Scheduled S/D Due to Maintainace
|  | 08:30 | Chandpur 132/33kV S/S 200KVA Aux. T-1 LT is restored.
| 08:37 | 15:50 | Bagerhat-Mongla 132 kV Ckt-1 Scheduled S/D from Mongla 132/33kV end Due to Annual
Maintenance Work and from Bagerhat 132/33kV end Due to Yearly maintenance.
| 08:40 | 15:18 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Scheduled S/D from Bog-Sherpur 132/33kV end Due to
Annual Maintenance. and from Sirajganj 132/33kV end Due to annual maintenance
| 08:40 | 17:12 | Narshingdi 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
| 08:40 | 17:12 | Narshingdi 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
| 08:42 |  | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
maintenance by kaliakoir grid SS. and from Kaliakoir 400/230/132kV end Due to Annual
Maintenance.
| 08:44 | 14:15 | Palashbari 132/33kV S/S TR3-424T LT Scheduled S/D Due to Annual Maintenance
| 08:45 | 14:14 | Palashbari 132/33kV S/S TR3-424T HT Scheduled S/D Due to Annual Maintenance
| 08:53 | 18:20 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to annul maintenance
| 09:00 | 17:15 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenance work
| 09:01 | 17:05 | Jhenaidah-Magura 132 kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to Annual
Maintenance.
| 09:02 | 16:15 | Jhenaidah 132/33kV S/S Jhenaidah-Magura, 132kV Circuit-1(L7) Scheduled S/D Due to Annual
maintenance
| 09:02 | 16:26 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to Annual
Maintenance
| 09:03 | 16:25 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to Annual
Maintenance
| 09:05 | 17:17 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Annual Maintenance
| 09:06 | 17:16 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Annual Maintenance
| 09:06 | 15:54 | BIPTC S/S 20DF22 Scheduled S/D
| 09:08 | 16:06 | Joydebpur 132/33kV S/S GT-3 HT Scheduled S/D Due to Annual maintenance
| 09:09 | 15:57 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance work
| 09:10 | 19:36 | Haripur-Siddirganj 230kV Ckt-1 Scheduled S/D from Siddhirganj 230/132kV end Due to
annual maintence work and from Haripur 230/132kV end Due to Annual Maintenance.
| 09:10 | 17:15 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance work
| 09:20 | 17:31 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
| 09:25 | 16:25 | Sonargaon 132/33kV S/S Bashundhara Line Scheduled S/D Due to Annual maintenance work.
|  | 10:05 | Bhaluka 132/33kV S/S 03. Transformer-03 HT is restored.
|  | 10:07 | Bhaluka 132/33kV S/S 03. Transformer-03 LT is restored.
| 11:06 | 17:15 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
SCADA operation test by Muradnagar S/S end.
| 11:10 | 16:04 | New Tongi S/S Tr-2(4161-3) Scheduled S/D Due to Annual Maintanance.
| 11:10 | 16:04 | New Tongi S/S Tr-2(4161-3) Scheduled S/D Due to Annual Maintanance.
| 11:20 | 11:43 | Coxsbazar 132/33kV S/S 405T-T1 LT Tripped showing Over current relays Due to Due to 33kv | [7 empty] | 26.0MW load
|  |  | kolatoli-1, kolatoli-2 Tripped. | [7 empty] | interrup.
| 11:25 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Project Work.
|  | 11:50 | Ishurdi 132/33kV S/S 132 kV Baghabari Line is restored.
| 12:00 |  | Day peak generation 10281 MW
| 12:27 | 16:42 | Rampura 230/132kV S/S Auto Transformer - 04 LT Scheduled S/D Due to SCADA Integration
work under G2G Project(CCCE)
| 12:27 | 16:42 | Rampura 230/132kV S/S Auto Transformer - 04 HT Scheduled S/D Due to SCADA Integration
work under G2G Project(CCCE)
| 12:51 | 17:16 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 Project Work S/D Due to
SCADA Integration
| 12:51 |  | Muradnagar 132/33kV S/S 132KV Busbar-1 Project Work S/D Due to SCADA Integration
|  | 13:15 | Nawabganj 132/33kV S/S TR-2 HT is restored.
|  | 13:18 | Nawabganj 132/33kV S/S TR-2 LT is restored.
|  | 14:01 | Savar 132/33kV S/S Main Bus-I is restored.
|  | 14:09 | Savar 132/33kV S/S T-3 LT is restored.
|  | 14:09 | Savar 132/33kV S/S T-3 HT is restored.
|  | 14:52 | Chhatak 132/33kV S/S T-1 HT is restored.
|  | 14:53 | Chhatak 132/33kV S/S T-1 LT is restored.
| 16:10 | 16:40 | KSRM 132/33kV S/S Transformer-02 LT Scheduled S/D Due to due to shutdown oil leakage
check and transformer oil top up
|  | 16:39 | Korerhat 400/230/132kV S/S Chowmuhani-04 is restored.
|  | 16:39 | Korerhat 400/230/132kV S/S Chowmuhani-04 is restored.
|  | 17:22 | Bhulta-Rampura 230 kV Ckt-1 is restored.
|  | 17:30 | Baroaulia 132/33kV S/S T-1(405T) HT is restored.
| 18:00 |  | Evening Peak Generation is 11530 MW.
|  | 18:05 | Gopalganj(N)-Madaripur 132kV Ckt-1 is restored.
| 20:00 | 20:30 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB initiation relays Due to
Unknown
| 20:02 |  | Haripur-Siddirganj 230kV Ckt-1 Tripped from Haripur 230/132kV end showing Main-1: 1.
General Trip, 2. Differential Trip, 3. Start R Phase, 4. Start Y Phase, 5. Start B Phase,
6.EFCOM Rec, 7. 3Phsae Trip, 8. Fuse Fail. Main-2: 1. General Trip, 2. Differential
Trip, 3. Distance Trip, 4. ZCOM Trip, 5. Start R Phase, 6. Start Y Phase, 7. Start B
Phase, 8. 3PH Trip. relays Due to LA Burst and from Siddhirganj 230/132kV end showing
DIFFERENTIAL relays.
|  | 20:09 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-1 is restored.
| 00:45 | 00:57 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Over Current and Earth Fault. relays | [7 empty] | 18.0MW load
|  |  | Due to Shaistaganj Feeder Phase to Ground Fault and Chunarughat Feeder Under Frequency | [7 empty] | interrup.
Fault.
| 03:03 |  | Chandpur 150 MW CCPP was shutdown due to GT air filter change and maintenance purpose
| 04:05 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT11 was synchronized
| 05:00 |  | Minimum generation 8060 MW
| 06:03 |  | JERA Meghnaghat Power Limited 718 MW CCPP ST10 was synchronized
| 06:09 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to Removal of | [7 empty] | 45.0MW load
|  |  | jumpering of Chhatak ckt-I & II | [7 empty] | interrup. Sylhet
132/33kV end
| 06:19 |  | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 30.0MW load
interrup.
| 07:22 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- GT1
| 07:25 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized
| 07:33 |  | Nawabganj 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance
| 07:34 |  | Nawabganj 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance
| 07:35 |  | Patiya 132/33kV S/S Sikalbaha-Patiya Ckt-01 Scheduled S/D Due to Annual mantainance
| 07:36 |  | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to For annual maintenance work
purpose
| 07:37 |  | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to For annual maintenance work
purpose
| 07:42 |  | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance
| 07:43 |  | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance
| 07:50 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end.
| 07:55 |  | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 366 | 8560800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9253300 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7768567 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 129600 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 90 | 228960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 134216 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 142991 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 477000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 344520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 252480 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 492535 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 229104 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 437760 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 404640 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 205300 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 7 | 39600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 60 | 133200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1718 | 29234573
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134865 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 21 | 87360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2073480 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5153407 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 81 | 552836 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 112413 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 129446 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 974400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 480000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20203 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 10 | 17564 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 26 | 124617 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 192000 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 2 | 30109 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 40 | 30109 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 600 | 12643635 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 4 | 100320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15432727.27 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 1926 | 38289491.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4312000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 220 | 5434000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5294000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 21120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 107 | 572072 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 104 | 2520505 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 64 | 402720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 96 | 2024640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 367630 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 48 | 216000 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 506209 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1055 | 21670896
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 39 | 1353600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 56 | 796800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 337200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 276500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 114 | 2776200
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1139400 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3705300 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 692928 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1662720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 159 | 3702960 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 334000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 468408 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7561000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 392 | 9142000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1239 | 28408716
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 859 | 20728000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6329088 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 514080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1136 | 22843640 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2245 | 50414808
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 505 | 8959104 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2831000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 785 | 17265454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5179170 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3507 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1630 | 34238235.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 385510 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4269636 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8947418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 92715 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 321312 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 15 | 30720 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30120 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 765 | 14524042 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 360752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 600820 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1458 | 29563045
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 75 | 499564 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35767.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 205044 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 206443 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1148400 | -
Rangpur Area Total |  |  |  |  | 950 | 145 | 2095218.68
Eastern Grid Total |  |  |  |  | 17383.855 | 6052 | 120379876.27
Western Grid Total |  |  |  |  | 10821.56 | 5478 | 116311307.23
National Grid Total |  |  |  |  | 28205.415 | 11530 | 236691183.5
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8058.45 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3203.5 | MW
i) Dhaka area |  |  | 4531.22 |  | MW | i) Khulna area |  |  |  | 1203 | MW
ii) Chattogram area |  |  | 1281.5 |  | MW | ii) Barishal area |  |  |  | 311.5 | MW
iii) Cumilla area |  |  | 968.73 |  | MW | iii) Rajshahi area |  |  |  | 987 | MW
iv) Mymensingh area |  |  | 852 |  | MW | iv) Rangpur area |  |  |  | 702 | MW
v) Sylhet area |  |  | 425 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11261.95 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 61 | 13:00 | 133 | Niamatpur | 39 | 18:00
2 | AKSML | 96 | 04:00 | 68 | Ishurdi | 58 | 18:30 | 134 | Noapara | 36 | 18:30
3 | Aftabnagar | 30 | 13:00 | 69 | Jaldhaka | 54 | 18:00 | 135 | PHP | 8 | 04:00
4 | Agargaon | 98 | 13:00 | 70 | Jamalpur | 85 | 18:00 | 136 | Pabna | 70 | 18:00
5 | Agrabad | 80 | 18:00 | 71 | Jashore | 96 | 18:00 | 137 | Palashbari | 74 | 18:30
6 | Amnura | 14 | 07:00 | 72 | Jhenaidah | 90 | 18:00 | 138 | Panchagarh | 43 | 18:30
7 | Ashuganj | 57 | 00:00 | 73 | Joydebpur | 114 | 17:00 | 139 | Patiya | 7 | 18:00
8 | BSRM | 203 | 23:00 | 74 | Joypurhat | 42 | 18:00 | 140 | Patuakhali | 53.5 | 20:00
9 | Bagerhat | 62 | 18:00 | 75 | Juldah | 13 | 12:00 | 141 | Payra | 22 | 20:00
10 | Bajitpur | 58 | 18:00 | 76 | KSRM | 30 | 16:00 | 142 | Postogola | 51 | 13:00
11 | Bakulia | 69 | 18:00 | 77 | Kabirpur | 192 | 18:30 | 143 | Purbachal | 14 | 11:00
12 | Banani | 39 | 13:00 | 78 | Kachua | 57 | 18:00 | 144 | Purbasadipur | 93 | 18:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kallyanpur | 82 | 13:00 | 145 | Rahanpur | 20 | 18:00
14 | Barapukuria | 49 | 18:00 | 80 | Kalurghat | 44 | 11:00 | 146 | Rahim | 43 | 12:00
15 | Barguna | 0 | 00:00 | 81 | Kamrangirchar | 64 | 13:00 | 147 | Rajbari | 56 | 18:00
16 | Barishal | 86 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 104 | 12:00
17 | Barishal-230 | 66 | 18:00 | 83 | Kasba | 24 | 18:00 | 149 | Rajshahi | 78 | 13:00
18 | Baroaulia | 43 | 18:00 | 84 | Kazla | 81 | 22:00 | 150 | Rajshahi-230 | 52 | 13:00
19 | Baroirhat | 38 | 18:00 | 85 | Keranigonj | 56 | 18:00 | 151 | Ramganj | 66 | 18:00
20 | Bashundhara | 162 | 13:00 | 86 | Khagrachori | 22 | 17:00 | 152 | Rampur | 33 | 18:00
21 | BashundharaCement | 8 | 14:00 | 87 | Khulna | 53 | 13:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 50 | 18:00 | 88 | Khulshi | 153 | 15:00 | 154 | Rangpur | 101 | 18:00
23 | Benapole | 44 | 18:00 | 89 | Kishoreganj | 86 | 18:00 | 155 | Ruppur | 5.2 | 10:00
24 | Bhaluka | 129 | 18:00 | 90 | Kodda | 279 | 16:00 | 156 | SSM | 2 | 21:00
25 | Bhandaria | 40 | 20:00 | 91 | Kulaura | 31 | 18:00 | 157 | Saidpur | 81 | 18:30
26 | Bhangura | 25 | 18:00 | 92 | Kurigram | 52 | 18:00 | 158 | Satkhira | 80 | 07:00
27 | Bheramara(GK) | 42 | 18:00 | 93 | Kushtia | 110 | 18:00 | 159 | Satmasjid | 86 | 13:00
28 | Bhulta | 200 | 19:30 | 94 | Laksam | 22 | 18:00 | 160 | Savar | 166 | 15:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 20 | 18:00 | 161 | SevenRings | 11.92 | 23:00
30 | Bogura | 117 | 12:00 | 96 | Lalbag | 61 | 13:00 | 162 | ShahCement | 32 | 23:00
31 | Borhanuddin | 63 | 21:00 | 97 | Lalmonirhat | 42 | 18:00 | 163 | Shahjadpur | 58 | 18:30
32 | Brahmanbaria | 97 | 18:30 | 98 | MI_Cement | 15.3 | 03:00 | 164 | Shahjibazar | 81 | 18:30
33 | Cantonment | 94 | 13:00 | 99 | Madanganj | 40 | 18:00 | 165 | Shahmirpur | 38 | 18:00
34 | Chandina | 9.73 | 18:00 | 100 | Madaripur | 65 | 18:00 | 166 | Shariatpur | 54 | 19:30
35 | Chandpur | 52 | 18:30 | 101 | Madartek | 66 | 13:00 | 167 | Sherpur | 102 | 18:30
36 | Chandraghona | 30 | 18:00 | 102 | Madunaghat | 38 | 12:00 | 168 | Shikalbaha | 24 | 00:00
37 | Chapai | 40 | 07:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 62.8 | 12:00
38 | Charsaidpur | 38 | 12:00 | 104 | Mahasthangarh | 48 | 18:00 | 170 | Sholosohor | 37 | 11:00
39 | Chauddagram | 48 | 18:00 | 105 | Maijdee | 22 | 18:00 | 171 | Shyampur | 126 | 09:00
40 | Chhatak | 24 | 18:30 | 106 | Manikganj | 93 | 18:00 | 172 | Siddhirganj | 103 | 13:00
41 | Chowmuhani | 112 | 19:00 | 107 | Maniknagar | 60 | 13:00 | 173 | Sirajganj | 82 | 18:00
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 39 | 18:30 | 174 | Sonargaon | 113 | 18:30
43 | Coxsbazar | 122 | 18:00 | 109 | Matuail | 58 | 10:00 | 175 | Sreemongol | 62 | 18:00
44 | Cumilla(N) | 81 | 11:00 | 110 | Metrorail_Motijheel | 22 | 09:00 | 176 | Sreepur | 95 | 18:00
45 | Cumilla(S) | 127 | 14:00 | 111 | Metrorail_Uttara | 6 | 18:30 | 177 | Srinagar | 31.45 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 97 | 12:00 | 178 | Sunamganj | 41 | 19:00
47 | Daudkandi | 114 | 18:00 | 113 | Mirpur | 121 | 18:00 | 179 | Sylhet | 36 | 18:00
48 | DhakaUniversity | 68 | 13:00 | 114 | Mirsorai | 9 | 15:00 | 180 | Sylhet-132 | 87 | 14:00
49 | Dhamrai | 104 | 18:00 | 115 | Mirzapur | 35 | 18:00 | 181 | TK | 18 | 18:00
50 | Dhanmondi | 101 | 13:00 | 116 | Mithapukur | 44 | 18:00 | 182 | Tangail | 118 | 18:00
51 | Dohazari | 76 | 13:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 15 | 18:00
52 | Faridpur | 110 | 18:30 | 118 | Mogbazar | 74.4 | 13:00 | 184 | Thakurgaon | 77 | 18:30
53 | Fatullah | 100 | 10:00 | 119 | Mongla | 30 | 09:00 | 185 | Tongi | 93 | 15:00
54 | Fenchuganj | 27 | 18:30 | 120 | Motijheel | 34 | 13:00 | 186 | Ullahpara | 27 | 18:00
55 | Feni | 87 | 18:00 | 121 | Muktagacha | 25 | 18:00 | 187 | Ullon | 44 | 19:00
56 | GPH | 85 | 23:00 | 122 | Munshiganj | 73 | 20:00 | 188 | Uttara | 68 | 15:00
57 | Ghatail | 62 | 07:00 | 123 | Muradnagar | 26 | 18:00 | 189 | UttaraNew | 20 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 133 | 18:30 | 190 | Zigatola | 57 | 14:00
59 | Ghorashal-230 | 79 | 00:00 | 125 | Naogaon | 85 | 18:00
60 | Goalpara | 24 | 13:00 | 126 | Narail | 38 | 18:00
61 | Gollamari | 72 | 13:00 | 127 | Narinda | 54 | 13:00
62 | Gopalganj | 76 | 18:00 | 128 | Narshingdi | 140 | 18:30
63 | Gulshan | 88 | 11:00 | 129 | Natore | 100 | 18:00
64 | Halishahar | 63.5 | 15:00 | 130 | Nawabganj | 29.2 | 21:00
65 | HaripurSBU | 142 | 13:00 | 131 | Netrakona | 97 | 17:00
66 | Hasnabad | 80 | 17:00 | 132 | New | 60 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9314 | 0 |  | 9314
1:00 | 8888 | 0 |  | 8888
2:00 | 8662 | 0 |  | 8662
3:00 | 8307 | 0 |  | 8307
4:00 | 8062 | 0 |  | 8062
5:00 | 7862 | 0 |  | 7862
6:00 | 8208 | 0 |  | 8208
7:00 | 9059.88 | 0 |  | 9059.88
8:00 | 9475.3 | 0 |  | 9475.3
9:00 | 9350.04 | 0 |  | 9350.04
10:00 | 9382.86 | 0 |  | 9382.86
11:00 | 9761.59 | 0 |  | 9761.59
12:00 | 10285.61 | 0 |  | 10285.61
13:00 | 10675.42 | 0 |  | 10675.42
14:00 | 10314.4 | 0 |  | 10314.4
15:00 | 10134.4 | 0 |  | 10134.4
16:00 | 9960.56 | 0 |  | 9960.56
17:00 | 10237.28 | 0 |  | 10237.28
18:00 | 11530 | 0 |  | 11530
19:00 | 11329.5 | 0 |  | 11329.5
19:30 | 11166.5 | 0 |  | 11166.5
20:00 | 10960.5 | 0 |  | 10960.5
21:00 | 10788.89 | 0 |  | 10788.89
22:00 | 10475.87 | 0 |  | 10475.87
23:00 | 9991.01 | 0 |  | 9991.01
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4746 | 4568 | 9314 | DAILY GENERATION CURVE
00:30 | 4734 | 4367 | 9101
01:00 | 4722 | 4166 | 8888 | 16-11-2025
01:30 | 4683.5 | 4091.5 | 8775
02:00 | 4645 | 4017 | 8662
02:30 | 4511 | 3973.5 | 8484.5
03:00 | 4377 | 3930 | 8307
03:30 | 4295.5 | 3889 | 8184.5
04:00 | 4214 | 3848 | 8062
04:30 | 4127 | 3835 | 7962
05:00 | 4040 | 3822 | 7862
05:30 | 4106 | 3929 | 8035
06:00 | 4172 | 4036 | 8208
06:30 | 4441.085 | 4192.855 | 8633.94
07:00 | 4710.17 | 4349.71 | 9059.88
07:30 | 4828.1 | 4439.49 | 9267.59
08:00 | 4946.03 | 4529.27 | 9475.3
08:30 | 4895.965 | 4516.705 | 9412.67
09:00 | 4845.9 | 4504.14 | 9350.04
09:30 | 4842.365 | 4524.085 | 9366.45
10:00 | 4838.83 | 4544.03 | 9382.86
10:30 | 4965.185 | 4607.04 | 9572.225
11:00 | 5091.54 | 4670.05 | 9761.59
11:30 | 5141.85 | 4881.75 | 10023.6
12:00 | 5192.16 | 5093.45 | 10285.61
12:30 | 5204.74 | 5275.775 | 10480.515
13:00 | 5217.32 | 5458.1 | 10675.42
13:30 | 5153.35 | 5341.56 | 10494.91
14:00 | 5089.38 | 5225.02 | 10314.4
14:30 | 5037.125 | 5187.275 | 10224.4
15:00 | 4984.87 | 5149.53 | 10134.4
15:30 | 4944.785 | 5102.695 | 10047.48
16:00 | 4904.7 | 5055.86 | 9960.56
16:30 | 5024.71 | 5074.21 | 10098.92
17:00 | 5144.72 | 5092.56 | 10237.28
17:30 | 5598.36 | 5285.28 | 10883.64
18:00 | 6052 | 5478 | 11530
18:30 | 5990.25 | 5439.5 | 11429.75
19:00 | 5928.5 | 5401 | 11329.5
19:30 | 5787.5 | 5379 | 11166.5
20:00 | 5584.5 | 5376 | 10960.5
20:30 | 5530 | 5344.695 | 10874.695 |  | Executive Engineer
21:00 | 5475.5 | 5313.39 | 10788.89 |  | Network Operation Division
21:30 | 5377.5 | 5254.88 | 10632.38
22:00 | 5279.5 | 5196.37 | 10475.87
22:30 | 5070.75 | 5162.69 | 10233.44
23:00 | 4862 | 5129.01 | 9991.01

## En-Curve
QF-LDC-12
Date | 16-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3092 | 1218 | 843 | 38 | 80 | 628 | 86 | 3299 | 0 | 0 | 27 | 0 | 0 | 3 | 0 | DAILY ENERGY CURVE
00:30 | 3166.5 | 1222 | 840.5 | 19 | 77 | 579 | 86 | 3093 | 0 | 0 | 13.5 | 0 | 0 | 4.5 | 0 | 16-11-2025
01:00 | 3241 | 1226 | 838 | 0 | 74 | 530 | 86 | 2887 | 0 | 0 | 0 | 0 | 0 | 6 | 0
01:30 | 3250.5 | 1224.5 | 837.5 | 0 | 73 | 480.5 | 86 | 2817 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | Energy Generated | 236.6912 |  | MKWHr
02:00 | 3260 | 1223 | 837 | 0 | 72 | 431 | 86 | 2747 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3221.5 | 1221 | 840 | 0 | 71 | 433.5 | 86 | 2604 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | Total Energy Requirement | 236.6912 |  | MKWHr
03:00 | 3183 | 1219 | 843 | 0 | 70 | 436 | 86 | 2461 | 0 | 0 | 0 | 0 | 0 | 9 | 0
03:30 | 3124 | 1169 | 845.5 | 0 | 70 | 431 | 86 | 2449 | 0 | 0 | 0 | 0 | 0 | 10 | 0
04:00 | 3065 | 1119 | 848 | 0 | 70 | 426 | 86 | 2437 | 0 | 0 | 0 | 0 | 0 | 11 | 0
04:30 | 3016.5 | 1066 | 848 | 0 | 70 | 423.5 | 86 | 2439.5 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0
05:00 | 2968 | 1013 | 848 | 0 | 70 | 421 | 86 | 2442 | 0 | 0 | 0 | 0 | 0 | 14 | 0
05:30 | 3040 | 1092 | 848 | 0 | 65 | 420.5 | 86 | 2464.5 | 0 | 0 | 6 | 0 | 0 | 13 | 0
06:00 | 3112 | 1171 | 848 | 0 | 60 | 420 | 86 | 2487 | 0 | 0 | 12 | 0 | 0 | 12 | 0
06:30 | 3194 | 1222.5 | 848 | 0 | 64 | 470.5 | 86 | 2668.5 | 29.44 | 2 | 38.5 | 0 | 0 | 10.5 | 0
07:00 | 3276 | 1274 | 848 | 0 | 68 | 521 | 86 | 2850 | 58.88 | 4 | 65 | 0 | 0 | 9 | 0
07:30 | 3212 | 1204 | 853.5 | 0 | 71 | 519.575 | 86 | 3000 | 159.515 | 31.5 | 123.5 | 0 | 0 | 7 | 0
08:00 | 3148 | 1134 | 859 | 0 | 74 | 518.15 | 86 | 3150 | 260.15 | 59 | 182 | 0 | 0 | 5 | 0
08:30 | 3138.5 | 1101 | 859 | 0 | 76 | 469.205 | 86 | 3097 | 361.465 | 45.5 | 176 | 0 | 0 | 3 | 0
09:00 | 3129 | 1068 | 859 | 0 | 78 | 420.26 | 86 | 3044 | 462.78 | 32 | 170 | 0 | 0 | 1 | 0
09:30 | 3147.5 | 1077.5 | 859 | 0 | 81 | 424.545 | 86 | 2979 | 524.905 | 24 | 160.5 | 0 | 0 | 2.5 | 0
10:00 | 3166 | 1087 | 859 | 0 | 84 | 428.83 | 86 | 2914 | 587.03 | 16 | 151 | 0 | 0 | 4 | 0
10:30 | 3217.5 | 1148.5 | 859 | 0 | 90 | 431.025 | 86 | 2933 | 633.7 | 16 | 151 | 0 | 0 | 6.5 | 0
11:00 | 3269 | 1210 | 859 | 0 | 96 | 433.22 | 86 | 2952 | 680.37 | 16 | 151 | 0 | 0 | 9 | 0
11:30 | 3302.5 | 1245.5 | 859.5 | 0 | 95 | 484.57 | 86 | 3090 | 680.03 | 20.5 | 152.5 | 0 | 0 | 7.5 | 0
12:00 | 3336 | 1281 | 860 | 0 | 94 | 535.92 | 86 | 3228 | 679.69 | 25 | 154 | 0 | 0 | 6 | 0
12:30 | 3280 | 1278 | 860 | 0 | 93 | 624.365 | 86 | 3358 | 651.65 | 33.5 | 213 | 0 | 0 | 3 | 0
13:00 | 3224 | 1275 | 860 | 0 | 92 | 712.81 | 86 | 3488 | 623.61 | 42 | 272 | 0 | 0 | 0 | 0
13:30 | 3212 | 1245.25 | 859.5 | 0 | 98 | 714.905 | 86 | 3447.5 | 577.255 | 25 | 229.5 | 0 | 0 | 0 | 0
14:00 | 3200 | 1215.5 | 859 | 0 | 104 | 717 | 86 | 3407 | 530.9 | 8 | 187 | 0 | 0 | 0 | 0
14:30 | 3209.5 | 1219.25 | 859 | 0 | 105 | 723 | 86 | 3422.5 | 456.15 | 13 | 131 | 0 | 0 | 0 | 0
15:00 | 3219 | 1223 | 859 | 0 | 106 | 729 | 86 | 3438 | 381.4 | 18 | 75 | 0 | 0 | 0 | 0
15:30 | 3231.5 | 1210.25 | 859.5 | 0 | 105 | 730.5 | 86 | 3463 | 265.23 | 21.5 | 75 | 0 | 0 | 0 | 0
16:00 | 3244 | 1197.5 | 860 | 0 | 104 | 732 | 86 | 3488 | 149.06 | 25 | 75 | 0 | 0 | 0 | 0
16:30 | 3199.5 | 1184.5 | 859.5 | 0 | 99 | 730 | 86 | 3515 | 78.42 | 104.5 | 241.5 | 0 | 0 | 1 | 0
17:00 | 3155 | 1171.5 | 859 | 0 | 94 | 728 | 86 | 3542 | 7.78 | 184 | 408 | 0 | 0 | 2 | 0
17:30 | 3238 | 1217.75 | 859 | 0 | 95 | 746.5 | 86 | 3609 | 3.89 | 288 | 737.5 | 0 | 0 | 3 | 0
18:00 | 3321 | 1264 | 859 | 0 | 96 | 765 | 86 | 3676 | 0 | 392 | 1067 | 0 | 0 | 4 | 0
18:30 | 3250 | 1260.25 | 859.5 | 0 | 94 | 765 | 86 | 3666 | 0 | 344.5 | 1099 | 0 | 0 | 5.5 | 0
19:00 | 3179 | 1256.5 | 860 | 0 | 92 | 765 | 86 | 3656 | 0 | 297 | 1131 | 0 | 0 | 7 | 0
19:30 | 3207 | 1253.5 | 859 | 0 | 98 | 762 | 86 | 3680 | 0 | 221 | 998 | 0 | 0 | 2 | 0
20:00 | 3243 | 1266.5 | 860 | 0 | 90 | 774 | 86 | 3680 | 0 | 158 | 802 | 0 | 0 | 1 | 0
20:30 | 3240 | 1278 | 859.5 | 0 | 89 | 772.195 | 86 | 3678 | 0 | 112.5 | 758.5 | 0 | 0 | 1 | 0
21:00 | 3237 | 1289.5 | 859 | 0 | 88 | 770.39 | 86 | 3676 | 0 | 67 | 715 | 0 | 0 | 1 | 0
21:30 | 3217.5 | 1280 | 859.5 | 0 | 87 | 769.38 | 86 | 3659.5 | 0 | 51 | 622 | 0 | 0 | 0.5 | 0
22:00 | 3198 | 1270.5 | 860 | 0 | 86 | 768.37 | 86 | 3643 | 0 | 35 | 529 | 0 | 0 | 0 | 0
22:30 | 3220.5 | 1265.75 | 860 | 0 | 85 | 759.19 | 86 | 3635.5 | 0 | 26 | 295.5 | 0 | 0 | 0 | 0
23:00 | 3243 | 1261 | 860 | 0 | 84 | 750.01 | 86 | 3628 | 0 | 17 | 62 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 05:00 | 377 | 12:00 | Meghnaghat | 397 | 05:00 | 377 | 16:00
Ashuganj | 403 | 5:00 | 381 | 16:00 | Payra | 415 | 02:00 | 409 | 13:00
Bhulta | 399 | 04:00 | 377 | 12:00 | Rahanpur | 410 | 04:00 | 395 | 13:00
Bibiana | 400 | 06:00 | 388 | 14:00 | Rampal | 413 | 03:00 | 397 | 13:00
BIPTC | 406 | 03:00 | 397 | 11:00
Bogura | 406 | 04:00 | 389 | 16:00
Gopalganj | 407 | 04:00 | 391 | 12:00
Kaliakoir | 392 | 05:00 | 373 | 12:00
Korerhat | 402 | 04:00 | 389 | 12:00
Madunaghat | 402 | 04:00 | 391 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 04:00 | 224 | 12:00 | Kaliakoir | 238 | 05:00 | 223 | 12:00
AKSML | 236 | 02:00 | 229 | 12:00 | Keranigonj | 236 | 04:00 | 222 | 12:00
Aminbazar | 238 | 04:00 | 225 | 12:00 | Khulna(S) | 240 | 02:00 | 230 | 13:00
Ashuganj | 236 | 05:00 | 224 | 13:00 | Korerhat | 240 | 04:00 | 230 | 03:00
Ashuganj-400 | 236 | 05:00 | 224 | 13:00 | Madunaghat | 238 | 03:00 | 230 | 15:00
Baghabari | 237 | 02:00 | 228 | 12:00 | Madunaghat-400 | 239 | 05:00 | 231 | 16:00
Barapukuria | 224 | 04:00 | 213 | 23:00 | Maniknagar | 230 | 03:00 | 219 | 15:00
Barapukuria-230 | 224 | 04:00 | 213 | 23:00 | Meghnaghat | 236 | 04:00 | 225 | 12:00
Barishal | 241 | 02:00 | 234 | 12:00 | Meghnaghat-400 | 234 | 04:00 | 222 | 12:00
Bheramara | 236 | 04:00 | 225 | 13:00 | Mirsorai | 236 | 04:00 | 225 | 13:00
Bhulta | 232 | 03:00 | 219 | 12:00 | Rajshahi | 235 | 02:00 | 224 | 13:00
Bibiana | 235 | 03:00 | 228 | 14:00 | Rampal | 239 | 03:00 | 227 | 13:00
BIPTC | 240 | 05:00 | 226 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bogura | 236 | 04:00 | 227 | 13:00 | Rampura | 232 | 04:00 | 216 | 16:00
Bogura-400 | 235 | 04:00 | 226 | 13:00 | Shikalbaha | 237 | 18:00 | 230 | 12:00
Borhanuddin | 242 | 03:00 | 238 | 18:00 | Shyampur | 235 | 05:00 | 221 | 12:00
BSRM | 236 | 05:00 | 225 | 13:00 | Siddhirganj | 230 | 05:00 | 220 | 11:00
Cumilla(N) | 234 | 05:00 | 223 | 12:00 | Sirajgonj | 242 | 04:00 | 235 | 12:00
Faridpur | 240 | 03:00 | 232 | 12:00 | Sreepur | 234 | 03:00 | 222 | 13:00
Fenchuganj | 238 | 06:00 | 231 | 16:00 | Tongi | 230 | 21:00 | 216 | 15:00
Ghorashal | 240 | 04:00 | 225 | 01:00
Ghorashal-230 | 233 | 04:00 | 218 | 16:00
Gopalganj | 241 | 04:00 | 232 | 12:00
GPH | 236 | 06:00 | 223 | 16:00
Haripur | 233 | 05:00 | 220 | 12:00
Hasnabad | 234 | 01:00 | 222 | 15:00
Hathazari | 235 | 18:00 | 229 | 11:00
Ishurdi | 240 | 04:00 | 229 | 13:00
Jhenaidah | 238 | 04:00 | 225 | 13:00
Kachua | 237 | 19:30 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 125 | 13:00 | Lalmonirhat | 130 | 02:00 | 122 | 07:00
Agargaon | 138 | 04:00 | 129 | 12:00 | Madanganj | 133 | 03:00 | 129 | 13:00
Agrabad | 137 | 07:00 | 130 | 14:00 | Madaripur | 137 | 02:00 | 134 | 13:00
AKS | 134 | 09:00 | 129 | 15:00 | Madartek | 135 | 03:00 | 124 | 13:00
Aminbazar | 138 | 04:00 | 129 | 12:00 | Madunaghat | 138 | 05:00 | 133 | 16:00
Amnura | 136 | 02:00 | 130 | 13:00 | Magura | 140 | 06:00 | 130 | 13:00
Ashuganj | 142 | 03:00 | 138 | 13:00 | Mahasthangarh | 134 | 04:00 | 128 | 13:00
Bagerhat | 138 | 04:00 | 129 | 13:00 | Maijdee | 137 | 03:00 | 128 | 16:00
Bajitpur | 137 | 03:00 | 131 | 12:00 | Manikganj | 136 | 05:00 | 113 | 01:00
Bakulia | 138 | 08:00 | 130 | 15:00 | Maniknagar | 141 | 05:00 | 131 | 13:00
Banani | 136 | 05:00 | 125 | 13:00 | Matarbari | 128 | 09:00 | 120 | 16:00
Bangabhaban | 141 | 04:00 | 132 | 16:00 | Matuail | 135 | 05:00 | 128 | 12:00
Barapukuria | 137 | 04:00 | 129 | 08:00 | Metrorail_Motijheel | 141 | 05:00 | 131 | 13:00
Barguna | N/A | N/A | N/A | N/A | Metrorail_Uttara | 139 | 03:00 | 127 | 12:00
Barishal | 139 | 05:00 | 133 | 13:00 | Millgate | 139 | 03:00 | 127 | 16:00
Barishal-230 | 139 | 02:00 | 133 | 13:00 | Mirpur | 137 | 02:00 | 128 | 12:00
Baroaulia | 138 | 18:00 | 132 | 15:00 | Mirzapur | 137 | 03:00 | 129 | 16:00
Baroirhat | 136 | 08:00 | 130 | 16:00 | Mithapukur | 134 | 03:00 | 128 | 07:00
Bashundhara | 137 | 04:00 | 125 | 13:00 | MI_Cement | 135.4 | 03:00 | 125 | 12:00
BashundharaCement | 133 | 03:00 | 129 | 13:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 134 | 02:00 | 130 | 14:00 | Mogbazar | 138 | 05:00 | 126 | 13:00
Benapole | 138 | 03:00 | 126 | 13:00 | Mongla | 136 | 06:00 | 128 | 13:00
Bhaluka | 134 | 05:00 | 126 | 13:00 | Motijheel | 141 | 04:00 | 132 | 16:00
Bhandaria | 137 | 06:00 | 131 | 13:00 | Muktagacha | 135 | 09:00 | 124 | 18:00
Bhangura | 137 | 03:00 | 130 | 15:00 | Munshiganj | 133 | 01:00 | 126 | 16:00
Bheramara | 140 | 04:00 | 135 | 12:00 | Muradnagar | 136 | 04:00 | 126 | 12:00
Bheramara(GK) | 140 | 03:00 | 135 | 12:00 | Mymensingh | 135 | 09:00 | 123 | 18:00
Bhulta | 130 | 06:00 | 125 | 12:00 | Naogaon | 133 | 03:00 | 120 | 12:00
Bog-Sherpur | 136 | 04:00 | 129 | 13:00 | Narail | 140 | 02:00 | 129 | 13:00
Bogura | 135 | 04:00 | 129 | 13:00 | Narinda | 141 | 05:00 | 131 | 13:00
Bogura-230 | 135 | 03:00 | 129 | 13:00 | Narshingdi | 136 | 08:00 | 122 | 12:00
Brahmanbaria | 135 | 04:00 | 130 | 12:00 | Natore | 135 | 01:00 | 130 | 13:00
Cantonment | 138 | 03:00 | 128 | 15:00 | Nawabganj | 138 | 04:00 | 128 | 12:00
Chandina | 139 | 04:00 | 131 | 13:00 | Netrakona | 132 | 06:00 | 124 | 17:00
Chandpur | 140 | 19:30 | 131 | 15:00 | New | 138 | 05:00 | 128 | 12:00
Chandraghona | 139 | 06:00 | 134 | 15:00 | Niamatpur | 137 | 04:00 | 132 | 13:00
Chapai | 137 | 03:00 | 131 | 13:00 | Noapara | 138 | 05:00 | 130 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 03:00 | 127 | 15:00 | Pabna | 138 | 01:00 | 133 | 12:00
Chauddagram | 137 | 02:00 | 130 | 12:00 | Palashbari | 131 | 01:00 | 126 | 07:00
Chhatak | 133 | 05:00 | 128 | 14:00 | Panchagarh | 140 | 17:00 | 125 | 07:00
Chowmuhani | 135 | 02:00 | 128 | 15:00 | Patiya | 137 | 07:00 | 131 | 15:00
Chuadanga | 138 | 06:00 | 130 | 13:00 | Patuakhali | 136 | 06:00 | 133 | 13:00
Coxsbazar | 128 | 09:00 | 120 | 18:00 | Payra | 136 | 01:00 | 134 | 12:00
Cumilla(N) | 138 | 02:00 | 132 | 12:00 | PHP | 137 | 04:00 | 130 | 13:00
Cumilla(S) | 138 | 03:00 | 126 | 08:00 | Postogola | 137 | 05:00 | 127 | 12:00
Daganbhuiyan | 138 | 04:00 | 130 | 12:00 | Purbachal | 136 | 03:00 | 125 | 13:00
Daudkandi | 134 | 02:00 | 124 | 13:00 | Purbasadipur | 133 | 17:00 | 124 | 07:00
DhakaUniversity | 137 | 04:00 | 125 | 13:00 | Rahanpur | 137 | 04:00 | 133 | 13:00
Dhamrai | 134 | 03:00 | 122 | 12:00 | Rahanpur-400 | 138 | 04:00 | 133 | 13:00
Dhanmondi | 137 | 05:00 | 126 | 13:00 | Rahim | 135 | 02:00 | 128 | 12:00
Dohazari | 135 | 18:00 | 128 | 15:00 | Rajbari | 139 | 03:00 | 133 | 13:00
Faridpur | 139 | 03:00 | 135 | 11:00 | Rajendrapur | 136 | 03:00 | 126 | 12:00
Fatullah | 138 | 02:00 | 126 | 12:00 | Rajshahi | 136 | 04:00 | 130 | 13:00
Fenchuganj | 140 | 03:00 | 137 | 15:00 | Rajshahi-230 | 136 | 04:00 | 129 | 13:00
Feni | 137 | 05:00 | 129 | 15:00 | Ramganj | 136 | 02:00 | 128 | 14:00
Ghatail | 134 | 09:00 | 124 | 18:00 | Rampur | 138 | 08:00 | 130 | 15:00
Ghorashal | 140 | 00:00 | 133 | 14:00 | Rampura | 136 | 04:00 | 125 | 13:00
Goalpara | 140 | 04:00 | 132 | 13:00 | Rangamati | 138 | 04:00 | 133 | 15:00
Gollamari | 139 | 04:00 | 132 | 13:00 | Rangpur | 133 | 17:00 | 122 | 12:00
Gopalganj | 139 | 03:00 | 133 | 12:00 | Ruppur | 140 | 04:00 | 135 | 13:00
Gopalganj-400 | 140 | 02:00 | 135 | 12:00 | Saidpur | 134 | 18:30 | 125 | 07:00
Gulshan | 136 | 05:00 | 125 | 13:00 | Satkhira | 138 | 04:00 | 130 | 13:00
Halishahar | 138 | 07:00 | 130 | 16:00 | Satmasjid | 138 | 03:00 | 128 | 13:00
Haripur | 136 | 04:00 | 128 | 12:00 | Savar | 136 | 03:00 | 127 | 15:00
HaripurSBU | 136 | 05:00 | 128 | 12:00 | SevenRings | 142 | 04:00 | 133 | 15:00
Hasnabad | 137 | 04:00 | 128 | 12:00 | ShahCement | 135 | 03:00 | 127 | 15:00
Hathazari | 138 | 06:00 | 134 | 15:00 | Shahjadpur | 140 | 03:00 | 136 | 18:00
Ishurdi | 141 | 03:00 | 135 | 12:00 | Shahjibazar | 138 | 02:00 | 134 | 14:00
Jaldhaka | 132 | 17:00 | 120 | 18:00 | Shahmirpur | 139 | 08:00 | 131 | 16:00
Jamalpur | 130 | 09:00 | 120 | 18:00 | Shariatpur | 139 | 04:00 | 132 | 12:00
Jashore | 138 | 04:00 | 127 | 13:00 | Sherpur | 128 | 15:00 | 115 | 01:00
Jhenaidah | 140 | 04:00 | 124 | 18:00 | Shikalbaha | 127 | 18:30 | 120 | 16:00
Jhenaidah-230 | 142 | 03:00 | 133 | 13:00 | Shikalbaha-230 | 139 | 09:00 | 133 | 00:00
Joydebpur | 139 | 19:30 | 128 | 12:00 | Shitalakhya | 135.4 | 03:00 | 125 | 12:00
Joypurhat | 132 | 04:00 | 127 | 12:00 | Sholosohor | 138 | 04:00 | 133 | 15:00
Juldah | 138 | 07:00 | 132 | 15:00 | Shyampur | 135 | 00:00 | 129 | 12:00
Kabirpur | 138 | 08:00 | 125 | 16:00 | Shyampur-230 | 139 | 05:00 | 130 | 12:00
Kachua | 140 | 03:00 | 131 | 12:00 | Siddhirganj | 136 | 03:00 | 128 | 12:00
Kaliakoir | 142 | 04:00 | 127 | 12:00 | Sirajganj | 134 | 01:00 | 129 | 16:00
Kallyanpur | 137 | 03:00 | 129 | 12:00 | Sonargaon | 135 | 03:00 | 127 | 12:00
Kalurghat | 139 | 08:00 | 133 | 15:00 | Sreemongol | 138 | 03:00 | 132 | 15:00
Kamrangirchar | 137 | 05:00 | 128 | 12:00 | Sreepur | 138 | 03:00 | 129 | 13:00
Kaptai | 136 | 6:00 | 129 | 12:00 | Srinagar | 137 | 02:00 | 128 | 12:00
Kasba | 137 | 05:00 | 126 | 13:00 | SSM | 140 | 00:00 | 138 | 06:00
Kazla | 140 | 04:00 | 132 | 13:00 | Sunamganj | 130 | 04:00 | 128 | 00:00
Keranigonj | 138 | 04:00 | 129 | 12:00 | Sylhet | 135 | 03:00 | 131 | 13:00
Khagrachori | 137 | 08:00 | 132 | 15:00 | Sylhet-132 | 133 | 04:00 | 131 | 10:00
Khulna | 138 | 03:00 | 131 | 13:00 | Tangail | 134 | 04:00 | 126 | 18:00
Khulna(S) | 140 | 04:00 | 132 | 13:00 | Taraganj | 133 | 02:00 | 126 | 12:00
Khulshi | 136 | 07:00 | 129 | 16:00 | Thakurgaon | 138 | 17:00 | 121 | 07:00
Kishoreganj | 135 | 06:00 | 130 | 12:00 | TK | 139 | 07:00 | 134 | 14:00
Kodda | 136 | 05:00 | 124 | 15:00 | Tongi | 139 | 04:00 | 130 | 15:00
KSRM | 139 | 19:30 | 132 | 15:00 | Ullahpara | 137 | 04:00 | 131 | 12:00
Kulaura | 140 | 03:00 | 136 | 12:00 | Ullon | 136 | 03:00 | 125 | 13:00
Kurigram | 130 | 02:00 | 122 | 07:00 | Uttara | 138 | 05:00 | 126 | 15:00
Kushtia | 138 | 05:00 | 129 | 13:00 | UttaraNew | 139 | 03:00 | 127 | 12:00
Laksam | 137 | 18:00 | 130 | 14:00 | Zigatola | 138 | 04:00 | 124 | 12:00
Lakshmipur | 137 | 03:00 | 129 | 12:00
Lalbag | 138 | 04:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division