## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-11-2025 | [28 empty] | Date: | 17-11-2025 | [28 empty] | Date: | 17-11-2025 | [28 empty] | Date: | 17-11-2025 | [28 empty] | Date: | 17-11-2025 | [14 empty] | Date: | 17-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 28 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 545 | 0 | 0 | 0 | 0 | 220 | 0 | 220 | 0 | 151 | 0 | 0 | 106 | 0 | 0 | 20 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 383 | 0 | 61 | 161 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 19 | 16 | 40 | 0 | 0 | 0 | 4762 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 717.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 409 | 748 | 0 | 4956.94 | 9718.94 | 100.93
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 650 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 483 | 0 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 151 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 364 | 0 | 30 | 158 | 16 | 0 | 81 | 30 | 0 | 0 | 158 | 0 | 19 | 16 | 51 | 0 | 0 | 0 | 4631.5 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 944 | 0 | 623.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 307 | 725 | 0 | 4572.33 | 9203.83 | 100.92
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 615 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 453 | 0 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 151 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 74 | 0 | 0 | 0 | 305 | 0 | 360 | 0 | 30 | 146 | 16 | 0 | 81 | 30 | 0 | 0 | 158 | 0 | 8 | 8 | 69 | 0 | 0 | 0 | 4534.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 0 | 521.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 307 | 680 | 0 | 4237.69 | 8772.19 | 100.92
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 590 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 458 | 0 | 0 | 0 | 0 | 250 | 0 | 220 | 0 | 151 | 0 | 0 | 20 | 0 | 0 | 13 | 0 | 74 | 0 | 0 | 0 | 305 | 0 | 377 | 0 | 30 | 146 | 16 | 0 | 41 | 20 | 0 | 0 | 158 | 0 | 8 | 0 | 70 | 0 | 0 | 0 | 4406.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 425.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 306 | 550 | 0 | 3989.46 | 8395.96 | 100.91
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 26 | 590 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 255 | 0 | 220 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 72 | 0 | 0 | 0 | 305 | 0 | 377 | 0 | 30 | 148 | 16 | 0 | 41 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 4352.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 422.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 275 | 500 | 0 | 3907.41 | 8259.91 | 100.91
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 500 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 255 | 0 | 220 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 398 | 0 | 30 | 150 | 16 | 0 | 11 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 4138.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 0 | 421.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 273 | 500 | 0 | 3922.65 | 8061.15 | 100.9
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 39 | 505 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 255 | 0 | 220 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 383 | 0 | 30 | 152 | 16 | 0 | 11 | 20 | 0 | 0 | 158 | 0 | 8 | 7 | 69 | 0 | 0 | 0 | 4230.5 | 860 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832 | 0 | 518.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 274 | 530 | 0 | 4124.91 | 8355.41 | 100.9
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.35 | 86 | 0 | 20 | 650 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 545 | 4 | 0 | 0 | 0 | 260 | 0 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 78 | 0 | 10 | 0 | 310 | 0 | 368 | 0 | 30 | 152 | 16 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 28 | 16 | 69 | 0 | 4.38 | 0 | 4653.73 | 859 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 896 | 0 | 612.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.05 | 8 | 0 | 0 | 4.17 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.18 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.3 | 17 | 0.04 | 0 | 0 | 120 | 220 | 0 | 453 | 580 | 0 | 4615.14 | 9268.87 | 100.89
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 152 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 14 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 86 | 0 | 12 | 650 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 545 | 10 | 0 | 0 | 0 | 260 | 0 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 88 | 0 | 37 | 0 | 305 | 0 | 381 | 0 | 30 | 147 | 16 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 66 | 16 | 32 | 1 | 21.09 | 0 | 4704.91 | 859 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 978 | 0 | 713.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.13 | 41 | 0 | 0 | 28.51 | 163 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 2.44 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 2.3 | 75 | 0.19 | 0 | 0 | 120 | 180 | 0 | 403 | 688 | 0 | 4938.18 | 9643.09 | 100.89
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 160 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 23 | 0 | 23.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.32 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 439 | 15 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 84 | 0 | 55 | 0 | 305 | 0 | 350 | 0 | 30 | 151 | 16 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 66 | 16 | 32 | 2 | 34.5 | 0 | 4549.02 | 862 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 960 | 0 | 719.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.73 | 70 | 0 | 0 | 46.5 | 167 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 4.08 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 3.8 | 125 | 0.38 | 0 | 0 | 100 | 180 | 0 | 402 | 710 | 0 | 5044.23 | 9593.25 | 100.88
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 162 | 0 | 0 | 16 | 0 | 0 | 0 | 3 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 29 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.99 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 467 | 18 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 84 | 0 | 66 | 0 | 320 | 0 | 381 | 0 | 30 | 153 | 16 | 0 | 40 | 20 | 0 | 0 | 158 | 0 | 45 | 8 | 32 | 2 | 43.04 | 0 | 4576.53 | 863 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 900 | 0 | 635.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.02 | 90 | 0 | 0 | 55.73 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.38 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 5.3 | 163 | 0.54 | 0 | 0 | 100 | 180 | 0 | 353 | 685 | 0 | 5013.21 | 9589.74 | 100.88
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 170 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 30 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 500 | 19 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 96 | 0 | 70 | 0 | 325 | 0 | 368 | 0 | 30 | 162 | 16 | 0 | 73 | 30 | 0 | 0 | 158 | 0 | 45 | 8 | 31 | 2 | 47.13 | 0 | 4761.41 | 862 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 901 | 0 | 614.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.02 | 100 | 0 | 0 | 66.31 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.68 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 5.8 | 184 | 0.58 | 0 | 0 | 115 | 220 | 0 | 373 | 695 | 0 | 5141.82 | 9903.23 | 100.88
12:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 175 | 0 | 0 | 19 | 0 | 45 | 0 | 17 | 25 | 0 | 200 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 31 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 3.3 | 86 | 0 | 8 | 650 | 0 | 0 | 1 | 0 | 7 | 220 | 0 | 0 | 0 | 580 | 19 | 0 | 4 | 0 | 230 | 0 | 220 | 0 | 150 | 0 | 0 | 0 | 10 | 1 | 11 | 0 | 96 | 0 | 70 | 0 | 325 | 0 | 382 | 0 | 30 | 161 | 16 | 0 | 76 | 30 | 0 | 0 | 159 | 0 | 49 | 8 | 31 | 2 | 47.65 | 0 | 4993.95 | 863 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.86 | 1018 | 0 | 701.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.41 | 108 | 0 | 0 | 65.47 | 196 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.51 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 6 | 188 | 0.61 | 0 | 0 | 115 | 220 | 0 | 452 | 705 | 0 | 5450.32 | 10444.27 | 100.87
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 195 | 0 | 0 | 50 | 0 | 145 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 27 | 0 | 23 | 21 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 3.02 | 86 | 20 | 15 | 650 | 0 | 0 | 39 | 0 | 67 | 218 | 0 | 0 | 0 | 558 | 16 | 0 | 76 | 0 | 230 | 0 | 220 | 0 | 150 | 0 | 10 | 0 | 98 | 9 | 11 | 0 | 106 | 0 | 66 | 0 | 315 | 0 | 354 | 0 | 30 | 155 | 16 | 0 | 76 | 30 | 0 | 0 | 159 | 0 | 97 | 19 | 30 | 2 | 45.85 | 0 | 5467.87 | 863 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 1086 | 0 | 753.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 103 | 0 | 0 | 57.45 | 203 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 5.08 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 5.7 | 175 | 0.55 | 0 | 0 | 115 | 180 | 0 | 450 | 755 | 0 | 5471.65 | 10939.52 | 100.86
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 275 | 17 | 0 | 68 | 0 | 145 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 23 | 0 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 2.44 | 86 | 30 | 9 | 650 | 0 | 0 | 50 | 0 | 82 | 189 | 0 | 0 | 0 | 535 | 15 | 0 | 110 | 0 | 230 | 0 | 220 | 0 | 152 | 0 | 28 | 0 | 123 | 8 | 11 | 0 | 96 | 0 | 55 | 0 | 305 | 0 | 372 | 0 | 30 | 147 | 16 | 0 | 78 | 20 | 0 | 0 | 159 | 0 | 99 | 19 | 30 | 2 | 39.52 | 0 | 5481.96 | 862 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.24 | 1055 | 0 | 756.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.35 | 88 | 0 | 0 | 53.31 | 164 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 4.59 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 4.7 | 148 | 0.46 | 0 | 0 | 100 | 180 | 0 | 307 | 778 | 0 | 5203.66 | 10685.62 | 100.86
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 319 | 0 | 0 | 68 | 0 | 145 | 0 | 0 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 16 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 1.65 | 86 | 0 | 6 | 650 | 0 | 0 | 50 | 0 | 83 | 217 | 0 | 0 | 0 | 528 | 11 | 0 | 110 | 0 | 235 | 0 | 220 | 0 | 152 | 0 | 33 | 0 | 135 | 8 | 14 | 0 | 98 | 0 | 39 | 0 | 315 | 0 | 355 | 0 | 30 | 155 | 12 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 99 | 19 | 30 | 1 | 28.18 | 0 | 5498.83 | 863 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.87 | 979 | 0 | 767.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.55 | 64 | 0 | 0 | 38.35 | 178 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 3.33 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3.3 | 105 | 0.31 | 0 | 0 | 115 | 220 | 0 | 306 | 780 | 0 | 5085.04 | 10583.87 | 100.85
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 332 | 17 | 0 | 33 | 0 | 95 | 0 | 0 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 7 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 25 | 0.75 | 86 | 0 | 6 | 650 | 0 | 0 | 50 | 0 | 80 | 217 | 0 | 0 | 0 | 550 | 5 | 0 | 60 | 0 | 270 | 0 | 220 | 0 | 151 | 0 | 31 | 0 | 100 | 8 | 14 | 0 | 104 | 0 | 18 | 0 | 310 | 0 | 389 | 0 | 30 | 150 | 12 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 59 | 19 | 30 | 0 | 10.73 | 0 | 5331.48 | 863 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1092 | 0 | 764.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.67 | 26 | 0 | 0 | 11.84 | 169 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 1.35 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1.4 | 42 | 0.13 | 0 | 0 | 115 | 220 | 0 | 307 | 750 | 0 | 4995.22 | 10326.7 | 100.85
17:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 303 | 17.5 | 0 | 35 | 45 | 125 | 16 | 0 | 35 | 0 | 180 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 1 | 17 | 22 | 21 | 0 | 0 | 10 | 15 | 0 | 0 | 2 | 16 | 0 | 0 | 38 | 25 | 0 | 86 | 7 | 11 | 650 | 15 | 0 | 50 | 1 | 97 | 221 | 0 | 0 | 0 | 575 | 0 | 0 | 71 | 0 | 250 | 0 | 220 | 0 | 155 | 0 | 17 | 0 | 118 | 0 | 14 | 0 | 104 | 1 | 1 | 0 | 310 | 0 | 341 | 0 | 30 | 154 | 20 | 0 | 78 | 30 | 0 | 0 | 160 | 3 | 59 | 19 | 30 | 0 | 0.3 | 0 | 5564.8 | 862 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.45 | 1119 | 0 | 769 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 0.84 | 1 | 0 | 0 | 0.61 | 179 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0.06 | 0 | 0 | 70 | 1 | 14 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 0 | 100 | 180 | 0 | 402 | 760 | 4 | 5034.97 | 10599.77 | 100.84
18:00 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 322 | 17.5 | 0 | 83 | 76 | 225 | 55 | 17 | 35 | 0 | 160 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 70 | 22 | 21 | 0 | 0 | 16 | 32 | 0 | 0 | 6 | 17 | 17 | 3 | 38 | 25 | 0 | 86 | 18 | 8 | 650 | 40 | 0 | 50 | 8 | 105 | 222 | 0 | 0 | 0 | 612 | 0 | 0 | 117 | 0 | 230 | 0 | 280 | 0 | 161 | 0 | 22 | 0 | 157 | 0 | 20 | 0 | 112 | 8 | 0 | 10 | 300 | 0 | 396 | 0 | 30 | 156 | 21 | 0 | 78 | 30 | 0 | 0 | 160 | 17 | 59 | 19 | 30 | 0 | 0 | 0 | 6241.5 | 863 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 774.52 | 0 | 0 | 0 | 60 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 92 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 504 | 760 | 17 | 5493.52 | 11735.02 | 100.84
19:00 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 296 | 17.5 | 0 | 103 | 45 | 278 | 15 | 17 | 35 | 0 | 160 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 35 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 38 | 0 | 38 | 25 | 0 | 86 | 59 | 20 | 650 | 0 | 0 | 50 | 8 | 96 | 221 | 0 | 0 | 0 | 580 | 0 | 0 | 122 | 0 | 230 | 0 | 240 | 0 | 162 | 0 | 16 | 0 | 155 | 0 | 20 | 0 | 98 | 0 | 0 | 23 | 300 | 0 | 389 | 0 | 30 | 150 | 21 | 0 | 78 | 30 | 0 | 0 | 159 | 17 | 59 | 19 | 31 | 0 | 0 | 0 | 6030.5 | 862 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 766 | 0 | 0 | 0 | 70 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 504 | 820 | 17 | 5538 | 11568.5 | 100.83
19:30 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 300 | 17.5 | 0 | 87 | 15 | 300 | 0 | 17 | 35 | 0 | 160 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 8 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 38 | 25 | 0 | 86 | 34 | 15 | 650 | 0 | 0 | 33 | 0 | 96 | 223 | 0 | 0 | 0 | 581 | 0 | 0 | 125 | 0 | 230 | 0 | 240 | 0 | 162 | 0 | 16 | 0 | 146 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 384 | 0 | 30 | 148 | 21 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 59 | 19 | 31 | 0 | 0 | 0 | 5852.5 | 862 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 767.16 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 503 | 820 | 17 | 5470.16 | 11322.66
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 306 | 17.5 | 0 | 90 | 15 | 195 | 0 | 17 | 35 | 0 | 160 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 0 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 0 | 86 | 0 | 11 | 650 | 0 | 0 | 33 | 0 | 93 | 222 | 0 | 0 | 0 | 581 | 0 | 0 | 120 | 0 | 230 | 0 | 240 | 0 | 162 | 0 | 0 | 0 | 143 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 393 | 0 | 30 | 147 | 21 | 0 | 79 | 30 | 0 | 0 | 159 | 0 | 62 | 19 | 31 | 0 | 0 | 0 | 5629.5 | 862 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 762.74 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 504 | 830 | 0 | 5415.74 | 11045.24 | 100.83
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 300 | 17.5 | 0 | 62 | 0 | 195 | 0 | 17 | 35 | 0 | 160 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 0 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 86 | 0 | 30 | 650 | 0 | 0 | 33 | 0 | 97 | 224 | 0 | 0 | 0 | 580 | 0 | 0 | 120 | 0 | 250 | 0 | 240 | 0 | 161 | 0 | 0 | 0 | 150 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 390 | 0 | 30 | 152 | 21 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 64 | 19 | 33 | 0 | 0 | 0 | 5601.5 | 863 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 765.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 860 | 0 | 5394.97 | 10996.47 | 100.82
22:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 295 | 17.5 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 0 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 86 | 0 | 33 | 650 | 0 | 0 | 0 | 0 | 95 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 30 | 0 | 240 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 100 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 374 | 0 | 30 | 145 | 21 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 59 | 19 | 33 | 0 | 0 | 0 | 5231.5 | 862 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 768.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 502 | 857 | 0 | 5290.01 | 10521.51 | 100.82
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 315 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 0 | 86 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 34 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 240 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 51 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 310 | 0 | 411 | 0 | 30 | 149 | 21 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 57 | 19 | 37 | 0 | 0 | 0 | 4933 | 862 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1117 | 0 | 765.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 502 | 820 | 0 | 5144.66 | 10077.66 | 100.81
Total KWH | 0 | 628800 | 269280 | 0 | 0 | 0 | 0 | 0 | 8784000 | 0 | 4672000 | 129960 | 0 | 720144 | 162240 | 1906658 | 119505 | 132776 | 367200 | 0 | 5962000 | 0 | 0 | 0 | 113559 | 6986148 | 0 | 0 | 204577 | 126000 | 451800 | 401760 | 0 | 0 | 117927 | 67745 | 0 | 0 | 36000 | 47346 | 62304 | 17241 | 179520 | 284160 | 21238 | 2065340 | 192363 | 442080 | 15178181.82 | 48509 | 0 | 445920 | 18961.2 | 1017018 | 5249851 | 0 | 0 | 0 | 12725453 | 130140 | 0 | 1018691 | 0 | 5900500 | 0 | 5524000 | 0 | 3799000 | 0 | 185280 | 306132 | 1441920 | 35280 | 373240 | 0 | 2159040 | 17443 | 491782 | 0 | 7532500 | 0 | 9389000 | 0 | 753720 | 3646963.64 | 48720 | 0 | 1581120 | 649152 | 0 | 0 | 3339000 | 48240 | 1177200 | 343200 | 941760 | 14650 | 323530 | 0 | 121526768.66 | 20860363 | 5471712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538560 | 23672730 | 0 | 16184861 | 0 | 0 | 0 | 153216 | 290496 | 0 | 0 | 0 | 0 | 395714 | 711980 | 108242 | 0 | 429008 | 4198545 | 0 | 0 | 0 | 0 | 0 | 8970836 | 0 | 36360 | 0 | 0 | 566842 | 230226 | 598377 | 0 | 0 | 0 | 38185.2 | 1231200 | 3816 | 0 | 0 | 2743000 | 5221490 | 0 | 9410909.09 | 17709090 | 49200 | 119824958.29 | 241351726.95

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-11-2025 | during | 18-11-2025 | during | 18-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 387 | 383 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 200 | 160 | 0 | 0 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.5 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 76 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 22 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 34 | 52.19 | 52.19 | 52 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 225 | 300 | 300 | 150 | 150 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 19 | 83 | 149 | 149 | 17 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 88 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 25 | 35 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 175 | 322 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1282 | 1875.5 | 5466.6 | 5434.6 | 2388.61 | 2373.61
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 222 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 7 | 105 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 17 | 56 | 64 | 56 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 8 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.3 | 0 | 3.33 | 0 | 3.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 3 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 18 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 17 | 25 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 16 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 40 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 6 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1603.3 | 1953 | 2943.05 | 2935.72 | 2378.83 | 2371.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 150 | 161 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 220 | 280 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 230 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 4 | 117 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 10 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 109 | 109 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 10 | 157 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 96 | 112 | 160 | 160 | 106 | 106 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 22 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 792 | 1117 | 2438.21 | 2368.21 | 1884.51 | 1814.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-11-2025 | during | 18-11-2025 | during | 18-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 31 | 30 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.65 | 0 | 35.83 | 0 | 35.83 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 137.65 | 125 | 351.83 | 314 | 292.33 | 254.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 161 | 156 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 382 | 396 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1179 | 1171 | 1207 | 1207 | 1175 | 1175
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 863 | 863 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 215 | 190 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82.86 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1018 | 1122 | 0 | 0 | 1140 | 1140 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2178.86 | 2175 | 2392 | 2310 | 2567.1 | 2485.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 452 | 504 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 705 | 760 | 857 | 857 | 827 | 827 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1492.61 | 1616 | 1458 | 1458 | 1295 | 1295
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 60.41 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 196 | 186 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 56 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 60 | 113 | 113 | 20 | 20 | Under Maintenance
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.51 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 701.46 | 774.52 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.47 | 0 | 58 | 1 | 58 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1550.85 | 1514.52 | 2396.61 | 2233.99 | 1690.83 | 1528.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 96 | 113 | 113 | 40 | 40 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 92 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 188 | 0 | 188.07 | 0 | 188.07 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 228 | 188 | 465.87 | 242 | 358.87 | 135
System Total |  |  |  |  | 28823.2 | 28205.415 | 10444.27 | 11735.02 | 19119.17 | 18503.52 | 14031.08 | 13432.43
Forecast Scenario (18-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9810 |  | 0 |  | 9810
|  |  |  | 1:00 | 9300 |  | 0 |  | 9300
|  |  |  | 2:00 | 8870 |  | 0 |  | 8870
|  |  |  | 3:00 | 8490 |  | 0 |  | 8490
|  |  |  | 4:00 | 8360 |  | 0 |  | 8360
|  |  |  | 5:00 | 8160 |  | 0 |  | 8160
|  |  |  | 6:00 | 8450 |  | 0 |  | 8450
|  |  |  | 7:00 | 9360 |  | 0 |  | 9360
|  |  |  | 8:00 | 9740 |  | 0 |  | 9740
|  |  |  | 9:00 | 9690 |  | 0 |  | 9690
|  |  |  | 10:00 | 9690 |  | 0 |  | 9690
|  |  |  | 11:00 | 10000 |  | 0 |  | 10000
|  |  |  | 12:00 | 10540 |  | 0 |  | 10540
|  |  |  | 13:00 | 11040 |  | 0 |  | 11040
|  |  |  | 14:00 | 10780 |  | 0 |  | 10780
|  |  |  | 15:00 | 10680 |  | 0 |  | 10680
|  |  |  | 16:00 | 10420 |  | 0 |  | 10420
|  |  |  | 17:00 | 10700 |  | 0 |  | 10700
|  |  |  | 18:00 | 11830 |  | 0 |  | 11830
|  |  |  | 18:30 | 11700 |  | 0 |  | 11700
|  |  |  | 19:00 | 11660 |  | 0 |  | 11660
|  |  |  | 19:30 | 11420 |  | 0 |  | 11420
|  |  |  | 20:00 | 11140 |  | 0 |  | 11140
|  |  |  | 21:00 | 11090 |  | 0 |  | 11090
|  |  |  | 22:00 | 10620 |  | 0 |  | 10620
|  |  |  | 23:00 | 10100 |  | 0 |  | 10100
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 10540.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11830.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11830.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 240.52 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:08 hrs on 18-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10444.27 | MW | 12:00 Hr. | Energy Generated |  |  | 241.3517 |  | MKWHr.
| Day Peak Demand |  |  | 10444.27 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11735.02 | MW | 18:00 Hr. | Energy Demand |  |  | 241.3517 |  | MKWHr.
| Evening Peak Demand |  |  | 11735.02 | MW | 18:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 8061.15 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 752.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 11735.02 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.765 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 27.2577 | 0 | 4.6761 | 0 | 0 | 0.20458 | 0 | 0 | 32.1384 | Gas | 103.34 | Gas | 363405911.7024
| Chattogram Zone |  |  | 5.6919 | 27.9036 | 2.499 | 0 | 2.0653 | 0.15138 | 0 | 0.036 | 38.3473 | Coal | 78.6964 | Coal | 502636022.1629
| Cumilla Zone |  |  | 15.9029 | 0 | 2.6986 | 0 | 0 | 0.49178 | 2.159 | 0 | 21.2523 | HFO | 13.2088 | HFO | 224465908.424
| Mymensingh Zone |  |  | 0.94176 | 0 | 1.5686 | 0 | 0 | 0.33818 | 0 | 0 | 2.8486 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9402 | Hydro | 2.0653 | Hydro | 206534
| Khulna Zone |  |  | 5.4717 | 23.6727 | 0 | 0 | 0 | 0.53856 | 20.8604 | 0 | 50.5434 | Solar | 4.801 | Solar | 76920129.332
| Barishal Zone |  |  | 7.9645 | 27.12 | 0.0492 | 0 | 0 | 0.003816 | 0 | 0 | 35.1375 | Import | 39.2043 | Import | 223220059.7
| Rajshahi Zone |  |  | 13.1694 | 0 | 0.55195 | 0 | 0 | 1.5731 | 16.1849 | 0 | 31.4793 | Wind | 0.036 | Wind | 529560
| Rangpur Zone |  |  | 0 | 0 | 1.1652 | 0 | 0 | 1.4996 | 0 | 0 | 2.6648
| Total |  |  | 103.34 | 78.6964 | 13.2088 | 0 | 2.0653 | 4.801 | 39.2043 | 0.036 | 241.3517
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 363405911.7024 |  | Hydro | 206534
|  |  |  | Coal | 502636022.1629 |  | Solar | 76920129.332
|  |  |  | HFO | 224465908.424 |  | Import | 223220059.7
|  |  |  | HSD | 0 |  | Wind | 529560
[5 empty] | Total: | 139,13,84,125 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8604 | Peak Hr Flow | 863.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48203662.61 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.1849 | Peak Hr Flow | 774.52 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2149 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.159 | Peak Hr Flow | 112.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2821 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.2043 | Peak Hr Flow | 1749.52 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4564
|  |  |  | Chattogram |  | 0 |  | 1429
|  |  |  | Cumilla |  | 0 |  | 1009
|  |  |  | Mymensingh |  | 0 |  | 861
|  |  |  | Sylhet |  | 0 |  | 445
|  |  |  | Khulna |  | 0 |  | 1201
|  |  |  | Barishal |  | 0 |  | 312
|  |  |  | Rajshahi |  | 0 |  | 989
|  |  |  | Rangpur |  | 0 |  | 695
|  |  |  | Total |  | 0 |  | 11505
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:12 | 16:13 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual Maintenance.
| 08:13 | 16:12 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual Maintenance.
| 08:17 | 16:22 | Barapukuria-Saidpur 132 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
annual maintenance
| 08:17 | 16:23 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to QF-
GMD-39 and as the instruction of ALDC Bogura (499264)
| 08:18 | 15:01 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Scheduled S/D from Bog-Sherpur 132/33kV end Due to
Annual Maintenance work.
| 08:20 | 16:24 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Annaul Maintenance.
| 08:20 | 15:20 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
Maintenance work dead line checking.
| 08:22 | 16:22 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Annaul Maintenance.
| 08:23 | 17:00 | Madaripur-Shariatpur 132kV Ckt-1 Scheduled S/D from Shariatpur 132/33kV end Due to
Annual Maintenance Work. and from Madaripur 132/33kV end Due to Annual Maintenance
| 08:26 | 18:07 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Gopalganj 400/132kV end Due to Annual Maintenance
| 08:30 | 15:53 | Palashbari 132/33kV S/S TR4-434T LT Scheduled S/D Due to Annual maintenance
| 08:31 | 16:58 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Scheduled S/D Due to Annual Maintenance
| 08:31 | 15:52 | Palashbari 132/33kV S/S TR4-434T HT Scheduled S/D Due to Annual maintenance
| 08:31 | 15:39 | Bogura 230/132kV S/S Bogura (W) CKT-2 Scheduled S/D Due to Annual Maintenance Work
| 08:32 | 16:56 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Scheduled S/D Due to Annual Maintenance
| 08:32 | 15:39 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Scheduled S/D Due to Annual maintenance
| 08:32 | 16:50 | Baroirhat 132/33kV S/S TR-1, 406T HT Scheduled S/D Due to Annual maintenance
| 08:32 | 16:50 | Baroirhat 132/33kV S/S TR-1, 406T LT Scheduled S/D Due to Annual maintenance
| 08:35 | 17:35 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Scheduled S/D Due to OFCN Work
| 08:37 | 17:24 | Bibiana 400/230kV S/S ICT-01 LT Scheduled S/D Due to AM
| 08:38 | 17:24 | Bibiana 400/230kV S/S ICT-01 HT Scheduled S/D Due to AM
| 08:46 | 15:55 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-2 Scheduled S/D Due to Annual
Maintenance.
| 08:46 | 15:10 | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to Annual maintenance
| 08:50 | 11:58 | Narshingdi 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maitenance
| 08:50 | 11:57 | Narshingdi 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
| 08:52 | 17:39 | Bheramara P/S-Faridpur 132 kV Ckt-2 Scheduled S/D from Bheramara 230/132kV end Due to
Annual Maintaince
| 08:55 |  | Kallyanpur 132/33kV S/S GT-2 (132kV) LT Scheduled S/D
|  | 08:56 | Chattak-Sylhet 132 kV Ckt-2 is restored.
| 08:56 | 18:12 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to Annaul Maintenance
| 09:00 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized
|  | 09:00 | Chattak-Sylhet 132 kV Ckt-1 is restored.
| 09:02 | 16:01 | Joydebpur 132/33kV S/S GT-4 HT Scheduled S/D Due to Annual Maintenance
| 09:05 | 17:06 | Tangail 132/33kV S/S Tr-3 LT Scheduled S/D Due to Annaual Maintenance
| 09:06 | 17:05 | Tangail 132/33kV S/S Tr-3 HT Scheduled S/D Due to Annaual Maintenance.
| 09:07 | 16:58 | Rajendrapur 132/33kV S/S MTR-3 LT Scheduled S/D Due to Annual Maintenance 2025
| 09:07 | 16:58 | Rajendrapur 132/33kV S/S MTR-3 HT Scheduled S/D Due to Annual Maintenance 2025
| 09:09 | 14:45 | BIPTC S/S 20DF23 Scheduled S/D Due to Annual Maintenance
| 09:10 | 17:40 | Bheramara P/S-Faridpur 132 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to
Annual Maintaince
| 09:10 | 17:38 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance
| 09:11 | 17:36 | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to Shutdown is provided to Rajbari
Grid for scheduled shutdown of Bheramara Grid.
| 09:12 | 17:36 | Rajbari 132/33kV S/S Bheramara-2 Scheduled S/D
| 09:17 | 16:02 | Jhenaidah 132/33kV S/S Jhenaidah-Magura, 132kV Circuit-1(L7) Scheduled S/D Due to Annual
maintenance
| 09:17 | 16:03 | Jhenaidah-Magura 132 kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to Annual
Maintenance.
| 09:20 | 16:15 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance work
| 09:21 | 16:41 | Faridpur 132/33kV S/S Bus-A Scheduled S/D Due to Annual Maintenance
|  | 09:30 | Sunamganj 132/33kV S/S Tr-1 HT is restored.
| 09:32 | 16:45 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance work
| 09:32 | 16:45 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance work
|  | 09:49 | Haripur-Meghnaghat 230kV Ckt-1 is restored.
| 09:57 | 18:33 | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end. and from Haripur
230/132kV end Due to other end
| 10:10 | 10:58 | Taraganj 132/33kV S/S TR-03 (404T) LT Scheduled S/D Due to 132 KV SF6 gas pressure meter
problem
| 10:11 | 10:57 | Taraganj 132/33kV S/S TR-03 (404T) HT Scheduled S/D Due to 132 KV SF6 gas pressure meter
problem
| 10:38 | 17:08 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to To check LT side
conductor
| 10:40 | 13:58 | Mirpur 132/33kV S/S T3 HT Tripped showing Siemens SIPROTEC relays Due to Main-1 Diff | [7 empty] | 56.0MW load
|  |  | Relay Operated | [7 empty] | interrup.
| 10:47 | 12:49 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-01 Project Work S/D Due to SCADA
Integration
| 10:49 | 16:57 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to
Maintenance work at Muradnagar Substation
| 11:53 | 16:07 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to Annual Maintenance.
| 11:53 | 16:07 | Narshingdi 132/33kV S/S T-4 LT Scheduled S/D Due to Annual Maintenance.
| 12:00 |  | Day Peak Generation: 10440 MW.
| 12:11 | 16:50 | Bhulta-Rampura 230 kV Ckt-1 Project Work S/D from Bhulta 400/230kV end Due to For
installing OPGW and from Rampura 230/132kV end Due to Command by NLDC.
|  | 12:50 | Nawabganj 132/33kV S/S TR-1 HT is restored.
|  | 12:51 | Nawabganj 132/33kV S/S TR-1 LT is restored.
| 14:09 | 15:45 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-01 Project Work S/D Due to SCADA
Integration
| 14:10 | 15:46 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-1 Scheduled S/D Due to Shutdown taken by
Muradnagar for Scada work
| 14:52 | 17:13 | Muradnagar 132/33kV S/S 132KV Busbar-1 Project Work S/D Due to SCADA Integration
|  | 15:05 | Savar 132/33kV S/S Bus-B is restored.
|  | 15:22 | Savar 132/33kV S/S T-3 HT is restored.
|  | 15:24 | Savar 132/33kV S/S T-3 LT is restored.
| 15:55 | 16:32 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-02 Project Work S/D Due to SCADA
Integration
| 15:55 | 16:33 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-2 Scheduled S/D Due to shutdown taken by
muradnagar for scada work
|  | 16:18 | Narail 132/33kV S/S TR2 (413-T) HT is restored.
|  | 16:19 | Narail 132/33kV S/S TR2 (413-T) LT is restored.
| 16:22 | 16:29 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Forced S/D from Cumilla(N) 230/132/33kV end Due to
Ashuganj end CB problem.
| 18:00 |  | Evening Peak Generation: 11734 MW.
|  | 20:17 | Monakasha-Rahanpur 400kV Ckt-1 is restored.
| 05:00 |  | Minimum Generation is 8163 MW.
| 05:50 | 06:30 | Khulna (C) S/S Tr-2 415 T HT Tripped showing No relay shown relays Due to Unidentify
| 06:22 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- ST
| 06:27 |  | Meghnaghat 450 MW CCPP was shut down for minor inspection.
| 06:27 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- GT2
| 07:05 |  | Khulna (C) S/S Tr-2 415 T HT Tripped showing No relay relays Due to Unidentify
| 07:05 |  | 132/33kV T-2 Transformer tripped at Khulna-Central Substation.
| 07:06 |  | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 Scheduled S/D Due to Annual maintenance
| 07:06 |  | Sunamganj 132/33kV S/S Tr-2 HT Scheduled S/D Due to Due to annual maintenance
| 07:41 |  | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to Annual Maintenance
| 07:41 |  | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 383 | 8784000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 160 | 5962000 | GT-1 shut down for schedule outage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 119505 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6986148 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 129960 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 76 | 162240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 132776 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 113559 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 451800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 401760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 269280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 225 | 1906658 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 83 | 720144 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 628800 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 367200 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204577 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 322 | 4672000 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 126000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1875.5 | 32138407
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 18961.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130140 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 445920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2065340 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5249851 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1017018 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 17 | 62304 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 47346 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 179520 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 442080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 67745 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 3 | 17241 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 18 | 192363 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 284160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 16 | 117927 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 40 | 48509 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12725453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 36000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15178181.82 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 1953 | 38347298.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 161 | 3799000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 280 | 5524000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 5900500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 0 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 117 | 1018691 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 10 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 306132 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 157 | 1441920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 112 | 2159040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 17443 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 373240 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 35280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 22 | 185280 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 491782 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1117 | 21252308
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 30 | 941760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 343200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1177200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 323530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 48240 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 125 | 2848580
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 753720 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3646963.64 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 649152 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1581120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3339000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 48720 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7532500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 396 | 9389000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1171 | 26940175.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 863 | 20860363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 190 | 5471712 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 538560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1122 | 23672730 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2175 | 50543365
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 504 | 9410909.09 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2743000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 760 | 17709090 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5221490 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 49200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3816 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1616 | 35137505.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 395714 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4198545 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8970836 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 108242 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 56 | 290496 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 60 | 153216 | Under Maintenance
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 774.52 | 16184861 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 429008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 711980 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1514.52 | 31479258
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 96 | 598377 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38185.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 92 | 566842 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230226 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1231200 | -
Rangpur Area Total |  |  |  |  | 950 | 188 | 2664830.2
Eastern Grid Total |  |  |  |  | 17383.855 | 6241.5 | 121526768.66
Western Grid Total |  |  |  |  | 10821.56 | 5493.52 | 119824958.29
National Grid Total |  |  |  |  | 28205.415 | 11735.02 | 241351726.95
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8307.89 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3196.6 | MW
i) Dhaka area |  |  | 4564.16 |  | MW | i) Khulna area |  |  |  | 1201 | MW
ii) Chattogram area |  |  | 1429.2 |  | MW | ii) Barishal area |  |  |  | 312 | MW
iii) Cumilla area |  |  | 1008.53 |  | MW | iii) Rajshahi area |  |  |  | 988.6 | MW
iv) Mymensingh area |  |  | 861 |  | MW | iv) Rangpur area |  |  |  | 695 | MW
v) Sylhet area |  |  | 445 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11504.49 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 71 | 18:00 | 133 | Niamatpur | 41 | 18:00
2 | AKSML | 147 | 16:00 | 68 | Ishurdi | 59 | 20:00 | 134 | Noapara | 36 | 18:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jaldhaka | 64 | 18:00 | 135 | PHP | 8 | 01:00
4 | Agargaon | 110 | 13:00 | 70 | Jamalpur | 91 | 19:00 | 136 | Pabna | 70 | 18:00
5 | Agrabad | 88 | 18:00 | 71 | Jashore | 100 | 13:00 | 137 | Palashbari | 78 | 18:30
6 | Amnura | 22 | 18:00 | 72 | Jhenaidah | 94 | 18:00 | 138 | Panchagarh | 45 | 18:00
7 | Ashuganj | 62 | 13:00 | 73 | Joydebpur | 120 | 12:00 | 139 | Patiya | 8.2 | 18:00
8 | BSRM | 205 | 05:00 | 74 | Joypurhat | 40 | 18:00 | 140 | Patuakhali | 53 | 21:00
9 | Bagerhat | 61 | 18:30 | 75 | Juldah | 14 | 12:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 57 | 19:00 | 76 | KSRM | 31 | 16:00 | 142 | Postogola | 54 | 13:00
11 | Bakulia | 72 | 18:30 | 77 | Kabirpur | 204 | 16:00 | 143 | Purbachal | 15 | 13:00
12 | Banani | 39.2 | 13:00 | 78 | Kachua | 58 | 18:30 | 144 | Purbasadipur | 90 | 18:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 90 | 13:00 | 145 | Rahanpur | 22 | 20:00
14 | Barapukuria | 47 | 18:00 | 80 | Kalurghat | 46 | 18:00 | 146 | Rahim | 38 | 10:00
15 | Barguna | 0 | 00:00 | 81 | Kamrangirchar | 68 | 13:00 | 147 | Rajbari | 59 | 18:00
16 | Barishal | 88 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 104 | 18:30
17 | Barishal-230 | 64 | 18:00 | 83 | Kasba | 25 | 21:00 | 149 | Rajshahi | 78 | 20:00
18 | Baroaulia | 55 | 11:00 | 84 | Kazla | 92 | 13:00 | 150 | Rajshahi-230 | 52 | 13:00
19 | Baroirhat | 42 | 18:00 | 85 | Keranigonj | 69 | 13:00 | 151 | Ramganj | 68 | 18:00
20 | Bashundhara | 165 | 13:00 | 86 | Khagrachori | 26 | 18:00 | 152 | Rampur | 36 | 18:00
21 | BashundharaCement | 13 | 13:00 | 87 | Khulna | 51 | 13:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 48 | 18:00 | 88 | Khulshi | 168 | 18:00 | 154 | Rangpur | 108 | 18:30
23 | Benapole | 42 | 07:00 | 89 | Kishoreganj | 89 | 18:00 | 155 | Ruppur | 3.4 | 11:00
24 | Bhaluka | 138 | 18:00 | 90 | Kodda | 271 | 18:00 | 156 | SSM | 10 | 04:00
25 | Bhandaria | 40 | 20:00 | 91 | Kulaura | 33 | 18:30 | 157 | Saidpur | 80 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 45 | 07:00 | 158 | Satkhira | 82 | 18:30
27 | Bheramara(GK) | 39 | 19:00 | 93 | Kushtia | 112 | 18:00 | 159 | Satmasjid | 84 | 13:00
28 | Bhulta | 208 | 12:00 | 94 | Laksam | 21 | 18:00 | 160 | Savar | 180 | 12:00
29 | Bog-Sherpur | 60 | 18:00 | 95 | Lakshmipur | 20 | 18:00 | 161 | SevenRings | 13.58 | 00:00
30 | Bogura | 116 | 18:30 | 96 | Lalbag | 62 | 13:00 | 162 | ShahCement | 33 | 01:00
31 | Borhanuddin | 64 | 22:00 | 97 | Lalmonirhat | 42 | 18:00 | 163 | Shahjadpur | 58 | 18:00
32 | Brahmanbaria | 97 | 18:30 | 98 | MI_Cement | 11.5 | 15:00 | 164 | Shahjibazar | 89 | 18:30
33 | Cantonment | 100 | 13:00 | 99 | Madanganj | 38 | 11:00 | 165 | Shahmirpur | 44 | 18:00
34 | Chandina | 8.03 | 14:00 | 100 | Madaripur | 67 | 19:30 | 166 | Shariatpur | 56 | 21:00
35 | Chandpur | 52 | 18:00 | 101 | Madartek | 68 | 13:00 | 167 | Sherpur | 102 | 18:00
36 | Chandraghona | 30 | 18:00 | 102 | Madunaghat | 43 | 18:30 | 168 | Shikalbaha | 21 | 18:00
37 | Chapai | 43 | 13:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 68.7 | 12:00
38 | Charsaidpur | 38 | 00:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 39 | 12:00
39 | Chauddagram | 46 | 18:00 | 105 | Maijdee | 22 | 18:00 | 171 | Shyampur | 128 | 13:00
40 | Chhatak | 24 | 13:00 | 106 | Manikganj | 92 | 18:00 | 172 | Siddhirganj | 103 | 16:00
41 | Chowmuhani | 119 | 18:00 | 107 | Maniknagar | 56 | 13:00 | 173 | Sirajganj | 84 | 18:30
42 | Chuadanga | 68 | 13:00 | 108 | Matarbari | 42 | 18:00 | 174 | Sonargaon | 110 | 16:00
43 | Coxsbazar | 120 | 18:00 | 109 | Matuail | 66 | 12:00 | 175 | Sreemongol | 64 | 18:00
44 | Cumilla(N) | 80 | 18:00 | 110 | Metrorail_Motijheel | 22 | 10:00 | 176 | Sreepur | 93 | 18:30
45 | Cumilla(S) | 136 | 18:00 | 111 | Metrorail_Uttara | 5 | 17:00 | 177 | Srinagar | 43.7 | 18:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 98 | 15:00 | 178 | Sunamganj | 41 | 19:00
47 | Daudkandi | 114 | 21:00 | 113 | Mirpur | 119 | 10:00 | 179 | Sylhet | 40 | 21:00
48 | DhakaUniversity | 68 | 13:00 | 114 | Mirsorai | 17 | 11:00 | 180 | Sylhet-132 | 88 | 18:00
49 | Dhamrai | 110 | 18:00 | 115 | Mirzapur | 36 | 18:00 | 181 | TK | 19 | 18:30
50 | Dhanmondi | 105 | 13:00 | 116 | Mithapukur | 46 | 18:00 | 182 | Tangail | 116 | 18:00
51 | Dohazari | 81 | 19:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 16 | 18:00
52 | Faridpur | 113 | 18:00 | 118 | Mogbazar | 75.6 | 14:00 | 184 | Thakurgaon | 73 | 18:30
53 | Fatullah | 99 | 10:00 | 119 | Mongla | 25 | 10:00 | 185 | Tongi | 100 | 18:00
54 | Fenchuganj | 27 | 18:00 | 120 | Motijheel | 33 | 13:00 | 186 | Ullahpara | 26 | 18:00
55 | Feni | 88 | 17:00 | 121 | Muktagacha | 26 | 18:00 | 187 | Ullon | 48 | 18:00
56 | GPH | 98 | 08:00 | 122 | Munshiganj | 72 | 13:00 | 188 | Uttara | 69 | 13:00
57 | Ghatail | 60 | 18:00 | 123 | Muradnagar | 27 | 18:00 | 189 | UttaraNew | 22 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 127 | 19:00 | 190 | Zigatola | 54 | 13:00
59 | Ghorashal-230 | 77 | 14:00 | 125 | Naogaon | 81 | 18:30
60 | Goalpara | 24 | 12:00 | 126 | Narail | 40 | 18:00
61 | Gollamari | 76 | 13:00 | 127 | Narinda | 58 | 13:00
62 | Gopalganj | 80 | 18:00 | 128 | Narshingdi | 140 | 18:30
63 | Gulshan | 94 | 13:00 | 129 | Natore | 99 | 18:30
64 | Halishahar | 66 | 15:00 | 130 | Nawabganj | 30.6 | 13:00
65 | HaripurSBU | 148 | 12:00 | 131 | Netrakona | 97 | 18:00
66 | Hasnabad | 77 | 13:00 | 132 | New | 61.6 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9718.94 | 0 |  | 9718.94
1:00 | 9203.83 | 0 |  | 9203.83
2:00 | 8772.19 | 0 |  | 8772.19
3:00 | 8395.96 | 0 |  | 8395.96
4:00 | 8259.91 | 0 |  | 8259.91
5:00 | 8061.15 | 0 |  | 8061.15
6:00 | 8355.41 | 0 |  | 8355.41
7:00 | 9268.87 | 0 |  | 9268.87
8:00 | 9643.09 | 0 |  | 9643.09
9:00 | 9593.25 | 0 |  | 9593.25
10:00 | 9589.74 | 0 |  | 9589.74
11:00 | 9903.23 | 0 |  | 9903.23
12:00 | 10444.27 | 0 |  | 10444.27
13:00 | 10939.52 | 0 |  | 10939.52
14:00 | 10685.62 | 0 |  | 10685.62
15:00 | 10583.87 | 0 |  | 10583.87
16:00 | 10326.7 | 0 |  | 10326.7
17:00 | 10599.77 | 0 |  | 10599.77
18:00 | 11735.02 | 0 |  | 11735.02
19:00 | 11568.5 | 0 |  | 11568.5
19:30 | 11322.66 | 0 |  | 11322.66
20:00 | 11045.24 | 0 |  | 11045.24
21:00 | 10996.47 | 0 |  | 10996.47
22:00 | 10521.51 | 0 |  | 10521.51
23:00 | 10077.66 | 0 |  | 10077.66
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4762 | 4956.94 | 9718.94 | DAILY GENERATION CURVE
00:30 | 4696.75 | 4764.635 | 9461.385
01:00 | 4631.5 | 4572.33 | 9203.83 | 17-11-2025
01:30 | 4583 | 4405.01 | 8988.01
02:00 | 4534.5 | 4237.69 | 8772.19
02:30 | 4470.5 | 4113.575 | 8584.075
03:00 | 4406.5 | 3989.46 | 8395.96
03:30 | 4379.5 | 3948.435 | 8327.935
04:00 | 4352.5 | 3907.41 | 8259.91
04:30 | 4245.5 | 3915.03 | 8160.53
05:00 | 4138.5 | 3922.65 | 8061.15
05:30 | 4184.5 | 4023.78 | 8208.28
06:00 | 4230.5 | 4124.91 | 8355.41
06:30 | 4442.115 | 4370.025 | 8812.14
07:00 | 4653.73 | 4615.14 | 9268.87
07:30 | 4679.32 | 4776.66 | 9455.98
08:00 | 4704.91 | 4938.18 | 9643.09
08:30 | 4626.965 | 4991.205 | 9618.17
09:00 | 4549.02 | 5044.23 | 9593.25
09:30 | 4562.775 | 5028.72 | 9591.495
10:00 | 4576.53 | 5013.21 | 9589.74
10:30 | 4668.97 | 5077.515 | 9746.485
11:00 | 4761.41 | 5141.82 | 9903.23
11:30 | 4877.68 | 5296.07 | 10173.75
12:00 | 4993.95 | 5450.32 | 10444.27
12:30 | 5230.91 | 5460.985 | 10691.895
13:00 | 5467.87 | 5471.65 | 10939.52
13:30 | 5474.915 | 5337.655 | 10812.57
14:00 | 5481.96 | 5203.66 | 10685.62
14:30 | 5490.395 | 5144.35 | 10634.745
15:00 | 5498.83 | 5085.04 | 10583.87
15:30 | 5415.155 | 5040.13 | 10455.285
16:00 | 5331.48 | 4995.22 | 10326.7
16:30 | 5448.14 | 5015.095 | 10463.235
17:00 | 5564.8 | 5034.97 | 10599.77
17:30 | 5903.15 | 5264.245 | 11167.395
18:00 | 6241.5 | 5493.52 | 11735.02
18:30 | 6136 | 5515.76 | 11651.76
19:00 | 6030.5 | 5538 | 11568.5
19:30 | 5852.5 | 5470.16 | 11322.66
20:00 | 5629.5 | 5415.74 | 11045.24
20:30 | 5615.5 | 5405.355 | 11020.855 |  | Executive Engineer
21:00 | 5601.5 | 5394.97 | 10996.47 |  | Network Operation Division
21:30 | 5416.5 | 5342.49 | 10758.99
22:00 | 5231.5 | 5290.01 | 10521.51
22:30 | 5082.25 | 5217.335 | 10299.585
23:00 | 4933 | 5144.66 | 10077.66

## En-Curve
QF-LDC-12
Date | 17-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3230 | 1282 | 860 | 0 | 80 | 717.94 | 86 | 3428 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3190 | 1273.75 | 859.5 | 0 | 78 | 670.635 | 86 | 3268.5 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17-11-2025
01:00 | 3150 | 1265.5 | 859 | 0 | 76 | 623.33 | 86 | 3109 | 0 | 0 | 35 | 0 | 0 | 0 | 0
01:30 | 3144 | 1237 | 859.5 | 0 | 75 | 572.51 | 86 | 2988.5 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | Energy Generated | 241.3517 |  | MKWHr
02:00 | 3138 | 1208.5 | 860 | 0 | 74 | 521.69 | 86 | 2868 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3117.5 | 1188.5 | 860 | 0 | 74 | 473.575 | 86 | 2772.5 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | Total Energy Requirement | 241.3517 |  | MKWHr
03:00 | 3097 | 1168.5 | 860 | 0 | 74 | 425.46 | 86 | 2677 | 0 | 0 | 8 | 0 | 0 | 0 | 0
03:30 | 3091.5 | 1167 | 860 | 0 | 73 | 423.935 | 86 | 2620.5 | 0 | 0 | 4 | 0 | 0 | 2 | 0
04:00 | 3086 | 1165.5 | 860 | 0 | 72 | 422.41 | 86 | 2564 | 0 | 0 | 0 | 0 | 0 | 4 | 0
04:30 | 3076.5 | 1113 | 860 | 0 | 74 | 422.03 | 86 | 2525.5 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0
05:00 | 3067 | 1060.5 | 860 | 0 | 76 | 421.65 | 86 | 2487 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 3055 | 1084.5 | 860 | 0 | 76 | 470.28 | 86 | 2564 | 0 | 0 | 7.5 | 0 | 0 | 5 | 0
06:00 | 3043 | 1108.5 | 860 | 0 | 76 | 518.91 | 86 | 2641 | 0 | 0 | 15 | 0 | 0 | 7 | 0
06:30 | 3100.5 | 1171.75 | 859.5 | 0 | 77 | 565.655 | 86 | 2882.5 | 32.235 | 0 | 29.5 | 0 | 0 | 7.5 | 0
07:00 | 3158 | 1235 | 859 | 0 | 78 | 612.4 | 86 | 3124 | 64.47 | 0 | 44 | 0 | 0 | 8 | 0
07:30 | 3103.5 | 1202.5 | 859 | 0 | 83 | 663.005 | 86 | 3194 | 183.975 | 12.5 | 64.5 | 0 | 0 | 4 | 0
08:00 | 3049 | 1170 | 859 | 0 | 88 | 713.61 | 86 | 3264 | 303.48 | 25 | 85 | 0 | 0 | 0 | 0
08:30 | 2969.5 | 1176.6 | 860.5 | 0 | 86 | 716.675 | 86 | 3212.5 | 402.395 | 16.5 | 91.5 | 0 | 0 | 0 | 0
09:00 | 2890 | 1183.2 | 862 | 0 | 84 | 719.74 | 86 | 3161 | 501.31 | 8 | 98 | 0 | 0 | 0 | 0
09:30 | 2941.5 | 1169.85 | 862.5 | 0 | 84 | 677.49 | 86 | 3108 | 569.155 | 8 | 85 | 0 | 0 | 0 | 0
10:00 | 2993 | 1156.5 | 863 | 0 | 84 | 635.24 | 86 | 3055 | 637 | 8 | 72 | 0 | 0 | 0 | 0
10:30 | 3045.5 | 1191.25 | 862.5 | 0 | 90 | 624.835 | 86 | 3087 | 672.4 | 8 | 79 | 0 | 0 | 0 | 0
11:00 | 3098 | 1226 | 862 | 0 | 96 | 614.43 | 86 | 3119 | 707.8 | 8 | 86 | 0 | 0 | 0 | 0
11:30 | 3104.5 | 1230.5 | 862.5 | 0 | 96 | 657.945 | 86 | 3262 | 715.805 | 8 | 150.5 | 0 | 0 | 0 | 0
12:00 | 3111 | 1235 | 863 | 0 | 96 | 701.46 | 86 | 3405 | 723.81 | 8 | 215 | 0 | 0 | 0 | 0
12:30 | 3036 | 1221 | 863 | 0 | 101 | 727.565 | 86 | 3452 | 695.83 | 29 | 480.5 | 0 | 0 | 0 | 0
13:00 | 2961 | 1207 | 863 | 0 | 106 | 753.67 | 86 | 3499 | 667.85 | 50 | 746 | 0 | 0 | 0 | 0
13:30 | 2891.5 | 1234.5 | 862.5 | 0 | 101 | 754.84 | 86 | 3412 | 621.73 | 50 | 798.5 | 0 | 0 | 0 | 0
14:00 | 2822 | 1262 | 862 | 0 | 96 | 756.01 | 86 | 3325 | 575.61 | 50 | 851 | 0 | 0 | 0 | 0
14:30 | 2864 | 1301.5 | 862.5 | 0 | 97 | 761.67 | 86 | 3284 | 491.575 | 50 | 836.5 | 0 | 0 | 0 | 0
15:00 | 2906 | 1341 | 863 | 0 | 98 | 767.33 | 86 | 3243 | 407.54 | 50 | 822 | 0 | 0 | 0 | 0
15:30 | 2939 | 1343 | 863 | 0 | 101 | 766.08 | 86 | 3296 | 287.205 | 50 | 723 | 0 | 0 | 1 | 0
16:00 | 2972 | 1345 | 863 | 0 | 104 | 764.83 | 86 | 3349 | 166.87 | 50 | 624 | 0 | 0 | 2 | 0
16:30 | 2922 | 1319 | 862.5 | 0 | 104 | 766.915 | 86 | 3427.5 | 88.57 | 120.5 | 764.25 | 0 | 0 | 2 | 0
17:00 | 2872 | 1293 | 862 | 0 | 104 | 769 | 86 | 3506 | 10.27 | 191 | 904.5 | 0 | 0 | 2 | 0
17:30 | 2974.5 | 1310.5 | 862.5 | 0 | 108 | 771.76 | 86 | 3577 | 5.135 | 263.5 | 1204.5 | 0 | 0 | 4 | 0
18:00 | 3077 | 1328 | 863 | 0 | 112 | 774.52 | 86 | 3648 | 0 | 336 | 1504.5 | 0 | 0 | 6 | 0
18:30 | 3002.5 | 1318 | 862.5 | 0 | 105 | 770.26 | 86 | 3652.5 | 0 | 322.5 | 1529 | 0 | 0 | 3.5 | 0
19:00 | 2928 | 1308 | 862 | 0 | 98 | 766 | 86 | 3657 | 0 | 309 | 1553.5 | 0 | 0 | 1 | 0
19:30 | 2929 | 1316 | 862 | 0 | 100 | 767.16 | 86 | 3656 | 0 | 204 | 1402.5 | 0 | 0 | 0 | 0
20:00 | 2951 | 1318 | 862 | 0 | 104 | 762.74 | 86 | 3683 | 0 | 157 | 1121.5 | 0 | 0 | 0 | 0
20:30 | 2951.5 | 1324.5 | 862.5 | 0 | 101 | 764.355 | 86 | 3700 | 0 | 140.5 | 1090.5 | 0 | 0 | 0 | 0
21:00 | 2952 | 1331 | 863 | 0 | 98 | 765.97 | 86 | 3717 | 0 | 124 | 1059.5 | 0 | 0 | 0 | 0
21:30 | 2928 | 1333.5 | 862.5 | 0 | 97 | 766.99 | 86 | 3707 | 0 | 87 | 891 | 0 | 0 | 0 | 0
22:00 | 2904 | 1336 | 862 | 0 | 96 | 768.01 | 86 | 3697 | 0 | 50 | 722.5 | 0 | 0 | 0 | 0
22:30 | 2952 | 1350.5 | 862 | 0 | 96 | 766.835 | 86 | 3683 | 0 | 25 | 476.75 | 0 | 0 | 1.5 | 0
23:00 | 3000 | 1365 | 862 | 0 | 96 | 765.66 | 86 | 3669 | 0 | 0 | 231 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 396 | 04:00 | 378 | 12:00 | Meghnaghat | 395 | 04:00 | 378 | 12:00
Ashuganj | 403 | 5:00 | 380 | 12:00 | Payra | 415 | 03:00 | 409 | 12:00
Bhulta | 399 | 04:00 | 376 | 12:00 | Rahanpur | 409 | 04:00 | 394 | 13:00
Bibiana | 399 | 04:00 | 388 | 12:00 | Rampal | 414 | 05:00 | 398 | 12:00
BIPTC | 405 | 03:00 | 394 | 18:00
Bogura | 405 | 04:00 | 390 | 13:00
Gopalganj | 407 | 04:00 | 391 | 12:00
Kaliakoir | 393 | 04:00 | 372 | 16:00
Korerhat | 402 | 06:00 | 389 | 12:00
Madunaghat | 401 | 05:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 04:00 | 224 | 12:00 | Kachua | 239 | 06:00 | 229 | 11:00
AKSML | 237 | 04:00 | 227 | 12:00 | Kaliakoir | 237 | 04:00 | 223 | 12:00
Aminbazar | 238 | 03:00 | 226 | 12:00 | Keranigonj | 236 | 05:00 | 221 | 12:00
Ashuganj | 235 | 03:00 | 224 | 12:00 | Khulna(S) | 241 | 04:00 | 223 | 17:00
Ashuganj-400 | 235 | 03:00 | 224 | 12:00 | Korerhat | 241 | 06:00 | 231 | 15:00
Baghabari | 237 | 04:00 | 228 | 12:00 | Madunaghat | 237 | 18:00 | 231 | 11:00
Barapukuria | 223 | 05:00 | 207 | 07:00 | Madunaghat-400 | 238 | 04:00 | 232 | 12:00
Barapukuria-230 | 223 | 05:00 | 207 | 07:00 | Maniknagar | 230 | 06:00 | 218 | 12:00
Barishal | 240 | 03:00 | 233 | 12:00 | Meghnaghat | 237 | 23:00 | 226 | 14:00
Bheramara | 236 | 04:00 | 225 | 13:00 | Meghnaghat-400 | 233 | 04:00 | 222 | 12:00
Bhulta | 232 | 04:00 | 218 | 12:00 | Mirsorai | 235 | 04:00 | 223 | 08:00
Bibiana | 237 | 04:00 | 224 | 08:00 | Rajshahi | 235 | 03:00 | 224 | 12:00
BIPTC | 239 | 04:00 | 226 | 12:00 | Rampal | 239 | 04:00 | 228 | 12:00
Bogura | 236 | 04:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 234 | 03:00 | 226 | 13:00 | Rampura | 231 | 04:00 | 216 | 12:00
Borhanuddin | 242 | 02:00 | 239 | 12:00 | Shikalbaha | 236 | 18:00 | 229 | 11:00
BSRM | 235 | 06:00 | 225 | 12:00 | Shyampur | 234 | 04:00 | 220 | 12:00
Cumilla(N) | 233 | 05:00 | 223 | 11:00 | Siddhirganj | 233 | 04:00 | 220 | 12:00
Faridpur | 240 | 03:00 | 231 | 12:00 | Sirajgonj | 241 | 02:00 | 234 | 12:00
Fenchuganj | 238 | 06:00 | 231 | 11:00 | Sreepur | 234 | 04:00 | 222 | 12:00
Feni | 233 | 7:00 | 224 | 12:00 | Tongi | 232 | 18:00 | 220 | 12:00
Ghorashal | 240 | 04:00 | 225 | 09:00
Ghorashal-230 | 233 | 04:00 | 218 | 12:00
Gopalganj | 241 | 04:00 | 232 | 12:00
GPH | 236 | 06:00 | 228 | 11:00
Haripur | 232 | 04:00 | 219 | 12:00
Hasnabad | 236 | 01:00 | 221 | 12:00
Hathazari | 235 | 18:30 | 228 | 11:00
Ishurdi | 239 | 03:00 | 229 | 11:00
Jhenaidah | 238 | 03:00 | 225 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 02:00 | 125 | 12:00 | Lalbag | 137 | 03:00 | 128 | 12:00
Agargaon | 138 | 04:00 | 128 | 12:00 | Lalmonirhat | 131 | 02:00 | 122 | 07:00
Agrabad | 136 | 01:00 | 131 | 10:00 | Madanganj | 132 | 01:00 | 129 | 10:00
AKS | 134 | 01:00 | 130 | 12:00 | Madaripur | 137 | 05:00 | 134 | 14:00
Aminbazar | 138 | 03:00 | 129 | 12:00 | Madartek | 135 | 06:00 | 124 | 12:00
Amnura | 137 | 02:00 | 130 | 12:00 | Madunaghat | 138 | 03:00 | 134 | 16:00
Ashuganj | 142 | 02:00 | 138 | 11:00 | Magura | 140 | 06:00 | 130 | 13:00
Bagerhat | 138 | 04:00 | 129 | 12:00 | Mahasthangarh | 134 | 04:00 | 128 | 07:00
Bajitpur | 137 | 05:00 | 130 | 12:00 | Maijdee | 137 | 03:00 | 129 | 11:00
Bakulia | 138 | 04:00 | 132 | 11:00 | Manikganj | 134 | 07:00 | 126 | 12:00
Banani | 136 | 04:00 | 125 | 12:00 | Maniknagar | 141 | 06:00 | 131 | 12:00
Bangabhaban | 141 | 04:00 | 131 | 12:00 | Matarbari | 128 | 03:00 | 118 | 12:00
Barapukuria | 138 | 21:00 | 125 | 07:00 | Matuail | 135.5 | 06:00 | 127 | 12:00
Barguna | 0 | 00:00 | N/A | N/A | Metrorail_Motijheel | 141 | 06:00 | 131 | 12:00
Barishal | 138 | 02:00 | 134 | 12:00 | Metrorail_Uttara | 138 | 01:00 | 128 | 12:00
Barishal-230 | 139 | 04:00 | 133 | 12:00 | Millgate | 138 | 03:00 | 128 | 11:00
Baroaulia | 137 | 18:30 | 130 | 05:00 | Mirpur | 138 | 06:00 | 128 | 12:00
Baroirhat | 136 | 02:00 | 130 | 11:00 | Mirzapur | 136 | 04:00 | 129 | 12:00
Bashundhara | 136 | 04:00 | 125 | 12:00 | Mithapukur | 136 | 19:00 | 127 | 07:00
BashundharaCement | 132 | 01:00 | 129 | 10:00 | MI_Cement | 136 | 04:00 | 124.3 | 12:00
Beanibazar | 134 | 05:00 | 130 | 11:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 137 | 02:00 | 126 | 13:00 | Mogbazar | 138 | 05:00 | 126 | 12:00
Bhaluka | 135 | 04:00 | 126 | 12:00 | Mongla | 137 | 03:00 | 129 | 12:00
Bhandaria | 137 | 04:00 | 129 | 12:00 | Motijheel | 141 | 04:00 | 131 | 12:00
Bhangura | 138 | 02:00 | 131 | 12:00 | Muktagacha | 133 | 08:00 | 125 | 18:00
Bheramara | 140 | 02:00 | 135 | 12:00 | Munshiganj | 133 | 02:00 | 125 | 12:00
Bheramara(GK) | 140 | 05:00 | 135 | 13:00 | Muradnagar | 136 | 04:00 | 129 | 11:00
Bhulta | 130 | 06:00 | 125 | 12:00 | Mymensingh | 134 | 09:00 | 126 | 07:00
Bog-Sherpur | 136 | 04:00 | 129 | 13:00 | Naogaon | 133 | 05:00 | 126 | 12:00
Bogura | 136 | 19:00 | 129 | 12:00 | Narail | 137 | 00:00 | 129 | 12:00
Bogura-230 | 136 | 19:00 | 129 | 13:00 | Narinda | 141 | 06:00 | 131 | 12:00
Brahmanbaria | 135 | 02:00 | 130 | 11:00 | Narshingdi | 135 | 03:00 | 123 | 10:00
Cantonment | 137 | 02:00 | 128 | 12:00 | Natore | 136 | 05:00 | 130 | 12:00
Chandina | 138 | 03:00 | 131 | 12:00 | Nawabganj | 137 | 03:00 | 129 | 11:00
Chandpur | 140 | 15:00 | 131 | 11:00 | Netrakona | 130 | 00:00 | 124 | 12:00
Chandraghona | 139 | 04:00 | 134 | 12:00 | New | 138 | 06:00 | 129 | 12:00
Chapai | 137 | 21:00 | 132 | 10:00 | Niamatpur | 137 | 03:00 | 132 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 05:00 | 127 | 12:00 | Noapara | 139 | 05:00 | 131 | 12:00
Chauddagram | 137 | 03:00 | 130 | 12:00 | Pabna | 139 | 01:00 | 132 | 13:00
Chhatak | 132 | 00:00 | 128 | 11:00 | Palashbari | 133 | 19:00 | 124 | 08:00
Chowmuhani | 136 | 01:00 | 130 | 10:00 | Panchagarh | 138 | 04:00 | 122 | 23:00
Chuadanga | 142 | 05:00 | 130 | 12:00 | Patiya | 136 | 18:30 | 130 | 11:00
Coxsbazar | 126 | 03:00 | 118 | 12:00 | Patuakhali | 136 | 17:00 | 133 | 12:00
Cumilla(N) | 137 | 03:00 | 132 | 11:00 | Payra | 137 | 04:00 | 134 | 11:00
Cumilla(S) | 138 | 02:00 | 125 | 13:00 | PHP | 137 | 06:00 | 130 | 16:00
Daganbhuiyan | 137 | 04:00 | 130 | 12:00 | Postogola | 136 | 03:00 | 128 | 12:00
Daudkandi | 133 | 04:00 | 125 | 12:00 | Purbachal | 137 | 04:00 | 125 | 12:00
DhakaUniversity | 136 | 03:00 | 126 | 12:00 | Purbasadipur | 135 | 22:00 | 124 | 08:00
Dhamrai | 136 | 06:00 | 128 | 12:00 | Rahanpur | 138 | 04:00 | 132 | 12:00
Dhanmondi | 137 | 05:00 | 128 | 12:00 | Rahanpur-400 | 138 | 04:00 | 132 | 13:00
Dohazari | 133 | 05:00 | 126 | 12:00 | Rahim | 135 | 06:00 | 128 | 12:00
Faridpur | 139 | 03:00 | 134 | 12:00 | Rajbari | 139 | 03:00 | 133 | 12:00
Fatullah | 139 | 05:00 | 126 | 12:00 | Rajendrapur | 135 | 04:00 | 126 | 12:00
Fenchuganj | 141 | 06:00 | 136 | 11:00 | Rajshahi | 136 | 06:00 | 130 | 12:00
Feni | 136 | 06:00 | 130 | 11:00 | Rajshahi-230 | 136 | 04:00 | 129 | 12:00
Feni-230 | 136 | 7:00 | 131 | 11:00 | Ramganj | 136 | 01:00 | 129 | 11:00
Ghatail | 133 | 09:00 | 125 | 18:00 | Rampur | 136 | 06:00 | 131 | 11:00
Ghorashal | 141 | 05:00 | 129 | 08:00 | Rampura | 136 | 04:00 | 126 | 12:00
Goalpara | 140 | 04:00 | 132 | 12:00 | Rangamati | 138 | 05:00 | 133 | 11:00
Gollamari | 139 | 03:00 | 132 | 12:00 | Rangpur | 136 | 19:00 | 128 | 07:00
Gopalganj | 139 | 04:00 | 133 | 12:00 | Ruppur | 139 | 02:00 | 135 | 12:00
Gopalganj-400 | 140 | 04:00 | 135 | 12:00 | Saidpur | 134 | 17:00 | 124 | 08:00
Gulshan | 135 | 06:00 | 125 | 12:00 | Satkhira | 138 | 04:00 | 130 | 12:00
Halishahar | 137 | 04:00 | 132 | 11:00 | Satmasjid | 138 | 04:00 | 128 | 13:00
Haripur | 136 | 04:00 | 128 | 12:00 | Savar | 136 | 03:00 | 126 | 12:00
HaripurSBU | 135 | 04:00 | 128 | 12:00 | SevenRings | 141 | 04:00 | 133 | 11:00
Hasnabad | 136 | 03:00 | 126 | 13:00 | ShahCement | 135 | 05:00 | 127 | 12:00
Hathazari | 137 | 03:00 | 134 | 12:00 | Shahjadpur | 140 | 04:00 | 135 | 10:00
Ishurdi | 141 | 02:00 | 135 | 13:00 | Shahjibazar | 138 | 14:00 | 134 | 17:00
Jaldhaka | 133 | 22:00 | 122 | 07:00 | Shahmirpur | 137 | 17:00 | 132 | 12:00
Jamalpur | 134 | 14:00 | 120 | 18:00 | Shariatpur | 139 | 05:00 | 132 | 12:00
Jashore | 136 | 00:00 | 127 | 13:00 | Sherpur | 131 | 15:00 | 118 | 18:00
Jhenaidah | 142 | 03:00 | 122 | 18:00 | Shikalbaha | 127 | 06:00 | 121 | 12:00
Jhenaidah-230 | 145 | 04:00 | 132 | 13:00 | Shikalbaha-230 | 138 | 03:00 | 134 | 11:00
Joydebpur | 140 | 19:00 | 128 | 11:00 | Shitalakhya | 136 | 04:00 | 124.3 | 12:00
Joypurhat | 132 | 03:00 | 125 | 13:00 | Sholosohor | 138 | 05:00 | 134 | 11:00
Juldah | 137 | 19:00 | 132 | 11:00 | Shyampur | 137 | 03:00 | 130 | 13:00
Kabirpur | 139 | 18:30 | 127 | 16:00 | Shyampur-230 | 138 | 04:00 | 130 | 12:00
Kachua | 140 | 06:00 | 134 | 11:00 | Siddhirganj | 135 | 03:00 | 128 | 11:00
Kaliakoir | 141 | 03:00 | 129 | 12:00 | Sirajganj | 134 | 00:00 | 128 | 11:00
Kallyanpur | 137 | 05:00 | 129 | 12:00 | Sonargaon | 134 | 04:00 | 126 | 12:00
Kalurghat | 138 | 04:00 | 134 | 11:00 | Sreemongol | 137 | 01:00 | 133 | 11:00
Kamrangirchar | 138 | 06:00 | 127 | 12:00 | Sreepur | 138 | 05:00 | 129 | 12:00
Kaptai | 140 | 3:00 | 136 | 10:00 | Srinagar | 137 | 02:00 | 128 | 12:00
Kasba | 136 | 04:00 | 129 | 12:00 | SSM | 140 | 18:00 | 138 | 02:00
Kazla | 141 | 05:00 | 131 | 12:00 | Sunamganj | 131 | 04:00 | 127 | 12:00
Keranigonj | 138 | 04:00 | 128 | 12:00 | Sylhet | 135 | 04:00 | 131 | 11:00
Khagrachori | 137 | 04:00 | 132 | 12:00 | Sylhet-132 | 134 | 06:00 | 130 | 13:00
Khulna | 138 | 03:00 | 131 | 12:00 | Tangail | 133 | 09:00 | 126 | 12:00
Khulna(S) | 140 | 04:00 | 133 | 12:00 | Taraganj | 135 | 21:00 | 124 | 07:00
Khulshi | 136 | 06:00 | 130 | 18:00 | Thakurgaon | 138 | 21:00 | 120 | 23:00
Kishoreganj | 137 | 05:00 | 130 | 12:00 | TK | 138 | 01:00 | 133 | 11:00
Kodda | 137 | 18:00 | 125 | 11:00 | Tongi | 139 | 04:00 | 130 | 12:00
KSRM | 138 | 05:00 | 132 | 11:00 | Ullahpara | 137 | 05:00 | 130 | 12:00
Kulaura | 139 | 02:00 | 135 | 12:00 | Ullon | 137 | 05:00 | 125 | 12:00
Kurigram | 133 | 19:00 | 121 | 07:00 | Uttara | 138 | 05:00 | 127 | 12:00
Kushtia | 137 | 01:00 | 129 | 12:00 | UttaraNew | 138 | 02:00 | 128 | 12:00
Laksam | 139 | 06:00 | 133 | 11:00 | Zigatola | 138 | 06:00 | 128 | 13:00
Lakshmipur | 137 | 04:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division