## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-11-2025 | during | 19-11-2025 | during | 19-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 369 | 377 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Shut down for Maintenance
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 26 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.5 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 75 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 3 | 55 | 55 | 17 | 17 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 22.8 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 34 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 30 | 270 | 300 | 300 | 150 | 150 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 92 | 149 | 149 | 17 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 17 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | Shut down for Maintenance
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 300 | 500 | 718 | 718 | 500 | 500 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1226 | 1961.3 | 5451.4 | 5419.4 | 3263.61 | 3248.61
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 221 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 39 | 80 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 55 | 0 | 0 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 34 | 50 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 0 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.3 | 0 | 3.3 | 0 | 3.3 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 7 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 61 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 570 | 612 | 612 | 612 | 612 | 612 | U-2 Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 9 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | machine problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1652.3 | 1935 | 2887.02 | 2869.72 | 2378.8 | 2369.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 198 | 205 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 318.81 | 318.81 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 395 | 365 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 27 | 46.7 | 46.7 | 16 | 16 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 3 | 41 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 103 | 150 | 150 | 142 | 142 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 30 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 109 | 109 | Schedule Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 23 | 132 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 98 | 104 | 160 | 160 | 112 | 112 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 43 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 821 | 1067 | 2438.21 | 2368.21 | 1906.51 | 1836.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-11-2025 | during | 19-11-2025 | during | 19-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 12 | 157.5 | 157.5 | 70 | 70 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 61 | 58 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.66 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 160.66 | 105 | 364 | 314 | 217 | 167
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 156 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 78 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 158 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 0 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 395 | 381 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1160 | 1179 | 1187 | 1187 | 1175 | 1175
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 867 | 889 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 185 | 160 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81 | 0 | 83 | 0 | 83 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1114 | 1094 | 0 | 0 | 1140 | 1140 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2247 | 2143 | 2401 | 2318 | 2780.1 | 2697.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 503 | 501 | 0 | 0 | 0 | 0 | machine problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 6 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 50 | 50 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 690 | 865 | 982 | 982 | 827 | 827 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1463.55 | 1659 | 1583 | 1583 | 1295 | 1295
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 61.59 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 190 | 180 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 81 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.59 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 697.92 | 758 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.13 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 106 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1538.23 | 1572 | 3177.49 | 3011.87 | 2930.11 | 2764.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 50 | 50 | 0 | 0 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 74 | 113 | 113 | 40 | 40 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.2 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 183 | 0 | 185.39 | 0 | 185.39 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 226.2 | 164 | 499.19 | 278 | 356.19 | 135
System Total |  |  |  |  | 28823.2 | 28205.415 | 10494.94 | 11785.3 | 19988.31 | 19349.2 | 16302.32 | 15688.21
Forecast Scenario (19-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9830 |  | 0 |  | 9830
|  |  |  | 1:00 | 9350 |  | 0 |  | 9350
|  |  |  | 2:00 | 8870 |  | 0 |  | 8870
|  |  |  | 3:00 | 8560 |  | 0 |  | 8560
|  |  |  | 4:00 | 8390 |  | 0 |  | 8390
|  |  |  | 5:00 | 8260 |  | 0 |  | 8260
|  |  |  | 6:00 | 8550 |  | 0 |  | 8550
|  |  |  | 7:00 | 9410 |  | 0 |  | 9410
|  |  |  | 8:00 | 9760 |  | 0 |  | 9760
|  |  |  | 9:00 | 9630 |  | 0 |  | 9630
|  |  |  | 10:00 | 9620 |  | 0 |  | 9620
|  |  |  | 11:00 | 10200 |  | 0 |  | 10200
|  |  |  | 12:00 | 10590 |  | 0 |  | 10590
|  |  |  | 13:00 | 10970 |  | 0 |  | 10970
|  |  |  | 14:00 | 10590 |  | 0 |  | 10590
|  |  |  | 15:00 | 10540 |  | 0 |  | 10540
|  |  |  | 16:00 | 10470 |  | 0 |  | 10470
|  |  |  | 17:00 | 10730 |  | 0 |  | 10730
|  |  |  | 18:00 | 11910 |  | 0 |  | 11910
|  |  |  | 18:30 | 11700 |  | 0 |  | 11700
|  |  |  | 19:00 | 11470 |  | 0 |  | 11470
|  |  |  | 19:30 | 11380 |  | 0 |  | 11380
|  |  |  | 20:00 | 11340 |  | 0 |  | 11340
|  |  |  | 21:00 | 11100 |  | 0 |  | 11100
|  |  |  | 22:00 | 10710 |  | 0 |  | 10710
|  |  |  | 23:00 | 10300 |  | 0 |  | 10300
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 10590.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11910.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11910.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 241.15 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:43 hrs on 19-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-11-2025 | [28 empty] | Date: | 18-11-2025 | [28 empty] | Date: | 18-11-2025 | [28 empty] | Date: | 18-11-2025 | [28 empty] | Date: | 18-11-2025 | [14 empty] | Date: | 18-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 250 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 387 | 0 | 30 | 152 | 21 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 59 | 19 | 35 | 0 | 0 | 0 | 4718 | 863 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 0 | 752.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 428 | 820 | 0 | 5013.34 | 9731.34 | 100.81
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 250 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 370 | 0 | 30 | 152 | 16 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 4650 | 862 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 0 | 622.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 306 | 790 | 0 | 4608.6 | 9258.6 | 100.8
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 250 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 377 | 0 | 30 | 150 | 16 | 0 | 30 | 30 | 0 | 0 | 158 | 0 | 8 | 0 | 35 | 0 | 0 | 0 | 4483 | 863 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 825 | 0 | 527.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 306 | 720 | 0 | 4289.41 | 8772.41 | 100.8
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 250 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 384 | 0 | 30 | 153 | 16 | 0 | 30 | 30 | 0 | 0 | 158 | 0 | 8 | 0 | 36 | 0 | 0 | 0 | 4422 | 863 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 0 | 422.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 307 | 605 | 0 | 4045.18 | 8467.18 | 100.79
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 35 | 600 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 250 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 305 | 0 | 339 | 0 | 30 | 151 | 16 | 0 | 30 | 30 | 0 | 0 | 158 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 4307 | 862 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803 | 0 | 435.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 306 | 560 | 0 | 3982.6 | 8289.6 | 100.79
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 600 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 250 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 72 | 0 | 0 | 0 | 305 | 0 | 353 | 0 | 30 | 148 | 16 | 0 | 11 | 30 | 0 | 0 | 157 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 4286 | 863 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 437.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 306 | 545 | 0 | 3877.18 | 8163.18 | 100.78
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 38 | 600 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 508 | 0 | 0 | 0 | 0 | 250 | 0 | 240 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 370 | 0 | 30 | 153 | 16 | 0 | 11 | 30 | 0 | 0 | 158 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4442 | 863 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 0 | 440.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 304 | 550 | 0 | 4013.76 | 8455.76 | 100.78
07:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.42 | 86 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 560 | 4 | 0 | 0 | 0 | 255 | 0 | 240 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 78 | 0 | 9 | 0 | 315 | 0 | 370 | 0 | 30 | 158 | 16 | 0 | 79 | 30 | 0 | 0 | 157 | 0 | 22 | 18 | 34 | 0 | 4.27 | 0 | 4681.69 | 863 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1000 | 0 | 567.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.62 | 8 | 0 | 0 | 2.81 | 180 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0.26 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.4 | 18 | 0.35 | 0 | 0 | 120 | 220 | 0 | 456 | 600 | 0 | 4629.49 | 9311.18 | 100.77
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 300 | 0 | 0 | 0 | 0 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 14 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1.41 | 86 | 0 | 13 | 650 | 0 | 0 | 0 | 0 | 8 | 227 | 0 | 0 | 0 | 550 | 10 | 0 | 0 | 0 | 230 | 0 | 240 | 0 | 189 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 90 | 0 | 37 | 0 | 310 | 0 | 355 | 0 | 30 | 152 | 16 | 0 | 79 | 30 | 0 | 0 | 157 | 0 | 56 | 18 | 30 | 1 | 21.26 | 0 | 4713.67 | 863 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1102 | 0 | 622.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.7 | 43 | 0 | 0 | 29.59 | 170 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 2.53 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 2.1 | 74 | 0.19 | 0 | 0 | 120 | 180 | 0 | 440 | 680 | 0 | 4948.16 | 9661.83 | 100.77
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 302 | 0 | 0 | 0 | 0 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 23 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 12 | 2.34 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 34 | 227 | 0 | 0 | 0 | 502 | 15 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 88 | 0 | 56 | 0 | 305 | 0 | 351 | 0 | 30 | 146 | 16 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 59 | 18 | 31 | 2 | 34.43 | 0 | 4510.77 | 862 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 1032 | 0 | 632.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.74 | 70 | 0 | 0 | 47.55 | 164 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 4.11 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 3.9 | 128 | 0.36 | 0 | 0 | 120 | 220 | 0 | 357 | 695 | 0 | 5019.78 | 9530.55 | 100.76
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 305 | 0 | 0 | 1 | 0 | 30 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 28 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 12 | 3.01 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 30 | 224 | 0 | 0 | 0 | 505 | 18 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 14 | 0 | 11 | 0 | 96 | 0 | 66 | 0 | 300 | 0 | 360 | 0 | 30 | 149 | 16 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 61 | 19 | 31 | 2 | 43.73 | 0 | 4690.74 | 862 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 884 | 0 | 537.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.49 | 83 | 0 | 0 | 57.89 | 162 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 5 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5.3 | 162 | 0.51 | 0 | 0 | 120 | 220 | 0 | 354 | 665 | 0 | 4834.23 | 9524.97 | 100.76
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 298 | 0 | 0 | 17 | 0 | 30 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 31 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 12 | 3.28 | 86 | 0 | 6 | 595 | 0 | 0 | 0 | 0 | 32 | 221 | 0 | 0 | 0 | 580 | 19 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 203 | 16 | 0 | 0 | 16 | 0 | 11 | 0 | 98 | 0 | 72 | 0 | 320 | 0 | 345 | 0 | 30 | 157 | 16 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 59 | 19 | 31 | 2 | 48.48 | 0 | 4891.76 | 863 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1052 | 0 | 618.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.65 | 104 | 0 | 0 | 63.83 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.44 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 180 | 0.55 | 0 | 0 | 120 | 220 | 0 | 354 | 680 | 0 | 5216.22 | 10107.98 | 100.75
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 300 | 0 | 0 | 17 | 0 | 30 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 31 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 10 | 12 | 3.3 | 86 | 0 | 9 | 650 | 0 | 0 | 1 | 0 | 39 | 218 | 0 | 0 | 0 | 570 | 19 | 0 | 1 | 0 | 395 | 0 | 0 | 3 | 198 | 20 | 0 | 0 | 23 | 0 | 11 | 0 | 98 | 0 | 72 | 0 | 315 | 0 | 395 | 0 | 30 | 151 | 0 | 0 | 79 | 30 | 0 | 0 | 160 | 0 | 61 | 19 | 30 | 2 | 48.66 | 0 | 5019.96 | 867 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 1114 | 0 | 697.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.59 | 106 | 0 | 0 | 63.13 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.59 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 6.2 | 183 | 0.55 | 0 | 0 | 50 | 220 | 0 | 503 | 690 | 0 | 5474.98 | 10494.94 | 100.75
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 280 | 0 | 0 | 45 | 0 | 195 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 30 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33 | 10 | 0 | 12 | 12 | 3.05 | 86 | 20 | 15 | 650 | 0 | 0 | 37 | 0 | 88 | 218 | 0 | 0 | 0 | 570 | 17 | 0 | 58 | 0 | 395 | 0 | 0 | 10 | 192 | 21 | 13 | 0 | 93 | 0 | 11 | 0 | 102 | 0 | 67 | 0 | 305 | 0 | 358 | 0 | 30 | 161 | 0 | 0 | 79 | 30 | 0 | 0 | 160 | 0 | 66 | 19 | 28 | 2 | 45.62 | 0 | 5421.67 | 866 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1100 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.97 | 99 | 0 | 0 | 61.74 | 178 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 5.34 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 5.8 | 173 | 0.53 | 0 | 0 | 50 | 220 | 0 | 502 | 690 | 0 | 5448.38 | 10870.05 | 100.74
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 305 | 0 | 0 | 52 | 0 | 195 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 25 | 0 | 19.3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 24 | 0 | 12 | 12 | 2.49 | 86 | 31 | 5 | 650 | 0 | 0 | 50 | 0 | 89 | 216 | 0 | 0 | 0 | 502 | 16 | 0 | 100 | 0 | 320 | 0 | 0 | 20 | 206 | 19 | 33 | 0 | 93 | 0 | 11 | 0 | 106 | 0 | 55 | 0 | 310 | 0 | 399 | 0 | 30 | 147 | 16 | 0 | 79 | 30 | 0 | 0 | 160 | 0 | 59 | 19 | 12 | 2 | 39.15 | 0 | 5380.94 | 876 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 965 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.36 | 81 | 0 | 0 | 51.3 | 171 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 4.65 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 4.8 | 147 | 0.43 | 0 | 0 | 50 | 180 | 0 | 450 | 692 | 0 | 5117.54 | 10498.48 | 100.74
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 318 | 0 | 0 | 52 | 0 | 195 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 19 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 48 | 23 | 0 | 12 | 12 | 1.67 | 86 | 32 | 3 | 650 | 0 | 0 | 50 | 0 | 90 | 214 | 0 | 0 | 0 | 500 | 11 | 0 | 100 | 0 | 320 | 0 | 0 | 20 | 202 | 22 | 33 | 0 | 100 | 0 | 11 | 0 | 106 | 0 | 41 | 0 | 315 | 0 | 398 | 0 | 30 | 155 | 16 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 59 | 18 | 12 | 1 | 28.54 | 0 | 5410.71 | 878 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 922 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.06 | 56 | 0 | 0 | 38.43 | 178 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 3.48 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3.2 | 104 | 0.29 | 0 | 0 | 50 | 220 | 0 | 452 | 700 | 0 | 5034.46 | 10445.17 | 100.73
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 323 | 17.5 | 0 | 52 | 0 | 195 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 8 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 40 | 24 | 0 | 12 | 12 | 0.78 | 86 | 24 | 3 | 615 | 0 | 0 | 33 | 0 | 68 | 216 | 0 | 0 | 0 | 575 | 6 | 0 | 80 | 0 | 365 | 0 | 0 | 23 | 207 | 25 | 16 | 0 | 100 | 0 | 11 | 0 | 106 | 0 | 20 | 0 | 320 | 0 | 392 | 0 | 30 | 157 | 16 | 0 | 78 | 30 | 0 | 0 | 159 | 0 | 57 | 18 | 12 | 0 | 11.19 | 0 | 5372.97 | 888 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 988 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.6 | 25 | 0 | 0 | 12.38 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.38 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.3 | 44 | 0.11 | 0 | 0 | 50 | 220 | 0 | 480 | 730 | 0 | 5000.77 | 10373.74 | 100.73
17:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 350 | 17.5 | 0 | 52 | 70 | 220 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 1 | 55 | 20 | 21 | 0 | 0 | 11 | 30 | 0 | 0 | 4 | 50 | 30 | 0 | 25 | 12 | 0 | 86 | 34 | 0 | 650 | 0 | 0 | 0 | 0 | 66 | 218 | 0 | 0 | 0 | 560 | 0 | 0 | 85 | 0 | 370 | 0 | 0 | 40 | 195 | 27 | 17 | 0 | 103 | 0 | 11 | 0 | 100 | 0 | 0 | 3 | 310 | 0 | 396 | 0 | 30 | 152 | 16 | 0 | 78 | 30 | 0 | 15 | 158 | 2 | 58 | 18 | 12 | 0 | 0.36 | 0 | 5572.86 | 889 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1010 | 0 | 761 | 0 | 0 | 0 | 25 | 33 | 0 | 0 | 13 | 0 | 0.76 | 2 | 18 | 0 | 0.58 | 185 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0.06 | 0 | 0 | 50 | 1 | 16 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 0 | 50 | 180 | 0 | 500 | 820 | 5 | 5064.51 | 10637.37 | 100.72
18:00 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 500 | 17.5 | 0 | 92 | 75 | 270 | 26 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 70 | 22.8 | 21 | 0 | 0 | 35 | 32 | 0 | 0 | 9 | 50 | 55 | 7 | 25 | 12 | 0 | 86 | 61 | 0 | 650 | 0 | 0 | 0 | 0 | 80 | 221 | 0 | 0 | 0 | 612 | 0 | 0 | 103 | 0 | 365 | 0 | 0 | 41 | 205 | 27 | 43 | 0 | 132 | 0 | 17 | 0 | 104 | 0 | 0 | 30 | 310 | 0 | 381 | 0 | 30 | 156 | 21 | 0 | 78 | 30 | 0 | 15 | 158 | 17 | 58 | 18 | 12 | 0 | 0 | 0 | 6247.3 | 889 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 0 | 758 | 0 | 0 | 0 | 90 | 81 | 0 | 0 | 28 | 0 | 0 | 0 | 21 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 90 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 50 | 220 | 0 | 501 | 865 | 17 | 5538 | 11785.3 | 100.72
19:00 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 446 | 17.5 | 0 | 149 | 0 | 278 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 10 | 23 | 21 | 0 | 0 | 69 | 0 | 0 | 0 | 5 | 0 | 54 | 0 | 25 | 37 | 0 | 86 | 100 | 0 | 650 | 0 | 0 | 0 | 0 | 93 | 221 | 0 | 0 | 0 | 580 | 0 | 0 | 118 | 0 | 350 | 0 | 0 | 41 | 202 | 33 | 16 | 0 | 153 | 0 | 17 | 0 | 92 | 0 | 0 | 0 | 300 | 0 | 382 | 0 | 30 | 149 | 21 | 0 | 78 | 30 | 0 | 15 | 158 | 0 | 58 | 18 | 17 | 0 | 0 | 0 | 5864.5 | 889 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 0 | 753 | 0 | 48 | 0 | 70 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 95 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 220 | 0 | 500 | 880 | 17 | 5511 | 11375.5 | 100.71
19:30 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 440 | 17.5 | 0 | 149 | 0 | 278 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 20.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 54 | 0 | 25 | 37 | 0 | 86 | 45 | 0 | 650 | 0 | 0 | 0 | 0 | 92 | 222 | 0 | 0 | 0 | 581 | 0 | 0 | 125 | 0 | 350 | 0 | 0 | 41 | 204 | 33 | 15 | 0 | 162 | 0 | 17 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 382 | 0 | 30 | 146 | 21 | 0 | 78 | 30 | 0 | 15 | 159 | 0 | 59 | 18 | 18 | 0 | 0 | 0 | 5748 | 889 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1097 | 0 | 758 | 0 | 48 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 41 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 220 | 0 | 501 | 890 | 17 | 5539 | 11287
20:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 429 | 17.5 | 0 | 149 | 0 | 278 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 54 | 0 | 25 | 37 | 0 | 86 | 34 | 0 | 650 | 0 | 0 | 0 | 0 | 96 | 223 | 0 | 0 | 0 | 575 | 0 | 0 | 125 | 0 | 393 | 0 | 0 | 42 | 197 | 33 | 15 | 0 | 165 | 0 | 17 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 382 | 0 | 30 | 144 | 21 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 59 | 18 | 21 | 0 | 0 | 0 | 5749 | 890 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 0 | 757 | 0 | 48 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 53 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 220 | 0 | 501 | 890 | 17 | 5491 | 11240 | 100.71
21:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 450 | 17.5 | 0 | 52 | 0 | 278 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 31 | 0 | 25 | 37 | 0 | 86 | 33 | 0 | 650 | 0 | 0 | 0 | 0 | 95 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 32 | 0 | 393 | 0 | 0 | 42 | 202 | 31 | 15 | 0 | 136 | 0 | 17 | 0 | 96 | 0 | 0 | 0 | 310 | 0 | 394 | 0 | 30 | 144 | 21 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 49 | 18 | 22 | 0 | 0 | 0 | 5543 | 889 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 768 | 0 | 48 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 53 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 503 | 895 | 17 | 5461 | 11004 | 100.7
22:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 436 | 17.5 | 0 | 35 | 0 | 95 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 25 | 37 | 0 | 86 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 96 | 224 | 0 | 0 | 0 | 575 | 0 | 0 | 32 | 0 | 393 | 0 | 0 | 42 | 198 | 35 | 16 | 0 | 100 | 0 | 17 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 394 | 0 | 30 | 145 | 21 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 59 | 18 | 31 | 0 | 0 | 0 | 5274 | 889 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 770 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 56 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 503 | 890 | 0 | 5344 | 10618 | 100.7
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 448 | 0 | 0 | 0 | 0 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 86 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 95 | 225 | 0 | 0 | 0 | 580 | 0 | 5 | 0 | 0 | 393 | 0 | 0 | 42 | 204 | 35 | 0 | 0 | 95 | 0 | 17 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 386 | 0 | 30 | 144 | 21 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 59 | 0 | 36 | 0 | 0 | 0 | 4977 | 889 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 220 | 0 | 504 | 890 | 0 | 5239 | 10216 | 100.69
Total KWH | 0 | 502080 | 257280 | 0 | 0 | 0 | 0 | 0 | 8794800 | 0 | 8090240 | 128880 | 0 | 797472 | 122400 | 2378869 | 64563 | 135248 | 514080 | 0 | 1141800 | 0 | 0 | 0 | 104240 | 6998694 | 0 | 0 | 214285 | 121200 | 396000 | 555480 | 0 | 0 | 148036 | 70255 | 0 | 0 | 94080 | 388862 | 308614 | 22201 | 200640 | 308160 | 21602 | 2075000 | 462509 | 342240 | 15338181.82 | 0 | 0 | 209760 | 0 | 1200182 | 5283716 | 0 | 0 | 0 | 12949089 | 135000 | 21592 | 901600 | 0 | 7992000 | 0 | 2168000 | 408960 | 4661000 | 352512 | 245760 | 0 | 1486560 | 0 | 313420 | 0 | 2225280 | 0 | 500145 | 46272 | 7553500 | 0 | 9149000 | 0 | 720600 | 3633791 | 36168 | 0 | 1577280 | 715968 | 0 | 107000 | 4330810 | 33840 | 1062000 | 295200 | 588480 | 14700 | 326750 | 0 | 122343926.82 | 21152000 | 4385952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530640 | 23680000 | 0 | 15502980 | 0 | 149010 | 0 | 286272 | 397632 | 0 | 0 | 34838 | 0 | 399668 | 695217 | 113106 | 0 | 430496 | 4307273 | 0 | 0 | 0 | 0 | 0 | 8975854 | 0 | 37500 | 0 | 431563 | 597594 | 231024 | 438816 | 0 | 0 | 0 | 37193.88 | 1223280 | 3586 | 20160 | 0 | 1993000 | 5277800 | 0 | 10189091 | 19412900 | 86400 | 121020845.88 | 243364772.7

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10494.94 | MW | 12:00 Hr. | Energy Generated |  |  | 243.3648 |  | MKWHr.
| Day Peak Demand |  |  | 10494.94 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.03 |  | MKWHr.
| Evening Peak Generation |  |  | 11785.3 | MW | 18:00 Hr. | Energy Demand |  |  | 243.3948 |  | MKWHr.
| Evening Peak Demand |  |  | 11816.3 | MW | 18:00 Hr. | Maximum Temperature |  |  | 32.2 |  | °C
| Minimum Generation of the Day |  |  | 8163.18 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 726.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 11785.3 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.8695 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.977 | 0 | 5.1263 | 0 | 0 | 0.21429 | 0 | 0 | 31.3176 | Gas | 100.8729 | Gas | 355405728.43
| Chattogram Zone |  |  | 5.626 | 28.2873 | 3.3192 | 0 | 2.075 | 0.1566 | 0 | 0.09408 | 39.5581 | Coal | 82.0008 | Coal | 524944590.6254
| Cumilla Zone |  |  | 15.9175 | 0 | 2.6802 | 0 | 0 | 0.50014 | 2.2253 | 0 | 21.3231 | HFO | 14.6406 | HFO | 249297065.71
| Mymensingh Zone |  |  | 0.58848 | 0 | 1.391 | 0 | 0 | 0.34145 | 0 | 0 | 2.321 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.8241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.8241 | Hydro | 2.075 | Hydro | 207500
| Khulna Zone |  |  | 4.386 | 23.68 | 0 | 0 | 0 | 0.53064 | 21.152 | 0 | 49.7486 | Solar | 4.8011 | Solar | 76891330.6448
| Barishal Zone |  |  | 7.2708 | 29.602 | 0.10656 | 0 | 0 | 0.003586 | 0 | 0 | 36.9829 | Import | 38.8803 | Import | 220289616.6
| Rajshahi Zone |  |  | 13.2831 | 0 | 0.98086 | 0 | 0 | 1.5629 | 15.503 | 0 | 31.3298 | Wind | 0.09408 | Wind | 1383916.8
| Rangpur Zone |  |  | 0 | 0.43156 | 1.0364 | 0 | 0 | 1.4915 | 0 | 0 | 2.9595
| Total |  |  | 100.8729 | 82.0008 | 14.6406 | 0 | 2.075 | 4.8011 | 38.8803 | 0.09408 | 243.3648
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 355405728.43 |  | Hydro | 207500
|  |  |  | Coal | 524944590.6254 |  | Solar | 76891330.6448
|  |  |  | HFO | 249297065.71 |  | Import | 220289616.6
|  |  |  | HSD | 0 |  | Wind | 1383916.8
[5 empty] | Total: | 142,84,19,748 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.152 | Peak Hr Flow | 889.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47426200.06 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.503 | Peak Hr Flow | 758.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2043 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2253 | Peak Hr Flow | 104.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2715 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 38.8803 | Peak Hr Flow | 1751.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4577
|  |  |  | Chattogram |  | 0 |  | 1384
|  |  |  | Cumilla |  | 0 |  | 1029
|  |  |  | Mymensingh |  | 30 |  | 868
|  |  |  | Sylhet |  | 0 |  | 438
|  |  |  | Khulna |  | 0 |  | 1276
|  |  |  | Barishal |  | 0 |  | 322
|  |  |  | Rajshahi |  | 0 |  | 1006
|  |  |  | Rangpur |  | 0 |  | 761
|  |  |  | Total |  | 30 |  | 11661
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:13 | 16:48 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual Maintenance Work.
| 08:14 | 16:47 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual Maintenance Work.
| 08:16 | 15:49 | Bheramara P/S-Faridpur 132 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to
AnnualMaintennance
| 08:17 | 16:38 | Chapai 132/33kV S/S Chapai Rahanpur ckt 2 Scheduled S/D Due to Annual maintenance
| 08:20 | 15:50 | Bheramara P/S-Faridpur 132 kV Ckt-2 Scheduled S/D from Bheramara 230/132kV end Due to
AnnualMaintennance
| 08:21 | 16:07 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance and from Barapukuria 230/132/33kV end Due to Annual maintenance for dead line
cheeking.
| 08:21 | 16:15 | Baroirhat 132/33kV S/S TR-2, 416T HT Scheduled S/D Due to Annual Maintenance
| 08:22 | 15:36 | Madaripur-Shariatpur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to Annual
maintaince and from Shariatpur 132/33kV end Due to Annual Maintenance.
| 08:26 | 16:38 | Bibiana 400/230kV S/S ICT-01 LT Scheduled S/D
| 08:26 | 16:38 | Bibiana 400/230kV S/S ICT-01 HT Scheduled S/D
| 08:29 | 16:38 | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 Scheduled S/D Due to
Annual Maintenance
| 08:33 | 15:49 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Scheduled S/D Due to Annual maintenance
| 08:34 | 15:48 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Scheduled S/D Due to Annual maintenance
| 08:35 | 14:49 | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to Annual Maintenance work.
| 08:36 | 15:49 | Rajbari 132/33kV S/S Bheramara-2 Scheduled S/D Due to l Annual Maintenance work.
| 08:39 | 17:59 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end. and from
Gopalganj 400/132kV end Due to Annual Maintenance
| 08:39 | 17:29 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Scheduled S/D Due to From Other End
| 08:43 | 14:48 | Shyampur-Shyampur(New) 132kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to | [7 empty] | 50.0MW load
|  |  | normalize 132 kV Shyampur Ckt-2 (Jumper out from 132kV Shyampur Ckt-1) | [7 empty] | interrup. Shyampur
230/132kV end
| 08:48 | 16:35 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR-01(AB) shutdown for annual
maintenance
| 08:48 | 16:35 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR-01(AB) shutdown for annual
maintenance
| 08:49 | 16:24 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to A/N
| 08:51 | 11:12 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -01 Scheduled S/D Due to due to silicon paint
work outside the GIS building wall.
| 08:51 | 17:33 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 08:51 | 15:54 | Tangail 132/33kV S/S Tr-3 LT Scheduled S/D Due to annual Maintenance
| 08:52 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- Plant
| 08:52 | 15:54 | Tangail 132/33kV S/S Tr-3 HT Scheduled S/D Due to annual Maintenance
| 08:55 | 16:37 | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Yearly
maintenance work. and from Mongla 132/33kV end Due to Annual Maintenance
| 08:58 | 16:15 | Sonargaon 132/33kV S/S BUS A Scheduled S/D Due to Annual Maintenance
| 09:02 | 15:28 | Palashbari 132/33kV S/S TR4-434T LT Scheduled S/D Due to Annual Maintenance
| 09:03 | 15:27 | Palashbari 132/33kV S/S TR4-434T HT Scheduled S/D Due to Annual Maintenance
| 09:07 | 16:34 | Jhenaidah-Magura 132 kV Ckt-2 Scheduled S/D from Magura 132/33kV end Due to Annual
Maintenance.
| 09:09 | 17:32 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance
| 09:11 |  | Shyampur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to SF6 Gas change.
| 09:12 |  | Shyampur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to SF6 Gas change.
| 09:28 | 17:27 | Haripur-Haripur (360MW) 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to
Annual Maintenance
| 09:30 | 16:06 | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to OUR of annual Maintenance.
| 09:30 | 16:08 | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to Purpose of Annual Maintenance
| 09:40 | 17:03 | New Tongi S/S T2(413T) HT Scheduled S/D Due to Annual Maintenance
| 09:45 | 15:50 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance work
| 09:45 | 15:50 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance work
| 09:49 | 16:24 | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Annual
Maintenance Work and from Haripur 230/132kV end Due to From Other End
| 09:54 | 19:33 | Gopalganj 400/132kV S/S 230kV Barisal CKT-01 Project Work S/D Due to G2G Project work
| 09:55 | 19:34 | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 Project Work S/D Due to G2G Project work
| 09:56 | 19:31 | Barishal 230/132kV S/S Gopalgonj CKT-1 Project Work S/D Due to Barishal (N) -Patuakhali
230 kv line conductor stringing purpose Gopalgonj ckt-1 shutdown.
| 09:56 | 19:34 | Barishal 230/132kV S/S Gopalgonj CKT-2 Project Work S/D Due to Barishal (N) -Patuakhali
230 kv line conductor stringing purpose Gopalgonj ckt-2 shutdown.
| 09:59 | 15:24 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Scheduled S/D Due to Annual
Maintenance work.
| 10:16 | 13:55 | Bajitpur 132/33kV S/S 132 kV Bus-1 Scheduled S/D Due to Annual maintenance
| 10:20 | 16:51 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end.
| 10:45 | 10:58 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing 33kv over current earth fault relay
relays Due to Pbs's Madhabpur-3 and Chunarughat 33 kv Feeder Trip
| 10:59 | 11:08 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing 33 kv OC/EF relays Due to PBS's
Shayestaganj 33 kv feeder Trip
| 10:59 | 14:40 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual Maintenance
|  | 11:06 | Sunamganj 132/33kV S/S Tr-2 HT is restored.
| 11:15 | 12:59 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -02 Scheduled S/D Due to Due to paint work
outside the GIS building wall.
| 11:18 |  | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to due to shutdown oil leakage
check and transformer oil top up .
| 12:00 |  | Day peak Generation is 10491 MW
|  | 13:33 | Khulna (C) S/S Tr-2 415 T HT is restored.
|  | 15:08 | Baroaulia-Khulshi 132 kV Ckt-1 is restored.
|  | 15:09 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 is restored.
| 16:57 | 23:13 | Halishahar 132/33kV S/S 405T(TR-1) HT Tripped showing F87T-1 & F87T-2 relays Due to 33 kv | [7 empty] | 20.0MW load
|  |  | XLPE(R-phase) cable punctured. | [7 empty] | interrup.
| 16:57 | 23:15 | Halishahar 132/33kV S/S 405T(TR-1) LT Tripped showing F-51 relays Due to 33 Kv | [7 empty] | 20.0MW load
|  |  | XLPE(R-phase) Cable punctured. | [7 empty] | interrup.
|  | 17:01 | Dohazari-Sikalbaha 132 kV Ckt-1 is restored.
| 18:00 |  | Evening Peak Generation: 11784 MW.
| 05:00 |  | Minimum Generation: 8247 MW.
| 06:05 |  | Rahanpur 400/132kV S/S Rahanpur-Monakasha 400KV Line ckt-02 Scheduled S/D
| 06:11 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- ST
| 06:11 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST sd-0611 ON 19.11.25
| 07:16 |  | Narail 132/33kV S/S Auxiliary TR 1 HT Scheduled S/D Due to Looping connection of new | [7 empty] | 20.0MW load
|  |  | section DS of 33 kv bay extension work. | [7 empty] | interrup.
| 07:16 |  | Narail 132/33kV S/S Auxiliary TR 1 LT Scheduled S/D Due to Looping connection of new | [7 empty] | 20.0MW load
|  |  | section DS of 33 kv bay extension work | [7 empty] | interrup.
| 07:20 |  | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance. and from Bhulta 400/230kVend.
| 07:37 |  | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
R-Phase wire armouring.
| 07:51 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Scheduled S/D Due to Annual Maintenance
Work
| 07:52 |  | Nawabganj 132/33kV S/S 132kV Main Bus-1 Scheduled S/D Due to Annual maintenance
| 07:52 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Scheduled S/D Due to Annual Maintenance
Work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 377 | 8794800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 1141800 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 26 | 64563 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 6998694 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 128880 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 75 | 122400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 3 | 135248 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 104240 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22.8 | 396000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 555480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 257280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 270 | 2378869 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 92 | 797472 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 502080 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 514080 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 214285 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Shutdown due to maintenance
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 500 | 8090240 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 121200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1961.3 | 31317611
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 135000 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 209760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2075000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5283716 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under Maintenance
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 80 | 1200182 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 55 | 308614 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 388862 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 200640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 342240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 70255 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 7 | 22201 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 61 | 462509 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 308160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 148036 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12949089 | U-2 Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 94080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15338181.82 | machine problem
Chattogram Area Total |  |  |  |  | 4895.723 | 1935 | 39558127.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 205 | 4661000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 2168000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 365 | 7992000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 27 | 352512 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 41 | 408960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 0 | 21592 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 103 | 901600 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 46272 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Schedule Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 132 | 1486560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 104 | 2225280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 313420 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 43 | 245760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 500145 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1067 | 21323101
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 12 | 588480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 295200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 1062000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 326750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 33840 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 105 | 2320970
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720600 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3633791 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715968 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1577280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 4330810 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 107000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 36168 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7553500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 9149000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1179 | 27824117
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 889 | 21152000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 160 | 4385952 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 530640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1094 | 23680000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2143 | 49748592
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 501 | 10189091 | machine problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 6 | 20160 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 50 | 1993000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 865 | 19412900 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5277800 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 86400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3586 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1659 | 36982937
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 399668 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 149010 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 34838 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 4307273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8975854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 113106 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 81 | 397632 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 90 | 286272 | Under Maintenance
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 37500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 758 | 15502980 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 430496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 695217 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1572 | 31329846
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 431563 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 74 | 438816 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37193.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 597594 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 231024 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1223280 | -
Rangpur Area Total |  |  |  |  | 950 | 164 | 2959470.88
Eastern Grid Total |  |  |  |  | 17383.855 | 6247.3 | 122343926.82
Western Grid Total |  |  |  |  | 10821.56 | 5538 | 121020845.88
National Grid Total |  |  |  |  | 28205.415 | 11785.3 | 243364772.7
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8265.82 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3364.2 | MW
i) Dhaka area |  |  | 4576.84 |  | MW | i) Khulna area |  |  |  | 1275.6 | MW
ii) Chattogram area |  |  | 1383.7 |  | MW | ii) Barishal area |  |  |  | 322 | MW
iii) Cumilla area |  |  | 1029.28 |  | MW | iii) Rajshahi area |  |  |  | 1005.6 | MW
iv) Mymensingh area |  |  | 838 |  | MW | iv) Rangpur area |  |  |  | 761 | MW
v) Sylhet area |  |  | 438 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11630.02 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 65 | 18:00 | 133 | Niamatpur | 41 | 18:00
2 | AKSML | 136 | 05:00 | 68 | Ishurdi | 59 | 18:30 | 134 | Noapara | 37 | 18:00
3 | Aftabnagar | 32 | 18:00 | 69 | Jaldhaka | 62 | 18:00 | 135 | PHP | 8 | 20:00
4 | Agargaon | 110 | 13:00 | 70 | Jamalpur | 81 | 22:00 | 136 | Pabna | 73 | 18:00
5 | Agrabad | 88 | 18:00 | 71 | Jashore | 100 | 18:00 | 137 | Palashbari | 86 | 18:00
6 | Amnura | 16 | 07:00 | 72 | Jhenaidah | 99 | 18:00 | 138 | Panchagarh | 45 | 18:00
7 | Ashuganj | 66 | 16:00 | 73 | Joydebpur | 133 | 18:00 | 139 | Patiya | 7.7 | 18:00
8 | BSRM | 205 | 23:00 | 74 | Joypurhat | 41 | 18:00 | 140 | Patuakhali | 56 | 21:00
9 | Bagerhat | 61 | 19:30 | 75 | Juldah | 15 | 15:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 57 | 19:30 | 76 | KSRM | 31 | 08:00 | 142 | Postogola | 55 | 13:00
11 | Bakulia | 74 | 18:00 | 77 | Kabirpur | 199 | 18:00 | 143 | Purbachal | 30 | 15:00
12 | Banani | 39.8 | 13:00 | 78 | Kachua | 61 | 18:00 | 144 | Purbasadipur | 100 | 18:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kallyanpur | 90 | 12:00 | 145 | Rahanpur | 21 | 18:00
14 | Barapukuria | 49 | 18:00 | 80 | Kalurghat | 46 | 15:00 | 146 | Rahim | 38 | 16:00
15 | Barguna | 0 | 00:00 | 81 | Kamrangirchar | 69 | 13:00 | 147 | Rajbari | 58 | 18:00
16 | Barishal | 92 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 109 | 19:00
17 | Barishal-230 | 66 | 18:00 | 83 | Kasba | 24 | 18:30 | 149 | Rajshahi | 80 | 13:00
18 | Baroaulia | 57 | 13:00 | 84 | Kazla | 92 | 12:00 | 150 | Rajshahi-230 | 52 | 13:00
19 | Baroirhat | 44 | 18:00 | 85 | Keranigonj | 69 | 18:00 | 151 | Ramganj | 68 | 19:30
20 | Bashundhara | 162 | 12:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 46 | 18:30
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 50 | 13:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 50 | 18:00 | 88 | Khulshi | 156 | 18:30 | 154 | Rangpur | 113 | 18:00
23 | Benapole | 40 | 18:00 | 89 | Kishoreganj | 86 | 18:00 | 155 | Ruppur | 3.6 | 15:00
24 | Bhaluka | 134 | 18:00 | 90 | Kodda | 279 | 15:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 40 | 21:00 | 91 | Kulaura | 31 | 18:00 | 157 | Saidpur | 85 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 44 | 18:00 | 158 | Satkhira | 85 | 18:00
27 | Bheramara(GK) | 43 | 18:00 | 93 | Kushtia | 113 | 18:00 | 159 | Satmasjid | 81 | 13:00
28 | Bhulta | 196 | 11:00 | 94 | Laksam | 22 | 18:00 | 160 | Savar | 188 | 15:00
29 | Bog-Sherpur | 58 | 18:00 | 95 | Lakshmipur | 20 | 18:00 | 161 | SevenRings | 13.16 | 03:00
30 | Bogura | 115 | 14:00 | 96 | Lalbag | 60 | 18:00 | 162 | ShahCement | 29 | 00:00
31 | Borhanuddin | 64 | 21:00 | 97 | Lalmonirhat | 41 | 18:00 | 163 | Shahjadpur | 59 | 18:00
32 | Brahmanbaria | 95 | 18:00 | 98 | MI_Cement | 15.1 | 23:00 | 164 | Shahjibazar | 88 | 18:00
33 | Cantonment | 102 | 13:00 | 99 | Madanganj | 40 | 18:00 | 165 | Shahmirpur | 44 | 18:00
34 | Chandina | 9.74 | 14:00 | 100 | Madaripur | 74 | 18:00 | 166 | Shariatpur | 52 | 21:00
35 | Chandpur | 54 | 18:00 | 101 | Madartek | 62 | 13:00 | 167 | Sherpur | 102 | 07:00
36 | Chandraghona | 29 | 17:00 | 102 | Madunaghat | 43 | 18:00 | 168 | Shikalbaha | 28 | 18:30
37 | Chapai | 42 | 13:00 | 103 | Magura | 44 | 18:00 | 169 | Shitalakhya | 69.3 | 12:00
38 | Charsaidpur | 36 | 00:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 40 | 16:00
39 | Chauddagram | 47 | 14:00 | 105 | Maijdee | 27 | 20:00 | 171 | Shyampur | 116 | 23:00
40 | Chhatak | 23 | 18:00 | 106 | Manikganj | 94 | 18:00 | 172 | Siddhirganj | 107 | 18:00
41 | Chowmuhani | 113 | 18:00 | 107 | Maniknagar | 60 | 18:00 | 173 | Sirajganj | 82 | 18:30
42 | Chuadanga | 79 | 18:00 | 108 | Matarbari | 44 | 18:00 | 174 | Sonargaon | 108 | 16:00
43 | Coxsbazar | 130 | 18:00 | 109 | Matuail | 66 | 12:00 | 175 | Sreemongol | 58 | 21:00
44 | Cumilla(N) | 83 | 18:30 | 110 | Metrorail_Motijheel | 24 | 10:00 | 176 | Sreepur | 90 | 12:00
45 | Cumilla(S) | 137 | 14:00 | 111 | Metrorail_Uttara | 8 | 11:00 | 177 | Srinagar | 32.1 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 99 | 15:00 | 178 | Sunamganj | 42 | 18:00
47 | Daudkandi | 114 | 20:00 | 113 | Mirpur | 123 | 18:30 | 179 | Sylhet | 43 | 18:00
48 | DhakaUniversity | 66 | 12:00 | 114 | Mirsorai | 8 | 11:00 | 180 | Sylhet-132 | 85 | 17:00
49 | Dhamrai | 110 | 18:00 | 115 | Mirzapur | 37 | 18:00 | 181 | TK | 19 | 18:00
50 | Dhanmondi | 87 | 13:00 | 116 | Mithapukur | 44 | 18:00 | 182 | Tangail | 127 | 18:00
51 | Dohazari | 82 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 16 | 18:00
52 | Faridpur | 118 | 18:30 | 118 | Mogbazar | 75.8 | 14:00 | 184 | Thakurgaon | 76 | 18:00
53 | Fatullah | 101 | 11:00 | 119 | Mongla | 28 | 18:00 | 185 | Tongi | 105 | 18:00
54 | Fenchuganj | 23 | 17:00 | 120 | Motijheel | 31 | 12:00 | 186 | Ullahpara | 28 | 07:00
55 | Feni | 91 | 18:30 | 121 | Muktagacha | 26 | 07:00 | 187 | Ullon | 49 | 13:00
56 | GPH | 95 | 11:00 | 122 | Munshiganj | 76 | 13:00 | 188 | Uttara | 69 | 13:00
57 | Ghatail | 56 | 07:00 | 123 | Muradnagar | 26 | 18:30 | 189 | UttaraNew | 36 | 14:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 125 | 18:00 | 190 | Zigatola | 53 | 14:00
59 | Ghorashal-230 | 80 | 19:30 | 125 | Naogaon | 82 | 18:00
60 | Goalpara | 24 | 12:00 | 126 | Narail | 42 | 18:00
61 | Gollamari | 78 | 13:00 | 127 | Narinda | 58 | 13:00
62 | Gopalganj | 76.6 | 18:00 | 128 | Narshingdi | 140 | 18:30
63 | Gulshan | 108 | 14:00 | 129 | Natore | 97 | 18:00
64 | Halishahar | 65 | 15:00 | 130 | Nawabganj | 29.8 | 21:00
65 | HaripurSBU | 150 | 09:00 | 131 | Netrakona | 101 | 18:30
66 | Hasnabad | 76 | 12:00 | 132 | New | 64 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9731.34 | 0 |  | 9731.34
1:00 | 9258.6 | 0 |  | 9258.6
2:00 | 8772.41 | 0 |  | 8772.41
3:00 | 8467.18 | 0 |  | 8467.18
4:00 | 8289.6 | 0 |  | 8289.6
5:00 | 8163.18 | 0 |  | 8163.18
6:00 | 8455.76 | 0 |  | 8455.76
7:00 | 9311.18 | 0 |  | 9311.18
8:00 | 9661.83 | 0 |  | 9661.83
9:00 | 9530.55 | 0 |  | 9530.55
10:00 | 9524.97 | 0 |  | 9524.97
11:00 | 10107.98 | 0 |  | 10107.98
12:00 | 10494.94 | 0 |  | 10494.94
13:00 | 10870.05 | 0 |  | 10870.05
14:00 | 10498.48 | 0 |  | 10498.48
15:00 | 10445.17 | 0 |  | 10445.17
16:00 | 10373.74 | 0 |  | 10373.74
17:00 | 10637.37 | 0 |  | 10637.37
18:00 | 11785.3 | 30 |  | 11816.3
19:00 | 11375.5 | 0 |  | 11375.5
19:30 | 11287 | 0 |  | 11287
20:00 | 11240 | 0 |  | 11240
21:00 | 11004 | 0 |  | 11004
22:00 | 10618 | 0 |  | 10618
23:00 | 10216 | 0 |  | 10216
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4718 | 5013.34 | 9731.34 | DAILY GENERATION CURVE
00:30 | 4684 | 4810.97 | 9494.97
01:00 | 4650 | 4608.6 | 9258.6 | 18-11-2025
01:30 | 4566.5 | 4449.005 | 9015.505
02:00 | 4483 | 4289.41 | 8772.41
02:30 | 4452.5 | 4167.295 | 8619.795
03:00 | 4422 | 4045.18 | 8467.18
03:30 | 4364.5 | 4013.89 | 8378.39
04:00 | 4307 | 3982.6 | 8289.6
04:30 | 4296.5 | 3929.89 | 8226.39
05:00 | 4286 | 3877.18 | 8163.18
05:30 | 4364 | 3945.47 | 8309.47
06:00 | 4442 | 4013.76 | 8455.76
06:30 | 4561.845 | 4321.625 | 8883.47
07:00 | 4681.69 | 4629.49 | 9311.18
07:30 | 4697.68 | 4788.825 | 9486.505
08:00 | 4713.67 | 4948.16 | 9661.83
08:30 | 4612.22 | 4983.97 | 9596.19
09:00 | 4510.77 | 5019.78 | 9530.55
09:30 | 4600.755 | 4927.005 | 9527.76
10:00 | 4690.74 | 4834.23 | 9524.97
10:30 | 4791.25 | 5025.225 | 9816.475
11:00 | 4891.76 | 5216.22 | 10107.98
11:30 | 4955.86 | 5345.6 | 10301.46
12:00 | 5019.96 | 5474.98 | 10494.94
12:30 | 5220.815 | 5461.68 | 10682.495
13:00 | 5421.67 | 5448.38 | 10870.05
13:30 | 5401.305 | 5282.96 | 10684.265
14:00 | 5380.94 | 5117.54 | 10498.48
14:30 | 5395.825 | 5076 | 10471.825
15:00 | 5410.71 | 5034.46 | 10445.17
15:30 | 5391.84 | 5017.615 | 10409.455
16:00 | 5372.97 | 5000.77 | 10373.74
16:30 | 5472.915 | 5032.64 | 10505.555
17:00 | 5572.86 | 5064.51 | 10637.37
17:30 | 5910.08 | 5301.255 | 11211.335
18:00 | 6247.3 | 5538 | 11785.3
18:30 | 6055.9 | 5524.5 | 11580.4
19:00 | 5864.5 | 5511 | 11375.5
19:30 | 5748 | 5539 | 11287
20:00 | 5749 | 5491 | 11240
20:30 | 5646 | 5476 | 11122 |  | Executive Engineer
21:00 | 5543 | 5461 | 11004 |  | Network Operation Division
21:30 | 5408.5 | 5402.5 | 10811
22:00 | 5274 | 5344 | 10618
22:30 | 5125.5 | 5291.5 | 10417
23:00 | 4977 | 5239 | 10216

## En-Curve
QF-LDC-12
Date | 18-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2980 | 1322 | 863 | 0 | 84 | 752.34 | 86 | 3565 | 0 | 0 | 78 | 0 | 0 | 1 | 0 | DAILY ENERGY CURVE
00:30 | 2960.5 | 1319 | 862.5 | 0 | 84 | 687.47 | 86 | 3436 | 0 | 0 | 56.5 | 0 | 0 | 3 | 0 | 18-11-2025
01:00 | 2941 | 1316 | 862 | 0 | 84 | 622.6 | 86 | 3307 | 0 | 0 | 35 | 0 | 0 | 5 | 0
01:30 | 2944 | 1288 | 862.5 | 0 | 84 | 575.005 | 86 | 3149 | 0 | 0 | 21.5 | 0 | 0 | 5.5 | 0 | Energy Generated | 243.3648 |  | MKWHr
02:00 | 2947 | 1260 | 863 | 0 | 84 | 527.41 | 86 | 2991 | 0 | 0 | 8 | 0 | 0 | 6 | 0 | Energy not Served | 0.03 |  | MKWHr
02:30 | 2951.5 | 1260.5 | 863 | 0 | 83 | 474.795 | 86 | 2887 | 0 | 0 | 8 | 0 | 0 | 6 | 0 | Total Energy Requirement | 243.3948 |  | MKWHr
03:00 | 2956 | 1261 | 863 | 0 | 82 | 422.18 | 86 | 2783 | 0 | 0 | 8 | 0 | 0 | 6 | 0
03:30 | 2938 | 1236.5 | 862.5 | 0 | 80 | 428.89 | 86 | 2736 | 0 | 0 | 4 | 0 | 0 | 6.5 | 0
04:00 | 2920 | 1212 | 862 | 0 | 78 | 435.6 | 86 | 2689 | 0 | 0 | 0 | 0 | 0 | 7 | 0
04:30 | 2881 | 1199 | 862.5 | 0 | 75 | 436.39 | 86 | 2677.5 | 0 | 0 | 0 | 0 | 0 | 9 | 0
05:00 | 2842 | 1186 | 863 | 0 | 72 | 437.18 | 86 | 2666 | 0 | 0 | 0 | 0 | 0 | 11 | 0
05:30 | 2912.5 | 1203 | 863 | 0 | 75 | 438.97 | 86 | 2721 | 0 | 0 | 0 | 0 | 0 | 10 | 0
06:00 | 2983 | 1220 | 863 | 0 | 78 | 440.76 | 86 | 2776 | 0 | 0 | 0 | 0 | 0 | 9 | 0
06:30 | 3071.5 | 1200 | 863 | 0 | 78 | 503.905 | 86 | 3021 | 32.065 | 1 | 20 | 0 | 0 | 7 | 0
07:00 | 3160 | 1180 | 863 | 0 | 78 | 567.05 | 86 | 3266 | 64.13 | 2 | 40 | 0 | 0 | 5 | 0
07:30 | 3067.5 | 1135 | 863 | 0 | 84 | 594.55 | 86 | 3344 | 184.955 | 26 | 99 | 0 | 0 | 2.5 | 0
08:00 | 2975 | 1090 | 863 | 0 | 90 | 622.05 | 86 | 3422 | 305.78 | 50 | 158 | 0 | 0 | 0 | 0
08:30 | 2859 | 1104 | 862.5 | 0 | 89 | 627.085 | 86 | 3329 | 405.105 | 62 | 172.5 | 0 | 0 | 0 | 0
09:00 | 2743 | 1118 | 862 | 0 | 88 | 632.12 | 86 | 3236 | 504.43 | 74 | 187 | 0 | 0 | 0 | 0
09:30 | 2788 | 1118.5 | 862 | 0 | 92 | 584.58 | 86 | 3147 | 568.18 | 78.5 | 203 | 0 | 0 | 0 | 0
10:00 | 2833 | 1119 | 862 | 0 | 96 | 537.04 | 86 | 3058 | 631.93 | 83 | 219 | 0 | 0 | 0 | 0
10:30 | 2926 | 1126.5 | 862.5 | 0 | 97 | 577.895 | 86 | 3159.5 | 669.08 | 83 | 229 | 0 | 0 | 0 | 0
11:00 | 3019 | 1134 | 863 | 0 | 98 | 618.75 | 86 | 3261 | 706.23 | 83 | 239 | 0 | 0 | 0 | 0
11:30 | 3016.5 | 1124.5 | 865 | 0 | 98 | 658.335 | 86 | 3394 | 713.125 | 83.5 | 262 | 0 | 0 | 0.5 | 0
12:00 | 3014 | 1115 | 867 | 0 | 98 | 697.92 | 86 | 3527 | 720.02 | 84 | 285 | 0 | 0 | 1 | 0
12:30 | 2973 | 1114 | 866.5 | 0 | 100 | 725.96 | 86 | 3519.5 | 699.035 | 88.5 | 507.5 | 0 | 0 | 2.5 | 0
13:00 | 2932 | 1113 | 866 | 0 | 102 | 754 | 86 | 3512 | 678.05 | 93 | 730 | 0 | 0 | 4 | 0
13:30 | 2860 | 1113.65 | 871 | 0 | 104 | 754.5 | 86 | 3385.5 | 622.615 | 108.5 | 773.5 | 0 | 0 | 5 | 0
14:00 | 2788 | 1114.3 | 876 | 0 | 106 | 755 | 86 | 3259 | 567.18 | 124 | 817 | 0 | 0 | 6 | 0
14:30 | 2830.5 | 1141.9 | 877 | 0 | 106 | 755 | 86 | 3241.5 | 485.425 | 122.5 | 821 | 0 | 0 | 5 | 0
15:00 | 2873 | 1169.5 | 878 | 0 | 106 | 755 | 86 | 3224 | 403.67 | 121 | 825 | 0 | 0 | 4 | 0
15:30 | 2919.5 | 1177 | 883 | 0 | 106 | 757.5 | 86 | 3306 | 287.205 | 117.5 | 763.25 | 0 | 0 | 6.5 | 0
16:00 | 2966 | 1184.5 | 888 | 0 | 106 | 760 | 86 | 3388 | 170.74 | 114 | 701.5 | 0 | 0 | 9 | 0
16:30 | 2893.5 | 1181.25 | 888.5 | 0 | 103 | 760.5 | 86 | 3464 | 90.305 | 233 | 799 | 0 | 0 | 6.5 | 0
17:00 | 2821 | 1178 | 889 | 0 | 100 | 761 | 86 | 3540 | 9.87 | 352 | 896.5 | 0 | 0 | 4 | 0
17:30 | 2888.5 | 1282.4 | 889 | 0 | 102 | 759.5 | 86 | 3631 | 4.935 | 401.5 | 1160 | 0 | 0 | 6.5 | 15
18:00 | 2956 | 1386.8 | 889 | 0 | 104 | 758 | 86 | 3722 | 0 | 451 | 1423.5 | 0 | 0 | 9 | 30
18:30 | 2896 | 1351.4 | 889 | 0 | 98 | 755.5 | 86 | 3699 | 0 | 301 | 1497.5 | 0 | 0 | 7 | 15
19:00 | 2836 | 1316 | 889 | 0 | 92 | 753 | 86 | 3676 | 0 | 151 | 1571.5 | 0 | 0 | 5 | 0
19:30 | 2853 | 1314.5 | 889 | 0 | 92 | 758 | 86 | 3760 | 0 | 139 | 1390.5 | 0 | 0 | 5 | 0
20:00 | 2867 | 1299.5 | 890 | 0 | 92 | 757 | 86 | 3763 | 0 | 131 | 1351.5 | 0 | 0 | 3 | 0
20:30 | 2885.5 | 1312.5 | 889.5 | 0 | 94 | 762.5 | 86 | 3767.5 | 0 | 119.5 | 1203 | 0 | 0 | 2 | 0
21:00 | 2904 | 1325.5 | 889 | 0 | 96 | 768 | 86 | 3772 | 0 | 108 | 1054.5 | 0 | 0 | 1 | 0
21:30 | 2900.5 | 1316.5 | 889 | 0 | 97 | 769 | 86 | 3768.5 | 0 | 84 | 900 | 0 | 0 | 0.5 | 0
22:00 | 2897 | 1307.5 | 889 | 0 | 98 | 770 | 86 | 3765 | 0 | 60 | 745.5 | 0 | 0 | 0 | 0
22:30 | 2906 | 1313.75 | 889 | 0 | 96 | 769 | 86 | 3775 | 0 | 30 | 551.75 | 0 | 0 | 0.5 | 0
23:00 | 2915 | 1320 | 889 | 0 | 94 | 768 | 86 | 3785 | 0 | 0 | 358 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 05:00 | 381 | 12:00 | Meghnaghat | 397 | 05:00 | 382 | 12:00
Ashuganj | 404 | 5:00 | 383 | 12:00 | Payra | 416 | 03:00 | 410 | 12:00
Bhulta | 400 | 05:00 | 379 | 12:00 | Rahanpur | 415 | 05:00 | 404 | 12:00
Bibiana | 399 | 05:00 | 390 | 12:00 | Rampal | 414 | 05:00 | 400 | 16:00
BIPTC | 404 | 03:00 | 391 | 18:00
Bogura | 409 | 05:00 | 395 | 16:00
Gopalganj | 408 | 05:00 | 394 | 12:00
Kaliakoir | 393 | 04:00 | 378 | 12:00
Korerhat | 402 | 03:00 | 393 | 11:00
Madunaghat | 400 | 05:00 | 392 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 05:00 | 226 | 12:00 | Kachua | 237 | 19:00 | 228 | 11:00
AKSML | 236 | 03:00 | 231 | 11:00 | Kaliakoir | 237 | 03:00 | 227 | 12:00
Aminbazar | 243 | 09:00 | 228 | 15:00 | Keranigonj | 236 | 04:00 | 224 | 12:00
Ashuganj | 236 | 05:00 | 223 | 12:00 | Khulna(S) | 241 | 03:00 | 231 | 13:00
Ashuganj-400 | 236 | 05:00 | 223 | 12:00 | Korerhat | 237 | 05:00 | 231 | 11:00
Baghabari | 237 | 04:00 | 230 | 12:00 | Madunaghat | 237 | 07:00 | 233 | 11:00
Barapukuria | 225 | 19:00 | 212 | 07:00 | Madunaghat-400 | 237 | 7:00 | 232 | 12:00
Barapukuria-230 | 225 | 19:00 | 212 | 07:00 | Maniknagar | 230 | 05:00 | 220 | 12:00
Barishal | 240 | 03:00 | 234 | 12:00 | Meghnaghat | 236 | 00:00 | 228 | 12:00
Bheramara | 236 | 05:00 | 227 | 12:00 | Meghnaghat-400 | 234 | 05:00 | 223 | 12:00
Bhulta | 232 | 04:00 | 219 | 12:00 | Mirsorai | 233 | 02:00 | 221 | 12:00
Bibiana | 237 | 05:00 | 228 | 12:00 | Rajshahi | 237 | 06:00 | 226 | 12:00
BIPTC | 240 | 04:00 | 227 | 16:00 | Rampal | 239 | 05:00 | 229 | 12:00
Bogura | 237 | 03:00 | 229 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 237 | 05:00 | 228 | 16:00 | Rampura | 232 | 05:00 | 218 | 12:00
Borhanuddin | 242 | 06:00 | 238 | 13:00 | Shikalbaha | 237 | 18:00 | 231 | 00:00
BSRM | 234 | 05:00 | 227 | 12:00 | Shyampur | 234 | 04:00 | 222 | 12:00
Cumilla(N) | 234 | 04:00 | 223 | 11:00 | Siddhirganj | 232 | 04:00 | 224 | 14:00
Faridpur | 241 | 04:00 | 231 | 12:00 | Sirajgonj | 241 | 3:00 | 235 | 12:00
Fenchuganj | 238 | 03:00 | 230 | 12:00 | Sreepur | 237 | 17:00 | 221 | 12:00
Feni | 232 | 8:00 | 226 | 11:00 | Tongi | 234 | 05:00 | 222 | 11:00
Ghorashal | 236 | 01:00 | 230 | 10:00
Ghorashal-230 | 233 | 06:00 | 219 | 12:00
Gopalganj | 241 | 04:00 | 231 | 16:00
GPH | 236 | 05:00 | 231 | 11:00
Haripur | 233 | 05:00 | 221 | 12:00
Hasnabad | 236 | 03:00 | 224 | 12:00
Hathazari | 236 | 02:00 | 230 | 11:00
Ishurdi | 240 | 05:00 | 230 | 12:00
Jhenaidah | 239 | 05:00 | 227 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 127 | 12:00 | Lalbag | 137 | 03:00 | 128 | 13:00
Agargaon | 138 | 04:00 | 130 | 12:00 | Lalmonirhat | 132 | 04:00 | 123 | 13:00
Agrabad | 136 | 04:00 | 132 | 11:00 | Madanganj | 133 | 21:00 | 129 | 12:00
AKS | 134 | 04:00 | 130 | 11:00 | Madaripur | 137 | 04:00 | 134 | 13:00
Aminbazar | 136 | 01:00 | 132 | 15:00 | Madartek | 135 | 02:00 | 126 | 12:00
Amnura | 139 | 03:00 | 130 | 12:00 | Madunaghat | 137 | 05:00 | 135 | 00:00
Ashuganj | 142 | 03:00 | 137 | 12:00 | Magura | 140 | 05:00 | 131 | 12:00
Bagerhat | 136 | 06:00 | 129 | 18:00 | Mahasthangarh | 135 | 05:00 | 129 | 07:00
Bajitpur | 137 | 05:00 | 132 | 07:00 | Maijdee | 134 | 03:00 | 129 | 11:00
Bakulia | 136 | 05:00 | 133 | 11:00 | Manikganj | 135 | 04:00 | 128 | 11:00
Banani | 136 | 03:00 | 126 | 12:00 | Maniknagar | 141 | 04:00 | 132 | 12:00
Bangabhaban | 141 | 04:00 | 132 | 12:00 | Matarbari | 132 | 11:00 | 120 | 18:00
Barapukuria | 138 | 19:00 | 127 | 07:00 | Matuail | 135 | 04:00 | 128.6 | 12:00
Barguna | 0 | 00:00 | N/A | N/A | Metrorail_Motijheel | 141 | 04:00 | 132 | 12:00
Barishal | 139 | 02:00 | 133 | 12:00 | Metrorail_Uttara | 138 | 04:00 | 127 | 12:00
Barishal-230 | 139 | 03:00 | 134 | 12:00 | Millgate | 138 | 03:00 | 129 | 12:00
Baroaulia | 137 | 02:00 | 133 | 11:00 | Mirpur | 137 | 02:00 | 131 | 12:00
Baroirhat | 136 | 05:00 | 132 | 11:00 | Mirzapur | 137 | 05:00 | 128 | 19:00
Bashundhara | 137 | 05:00 | 126 | 12:00 | Mithapukur | 136 | 20:00 | 127 | 08:00
BashundharaCement | 133 | 21:00 | 129 | 12:00 | MI_Cement | 135.8 | 05:00 | 126 | 12:00
Beanibazar | 134 | 03:00 | 130 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 138 | 03:00 | 127 | 13:00 | Mogbazar | 138 | 04:00 | 126 | 13:00
Bhaluka | 134 | 05:00 | 126 | 12:00 | Mongla | 134 | 00:00 | 129 | 18:00
Bhandaria | 137 | 06:00 | 131 | 12:00 | Motijheel | 141 | 04:00 | 132 | 12:00
Bhangura | 137.5 | 03:00 | 132 | 12:00 | Muktagacha | 135 | 09:00 | 121 | 19:00
Bheramara | 140 | 04:00 | 136 | 12:00 | Munshiganj | 134 | 04:00 | 127 | 12:00
Bheramara(GK) | 139 | 03:00 | 135 | 12:00 | Muradnagar | 136 | 05:00 | 129 | 12:00
Bhulta | 131 | 05:00 | 126 | 12:00 | Mymensingh | 135 | 10:00 | 121 | 18:00
Bog-Sherpur | 136 | 04:00 | 130 | 12:00 | Naogaon | 134 | 19:00 | 128 | 12:00
Bogura | 136 | 19:00 | 131 | 07:00 | Narail | 140 | 05:00 | 130 | 13:00
Bogura-230 | 136 | 04:00 | 130 | 16:00 | Narinda | 141 | 04:00 | 132 | 12:00
Brahmanbaria | 134 | 01:00 | 129 | 12:00 | Narshingdi | 136 | 07:00 | 123 | 12:00
Cantonment | 138 | 04:00 | 130 | 12:00 | Natore | 136 | 06:00 | 131 | 12:00
Chandina | 137 | 03:00 | 132 | 11:00 | Nawabganj | 137 | 03:00 | 130 | 12:00
Chandpur | 140 | 19:30 | 132 | 11:00 | Netrakona | 132 | 01:00 | 124 | 09:00
Chandraghona | 139 | 06:00 | 135 | 01:00 | New | 138 | 05:00 | 129 | 12:00
Chapai | 137 | 04:00 | 134 | 07:00 | Niamatpur | 139 | 06:00 | 136 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 05:00 | 128 | 12:00 | Noapara | 138 | 03:00 | 131 | 18:00
Chauddagram | 136 | 03:00 | 131 | 11:00 | Pabna | 139 | 03:00 | 133 | 16:00
Chhatak | 132 | 00:00 | 128 | 12:00 | Palashbari | 134 | 18:30 | 126 | 07:00
Chowmuhani | 134 | 19:30 | 129 | 11:00 | Panchagarh | 142 | 19:00 | 123 | 08:00
Chuadanga | 138 | 03:00 | 130 | 12:00 | Patiya | 136 | 03:00 | 132 | 11:00
Coxsbazar | 126 | 05:00 | 120 | 12:00 | Patuakhali | 135 | 00:00 | 134 | 11:00
Cumilla(N) | 137 | 04:00 | 132 | 11:00 | Payra | 137 | 03:00 | 134 | 12:00
Cumilla(S) | 136 | 06:00 | 125 | 11:00 | PHP | 135 | 03:00 | 131 | 11:00
Daganbhuiyan | 135 | 03:00 | 131 | 11:00 | Postogola | 137 | 05:00 | 128 | 12:00
Daudkandi | 134 | 06:00 | 127 | 12:00 | Purbachal | 137 | 04:00 | 126 | 12:00
DhakaUniversity | 136 | 02:00 | 127 | 12:00 | Purbasadipur | 136 | 19:00 | 124 | 08:00
Dhamrai | 134 | 00:00 | 128 | 16:00 | Rahanpur | 139 | 05:00 | 134 | 13:00
Dhanmondi | 137 | 04:00 | 127 | 12:00 | Rahanpur-400 | 140 | 04:00 | 136 | 12:00
Dohazari | 133 | 05:00 | 130 | 00:00 | Rahim | 135 | 05:00 | 130 | 11:00
Faridpur | 139 | 05:00 | 134 | 12:00 | Rajbari | 140 | 05:00 | 133 | 12:00
Fatullah | 138 | 05:00 | 127 | 12:00 | Rajendrapur | 135 | 03:00 | 126 | 12:00
Fenchuganj | 140 | 03:00 | 136 | 12:00 | Rajshahi | 136 | 05:00 | 131 | 12:00
Feni | 134 | 04:00 | 130 | 11:00 | Rajshahi-230 | 136 | 05:00 | 130 | 12:00
Feni-230 | 134 | 4:00 | 130 | 11:00 | Ramganj | 135 | 04:00 | 130 | 10:00
Ghatail | 134 | 09:00 | 120 | 19:00 | Rampur | 136 | 05:00 | 132 | 11:00
Ghorashal | 140 | 01:00 | 132 | 12:00 | Rampura | 136 | 03:00 | 126 | 12:00
Goalpara | 140 | 03:00 | 132 | 12:00 | Rangamati | 138 | 00:00 | 134 | 11:00
Gollamari | 139 | 04:00 | 133 | 11:00 | Rangpur | 136 | 19:00 | 126 | 08:00
Gopalganj | 140 | 05:00 | 133 | 12:00 | Ruppur | 140 | 04:00 | 135 | 16:00
Gopalganj-400 | 140 | 03:00 | 135 | 12:00 | Saidpur | 135 | 19:30 | 123 | 08:00
Gulshan | 136 | 05:00 | 126 | 12:00 | Satkhira | 139 | 04:00 | 129 | 18:00
Halishahar | 137 | 03:00 | 133 | 12:00 | Satmasjid | 137 | 04:00 | 130 | 12:00
Haripur | 136 | 04:00 | 129 | 12:00 | Savar | 137 | 04:00 | 129 | 16:00
HaripurSBU | 136 | 04:00 | 129 | 12:00 | SevenRings | 142 | 05:00 | 133 | 11:00
Hasnabad | 136 | 00:00 | 128 | 12:00 | ShahCement | 135 | 05:00 | 128 | 12:00
Hathazari | 138 | 19:00 | 135 | 10:00 | Shahjadpur | 140 | 03:00 | 135 | 12:00
Ishurdi | 141 | 04:00 | 136 | 16:00 | Shahjibazar | 137 | 08:00 | 132 | 12:00
Jaldhaka | 133 | 20:00 | 122 | 08:00 | Shahmirpur | 136 | 08:00 | 133 | 19:30
Jamalpur | 133 | 10:00 | 119 | 06:00 | Shariatpur | 139 | 03:00 | 133 | 12:00
Jashore | 138 | 04:00 | 128 | 18:00 | Sherpur | 130 | 10:00 | 118 | 18:00
Jhenaidah | 142 | 05:00 | 124 | 17:00 | Shikalbaha | 126 | 05:00 | 123 | 02:00
Jhenaidah-230 | 141 | 03:00 | 134 | 12:00 | Shikalbaha-230 | 138 | 04:00 | 134 | 11:00
Joydebpur | 139 | 18:00 | 126 | 12:00 | Shitalakhya | 135.8 | 05:00 | 126 | 12:00
Joypurhat | 133 | 05:00 | 127 | 16:00 | Sholosohor | 138 | 05:00 | 135 | 11:00
Juldah | 137 | 03:00 | 133 | 12:00 | Shyampur | 138 | 08:00 | 131 | 16:00
Kabirpur | 138 | 18:00 | 128 | 12:00 | Shyampur-230 | 138 | 02:00 | 130 | 16:00
Kachua | 139 | 19:00 | 133 | 11:00 | Siddhirganj | 135 | 04:00 | 129 | 12:00
Kaliakoir | 141 | 03:00 | 131 | 11:00 | Sirajganj | 136 | 03:00 | 130 | 16:00
Kallyanpur | 137 | 03:00 | 131 | 16:00 | Sonargaon | 133 | 02:00 | 128 | 12:00
Kalurghat | 138 | 18:30 | 134 | 11:00 | Sreemongol | 137 | 08:00 | 132 | 12:00
Kamrangirchar | 137 | 05:00 | 129 | 12:00 | Sreepur | 136 | 05:00 | 128 | 12:00
Kaptai | 140 | 4:00 | 137 | 12:00 | Srinagar | 137 | 03:00 | 129 | 12:00
Kasba | 135 | 03:00 | 129 | 12:00 | SSM | 141 | 05:00 | 138 | 11:00
Kazla | 141 | 05:00 | 132 | 12:00 | Sunamganj | 132 | 05:00 | 127 | 13:00
Keranigonj | 137 | 03:00 | 130 | 12:00 | Sylhet | 135 | 05:00 | 130 | 13:00
Khagrachori | 137 | 04:00 | 134 | 11:00 | Sylhet-132 | 133 | 03:00 | 130 | 12:00
Khulna | 138 | 05:00 | 132 | 12:00 | Tangail | 134 | 09:00 | 122 | 19:00
Khulna(S) | 140 | 03:00 | 133 | 13:00 | Taraganj | 135 | 19:30 | 124 | 08:00
Khulshi | 135 | 03:00 | 131 | 11:00 | Thakurgaon | 141 | 19:00 | 121 | 08:00
Kishoreganj | 137 | 04:00 | 128 | 12:00 | TK | 137 | 06:00 | 135 | 00:00
Kodda | 137 | 18:00 | 127 | 10:00 | Tongi | 139 | 06:00 | 131 | 11:00
KSRM | 138 | 01:00 | 134 | 11:00 | Ullahpara | 137 | 02:00 | 132 | 12:00
Kulaura | 139 | 03:00 | 135 | 12:00 | Ullon | 136 | 03:00 | 126 | 12:00
Kurigram | 133 | 20:00 | 122 | 07:00 | Uttara | 138 | 04:00 | 129 | 12:00
Kushtia | 137 | 05:00 | 128 | 18:00 | UttaraNew | 138 | 04:00 | 128 | 12:00
Laksam | 138 | 05:00 | 133 | 11:00 | Zigatola | 137 | 05:00 | 130 | 12:00
Lakshmipur | 135 | 04:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division