## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-11-2025 | during | 20-11-2025 | during | 20-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 356 | 383 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23.5 | 22 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 5 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 13 | 128 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 30 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 26 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 458 | 442 | 718 | 718 | 350 | 350 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1268.5 | 1882 | 5451.4 | 5419.4 | 3320.31 | 3288.31
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 214 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 12 | 101 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 47 | 40 | 48 | 40 | 48 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 8 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.38 | 0 | 3.3 | 0 | 3.3 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 25 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 91 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 30 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 582 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 3 | 0 | 7 | 0 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1561.38 | 1955 | 2928.02 | 2924.72 | 2363.8 | 2360.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 207 | 207 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 34 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 46 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 3 | 123 | 150 | 150 | 125 | 125 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 21 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 109 | 109 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 12 | 68 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 106 | 110 | 160 | 160 | 112 | 112 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 928 | 1082 | 2487.21 | 2419.21 | 1650.4 | 1582.4
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-11-2025 | during | 20-11-2025 | during | 20-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 30 | 157.5 | 157.5 | 70 | 70 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 18 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.95 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 95.95 | 108 | 365 | 314 | 218 | 167
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 157 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Gas shortage
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 158 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 399 | 407 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1202 | 1209 | 1237 | 1237 | 1159 | 1159
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 890 | 889 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 193 | 178 | 410 | 410 | 410 | 410
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 81 | 0 | 81 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1113 | 1107 | 0 | 0 | 1140 | 1140 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2278 | 2174 | 2399 | 2318 | 2778.1 | 2697.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 453 | 500 | 0 | 0 | 500 | 500 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 14 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 110 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 908 | 920 | 982 | 982 | 827 | 827 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 110 | 110 | 110 | 110 | GT-1 Shutdown under Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1601.57 | 1781 | 1473 | 1473 | 1685 | 1685
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 55.3 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 173 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 277 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 53 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 80 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.69 | 0 | 5.62 | 0 | 5.62 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 755.92 | 765 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.85 | 0 | 58 | 1 | 58 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1440.76 | 1578 | 3084.49 | 2921.87 | 3011.11 | 2848.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 55 | 55 | 55 | 55 | 55 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 83 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 184 | 0 | 181.82 | 1.62 | 181.82 | 1.62 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 278.1 | 228 | 534.62 | 318.62 | 500.62 | 284.62
System Total |  |  |  |  | 28823.2 | 28205.415 | 10654.26 | 11997 | 19959.74 | 19345.82 | 16686.34 | 16072.42
Forecast Scenario (20-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9850 |  | 0 |  | 9850
|  |  |  | 1:00 | 9470 |  | 0 |  | 9470
|  |  |  | 2:00 | 8970 |  | 0 |  | 8970
|  |  |  | 3:00 | 8570 |  | 0 |  | 8570
|  |  |  | 4:00 | 8420 |  | 0 |  | 8420
|  |  |  | 5:00 | 8340 |  | 0 |  | 8340
|  |  |  | 6:00 | 8650 |  | 0 |  | 8650
|  |  |  | 7:00 | 9620 |  | 0 |  | 9620
|  |  |  | 8:00 | 9860 |  | 0 |  | 9860
|  |  |  | 9:00 | 9860 |  | 0 |  | 9860
|  |  |  | 10:00 | 9760 |  | 0 |  | 9760
|  |  |  | 11:00 | 10290 |  | 0 |  | 10290
|  |  |  | 12:00 | 10750 |  | 0 |  | 10750
|  |  |  | 13:00 | 11070 |  | 0 |  | 11070
|  |  |  | 14:00 | 10810 |  | 0 |  | 10810
|  |  |  | 15:00 | 10640 |  | 0 |  | 10640
|  |  |  | 16:00 | 10490 |  | 0 |  | 10490
|  |  |  | 17:00 | 10780 |  | 0 |  | 10780
|  |  |  | 18:00 | 12090 |  | 0 |  | 12090
|  |  |  | 18:30 | 11900 |  | 0 |  | 11900
|  |  |  | 19:00 | 11840 |  | 0 |  | 11840
|  |  |  | 19:30 | 11630 |  | 0 |  | 11630
|  |  |  | 20:00 | 11340 |  | 0 |  | 11340
|  |  |  | 21:00 | 11240 |  | 0 |  | 11240
|  |  |  | 22:00 | 10900 |  | 0 |  | 10900
|  |  |  | 23:00 | 10500 |  | 0 |  | 10500
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 10750.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12090.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12090.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 244.11 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:21 hrs on 20-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-11-2025 | [28 empty] | Date: | 19-11-2025 | [28 empty] | Date: | 19-11-2025 | [28 empty] | Date: | 19-11-2025 | [28 empty] | Date: | 19-11-2025 | [14 empty] | Date: | 19-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 21 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 568 | 0 | 20 | 0 | 0 | 393 | 0 | 0 | 43 | 191 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 363 | 0 | 30 | 147 | 21 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 8 | 0 | 35 | 0 | 0 | 0 | 4626 | 889 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 220 | 0 | 458 | 902 | 0 | 5132 | 9758 | 100.69
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 23 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 575 | 0 | 35 | 0 | 0 | 393 | 0 | 0 | 42 | 192 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 365 | 0 | 30 | 149 | 16 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 4637 | 890 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 944 | 0 | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 220 | 0 | 309 | 910 | 0 | 4734 | 9371 | 100.68
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 22 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 575 | 0 | 35 | 0 | 0 | 393 | 0 | 0 | 42 | 193 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 368 | 0 | 30 | 151 | 16 | 0 | 79 | 30 | 0 | 15 | 157 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 4648 | 890 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 220 | 0 | 253 | 760 | 0 | 4228 | 8876 | 100.68
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 31 | 650 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 560 | 0 | 42 | 0 | 0 | 350 | 0 | 0 | 42 | 193 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 368 | 0 | 30 | 151 | 16 | 0 | 79 | 30 | 0 | 15 | 157 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 4578 | 889 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 180 | 0 | 255 | 650 | 0 | 3896 | 8474 | 100.67
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 464 | 0 | 5 | 0 | 0 | 350 | 0 | 0 | 23 | 203 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 392 | 0 | 30 | 156 | 16 | 0 | 41 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 4456 | 889 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 180 | 0 | 253 | 590 | 0 | 3871 | 8327 | 100.67
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 38 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 420 | 0 | 5 | 0 | 0 | 350 | 0 | 0 | 5 | 204 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 315 | 0 | 391 | 0 | 30 | 161 | 16 | 0 | 41 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4412 | 890 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 180 | 0 | 256 | 550 | 0 | 3835 | 8247 | 100.66
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 39 | 650 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 420 | 0 | 5 | 0 | 0 | 350 | 0 | 0 | 8 | 197 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 310 | 0 | 386 | 0 | 30 | 159 | 16 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4430 | 889 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 0 | 529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 180 | 0 | 305 | 635 | 0 | 4123 | 8553 | 100.66
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.48 | 86 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 543 | 4 | 44 | 0 | 0 | 393 | 0 | 0 | 42 | 206 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 76 | 0 | 8 | 0 | 315 | 0 | 408 | 0 | 30 | 162 | 16 | 0 | 76 | 30 | 0 | 15 | 159 | 0 | 5 | 5 | 34 | 0 | 5.1 | 0 | 4766.58 | 889 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.37 | 1065 | 0 | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.78 | 8 | 0 | 0 | 3.06 | 180 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0.28 | 0 | 59 | 0 | 3 | 0 | 0 | 0 | 0 | 0.3 | 16 | 0.34 | 0 | 0 | 60 | 220 | 0 | 402 | 735 | 0 | 4758.13 | 9524.71 | 100.65
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 14 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.36 | 86 | 0 | 12 | 650 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 570 | 10 | 51 | 0 | 0 | 393 | 0 | 0 | 42 | 193 | 32 | 0 | 0 | 0 | 0 | 11 | 0 | 80 | 0 | 20 | 0 | 305 | 0 | 360 | 0 | 30 | 157 | 16 | 0 | 76 | 30 | 0 | 15 | 159 | 0 | 35 | 19 | 30 | 1 | 20.94 | 0 | 4706.8 | 889 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.15 | 1085 | 0 | 727.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5 | 41 | 0 | 0 | 23.32 | 195 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 2.18 | 0 | 56 | 0 | 13 | 0 | 0 | 0 | 0 | 2.2 | 77 | 0.18 | 0 | 0 | 60 | 180 | 0 | 403 | 810 | 0 | 5054.68 | 9761.48 | 100.65
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 22 | 0 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 86 | 0 | 7 | 650 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 520 | 14 | 51 | 0 | 0 | 393 | 0 | 0 | 42 | 203 | 34 | 0 | 0 | 0 | 0 | 11 | 0 | 88 | 0 | 54 | 0 | 300 | 0 | 387 | 0 | 30 | 145 | 16 | 0 | 79 | 30 | 0 | 15 | 160 | 0 | 8 | 8 | 32 | 2 | 33.66 | 0 | 4717.04 | 889 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1020 | 0 | 671.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.26 | 70 | 0 | 0 | 44.84 | 164 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 3.72 | 0 | 56 | 0 | 21 | 0 | 0 | 0 | 0 | 3.9 | 125 | 0.35 | 0 | 0 | 60 | 180 | 0 | 351 | 855 | 0 | 5047.31 | 9764.35 | 100.64
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 28 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.36 | 86 | 0 | 6 | 585 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 520 | 17 | 51 | 0 | 0 | 393 | 0 | 0 | 41 | 205 | 32 | 0 | 0 | 0 | 0 | 11 | 0 | 96 | 0 | 65 | 0 | 305 | 0 | 394 | 0 | 30 | 152 | 16 | 0 | 79 | 30 | 0 | 15 | 160 | 0 | 8 | 8 | 30 | 2 | 43.3 | 0 | 4773.66 | 889 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 965 | 0 | 677.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.03 | 94 | 0 | 0 | 58.3 | 169 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 4.95 | 0 | 56 | 0 | 32 | 0 | 0 | 0 | 0 | 5.2 | 162 | 0.49 | 0 | 0 | 60 | 180 | 0 | 355 | 850 | 0 | 4890.13 | 9663.79 | 100.64
11:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 31 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.24 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 580 | 19 | 51 | 0 | 0 | 393 | 0 | 0 | 39 | 197 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 102 | 0 | 71 | 0 | 310 | 0 | 374 | 0 | 30 | 153 | 16 | 0 | 78 | 30 | 0 | 15 | 160 | 0 | 8 | 8 | 30 | 2 | 47.35 | 0 | 4962.59 | 889 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1002 | 0 | 756.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.39 | 103 | 0 | 0 | 65.24 | 171 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 5.61 | 0 | 52 | 0 | 36 | 0 | 0 | 0 | 0 | 5.9 | 180 | 0.6 | 0 | 0 | 60 | 180 | 0 | 404 | 890 | 0 | 5226.99 | 10189.58 | 100.63
12:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 458 | 0 | 0 | 13 | 0 | 5 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 31 | 0 | 23.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.38 | 86 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 12 | 216 | 0 | 0 | 0 | 582 | 6 | 51 | 3 | 0 | 393 | 0 | 0 | 40 | 207 | 34 | 0 | 0 | 12 | 0 | 11 | 0 | 106 | 0 | 71 | 0 | 315 | 0 | 399 | 0 | 30 | 156 | 16 | 0 | 81 | 30 | 0 | 15 | 160 | 0 | 18 | 18 | 11 | 2 | 46.95 | 0 | 5055.83 | 890 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 1113 | 0 | 755.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.3 | 105 | 0 | 0 | 65.85 | 176 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 5.69 | 0 | 52 | 0 | 36 | 0 | 0 | 0 | 0 | 6.1 | 184 | 0.57 | 0 | 0 | 60 | 180 | 0 | 453 | 908 | 0 | 5598.43 | 10654.26 | 100.63
13:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 402 | 0 | 0 | 32 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 30 | 0 | 23.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.22 | 86 | 0 | 10 | 650 | 0 | 0 | 19 | 0 | 70 | 217 | 0 | 0 | 0 | 572 | 13 | 51 | 31 | 0 | 393 | 0 | 0 | 41 | 199 | 34 | 0 | 0 | 62 | 0 | 11 | 0 | 108 | 0 | 64 | 0 | 310 | 0 | 376 | 0 | 30 | 159 | 16 | 0 | 80 | 30 | 0 | 15 | 160 | 0 | 56 | 19 | 11 | 2 | 44.49 | 0 | 5238.21 | 890 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1140 | 0 | 755.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.19 | 100 | 0 | 0 | 61.43 | 175 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 5.33 | 0 | 52 | 0 | 34 | 0 | 0 | 0 | 0 | 5.5 | 173 | 0.52 | 0 | 0 | 60 | 180 | 0 | 501 | 915 | 0 | 5731.76 | 10969.97 | 100.62
14:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 420 | 0 | 0 | 19 | 0 | 45 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 24 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2.44 | 86 | 0 | 8 | 650 | 0 | 0 | 32 | 0 | 51 | 216 | 0 | 0 | 0 | 565 | 15 | 51 | 30 | 0 | 385 | 0 | 0 | 43 | 199 | 34 | 0 | 0 | 68 | 5 | 11 | 0 | 106 | 0 | 55 | 0 | 305 | 0 | 400 | 0 | 30 | 152 | 16 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 58 | 19 | 11 | 2 | 37.41 | 0 | 5195.85 | 888 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1128 | 0 | 721.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.44 | 84 | 0 | 0 | 51.59 | 167 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 4.46 | 0 | 54 | 0 | 26 | 0 | 0 | 0 | 0 | 4.5 | 144 | 0.42 | 0 | 0 | 60 | 220 | 0 | 410 | 903 | 0 | 5518.12 | 10713.97 | 100.62
15:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 423 | 0 | 0 | 17 | 0 | 45 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1.62 | 86 | 0 | 4 | 650 | 0 | 0 | 32 | 0 | 50 | 216 | 0 | 0 | 0 | 580 | 11 | 51 | 24 | 0 | 370 | 0 | 0 | 45 | 200 | 34 | 0 | 0 | 66 | 18 | 11 | 0 | 104 | 0 | 40 | 0 | 310 | 0 | 393 | 0 | 30 | 154 | 16 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 58 | 19 | 11 | 1 | 26.73 | 0 | 5179.35 | 889 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1080 | 0 | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.71 | 60 | 0 | 0 | 37.48 | 174 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 3.2 | 101 | 0.29 | 0 | 0 | 60 | 220 | 0 | 403 | 915 | 0 | 5364.68 | 10544.03 | 100.61
16:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 426 | 0 | 0 | 17 | 0 | 45 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 8 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 86 | 0 | 4 | 650 | 0 | 0 | 32 | 0 | 51 | 217 | 0 | 0 | 0 | 580 | 5 | 51 | 24 | 0 | 393 | 0 | 0 | 45 | 214 | 34 | 0 | 0 | 66 | 17 | 11 | 0 | 102 | 0 | 19 | 0 | 310 | 0 | 399 | 0 | 30 | 153 | 16 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 59 | 19 | 11 | 0 | 9.7 | 0 | 5180.7 | 889 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1064 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.58 | 26 | 0 | 0 | 12.17 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 9 | 0 | 0 | 0 | 0 | 1.3 | 39 | 0.11 | 0 | 0 | 60 | 220 | 0 | 404 | 913 | 0 | 5213.16 | 10393.86 | 100.61
17:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 356 | 54 | 7 | 29 | 0 | 245 | 5 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 70 | 22 | 22 | 0 | 0 | 18 | 5 | 0 | 0 | 2 | 6 | 24 | 0 | 22 | 12 | 0.01 | 86 | 17 | 13 | 650 | 0 | 0 | 32 | 0 | 79 | 201 | 0 | 0 | 0 | 558 | 0 | 51 | 46 | 0 | 340 | 0 | 0 | 46 | 184 | 34 | 6 | 0 | 105 | 18 | 12 | 0 | 104 | 0 | 0 | 25 | 310 | 0 | 338 | 0 | 30 | 150 | 16 | 0 | 81 | 20 | 0 | 15 | 158 | 0 | 59 | 19 | 21 | 0 | 0.28 | 0 | 5427.29 | 888 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1080 | 0 | 761 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 8 | 0 | 0.78 | 1 | 10 | 0 | 0.71 | 168 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.06 | 0 | 54 | 70 | 0 | 12 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 0 | 80 | 180 | 0 | 500 | 912 | 17 | 5260.66 | 10687.95 | 100.6
18:00 | 0 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 442 | 54 | 17 | 128 | 0 | 294 | 40 | 17 | 26 | 0 | 0 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 0 | 30 | 25 | 0 | 0 | 3 | 33 | 47 | 0 | 24 | 12 | 0 | 86 | 91 | 8 | 650 | 0 | 0 | 19 | 0 | 101 | 214 | 0 | 0 | 0 | 612 | 0 | 51 | 123 | 0 | 393 | 0 | 0 | 46 | 207 | 34 | 16 | 0 | 68 | 0 | 13 | 0 | 110 | 0 | 0 | 21 | 315 | 0 | 407 | 0 | 30 | 157 | 16 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 30 | 0 | 0 | 0 | 6236 | 889 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 765 | 0 | 48 | 0 | 80 | 53 | 0 | 0 | 24 | 0 | 0 | 0 | 21 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 90 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 110 | 220 | 0 | 500 | 920 | 17 | 5761 | 11997 | 100.6
19:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 395 | 36 | 17 | 140 | 0 | 294 | 15 | 17 | 28 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 0 | 30 | 32 | 0 | 0 | 2 | 33 | 55 | 0 | 38 | 37 | 0 | 86 | 68 | 12 | 650 | 0 | 0 | 19 | 0 | 95 | 219 | 0 | 0 | 0 | 580 | 0 | 51 | 110 | 0 | 393 | 0 | 0 | 47 | 195 | 35 | 16 | 0 | 64 | 0 | 19 | 0 | 106 | 0 | 0 | 30 | 305 | 0 | 379 | 0 | 30 | 152 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 31 | 0 | 0 | 0 | 6052 | 889 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 768 | 0 | 48 | 0 | 50 | 50 | 0 | 0 | 32 | 0 | 0 | 0 | 21 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 95 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 115 | 220 | 0 | 501 | 910 | 17 | 5692 | 11744 | 100.59
19:30 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 395 | 17 | 0 | 103 | 0 | 294 | 15 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 0 | 30 | 32 | 0 | 0 | 2 | 31 | 55 | 0 | 38 | 37 | 0 | 86 | 48 | 12 | 650 | 0 | 0 | 19 | 0 | 90 | 221 | 0 | 0 | 0 | 580 | 0 | 51 | 80 | 0 | 395 | 0 | 0 | 47 | 193 | 35 | 16 | 0 | 62 | 0 | 20 | 0 | 106 | 0 | 0 | 24 | 305 | 0 | 368 | 0 | 30 | 142 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 34 | 0 | 0 | 0 | 5852 | 889 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 765 | 0 | 48 | 0 | 50 | 50 | 0 | 0 | 32 | 0 | 0 | 0 | 21 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 55 | 95 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 115 | 220 | 0 | 500 | 910 | 17 | 5680 | 11532 | 100.59
20:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 417 | 17 | 0 | 103 | 0 | 195 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 35 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 55 | 0 | 38 | 37 | 0 | 86 | 49 | 20 | 650 | 0 | 0 | 19 | 0 | 92 | 222 | 0 | 0 | 0 | 580 | 0 | 51 | 80 | 0 | 393 | 0 | 0 | 47 | 201 | 35 | 14 | 0 | 62 | 0 | 20 | 0 | 96 | 0 | 0 | 14 | 305 | 0 | 386 | 0 | 30 | 144 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 18 | 33 | 0 | 0 | 0 | 5648 | 889 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 764 | 0 | 48 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 53 | 95 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 910 | 17 | 5593 | 11241 | 100.59
21:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 438 | 0 | 0 | 100 | 0 | 195 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 35 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 38 | 37 | 0 | 86 | 50 | 24 | 650 | 0 | 0 | 19 | 0 | 96 | 222 | 0 | 0 | 0 | 580 | 0 | 51 | 80 | 0 | 393 | 0 | 0 | 47 | 200 | 35 | 16 | 0 | 65 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 387 | 0 | 30 | 149 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 18 | 34 | 0 | 0 | 0 | 5675 | 889 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1117 | 0 | 761.52 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 54 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 908 | 0 | 5472.52 | 11147.52 | 100.58
22:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 415 | 0 | 0 | 65 | 0 | 195 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 86 | 0 | 27 | 650 | 0 | 0 | 19 | 0 | 93 | 222 | 0 | 0 | 0 | 570 | 0 | 51 | 80 | 0 | 393 | 0 | 0 | 47 | 193 | 35 | 0 | 0 | 63 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 375 | 0 | 30 | 145 | 21 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 59 | 18 | 34 | 0 | 0 | 0 | 5365 | 889 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 762.47 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 54 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 500 | 901 | 0 | 5437.47 | 10802.47 | 100.58
23:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 440 | 0 | 0 | 25 | 0 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 86 | 0 | 30 | 650 | 0 | 0 | 19 | 0 | 34 | 223 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 0 | 393 | 0 | 0 | 45 | 205 | 36 | 0 | 0 | 62 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 391 | 0 | 30 | 148 | 21 | 0 | 82 | 30 | 0 | 15 | 159 | 0 | 59 | 18 | 34 | 0 | 0 | 0 | 5032 | 889 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 759.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 890 | 0 | 5323.2 | 10355.2 | 100.57
Total KWH | 0 | 110400 | 294720 | 0 | 0 | 0 | 0 | 0 | 8593200 | 0 | 10155700 | 130320 | 54000 | 708768 | 0 | 1693887 | 96522 | 133769 | 419040 | 0 | 0 | 0 | 0 | 0 | 70253 | 7196912 | 0 | 0 | 208177 | 184800 | 451200 | 519120 | 0 | 0 | 126709 | 85309 | 0 | 0 | 69600 | 79499 | 214992 | 0 | 157440 | 222720 | 20520 | 2061300 | 352100 | 449280 | 15534545.46 | 0 | 0 | 287040 | 0 | 973527 | 5214814 | 0 | 0 | 0 | 13276362 | 119880 | 1091072 | 709236 | 0 | 9229000 | 0 | 0 | 925920 | 4924000 | 818712 | 84480 | 0 | 874080 | 62160 | 315500 | 0 | 2178240 | 0 | 483418 | 81184 | 7526000 | 0 | 9448000 | 0 | 723240 | 3677073 | 39336 | 0 | 1805760 | 689376 | 0 | 365000 | 3697640 | 0 | 772800 | 283200 | 621120 | 14450 | 317030 | 0 | 122023452.46 | 21522909 | 4363200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535680 | 24356370 | 0 | 16067195 | 0 | 155290 | 0 | 212256 | 366144 | 0 | 0 | 57807 | 0 | 381864 | 709710 | 73381 | 0 | 423744 | 4160909 | 0 | 0 | 0 | 0 | 0 | 7512218 | 0 | 35280 | 0 | 1274618 | 634831 | 229149 | 469728 | 0 | 0 | 0 | 38484.48 | 1200240 | 3486 | 43968 | 0 | 1808000 | 5198390 | 0 | 9701818 | 22109500 | 68400 | 123714569.48 | 245738021.94

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10654.26 | MW | 12:00 Hr. | Energy Generated |  |  | 245.738 |  | MKWHr.
| Day Peak Demand |  |  | 10654.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11997 | MW | 18:00 Hr. | Energy Demand |  |  | 245.738 |  | MKWHr.
| Evening Peak Demand |  |  | 11997 | MW | 18:00 Hr. | Maximum Temperature |  |  | 30.8 |  | °C
| Minimum Generation of the Day |  |  | 8247 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 747.83 |  | MMCFD
| Maximum Generation of the Day |  |  | 11997 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.7385 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.9161 | 0 | 3.8965 | 0 | 0 | 0.20818 | 0 | 0 | 31.0208 | Gas | 101.5197 | Gas | 362766045.31
| Chattogram Zone |  |  | 5.6641 | 28.8109 | 2.4993 | 0 | 2.0613 | 0.1404 | 0 | 0.0696 | 39.2456 | Coal | 86.2532 | Coal | 552151846.1562
| Cumilla Zone |  |  | 17.3042 | 0 | 1.8111 | 0 | 0 | 0.48342 | 2.1782 | 0 | 21.777 | HFO | 11.3448 | HFO | 192969951.78
| Mymensingh Zone |  |  | 0.62112 | 0 | 1.056 | 0 | 0 | 0.33148 | 0 | 0 | 2.0086 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.9714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9714 | Hydro | 2.0613 | Hydro | 206130
| Khulna Zone |  |  | 4.3632 | 24.3564 | 0 | 0 | 0 | 0.53568 | 21.5229 | 0 | 50.7782 | Solar | 4.7211 | Solar | 75628838.2908
| Barishal Zone |  |  | 7.0064 | 31.8113 | 0.11237 | 0 | 0 | 0.003486 | 0 | 0 | 38.9336 | Import | 39.7683 | Import | 225412598.06
| Rajshahi Zone |  |  | 11.6731 | 0 | 0.86488 | 0 | 0 | 1.5506 | 16.0672 | 0 | 30.1558 | Wind | 0.0696 | Wind | 1023816
| Rangpur Zone |  |  | 0 | 1.2746 | 1.1046 | 0 | 0 | 1.4679 | 0 | 0 | 3.8471
| Total |  |  | 101.5197 | 86.2532 | 11.3448 | 0 | 2.0613 | 4.7211 | 39.7683 | 0.0696 | 245.738
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 362766045.31 |  | Hydro | 206130
|  |  |  | Coal | 552151846.1562 |  | Solar | 75628838.2908
|  |  |  | HFO | 192969951.78 |  | Import | 225412598.06
|  |  |  | HSD | 0 |  | Wind | 1023816
[5 empty] | Total: | 141,01,59,225 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5229 | Peak Hr Flow | 889.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49220527.29 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.0672 | Peak Hr Flow | 765.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2333 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.1782 | Peak Hr Flow | 110.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2743 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.7683 | Peak Hr Flow | 1764.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4654
|  |  |  | Chattogram |  | 0 |  | 1374
|  |  |  | Cumilla |  | 0 |  | 989
|  |  |  | Mymensingh |  | 0 |  | 858
|  |  |  | Sylhet |  | 0 |  | 435
|  |  |  | Khulna |  | 0 |  | 1222
|  |  |  | Barishal |  | 0 |  | 306
|  |  |  | Rajshahi |  | 0 |  | 1009
|  |  |  | Rangpur |  | 0 |  | 754
|  |  |  | Total |  | 0 |  | 11601
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 16:25 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Scheduled S/D Due to Annual maintenance
| 08:03 | 16:13 | Niamatpur 132/33kV S/S Transformer-3(426T) HT Scheduled S/D Due to Annual maintenace
| 08:09 | 12:48 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to Annual
maintenance and from Barapukuria 230/132/33kV end Due to Annual maintenance work
| 08:15 | 17:00 | Bibiana 400/230kV S/S ICT-01 LT Scheduled S/D Due to AM
| 08:16 | 16:59 | Bibiana 400/230kV S/S ICT-01 HT Scheduled S/D Due to AM
| 08:16 | 15:46 | Benapole 132/33kV S/S Bus-B Scheduled S/D Due to Annual Maintenance
| 08:26 |  | Sunamganj 132/33kV S/S Tr-2 LT Scheduled S/D
| 08:26 | 11:16 | Bakulia-Sikalbaha 132 kV Ckt-1 Project Work S/D from Bakulia 132/33kV end Due to CB-605B
spring auxiliary contact changing work.
| 08:28 | 11:48 | Sunamganj 132/33kV S/S Tr-2 HT Scheduled S/D
| 08:30 | 13:51 | Agargaon-Satmasjid 132kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to Annual
maintenance.
| 08:33 | 16:57 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
| 08:34 | 16:43 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual Maintenance
| 08:34 | 15:45 | Baroirhat 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance work
| 08:34 | 16:44 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual Maintenance
| 08:36 | 16:06 | Chapai 132/33kV S/S Chapai Rahanpur ckt 2 Scheduled S/D Due to Annual maintenance
| 08:36 | 16:04 | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 Scheduled S/D Due to
For annual maintenance
| 08:37 | 16:11 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
For Annual Maintenance
| 08:39 | 15:20 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual maintenance work
| 08:40 | 12:42 | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenance
| 08:40 | 14:29 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Annual maintenance of TR-1 (AB)
| 08:40 | 14:30 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Annual maintenance of TR-1 (AB)
| 08:40 | 12:41 | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance
| 08:42 | 19:11 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Scheduled S/D Due to From other end.
| 08:42 | 17:35 | Gopalganj 400/132kV S/S 230 kV Bus-02 Scheduled S/D Due to Annual Maintenance
| 08:45 | 16:54 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-01 Scheduled S/D Due to Yearly maintenance
| 08:52 | 11:32 | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to Work
| 08:54 | 16:45 | Barapukuria 230/132/33kV S/S 132 KV Bus A Scheduled S/D Due to Annual maintenance work
| 08:56 | 16:30 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance
| 08:57 | 15:52 | Madaripur-Shariatpur 132kV Ckt-2 Scheduled S/D from Shariatpur 132/33kV end Due to
Annual Maintenance work. and from Madaripur 132/33kV end Due to Annual Maintenance
| 09:00 | 15:45 | Jhenaidah-Magura 132 kV Ckt-2 Scheduled S/D from Jhenaidah 132/33kV end Due to Annual
maintenance and from Magura 132/33kV end Due to Annual Maintenance.
| 09:07 | 16:17 | Joydebpur 132/33kV S/S GT-2 HT Scheduled S/D Due to Annual maintenance
| 09:08 | 19:11 | Baghabari-Ishurdi 230 kV Ckt-1 Scheduled S/D from Ishurdi 230/132kV end Due to Annual
maintenance work and from Baghabari 230/132kVend.
| 09:11 | 17:22 | Bhulta-Rampura 230 kV Ckt-1 Project Work S/D from Bhulta 400/230kV end.
| 09:21 | 17:22 | Bhulta-Rampura 230 kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to taken by
Vulta Grid SS , instructed by NLDC
| 09:22 | 17:18 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance
| 09:23 | 16:48 | BIPTC S/S 10CF13 Scheduled S/D Due to Annual maintenance work
| 09:32 |  | Chandina 132/33kV S/S TR-2 LT Tripped showing K86 Lock out Realy-1&2, F51 TR Backup Relay
relays.
| 09:32 |  | Chandina 132/33kV S/S TR-2 HT Tripped showing K86 L-1&2, F87T2 Transformer Main-2 Relay.
relays Due to Diff Trip, REF
| 09:33 | 16:30 | Haripur-Haripur (360MW) 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to
Annual Maintenance.
| 09:35 | 12:44 | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Niamatpur 132/33kV end Due to Red
hot
| 09:42 | 14:38 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end.
| 09:50 | 13:20 | Bajitpur 132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to None
| 09:51 | 15:26 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance
|  | 10:39 | Narail 132/33kV S/S Auxiliary TR 1 LT is restored.
|  | 10:39 | Narail 132/33kV S/S Auxiliary TR 1 HT is restored.
| 11:01 | 14:00 | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to Annual
Maintenance
| 11:07 | 15:05 | Hathazari-Raozan 230kV Ckt-1 Forced S/D from Hathazari 230/132/33kV end Due to
Hathazari-Rawzan 230 kV circuir-01, R-phase has a shorted wire on the conductor,
requiring an emergency shutdown to remove it. Load sharing with Rawzan Circuit-02
| 11:10 |  | Jamalpur 132/33kV S/S T-1 HT Project Work S/D Due to Prject Work
| 11:10 |  | Jamalpur 132/33kV S/S T-1 LT Project Work S/D Due to 132kv CB, Grantry, Blastwall work
| 11:17 |  | Chandpur 132/33kV S/S 100MW(GT) Power Plant Incomer (T4) Scheduled S/D Due to Maintainace
| 11:20 | 15:34 | Bakulia-Sikalbaha 132 kV Ckt-2 Project Work S/D from Bakulia 132/33kV end Due to CB-605B
Spring Auxiliary Contact changing work.
| 11:23 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 11:47 | 14:26 | Jaldhaka 132/33kV S/S 416T-2 LT Forced S/D Due to LA Change phase -R
| 11:48 | 14:25 | Jaldhaka 132/33kV S/S 416T-2 HT Forced S/D Due to LA Change Phase -R
| 12:50 | 16:33 | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Annual Maintenance
| 12:50 | 16:33 | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintenance
| 12:58 | 16:35 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual Maintenance and from Rangpur 132/33kV end Due to Preventive Maintenance
| 13:35 | 14:37 | Bajitpur 132/33kV S/S 132 kV Bus-1 Scheduled S/D
|  | 13:48 | Chandraghona-Madunaghat 132 kV Ckt-2 is restored.
|  | 13:53 | Nawabganj 132/33kV S/S 132kV Main Bus-1 is restored.
|  | 14:23 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT is restored.
|  | 14:24 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT is restored.
| 14:34 | 15:58 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-02 Project Work S/D Due to SCADA
INTEGRATON
| 15:24 | 17:41 | Nawabganj 132/33kV S/S 132kV Main Bus-2 Scheduled S/D Due to For annual maintenance
|  | 15:26 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
| 15:43 |  | Ashuganj-Kishoreganj 132kV Ckt-1 Project Work S/D from Bajitpur 132/33kV end Due to 132
KV Ashuganj -Bajitpur Ckt-1 S/D Due to project work
| 16:10 | 16:59 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-02 Project Work S/D Due to
SCADA INTEGRATION
| 16:12 | 16:48 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Project Work S/D from Cumilla(N) 230/132/33kV end.
|  | 16:55 | Bhulta-Rampura 230 kV Ckt-2 is restored.
|  | 16:55 | Bhulta-Rampura 230 kV Ckt-2 is restored.
| 18:00 |  | Evening Peak Generation: 11997 MW.
|  | 19:04 | Rahanpur 400/132kV S/S Rahanpur-Monakasha 400KV Line ckt-02 is restored.
|  | 20:08 | Shyampur 230/132kV S/S Auto TR-1 HT is restored.
|  | 20:09 | Shyampur 230/132kV S/S Auto TR-1 LT is restored.
| 01:46 | 02:06 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing Earth fault Pro | [7 empty] | 48.0MW load
|  |  | trip,Lockout Relay K861,K862 Trip. relays Due to Due to Keranihat 33 kv feeder O/C & E/F. | [7 empty] | interrup.
| 05:00 |  | Minimum Generation: 8489 MW.
| 06:12 | 06:33 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent Protection p142, Lockout | [7 empty] | 9.8MW load
|  |  | relay-1, Lockout relay -2 relays Due to 33 kv PBS sholla feeder doesn't trip. | [7 empty] | interrup.
| 06:12 | 06:25 | Nawabganj 132/33kV S/S TR-1 LT Tripped showing Overcurrent Protection p142, Lockout | [7 empty] | 9.8MW load
|  |  | relay-1, Lockout relay -2 relays Due to 33 kv PBS sholla feeder doesn't trip. | [7 empty] | interrup.
| 07:05 |  | Pabna 132/33kV S/S T-2 LT Scheduled S/D | [7 empty] | 5.0MW load
interrup.
| 07:09 |  | Pabna 132/33kV S/S T-2 HT Scheduled S/D | [7 empty] | 5.0MW load
interrup.
| 07:09 |  | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance Work
| 07:14 |  | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance Work.
| 07:16 |  | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance and from Bhulta 400/230kV end Due to S/D taken by Rampura Grid Substation.
| 07:43 |  | Rampur 230/132/33 S/S Khulshi-1 Scheduled S/D Due to Annual Maintenance
| 07:45 |  | Halishahar-Khulshi 132kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual
maintenance at bay.
| 07:45 |  | Khulna(C )-Khulna (S) 132kV Ckt-2 Project Work S/D from Khulna (C) end Due to movement
of filing ring and from Khulna(S) 230/132kV end Due to Project work Central ss end.
| 07:55 |  | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to maintenance work by WDPDCL | [7 empty] | 10.0MW load
interrup.
| 07:55 |  | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Maintenance work by WZPDCL | [7 empty] | 10.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 383 | 8593200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | GT-1 shut down for schedule outage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 40 | 96522 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7196912 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 130320 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 133769 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 70253 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 451200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 519120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 294720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 1693887 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 128 | 708768 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 30 | 110400 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 26 | 419040 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 208177 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 54000 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 442 | 10155700 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 35 | 184800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1882 | 31020788
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119880 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 287040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2061300 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 5214814 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 101 | 973527 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 47 | 214992 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 79499 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 157440 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 449280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 25 | 85309 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 91 | 352100 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 222720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 126709 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13276362 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 69600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15534545.46 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4895.723 | 1955 | 39245637.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 207 | 4924000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 9229000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 818712 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 925920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1091072 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 709236 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 81184 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 874080 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 110 | 2178240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 315500 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 62160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 84480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 483418 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1082 | 21777002
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 30 | 621120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 283200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 772800 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 317030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 108 | 2008600
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3677073 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 689376 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1805760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3697640 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 365000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 39336 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7526000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 407 | 9448000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1209 | 27971425
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 889 | 21522909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 178 | 4363200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 535680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1107 | 24356370 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2174 | 50778159
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 500 | 9701818 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 14 | 43968 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 1808000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 920 | 22109500 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5198390 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 68400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3486 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1781 | 38933562
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 381864 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 155290 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 57807 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 173 | 4160909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 7512218 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 73381 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 53 | 366144 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 80 | 212256 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35280 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 765 | 16067195 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 423744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 709710 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1578 | 30155798
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1274618 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 83 | 469728 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38484.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 634831 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 229149 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1200240 | -
Rangpur Area Total |  |  |  |  | 950 | 228 | 3847050.48
Eastern Grid Total |  |  |  |  | 17383.855 | 6236 | 122023452.46
Western Grid Total |  |  |  |  | 10821.56 | 5761 | 123714569.48
National Grid Total |  |  |  |  | 28205.415 | 11997 | 245738021.94
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8309.98 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3291.4 | MW
i) Dhaka area |  |  | 4654.18 |  | MW | i) Khulna area |  |  |  | 1222 | MW
ii) Chattogram area |  |  | 1374 |  | MW | ii) Barishal area |  |  |  | 306 | MW
iii) Cumilla area |  |  | 988.8 |  | MW | iii) Rajshahi area |  |  |  | 1009.4 | MW
iv) Mymensingh area |  |  | 858 |  | MW | iv) Rangpur area |  |  |  | 754 | MW
v) Sylhet area |  |  | 435 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11601.38 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 77 | 19:00 | 133 | Niamatpur | 40 | 18:00
2 | AKSML | 148 | 03:00 | 68 | Ishurdi | 59 | 18:00 | 134 | Noapara | 36 | 18:30
3 | Aftabnagar | 30 | 13:00 | 69 | Jaldhaka | 58 | 18:00 | 135 | PHP | 9 | 08:00
4 | Agargaon | 101 | 13:00 | 70 | Jamalpur | 84 | 08:00 | 136 | Pabna | 73 | 18:00
5 | Agrabad | 88 | 18:00 | 71 | Jashore | 99 | 13:00 | 137 | Palashbari | 84 | 18:00
6 | Amnura | 18 | 13:00 | 72 | Jhenaidah | 93 | 18:00 | 138 | Panchagarh | 44 | 18:00
7 | Ashuganj | 62 | 13:00 | 73 | Joydebpur | 121 | 18:00 | 139 | Patiya | 7 | 18:00
8 | BSRM | 197 | 23:00 | 74 | Joypurhat | 41 | 18:30 | 140 | Patuakhali | 55 | 21:00
9 | Bagerhat | 61 | 18:00 | 75 | Juldah | 14 | 16:00 | 141 | Payra | 22 | 18:30
10 | Bajitpur | 65 | 18:00 | 76 | KSRM | 19 | 19:30 | 142 | Postogola | 57 | 13:00
11 | Bakulia | 73 | 18:00 | 77 | Kabirpur | 203 | 15:00 | 143 | Purbachal | 29 | 13:00
12 | Banani | 34 | 14:00 | 78 | Kachua | 61 | 18:00 | 144 | Purbasadipur | 99 | 18:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 78 | 18:00 | 145 | Rahanpur | 21 | 18:00
14 | Barapukuria | 49 | 18:00 | 80 | Kalurghat | 44 | 12:00 | 146 | Rahim | 43 | 01:00
15 | Barguna | 0 | 00:00 | 81 | Kamrangirchar | 71 | 13:00 | 147 | Rajbari | 60 | 18:00
16 | Barishal | 91 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 109 | 18:00
17 | Barishal-230 | 64 | 18:00 | 83 | Kasba | 24 | 20:00 | 149 | Rajshahi | 66 | 21:00
18 | Baroaulia | 59 | 17:00 | 84 | Kazla | 97 | 18:30 | 150 | Rajshahi-230 | 72 | 13:00
19 | Baroirhat | 41 | 18:00 | 85 | Keranigonj | 67 | 18:00 | 151 | Ramganj | 68 | 13:00
20 | Bashundhara | 134 | 14:00 | 86 | Khagrachori | 26 | 18:00 | 152 | Rampur | 35 | 18:00
21 | BashundharaCement | 13 | 10:00 | 87 | Khulna | 60 | 13:00 | 153 | Rangamati | 15 | 18:00
22 | Beanibazar | 48 | 18:00 | 88 | Khulshi | 159 | 11:00 | 154 | Rangpur | 110 | 18:00
23 | Benapole | 42 | 18:00 | 89 | Kishoreganj | 87 | 18:00 | 155 | Ruppur | 3.6 | 10:00
24 | Bhaluka | 136 | 18:00 | 90 | Kodda | 281 | 17:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 41 | 18:00 | 91 | Kulaura | 32 | 18:00 | 157 | Saidpur | 84 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 47 | 18:00 | 158 | Satkhira | 82 | 07:00
27 | Bheramara(GK) | 43 | 18:00 | 93 | Kushtia | 110 | 18:00 | 159 | Satmasjid | 87 | 14:00
28 | Bhulta | 202 | 18:00 | 94 | Laksam | 23 | 21:00 | 160 | Savar | 176 | 18:30
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 21 | 18:00 | 161 | SevenRings | 16.27 | 21:00
30 | Bogura | 118 | 18:00 | 96 | Lalbag | 62 | 17:00 | 162 | ShahCement | 21 | 00:00
31 | Borhanuddin | 65 | 21:00 | 97 | Lalmonirhat | 44 | 18:00 | 163 | Shahjadpur | 56 | 18:00
32 | Brahmanbaria | 93 | 18:30 | 98 | MI_Cement | 15.7 | 00:00 | 164 | Shahjibazar | 86 | 18:00
33 | Cantonment | 108 | 13:00 | 99 | Madanganj | 40 | 19:30 | 165 | Shahmirpur | 51 | 18:00
34 | Chandina | 11.8 | 18:00 | 100 | Madaripur | 69 | 18:00 | 166 | Shariatpur | 56 | 20:00
35 | Chandpur | 52 | 18:00 | 101 | Madartek | 66 | 23:00 | 167 | Sherpur | 102 | 18:30
36 | Chandraghona | 31 | 19:30 | 102 | Madunaghat | 36 | 18:00 | 168 | Shikalbaha | 27 | 16:00
37 | Chapai | 42 | 13:00 | 103 | Magura | 46 | 18:30 | 169 | Shitalakhya | 65.5 | 16:00
38 | Charsaidpur | 37 | 16:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 42 | 15:00
39 | Chauddagram | 50 | 18:00 | 105 | Maijdee | 26 | 19:00 | 171 | Shyampur | 136 | 09:00
40 | Chhatak | 22 | 18:00 | 106 | Manikganj | 94 | 18:00 | 172 | Siddhirganj | 106 | 18:00
41 | Chowmuhani | 111 | 18:30 | 107 | Maniknagar | 62 | 13:00 | 173 | Sirajganj | 80 | 18:00
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 45 | 18:00 | 174 | Sonargaon | 104 | 16:00
43 | Coxsbazar | 126 | 18:00 | 109 | Matuail | 65 | 12:00 | 175 | Sreemongol | 55 | 19:00
44 | Cumilla(N) | 86 | 18:30 | 110 | Metrorail_Motijheel | 28 | 13:00 | 176 | Sreepur | 89 | 17:00
45 | Cumilla(S) | 136 | 18:00 | 111 | Metrorail_Uttara | 8 | 18:00 | 177 | Srinagar | 30.8 | 22:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 95 | 11:00 | 178 | Sunamganj | 40 | 18:00
47 | Daudkandi | 112 | 21:00 | 113 | Mirpur | 122 | 18:00 | 179 | Sylhet | 40 | 19:30
48 | DhakaUniversity | 70 | 13:00 | 114 | Mirsorai | 9 | 15:00 | 180 | Sylhet-132 | 90 | 18:30
49 | Dhamrai | 116 | 18:00 | 115 | Mirzapur | 37 | 18:00 | 181 | TK | 16 | 18:30
50 | Dhanmondi | 104 | 14:00 | 116 | Mithapukur | 44 | 18:00 | 182 | Tangail | 118 | 18:00
51 | Dohazari | 82 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 16 | 18:00
52 | Faridpur | 113 | 18:30 | 118 | Mogbazar | 75.4 | 14:00 | 184 | Tasnim | 36 | 09:00
53 | Fatullah | 103 | 12:00 | 119 | Mongla | 47 | 18:30 | 185 | Thakurgaon | 75 | 18:00
54 | Fenchuganj | 28 | 18:00 | 120 | Motijheel | 32 | 13:00 | 186 | Tongi | 110 | 12:00
55 | Feni | 87 | 20:00 | 121 | Muktagacha | 27 | 18:00 | 187 | Ullahpara | 27 | 18:30
56 | GPH | 93 | 19:00 | 122 | Munshiganj | 76 | 13:00 | 188 | Ullon | 50 | 18:00
57 | Ghatail | 60 | 07:00 | 123 | Muradnagar | 26 | 18:00 | 189 | Uttara | 66 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 136 | 18:00 | 190 | UttaraNew | 21 | 14:00
59 | Ghorashal-230 | 79 | 00:00 | 125 | Naogaon | 85 | 18:00 | 191 | Zigatola | 54 | 13:00
60 | Goalpara | 24 | 12:00 | 126 | Narail | 42 | 18:00
61 | Gollamari | 72 | 13:00 | 127 | Narinda | 60 | 13:00
62 | Gopalganj | 80 | 18:00 | 128 | Narshingdi | 152 | 19:00
63 | Gulshan | 98 | 13:00 | 129 | Natore | 103 | 18:00
64 | Halishahar | 63 | 15:00 | 130 | Nawabganj | 29.8 | 21:00
65 | HaripurSBU | 152 | 13:00 | 131 | Netrakona | 98 | 18:00
66 | Hasnabad | 82 | 20:00 | 132 | New | 65 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9758 | 0 |  | 9758
1:00 | 9371 | 0 |  | 9371
2:00 | 8876 | 0 |  | 8876
3:00 | 8474 | 0 |  | 8474
4:00 | 8327 | 0 |  | 8327
5:00 | 8247 | 0 |  | 8247
6:00 | 8553 | 0 |  | 8553
7:00 | 9524.71 | 0 |  | 9524.71
8:00 | 9761.48 | 0 |  | 9761.48
9:00 | 9764.35 | 0 |  | 9764.35
10:00 | 9663.79 | 0 |  | 9663.79
11:00 | 10189.58 | 0 |  | 10189.58
12:00 | 10654.26 | 0 |  | 10654.26
13:00 | 10969.97 | 0 |  | 10969.97
14:00 | 10713.97 | 0 |  | 10713.97
15:00 | 10544.03 | 0 |  | 10544.03
16:00 | 10393.86 | 0 |  | 10393.86
17:00 | 10687.95 | 0 |  | 10687.95
18:00 | 11997 | 0 |  | 11997
19:00 | 11744 | 0 |  | 11744
19:30 | 11532 | 0 |  | 11532
20:00 | 11241 | 0 |  | 11241
21:00 | 11147.52 | 0 |  | 11147.52
22:00 | 10802.47 | 0 |  | 10802.47
23:00 | 10355.2 | 0 |  | 10355.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4626 | 5132 | 9758 | DAILY GENERATION CURVE
00:30 | 4631.5 | 4933 | 9564.5
01:00 | 4637 | 4734 | 9371 | 19-11-2025
01:30 | 4642.5 | 4481 | 9123.5
02:00 | 4648 | 4228 | 8876
02:30 | 4613 | 4062 | 8675
03:00 | 4578 | 3896 | 8474
03:30 | 4517 | 3883.5 | 8400.5
04:00 | 4456 | 3871 | 8327
04:30 | 4434 | 3853 | 8287
05:00 | 4412 | 3835 | 8247
05:30 | 4421 | 3979 | 8400
06:00 | 4430 | 4123 | 8553
06:30 | 4598.29 | 4440.565 | 9038.855
07:00 | 4766.58 | 4758.13 | 9524.71
07:30 | 4736.69 | 4906.405 | 9643.095
08:00 | 4706.8 | 5054.68 | 9761.48
08:30 | 4711.92 | 5050.995 | 9762.915
09:00 | 4717.04 | 5047.31 | 9764.35
09:30 | 4745.35 | 4968.72 | 9714.07
10:00 | 4773.66 | 4890.13 | 9663.79
10:30 | 4868.125 | 5058.56 | 9926.685
11:00 | 4962.59 | 5226.99 | 10189.58
11:30 | 5009.21 | 5412.71 | 10421.92
12:00 | 5055.83 | 5598.43 | 10654.26
12:30 | 5147.02 | 5665.095 | 10812.115
13:00 | 5238.21 | 5731.76 | 10969.97
13:30 | 5217.03 | 5624.94 | 10841.97
14:00 | 5195.85 | 5518.12 | 10713.97
14:30 | 5187.6 | 5441.4 | 10629
15:00 | 5179.35 | 5364.68 | 10544.03
15:30 | 5180.025 | 5288.92 | 10468.945
16:00 | 5180.7 | 5213.16 | 10393.86
16:30 | 5303.995 | 5236.91 | 10540.905
17:00 | 5427.29 | 5260.66 | 10687.95
17:30 | 5831.645 | 5510.83 | 11342.475
18:00 | 6236 | 5761 | 11997
18:30 | 6144 | 5726.5 | 11870.5
19:00 | 6052 | 5692 | 11744
19:30 | 5852 | 5680 | 11532
20:00 | 5648 | 5593 | 11241
20:30 | 5661.5 | 5532.76 | 11194.26 |  | Executive Engineer
21:00 | 5675 | 5472.52 | 11147.52 |  | Network Operation Division
21:30 | 5520 | 5454.995 | 10974.995
22:00 | 5365 | 5437.47 | 10802.47
22:30 | 5198.5 | 5380.335 | 10578.835
23:00 | 5032 | 5323.2 | 10355.2

## En-Curve
QF-LDC-12
Date | 19-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2855 | 1330 | 889 | 0 | 82 | 765 | 86 | 3743 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2853 | 1336.5 | 889.5 | 0 | 81 | 718 | 86 | 3593 | 0 | 0 | 4 | 0 | 0 | 3.5 | 0 | 19-11-2025
01:00 | 2851 | 1343 | 890 | 0 | 80 | 671 | 86 | 3443 | 0 | 0 | 0 | 0 | 0 | 7 | 0
01:30 | 2854.5 | 1344 | 890 | 0 | 80 | 600.5 | 86 | 3257.5 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | Energy Generated | 245.738 |  | MKWHr
02:00 | 2858 | 1345 | 890 | 0 | 80 | 530 | 86 | 3072 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2810 | 1320 | 889.5 | 0 | 80 | 480 | 86 | 2996.5 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | Total Energy Requirement | 245.738 |  | MKWHr
03:00 | 2762 | 1295 | 889 | 0 | 80 | 430 | 86 | 2921 | 0 | 0 | 0 | 0 | 0 | 11 | 0
03:30 | 2791.5 | 1267 | 889 | 0 | 77 | 432.5 | 86 | 2847 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0
04:00 | 2821 | 1239 | 889 | 0 | 74 | 435 | 86 | 2773 | 0 | 0 | 0 | 0 | 0 | 10 | 0
04:30 | 2819 | 1235 | 889.5 | 0 | 75 | 434.5 | 86 | 2740.5 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0
05:00 | 2817 | 1231 | 890 | 0 | 76 | 434 | 86 | 2708 | 0 | 0 | 0 | 0 | 0 | 5 | 0
05:30 | 2762.5 | 1240.5 | 889.5 | 0 | 77 | 481.5 | 86 | 2858 | 0 | 0 | 0 | 0 | 0 | 5 | 0
06:00 | 2708 | 1250 | 889 | 0 | 78 | 529 | 86 | 3008 | 0 | 0 | 0 | 0 | 0 | 5 | 0
06:30 | 2811 | 1319.5 | 889 | 0 | 77 | 582.5 | 86 | 3231 | 30.855 | 0 | 5 | 0 | 0 | 7 | 0
07:00 | 2914 | 1389 | 889 | 0 | 76 | 636 | 86 | 3454 | 61.71 | 0 | 10 | 0 | 0 | 9 | 0
07:30 | 2838 | 1339.75 | 889 | 0 | 78 | 681.575 | 86 | 3514 | 171.77 | 0 | 40.5 | 0 | 0 | 4.5 | 0
08:00 | 2762 | 1290.5 | 889 | 0 | 80 | 727.15 | 86 | 3574 | 281.83 | 0 | 71 | 0 | 0 | 0 | 0
08:30 | 2760.5 | 1278.75 | 889 | 0 | 84 | 699.195 | 86 | 3513 | 387.97 | 4 | 60.5 | 0 | 0 | 0 | 0
09:00 | 2759 | 1267 | 889 | 0 | 88 | 671.24 | 86 | 3452 | 494.11 | 8 | 50 | 0 | 0 | 0 | 0
09:30 | 2670 | 1274.5 | 889 | 0 | 92 | 674.2 | 86 | 3391.5 | 565.87 | 12 | 59 | 0 | 0 | 0 | 0
10:00 | 2581 | 1282 | 889 | 0 | 96 | 677.16 | 86 | 3331 | 637.63 | 16 | 68 | 0 | 0 | 0 | 0
10:30 | 2619.5 | 1302 | 889 | 0 | 99 | 716.705 | 86 | 3454.5 | 671.48 | 20.5 | 68 | 0 | 0 | 0 | 0
11:00 | 2658 | 1322 | 889 | 0 | 102 | 756.25 | 86 | 3578 | 705.33 | 25 | 68 | 0 | 0 | 0 | 0
11:30 | 2757.5 | 1340.75 | 889.5 | 0 | 104 | 756.085 | 86 | 3668 | 703.085 | 25 | 92 | 0 | 0 | 0 | 0
12:00 | 2857 | 1359.5 | 890 | 0 | 106 | 755.92 | 86 | 3758 | 700.84 | 25 | 116 | 0 | 0 | 0 | 0
12:30 | 2885 | 1329 | 890 | 0 | 107 | 755.855 | 86 | 3794 | 684.26 | 25 | 256 | 0 | 0 | 0 | 0
13:00 | 2913 | 1298.5 | 890 | 0 | 108 | 755.79 | 86 | 3830 | 667.68 | 25 | 396 | 0 | 0 | 0 | 0
13:30 | 2902 | 1324.75 | 889 | 0 | 107 | 738.75 | 86 | 3770 | 614.47 | 25 | 385 | 0 | 0 | 0 | 0
14:00 | 2891 | 1351 | 888 | 0 | 106 | 721.71 | 86 | 3710 | 561.26 | 25 | 374 | 0 | 0 | 0 | 0
14:30 | 2894 | 1355.5 | 888.5 | 0 | 105 | 726.355 | 86 | 3696 | 477.645 | 25 | 375 | 0 | 0 | 0 | 0
15:00 | 2897 | 1360 | 889 | 0 | 104 | 731 | 86 | 3682 | 394.03 | 25 | 376 | 0 | 0 | 0 | 0
15:30 | 2952 | 1361 | 889 | 0 | 103 | 725.5 | 86 | 3673.5 | 277.445 | 25 | 376.5 | 0 | 0 | 0 | 0
16:00 | 3007 | 1362 | 889 | 0 | 102 | 720 | 86 | 3665 | 160.86 | 25 | 377 | 0 | 0 | 0 | 0
16:30 | 2854 | 1310.5 | 888.5 | 0 | 103 | 740.5 | 86 | 3709.5 | 83.405 | 109 | 655.5 | 0 | 0 | 1 | 0
17:00 | 2701 | 1259 | 888 | 0 | 104 | 761 | 86 | 3754 | 5.95 | 193 | 934 | 0 | 0 | 2 | 0
17:30 | 2903.5 | 1326 | 888.5 | 0 | 107 | 763 | 86 | 3799 | 2.975 | 238.5 | 1225.5 | 0 | 0 | 2.5 | 0
18:00 | 3106 | 1393 | 889 | 0 | 110 | 765 | 86 | 3844 | 0 | 284 | 1517 | 0 | 0 | 3 | 0
18:30 | 3024.5 | 1370 | 889 | 0 | 108 | 766.5 | 86 | 3821 | 0 | 306.5 | 1496.5 | 0 | 0 | 2.5 | 0
19:00 | 2943 | 1347 | 889 | 0 | 106 | 768 | 86 | 3798 | 0 | 329 | 1476 | 0 | 0 | 2 | 0
19:30 | 2909 | 1338 | 889 | 0 | 106 | 765 | 86 | 3803 | 0 | 279 | 1355 | 0 | 0 | 2 | 0
20:00 | 2954 | 1366 | 889 | 0 | 96 | 764 | 86 | 3801 | 0 | 181 | 1101 | 0 | 0 | 3 | 0
20:30 | 2969 | 1383.5 | 889 | 0 | 98 | 762.76 | 86 | 3805.5 | 0 | 139.5 | 1059.5 | 0 | 0 | 1.5 | 0
21:00 | 2984 | 1401 | 889 | 0 | 100 | 761.52 | 86 | 3810 | 0 | 98 | 1018 | 0 | 0 | 0 | 0
21:30 | 2959 | 1389 | 889 | 0 | 99 | 761.995 | 86 | 3800.5 | 0 | 53 | 937.5 | 0 | 0 | 0 | 0
22:00 | 2934 | 1377 | 889 | 0 | 98 | 762.47 | 86 | 3791 | 0 | 8 | 857 | 0 | 0 | 0 | 0
22:30 | 2959 | 1387.5 | 889 | 0 | 97 | 760.835 | 86 | 3790.5 | 0 | 8 | 601 | 0 | 0 | 0 | 0
23:00 | 2984 | 1398 | 889 | 0 | 96 | 759.2 | 86 | 3790 | 0 | 8 | 345 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 05:00 | 378 | 12:00 | Meghnaghat | 397 | 03:00 | 380 | 16:00
Ashuganj | 403 | 3:00 | 382 | 12:00 | Payra | 416 | 03:00 | 407 | 13:00
Bhulta | 398 | 03:00 | 376 | 14:00 | Rahanpur | 414 | 03:00 | 395 | 12:00
Bibiana | 399 | 06:00 | 388 | 12:00 | Rampal | 413 | 03:00 | 398 | 15:00
BIPTC | 402 | 01:00 | 391 | 18:00
Bogura | 409 | 03:00 | 390 | 12:00
Gopalganj | 408 | 05:00 | 392 | 12:00
Kaliakoir | 393 | 03:00 | 373 | 12:00
Korerhat | 403 | 04:00 | 390 | 12:00
Madunaghat | 399 | 04:00 | 392 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 03:00 | 224 | 12:00 | Kachua | 235 | 05:00 | 224 | 11:00
AKSML | 235 | 02:00 | 228 | 12:00 | Kaliakoir | 237 | 03:00 | 223 | 12:00
Aminbazar | 236 | 05:00 | 224 | 12:00 | Keranigonj | 236 | 03:00 | 222 | 16:00
Ashuganj | 232 | 02:00 | 215 | 16:00 | Khulna(S) | 240 | 04:00 | 229 | 12:00
Ashuganj-400 | 232 | 3:00 | 216 | 12:00 | Korerhat | 237 | 06:00 | 228 | 12:00
Baghabari | 236 | 01:00 | 226 | 12:00 | Madunaghat | 237 | 03:00 | 230 | 12:00
Barapukuria | 225 | 10:00 | 213 | 07:00 | Madunaghat-400 | 238 | 20:00 | 232 | 12:00
Barapukuria-230 | 225 | 19:00 | 212 | 7:00 | Maniknagar | 229 | 04:00 | 219 | 11:00
Barishal | 240 | 03:00 | 233 | 12:00 | Meghnaghat | 239 | 03:00 | 225 | 12:00
Bheramara | 235 | 03:00 | 222 | 12:00 | Meghnaghat-400 | 234 | 03:00 | 222 | 12:00
Bhulta | 232 | 03:00 | 218 | 14:00 | Mirsorai | 234 | 02:00 | 225 | 12:00
Bibiana | 236 | 04:00 | 227 | 11:00 | Rajshahi | 235 | 04:00 | 222 | 12:00
BIPTC | 238 | 03:00 | 223 | 12:00 | Rampal | 239 | 05:00 | 226 | 13:00
Bogura | 237 | 03:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 236 | 03:00 | 226 | 13:00 | Rampura | 232 | 05:00 | 216 | 12:00
Borhanuddin | 243 | 03:00 | 236 | 13:00 | Shikalbaha | 236 | 19:00 | 229 | 14:00
BSRM | 233 | 02:00 | 224 | 12:00 | Shyampur | 233 | 02:00 | 219 | 13:00
Cumilla(N) | 230 | 01:00 | 221 | 12:00 | Siddhirganj | 231 | 00:00 | 221 | 12:00
Faridpur | 241 | 03:00 | 231 | 12:00 | Sirajgonj | 241 | 02:00 | 232 | 12:00
Fenchuganj | 237 | 06:00 | 226 | 12:00 | Sreepur | 233 | 03:00 | 220 | 11:00
Feni | N/A | N/A | N/A | N/A | Tongi | 232 | 04:00 | 217 | 15:00
Ghorashal | 235 | 00:00 | 225 | 14:00
Ghorashal-230 | 232 | 03:00 | 217 | 12:00
Gopalganj | 241 | 03:00 | 231 | 13:00
GPH | 236 | 02:00 | 228 | 12:00
Haripur | 233 | 05:00 | 220 | 12:00
Hasnabad | 238 | 20:00 | 222 | 12:00
Hathazari | 235 | 21:00 | 227 | 14:00
Ishurdi | 239 | 05:00 | 226 | 12:00
Jhenaidah | 238 | 05:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 123 | 11:00 | Lalbag | 136 | 04:00 | 127 | 12:00
Agargaon | 138 | 03:00 | 129 | 12:00 | Lalmonirhat | 132 | 01:00 | 121 | 09:00
Agrabad | 136 | 17:00 | 131 | 10:00 | Madanganj | 133 | 04:00 | 130 | 09:00
AKS | 133 | 01:00 | 130 | 11:00 | Madaripur | 139 | 05:00 | 134 | 13:00
Aminbazar | 137 | 03:00 | 129 | 16:00 | Madartek | 136 | 02:00 | 123 | 11:00
Amnura | 139 | 03:00 | 128 | 12:00 | Madunaghat | 138 | 03:00 | 133 | 12:00
Ashuganj | 142 | 04:00 | 138 | 16:00 | Magura | 140 | 03:00 | 128 | 12:00
Bagerhat | 135 | 04:00 | 126 | 13:00 | Mahasthangarh | 134 | 03:00 | 127 | 07:00
Bajitpur | 137 | 03:00 | 131 | 12:00 | Maijdee | 133 | 02:00 | 128 | 11:00
Bakulia | 137 | 05:00 | 130 | 11:00 | Manikganj | 133 | 22:00 | 120 | 14:00
Banani | 136 | 02:00 | 124 | 10:00 | Maniknagar | 141 | 03:00 | 131 | 13:00
Bangabhaban | 140 | 03:00 | 132 | 12:00 | Matarbari | 126 | 08:00 | 117 | 13:00
Barapukuria | 137 | 03:00 | 124 | 09:00 | Matuail | 136 | 04:00 | 128 | 12:00
Barguna | 0 | 00:00 | N/A | N/A | Metrorail_Motijheel | 141 | 03:00 | 131 | 13:00
Barishal | 139 | 03:00 | 133 | 12:00 | Metrorail_Uttara | 138 | 04:00 | 127 | 11:00
Barishal-230 | 138 | 02:00 | 133 | 12:00 | Millgate | 137 | 02:00 | 127 | 11:00
Baroaulia | 136 | 00:00 | 132 | 13:00 | Mirpur | 137 | 05:00 | 130 | 12:00
Baroirhat | 136 | 03:00 | 130 | 11:00 | Mirzapur | 134 | 03:00 | 126 | 12:00
Bashundhara | 136 | 04:00 | 121 | 12:00 | Mithapukur | 135 | 19:30 | 125 | 12:00
BashundharaCement | 133 | 04:00 | 130 | 09:00 | MI_Cement | 135 | 04:00 | 124 | 16:00
Beanibazar | 134 | 01:00 | 130 | 11:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 136 | 05:00 | 124 | 13:00 | Mogbazar | 137 | 03:00 | 125 | 11:00
Bhaluka | 134 | 03:00 | 125 | 12:00 | Mongla | 133 | 00:00 | 127 | 13:00
Bhandaria | 136 | 06:00 | 130 | 12:00 | Motijheel | 140 | 03:00 | 132 | 12:00
Bhangura | 137 | 02:00 | 129 | 13:00 | Muktagacha | 130 | 09:00 | 120 | 18:00
Bheramara | 140 | 05:00 | 134 | 12:00 | Munshiganj | 133 | 02:00 | 126 | 12:00
Bheramara(GK) | 139 | 01:00 | 134 | 12:00 | Muradnagar | 136 | 03:00 | 128 | 12:00
Bhulta | 133 | 03:00 | 125 | 11:00 | Mymensingh | 129 | 00:00 | 118 | 17:00
Bog-Sherpur | 136 | 04:00 | 129 | 12:00 | Naogaon | 133 | 04:00 | 126 | 12:00
Bogura | 136 | 04:00 | 129 | 13:00 | Narail | 141 | 04:00 | 127 | 13:00
Bogura-230 | 136 | 05:00 | 129 | 12:00 | Narinda | 141 | 3:00 | 131 | 13:00
Brahmanbaria | 135 | 01:00 | 128 | 14:00 | Narshingdi | 134 | 18:30 | 124 | 14:00
Cantonment | 138 | 03:00 | 128 | 12:00 | Natore | 134 | 01:00 | 129 | 12:00
Chandina | 138 | 03:00 | 131 | 11:00 | Nawabganj | 138 | 04:00 | 128 | 12:00
Chandpur | 139 | 17:00 | 130 | 11:00 | Netrakona | 130 | 00:00 | 122 | 13:00
Chandraghona | 138 | 03:00 | 133 | 11:00 | New | 138 | 04:00 | 128 | 12:00
Chapai | 136 | 04:00 | 132 | 18:30 | Niamatpur | 139 | 03:00 | 132 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 03:00 | 127 | 12:00 | Noapara | 138 | 06:00 | 129 | 13:00
Chauddagram | 136 | 02:00 | 129 | 11:00 | Pabna | 139 | 03:00 | 131 | 12:00
Chhatak | 132 | 00:00 | 128 | 12:00 | Palashbari | 133 | 05:00 | 124 | 12:00
Chowmuhani | 133 | 05:00 | 128 | 12:00 | Panchagarh | 137 | 22:00 | 120 | 09:00
Chuadanga | 140 | 02:00 | 128 | 13:00 | Patiya | 136 | 04:00 | 131 | 11:00
Coxsbazar | 126 | 03:00 | 115 | 12:00 | Patuakhali | 135 | 00:00 | 133 | 11:00
Cumilla(N) | 136 | 01:00 | 130 | 11:00 | Payra | 137 | 02:00 | 134 | 12:00
Cumilla(S) | 137 | 02:00 | 125 | 10:00 | PHP | 135 | 02:00 | 129 | 12:00
Daganbhuiyan | 135 | 03:00 | 129 | 11:00 | Postogola | 135 | 01:00 | 126 | 12:00
Daudkandi | 133 | 04:00 | 126 | 12:00 | Purbachal | 137 | 04:00 | 123 | 11:00
DhakaUniversity | 136 | 03:00 | 123 | 11:00 | Purbasadipur | 133 | 19:30 | 120 | 09:00
Dhamrai | 136 | 05:00 | 126 | 16:00 | Rahanpur | 139 | 05:00 | 132 | 12:00
Dhanmondi | 137 | 05:00 | 128 | 12:00 | Rahanpur-400 | 139 | 02:00 | 132 | 12:00
Dohazari | 133 | 06:00 | 123 | 14:00 | Rahim | 135 | 02:00 | 128 | 12:00
Faridpur | 140 | 03:00 | 133 | 13:00 | Rajbari | 139 | 02:00 | 133 | 12:00
Fatullah | 138 | 06:00 | 124 | 12:00 | Rajendrapur | 134 | 04:00 | 125 | 12:00
Fenchuganj | 140 | 03:00 | 135 | 13:00 | Rajshahi | 136 | 03:00 | 128 | 12:00
Feni | 134 | 06:00 | 129 | 11:00 | Rajshahi-230 | 136 | 03:00 | 128 | 12:00
Feni-230 | N/A | N/A | N/A | N/A | Ramganj | 135 | 17:00 | 129 | 10:00
Ghatail | 129 | 04:00 | 121 | 18:00 | Rampur | 137 | 04:00 | 130 | 12:00
Ghorashal | 140 | 02:00 | 132 | 01:00 | Rampura | 136 | 02:00 | 123 | 12:00
Goalpara | 140 | 04:00 | 131 | 12:00 | Rangamati | 137 | 05:00 | 133 | 12:00
Gollamari | 138 | 03:00 | 131 | 12:00 | Rangpur | 134 | 21:00 | 124 | 09:00
Gopalganj | 140 | 05:00 | 132 | 14:00 | Ruppur | 139 | 06:00 | 134 | 12:00
Gopalganj-400 | 141 | 05:00 | 134 | 12:00 | Saidpur | 134 | 05:00 | 121 | 09:00
Gulshan | 136 | 06:00 | 122 | 11:00 | Satkhira | 138 | 04:00 | 128 | 12:00
Halishahar | 137 | 04:00 | 131 | 12:00 | Satmasjid | 141 | 10:00 | 127 | 13:00
Haripur | 136 | 03:00 | 129 | 12:00 | Savar | 135 | 01:00 | 129 | 12:00
HaripurSBU | 136 | 03:00 | 129 | 13:00 | SevenRings | 140 | 03:00 | 133 | 12:00
Hasnabad | 135 | 03:00 | 126 | 10:00 | ShahCement | 134 | 04:00 | 127 | 12:00
Hathazari | 138 | 21:00 | 133 | 12:00 | Shahjadpur | 141 | 03:00 | 134 | 12:00
Ishurdi | 140 | 02:00 | 134 | 12:00 | Shahjibazar | 138 | 02:00 | 131 | 15:00
Jaldhaka | 132 | 22:00 | 118 | 09:00 | Shahmirpur | 137 | 18:30 | 132 | 03:00
Jamalpur | 127 | 14:00 | 117 | 00:00 | Shariatpur | 139 | 03:00 | 131 | 13:00
Jashore | 139 | 03:00 | 128 | 14:00 | Sherpur | 127 | 14:00 | 114 | 00:00
Jhenaidah | 141 | 04:00 | 120 | 18:00 | Shikalbaha | 126 | 04:00 | 121 | 12:00
Jhenaidah-230 | 142 | 03:00 | 131 | 13:00 | Shikalbaha-230 | 138 | 05:00 | 133 | 14:00
Joydebpur | 140 | 17:00 | 131 | 12:00 | Shitalakhya | 135 | 04:00 | 124 | 16:00
Joypurhat | 133 | 02:00 | 126 | 12:00 | Sholosohor | 137 | 01:00 | 133 | 12:00
Juldah | 136 | 03:00 | 132 | 12:00 | Shyampur | 137 | 06:00 | 130 | 14:00
Kabirpur | 136 | 05:00 | 125 | 12:00 | Shyampur-230 | 138 | 06:00 | 129 | 12:00
Kachua | 139 | 05:00 | 132 | 11:00 | Siddhirganj | 136 | 04:00 | 128 | 12:00
Kaliakoir | 139 | 03:00 | 129 | 12:00 | Sirajganj | 135 | 02:00 | 128 | 16:00
Kallyanpur | 138 | 04:00 | 130 | 13:00 | Sonargaon | 133 | 03:00 | 126 | 12:00
Kalurghat | 138 | 03:00 | 133 | 12:00 | Sreemongol | 137 | 04:00 | 132 | 12:00
Kamrangirchar | 136 | 02:00 | 127 | 16:00 | Sreepur | 136 | 03:00 | 128 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 138 | 05:00 | 128 | 12:00
Kasba | 136 | 03:00 | 127 | 16:00 | SSM | 140 | 00:00 | 135 | 12:00
Kazla | 141 | 05:00 | 131 | 13:00 | Sunamganj | 131 | 02:00 | 127 | 13:00
Keranigonj | 138 | 04:00 | 128 | 12:00 | Sylhet | 135 | 02:00 | 130 | 13:00
Khagrachori | 137 | 01:00 | 132 | 12:00 | Sylhet-132 | 133 | 01:00 | 130 | 13:00
Khulna | 138 | 03:00 | 129 | 13:00 | Tangail | 132 | 04:00 | 122 | 12:00
Khulna(S) | 140 | 04:00 | 131 | 13:00 | Taraganj | 134 | 17:00 | 122 | 09:00
Khulshi | 136 | 19:00 | 130 | 11:00 | Tasnim | 136 | 10:00 | 126 | 12:00
Kishoreganj | 135 | 04:00 | 129 | 12:00 | Thakurgaon | 138 | 22:00 | 118 | 09:00
Kodda | 137 | 16:00 | 125 | 12:00 | TK | 137 | 05:00 | 134 | 11:00
KSRM | 137 | 18:30 | 131 | 14:00 | Tongi | 139 | 04:00 | 129 | 15:00
Kulaura | 139 | 01:00 | 134 | 12:00 | Ullahpara | 137 | 04:00 | 130 | 12:00
Kurigram | 132 | 19:30 | 122 | 07:00 | Ullon | 136 | 03:00 | 123 | 12:00
Kushtia | 137 | 03:00 | 127 | 13:00 | Uttara | 137 | 04:00 | 126 | 12:00
Laksam | 138 | 17:00 | 132 | 11:00 | UttaraNew | 138 | 04:00 | 127 | 11:00
Lakshmipur | 134 | 03:00 | 127 | 11:00 | Zigatola | 138 | 06:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division