## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: October 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-10-02 |  | 2025-09-01 |  | 2024-10-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15644.99 | 2025-10-27 | 16279.02 | 2025-09-01 | 14677 | 2024-10-01 | 16794 | 2025-07-23
|  |  | 19:00 Hr. |  | 19:30 Hr. |  | 20:00 |  | 21:00 Hr.
2 | Minimum Generation (MW) | 9833.03 | 2025-10-03 | 10620.26 | 2025-09-22 | 8574 | 2024-10-25 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 15644.99 | 2025-10-27 | 16279.02 | 2025-09-01 | 15717 | 2024-09-19 | 16794 | 2025-07-23
|  |  | 19:00 Hr. |  | 19:30 Hr. |  | 21:00 |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 13866.67 | 2025-10-26 | 14965.88 | 2025-09-30 | 12738 | 2024-10-01 | 14965.88 | 2025-09-30
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 11:00 |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 15801.33 | 2025-10-22 | 16450.02 | 2025-09-01 | 15200 | 2024-10-30 | 17200 | 2024-04-29
|  |  | 19:00 Hr. |  | 19:30 Hr. |  | 20:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14385.22 |  | 15373.711 |  | 13360.3226 |  | - | -
7 | Average Generation (MW) at Day Peak | 12788.9568 |  | 13652.769 |  | 11846.0323 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 978 | 2025-10-23 | 979 | 2025-09-09 | 931 | 2024-10-30 | 979 | 2025-09-09
|  |  | 2:30 |  | 5:00 |  | 0:30 |  | 5:00
9 | Maximum Power Import from Tripura, India (MW) | 90 | 2025-10-24 | 66 | 2025-09-25 | 92 | 2024-10-19 | 194 | 12/06/19
|  |  | 1:00 |  | 18:00 |  | 13:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 570 | 2025-10-19 | 1308 | 2025-09-09 | 1301 | 2024-10-31 | 4395 | 04/10/2022
|  |  | 19:30 |  | 20:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14354.83 | 2025-10-19 | 14881 | 2025-09-09 | 12638 | 45596 | 14965 | 2024-05-16
|  |  | 19:30 |  | 20:00 |  | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-10-01 | 44 | 2025-09-05 | 0 | 45569 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 14115.2 | 2025-10-01 | 15064.21 | 2025-09-05 | 12218 | 2024-10-04 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 381 | 2025-10-21 | 318 | 2025-09-10 | 760 | 45567 | - | -
|  |  | 12:00 Hr. |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 13404.96 | 2025-10-21 | 14471.36 | 2025-09-10 | 12704 | 45567 | - | -
|  |  | 12:00 Hr. |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-10-01 | 23 | 2025-09-06 | 0 | 45569 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 11978.24 | 2025-10-01 | 13309.84 | 2025-09-06 | 10526 | 45569 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 23 |  | 30 |  | 23 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 14 |  | 15 |  | 22 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1137.6177 |  | 1248.3832 |  | 1472.1777 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 26.7752 |  | 30.8707 |  | 58.8403 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1110.8425 |  | 1217.5125 |  | 1413.3374 |  | - | -
23 | Net Generation of IPP (MKWH) | 2815.9484 |  | 2978.8553 |  | 2911.4144 |  | - | -
23b | Net Generation by Generation Companies | 3978.1653 |  | 4245.3018 |  | 2897.3002
24 | Net Generation of REB (MKWH) | 46.923 |  | 44.7809 |  | 93.2436 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 113.3794 |  | 139.669 |  | 131.2355 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 8065.2585 |  | 8626.1194 |  | 7446.531 |  | - | -
27 | Energy Generation by Gas (MKWH) | 3762.6905 |  | 4025.2813 |  | 3827.7099 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 0.006 |  | 23.9372 |  | 21.0254 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 1037.4024 |  | 1216.6848 |  | 1145.4273 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 161.6253 |  | 156.2217 |  | 143.6604 |  | - | -
31 | Energy Generation by Solar (MKWH) | 120.6303 |  | 119.0925 |  | 94.1464 |  | - | -
31b | Energy Generation by Wind (MKWH) | 2.9122 |  | 4.9805 |  | 4.2288 |  | - | -
32 | Energy Generation by Coal (MKWH) | 3006.767 |  | 3110.7922 |  | 2269.173 |  | - | -
33 | Enegry Import from India (MKWH) | 1576.7518 |  | 1483.7987 |  | 1444.8078 |  | - | -
34 | Monthly Load Factor (%) | 83.0661 |  | 86.5189 |  | 81.9637 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: October 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 15644.99 | 2025-10-27 | 19:00 Hr.
Generation Period
| Dhaka | MW | 5564.54
| Chattogram | MW | 1570.9
| Cumilla | MW | 1477.15
| Mymensingh | MW | 1098
| Sylhet | MW | 645
a) | Total supply in East zone | MW | 10355.59
| Khulna | MW | 1789
| Barisal | MW | 474
| Rajshahi | MW | 1395.6
| Rangpur | MW | 881
b) | Total supply in West zone | MW | 4539.6
c) | Total supply in both zone ( a+b) | MW | 14895.19
Ref: | 27.21.0000.603.16.087.20.942 | Date: 16/11/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 678 | 2025-10-01 | 8:00
|  | MW | 268
| b) Ghorashal end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 0 | - | -
|  | MW | 0
| b) Ghorashal end | AMPS | 672 | 2025-10-01 | 8:00
|  | MW | 252
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 6329.6 | 2025-10-06 | N/A
| b) Ghorashal end | MWh | 0 | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0 | -
| b) Ghorashal end | MWh | 6232.4 | 2025-10-06 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 118071.1292
| b) Ghorashal end | MWh | 0
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 114528.9953
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1940 | 2025-10-27 | 15:00
|  | MW | 740
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Serajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur | AMPS | 1940 | 2025-10-27 | 15:00
|  | MW | 704
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Serajganj end | MWh | 15440 | 2025-10-05 | 15:00
| b) Sreepur | MWh | 0
27 | Daily Maximum Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | - | - | -
28 | Total Energy Export through EWI/ NO-2
| a)Serajganj end | MWh | 425886 | - | -
| b) Sreepur | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | 411968 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 3.27 | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 3152 | 2025-10-22 | 23:00
|  | MW | 1958
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 3145 | 2025-10-22 | 23:00
|  | MW | 1957
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 41980 | 2025-10-22 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 41860 | 2025-10-22
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1095990
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1067015
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 2.644
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Tr-1(404T) | 2025-10-09 08:20 | 2025-10-09 09:54 | 0.065278 | E/O | 33 KV Bus section-1 shutdown for feeder maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-10-04 20:40 | 2025-10-04 22:25 | 0.072917 | E/O | 33/11 kv T4 Red hot | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-10-09 20:39 | 2025-10-09 21:54 | 0.052083 | E/O | 33 kv 33/11 kv Tr-4 (PDB) DS red hot maintenance. | 15 | 18.75 | Power interruption
Satmasjid 132/33kV | 132/33 KV Transformer-2 | 2025-10-15 11:10 | 2025-10-15 16:45 | 0.23264 | E/O | Auxiliary Transfformer 2 maintenances | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-10-04 07:40 | 2025-10-04 10:07 | 0.10208 | E/O | Breaker Maintenance. | 36 | 88.2 | Power interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2025-10-18 06:57 | 2025-10-18 09:32 | 0.10764 | E/O | Red Hot Maintenance (Bhalika-02) | 0 | 0 | No interruption
Tangail 132/33kV | Tr-3 | 2025-10-04 07:11 | 2025-10-04 09:26 | 0.09375 | E/O | Maintenance 33kv bus rising of ghatail feeder. | 47 | 105.75 | Power interruption
Tangail 132/33kV | Tr-2 | 2025-10-11 19:56 | 2025-10-11 20:54 | 0.040278 | E/O | 33kv bus high temperature | 50 | 48.3333 | Power interruption
Tangail 132/33kV | Tr-4 | 2025-10-11 19:56 | 2025-10-11 20:56 | 0.041667 | E/O | 33kv bus high temperature | 20 | 20 | Power interruption
|  |  | Total : | 0.80833 |  | Unserved Energy: |  | 281.0333
Dhaka (South) Grid Circle :
Nawabganj 132/33kV | TR-2 | 2025-10-14 21:00 | 2025-10-14 21:07 | 0.0048611 | T | For 33 kv pbs agla feeder. Overcurrent Protection P142. | 0 | 0 | No interruption
Shyampur 230/132kV | Bus-1 (132kV) | 2025-10-23 07:56 | 2025-10-23 07:56 | 0 | T | Bus Differential BB protection | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-2 | 2025-10-23 13:17 | 2025-10-23 20:41 | 0.30833 | E/O | 132 kv main Bus side D/S-221 R-Phase Finger Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 0.31319 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Dohazari 132/33kV | Power Transformer -T-2 | 2025-10-10 16:54 | 2025-10-10 17:19 | 0.017361 | T | Due to Bandarban 33kv Feeder Lockout Relay-K861 Lockout Relay-K862 | 52 | 21.6667 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2025-10-18 10:35 | 2025-10-18 10:44 | 0.00625 | T | Due to Patiya 33 Kv Feeder. General Trip, Phase A, B, C. 51/50-O/C Trip | 10 | 1.5 | Power interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-10-03 05:30 | 2025-10-03 12:40 | 0.29861 | T | PDB 33kv fault RET-670 RET -650 | 0 | 0 | No interruption
Agrabad 132/33kV | MTR-02 (416T) | 2025-10-26 07:35 | 2025-10-26 08:42 | 0.046528 | E/O | 132/33 KV MTR-2(416T) shutdown,purpose of Auxiliary Transformer-2 red phase barrel fuse replacement.No loadshed will happen.Load will be flow by MTR-1 (406T) | 0 | 0 | No interruption
Bakulia 132/33kV | T-3 (422T) | 2025-10-10 00:57 | 2025-10-10 02:18 | 0.05625 | E/O | Emergency maint.work | 20 | 27 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-10-21 22:30 | 2025-10-21 23:32 | 0.043056 | E/O | keranihut feeder 33kv redhot maintanance | 71 | 73.3667 | Power interruption
Hathazari 230/132/33kV | MT-01 | 2025-10-25 22:54 | 2025-10-26 20:40 | 0.90694 | E/O | Trip coil fault | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-10-05 07:22 | 2025-10-05 08:19 | 0.039583 | E/O | Due to temperature rise of Y-ph 33 KB incomer breaker -1. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-10-12 07:11 | 2025-10-12 08:57 | 0.073611 | E/O | Due to high temp DS (Y &B ph and 33 KV cable connector) maintenance. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-10-12 09:13 | 2025-10-12 10:03 | 0.034722 | E/O | high temperature on 33kv bus DS | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-10-19 12:10 | 2025-10-19 14:04 | 0.079167 | E/O | Isolator maintenance | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-10-28 07:37 | 2025-10-28 09:55 | 0.095833 | E/O | পাওয়ার ট্রান্সফরমার -২ এর LT সাইডে Bus side- DS & 33 KV cable connector high ট্যাম্প: জনিত মেরামত কাজের জন্য। | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-2 | 2025-10-31 17:16 | 2025-10-31 19:55 | 0.11042 | E/O | 33kV Bus-2 Shutdown due to Emergency Maintenance work khagrachari -2 33kV Feeder | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-10-19 13:21 | 2025-10-19 15:49 | 0.10278 | E/O | baraulia incoming feeder trip from baraulia S/S . | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2025-10-19 13:23 | 2025-10-19 15:51 | 0.10278 | E/O | baraulia incoming feeder trip from baraulia S/S . | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-03 | 2025-10-19 13:25 | 2025-10-19 15:53 | 0.10278 | E/O | baraulia incoming feeder trip from baraulia S/S . | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2025-10-18 09:01 | 2025-10-18 12:57 | 0.16389 | E/O | 33 Kv bus maintenance by PBS and PDB. | 15 | 59 | Power interruption
Madunaghat 132/33kV | 132kV BUS | 2025-10-21 21:09 | 2025-10-21 21:47 | 0.026389 | E/O | According to the instructions of NLDC. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 07:22 |  | Unserved Energy: |  | 182.5333
Cumilla Grid Circle :
Brahmanbaria 132/33kV | 403T | 2025-10-24 12:55 | 2025-10-24 13:30 | 0.024306 | T | OC/EF, | 17 | 9.9167 | Power interruption
Brahmanbaria 132/33kV | 402T | 2025-10-31 14:50 | 2025-10-31 15:05 | 0.010417 | T | OC/ EF OC/ EF | 50 | 12.5 | Power interruption
Daudkandi 132/33kV | Transformer-2 | 2025-10-11 09:40 | 2025-10-11 10:11 | 0.021528 | T | Overcurrent earth fault Flashing occurred at 33KV switchyard (PBS-3) Overcurrent relay | 30 | 15.5 | Power interruption
Daudkandi 132/33kV | Transformer-1 | 2025-10-11 09:40 | 2025-10-11 14:51 | 0.21597 | T | Overcurrent earth fault Flashing occurred at 33KV switchyard (PBS-3) Overcurrent relay | 30 | 155.5 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2025-10-11 09:40 | 2025-10-11 10:10 | 0.020833 | T | Overcurrent earth fault Flashing occurred at 33KV switchyard (PBS-3) Overcurrent relay | 30 | 15 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-06 12:56 | 2025-10-06 13:18 | 0.015278 | T | Shaistaganj Feeder Fault Locout Relay O/C,E/F Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-06 12:56 | 2025-10-06 13:15 | 0.013194 | T | Shaistaganj Feeder Lockout Relay, O/C,E/F Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-22 12:03 | 2025-10-22 12:16 | 0.0090278 | T | Jamuna Feeder Fault Lockout Relay O/C,E/F Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-22 12:03 | 2025-10-22 12:16 | 0.0090278 | T | Jamuna Feeder fault Lockout Realy ,O/C,E/F | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-27 12:20 | 2025-10-27 13:16 | 0.038889 | T | Flashing in 33kv switchyard bus O/C,E/F | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-27 12:20 | 2025-10-27 12:47 | 0.01875 | T | Flashing in 33kv switchyard bus Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-30 01:22 | 2025-10-30 02:03 | 0.028472 | T | Chunarughat Feeder Trip Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-30 01:22 | 2025-10-30 02:03 | 0.028472 | T | Chunarughat Feeder Trip Trip Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-10-30 01:22 | 2025-10-30 02:05 | 0.029861 | T | Shaitaganj and Habiganj Bypass Feeder Trip Non | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-31 07:14 | 2025-10-31 07:43 | 0.020139 | T | Flashing in 33 kv Bus OC/EF Relay, Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-31 17:51 | 2025-10-31 18:15 | 0.016667 | T | LA Blast of Bisic Feeder under PBS OC/EF Relay, Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-31 17:51 | 2025-10-31 18:28 | 0.025694 | T | LA Blast of Bisic Feeder under PBS OC/EF Relay, Lockout Relay | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2025-10-09 08:12 | 2025-10-09 09:33 | 0.05625 | E/O | Shutdown for T-3 GCB hydraulic oil leakage problem. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR1-415T | 2025-10-01 09:56 | 2025-10-01 10:31 | 0.024306 | E/O | STATION AUXILIARY TR-01 FUSE REPLACEMENT | 30 | 17.5 | Power interruption
Chowmuhani 132/33kV | TR3-435T | 2025-10-29 14:40 | 2025-10-29 16:40 | 0.083333 | E/O | lakshmipur 33kv feeder isolator maintenance | 35 | 70 | Power interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-16 14:52 | 2025-10-16 17:35 | 0.11319 | E/O | Energy Meter Division work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-20 14:08 | 2025-10-20 15:01 | 0.036806 | E/O | Auxiliary Energy Meter connection | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-1 | 2025-10-11 12:38 | 2025-10-11 14:50 | 0.091667 | E/O | Flushing occurred at 33KV switchyard (PBS-3). Need maintenance | 30 | 66 | Power interruption
Kachua 230/132/33kV | TR-1 | 2025-10-11 08:00 | 2025-10-11 11:00 | 0.125 | E/O | Emergency maintenance work | 15 | 45 | Power interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-10-12 10:04 | 2025-10-12 10:32 | 0.019444 | E/O | Sf6 gas refill of 33 KB CB works. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 02:19 |  | Unserved Energy: |  | 406.9167
Khulna Grid Circle :
Barishal 132/33kV | T-2 (415T) | 2025-10-14 14:21 | 2025-10-14 14:25 | 0.0027778 | T | 33 kv kasipur feeder fault. Over current | 40 | 2.6667 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-10-24 01:25 | 2025-10-24 01:30 | 0.0034722 | T | Due to polashpur 33 kV feeder WZPDCL O/C | 60 | 5 | Power interruption
Patuakhali 132/33kV | 415T (T-2) | 2025-10-02 23:09 | 2025-10-02 23:29 | 0.013889 | T | Due to Amtoli 33kv O/C, E/F with heavy flashing at the underground cable tip. O/C | 23 | 7.6667 | Power interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-10-02 23:09 | 2025-10-02 23:29 | 0.013889 | T | Due to Amtoli 33kv O/C, E/F with heavy flashing at the underground cable tip. O/C | 23 | 7.6667 | Power interruption
Barishal 230/132kV | T-5 | 2025-10-17 06:50 | 2025-10-17 16:21 | 0.39653 | E/O | Differtial trip due to 33kv feeder fault | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2025-10-05 16:44 | 2025-10-05 17:57 | 0.050694 | E/O | Red hot maintenance for PBS | 10 | 12.1667 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2025-10-20 09:45 | 2025-10-20 12:58 | 0.13403 | E/O | For PBS work, PT metering, core check and bus maintenance | 10 | 32.1667 | Power interruption
Goalpara 132/33kV | T-6 | 2025-10-27 09:10 | 2025-10-28 10:30 | 1899-12-31 01:20 | E/O | Bad Noise Heard in 33 kV side PT(R-Phase) | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 16:06 |  | Unserved Energy: |  | 67.3333
HVDC Grid Circle :
Ishurdi 132/33kV | 132/33 kV T-3 | 2025-10-09 11:40 | 2025-10-09 21:57 | 0.42847 | T | REF/SEF TRP | 33 | 339.35 | Power interruption
Kushtia 132/33kV | T2 | 2025-10-04 13:22 | 2025-10-04 13:46 | 0.016667 | T | Poradah feeder trip 50/51 trip, O/C DMT -1 | 0 | 0 | No interruption
BIPTC | 20DF31 | 2025-10-03 17:45 | 2025-10-03 20:17 | 0.10556 | T | None | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-10-11 06:58 | 2025-10-11 16:46 | 0.40833 | T | Tripped by C1 unbalance 60/61 CPR04 | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-10-11 15:42 | 2025-10-11 17:03 | 0.05625 | T | Dead bird has been found inside the fence. | 0 | 0 | No interruption
BIPTC | 10CF14 | 2025-10-12 11:28 | 2025-10-12 12:36 | 0.047222 | T | C1 unbalance 60/61 instant L2 trip | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-10-12 13:29 | 2025-10-12 16:55 | 0.14306 | T | C1 unbalance 60/61 CPR04 tripped | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-10-12 18:45 | 2025-10-13 13:25 | 0.77778 | T | tripped by C1 Unbalanced 60/61 | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-10-21 17:10 | 2025-10-22 11:23 | 0.75903 | T | A dead bird has been noticed inside the fence area. | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-10-30 15:29 | 2025-10-30 16:19 | 0.034722 | T | Tripped by zero sequence overcurrent. | 0 | 0 | No interruption
BIPTC | 20DF31 | 2025-10-03 19:40 | 2025-10-03 20:17 | 0.025694 | E/O | None | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-10-26 12:23 | 2025-10-26 13:21 | 0.040278 | E/O | 10CF25 tripped | 0 | 0 | No interruption
Bhangura 132/33kV | 33KV Single Bus | 2025-10-06 21:30 | 2025-10-06 22:22 | 0.036111 | E/O | Red hot remove | 37 | 32.0667 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-10-23 16:04 | 2025-10-23 17:50 | 0.073611 | E/O | remove red hot T2 33 kv bus | 10 | 17.6667 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-03 | 2025-10-11 14:43 | 2025-10-11 15:04 | 0.014583 | E/O | LT side breaker problem | 0 | 0 | No interruption
Jashore 132/33kV | T-1 | 2025-10-06 15:46 | 2025-10-06 17:49 | 0.085417 | E/O | 33kv busbur PBS riser maintanence. | 10 | 20.5 | Power interruption
Jashore 132/33kV | T-3 | 2025-10-10 07:15 | 2025-10-10 08:02 | 0.032639 | E/O | Emeregency maint.work | 15 | 11.75 | Power interruption
Kushtia 132/33kV | T-1 | 2025-10-18 11:08 | 2025-10-18 12:29 | 0.05625 | E/O | 33kv bus section B-phase red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 03:24 |  | Unserved Energy: |  | 421.3333
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) | 2025-10-08 12:46 | 2025-10-08 13:12 | 0.018056 | T | Fault in Gobratola 33kV feeder. O/C & E/F | 6 | 2.6 | Power interruption
Amnura 132/33kV | T-2 (416T) | 2025-10-08 12:46 | 2025-10-08 13:12 | 0.018056 | T | Fault in Gobratala 33 kV feeder O/C & E/F | 6 | 2.6 | Power interruption
Bogura 132/33kV | Transformer-3 | 2025-10-03 07:44 | 2025-10-03 08:04 | 0.013889 | T | 33 kv PBS Bogura-2 Feeder O/C & E/F Trip. Int. O/C & E/F Trip. | 28 | 9.3333 | Power interruption
Bogura 132/33kV | Transformer-4 | 2025-10-03 07:44 | 2025-10-03 08:04 | 0.013889 | T | 33 kv PBS Bogura-2 Feeder O/C & E/F Trip. Inst. O/C & E/F Trip. | 28 | 9.3333 | Power interruption
Naogaon 132/33kV | T-1 | 2025-10-16 07:40 | 2025-10-16 08:09 | 0.020139 | T | 33kV feeder(NESCO Argi-Naogaon) Trip Inst. E/F | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 | 2025-10-16 07:40 | 2025-10-16 08:04 | 0.016667 | T | 33kV feeder(NESCO Argi-Naogaon) Trip Inst. E/F | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-3(426T) | 2025-10-16 12:10 | 2025-10-16 12:36 | 0.018056 | T | পিবিএস এর হাজীনগর, ফিডারের জন্য ৩৩ কেভি ট্রিপ করে। SIMENS SIPROTEC, 7SJ81 Y phase IDMT Earth Fault Trip | 8 | 3.4667 | Power interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2025-10-08 23:36 | 2025-10-09 00:02 | 0.018056 | T | Feeder fault Siprotec siemens | 35 | 15.1667 | Power interruption
Rahanpur 400/132kV | AT-02 | 2025-10-03 02:41 | 2025-10-05 17:44 | 1900-01-01 15:03 | T | 87 Trip,R PH Trip,GEN Trip SIEMENS | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 132/33 kV T-01 (406T) | 2025-10-31 21:46 | 2025-10-31 22:11 | 0.017361 | T | NESCO FAULTY FEEDER TRIAL REF630 | 37.5 | 15.625 | Power interruption
Rajshahi 230/132/33kV | 132/33 kV T-02 (416T) | 2025-10-31 21:46 | 2025-10-31 22:12 | 0.018056 | T | NESCO faulty feeder trail REF630 | 37.5 | 16.25 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-10-04 20:02 | 2025-10-04 21:12 | 0.048611 | E/O | Red hot maintenance work | 18 | 21 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-10-15 08:18 | 2025-10-15 11:10 | 0.11944 | E/O | Emergency red hot maintenance. | 25 | 71.6667 | Power interruption
Bogura 132/33kV | Transformer-4 | 2025-10-04 09:37 | 2025-10-04 11:32 | 0.079861 | E/O | Red hot maintenance 33 kv side in CT | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-10-06 11:03 | 2025-10-06 12:37 | 0.065278 | E/O | For 33kV incomer CT (B-phase) red-hot maintenance work. | 12 | 18.8 | Power interruption
Mithapukur 132/33kV | TR-1(404T) | 2025-10-07 10:25 | 2025-10-07 11:59 | 0.065278 | E/O | T- 1 Shutdown due to red-hot maintenance work in Shodor doptor 33kv feeder by PBS-01. | 25.6 | 40.1067 | Power interruption
Naogaon 132/33kV | T-3 | 2025-10-02 21:30 | 2025-10-02 23:20 | 0.076389 | E/O | Atrai 33kv feeder jamper maintenance which is connected under T3(132/33kv) 33kv Bus.All loadshed purpose of the feeder . | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-10-07 07:09 | 2025-10-07 09:27 | 0.095833 | E/O | Red hot maintenance (Atrai 33kV feeder) | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-10-08 13:07 | 2025-10-08 13:13 | 0.0041667 | E/O | NESCO Auxiliary Transformer DS maintenance | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-10-08 23:48 | 2025-10-09 01:35 | 0.074306 | E/O | Baludanga 33kv feeder's 33kv Bus DS Red hot manitenance. | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2025-10-26 19:34 | 2025-10-26 20:45 | 0.049306 | E/O | PBS 33kV Niamatpur-2 feeder source DS R-Phase Red Hot Maintenance | 32 | 37.8667 | Power interruption
Panchagarh 132/33kV | T-1(407T) | 2025-10-06 13:13 | 2025-10-06 14:46 | 0.064583 | E/O | Red hot of 33kV bus section 01 Y-Phase | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2025-10-08 13:12 | 2025-10-08 17:14 | 0.16806 | E/O | Kaunia feeder fault & 33 Bus l A fault & PT problem one phase | 50 | 201.6667 | Power interruption
Saidpur 132/33kV | TR-3 (424T) | 2025-10-24 07:21 | 2025-10-24 09:22 | 0.084028 | E/O | CT clamp replacement | 12 | 24.2 | Power interruption
Sirajganj 132/33kV | T1-(415) | 2025-10-26 22:34 | 2025-10-26 23:27 | 0.036806 | E/O | Sirajgonj PBS-2 has taken S/D on an emergency basis due to Mulibari 33kV Feeder Red Hot maintenance(33kV BUS DS-R-Phase) | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 19:57 |  | Unserved Energy: |  | 489.6817
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-12 04:03 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Mirpur-01 | 2025-10-08 02:09 | 2025-10-08 04:10 | 0.084028 | T | Trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Mirpur-02 | 2025-10-08 02:09 | 2025-10-08 02:52 | 0.029861 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2025-10-05 19:48 | 2025-10-05 20:04 | 0.011111 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-10-07 13:38 | 2025-10-07 13:53 | 0.010417 | T | Trip by R-Y phase, Zone 01 | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2025-10-07 13:38 | 2025-10-07 13:53 | 0.010417 | T | Trip by R-Y phase, Zone 01 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2025-10-15 10:37 | 2025-10-15 11:17 | 0.027778 | T | Trip | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2025-10-18 09:56 | 2025-10-18 19:13 | 0.38681 | T | general trip, 21 Trip, 67N | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-1 | 2025-10-03 05:54 | 2025-10-03 06:45 | 0.035417 | T | Zone-2 | 72 | 61.2 | Power interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-2 | 2025-10-03 05:54 | 2025-10-03 06:52 | 0.040278 | T | Zone-2 | 18 | 17.4 | Power interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-10-08 02:12 | 2025-10-08 02:58 | 0.031944 | T | Tripped due to fault. | 95 | 72.8333 | Power interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-10-27 09:55 | 2025-10-27 17:15 | 0.30556 | E/O | Work in Meghnaghat end | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-10-27 09:55 | 2025-10-27 17:15 | 0.30556 | E/O | Work in Meghnaghat end | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2025-10-20 09:00 | 2025-10-20 09:38 | 0.026389 | E/O | NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2025-10-20 10:21 | 2025-10-20 17:54 | 0.31458 | E/O | Due to annual maintenance by NLDC | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2025-10-10 14:34 | 2025-10-10 16:49 | 0.09375 | E/O | Red Hot maintenance work Main Bus loop Y Phase . | 0 | 0 | No interruption
Muktagacha 132/33kV | Ghatail-1 | 2025-10-18 13:15 | 2025-10-18 13:49 | 0.023611 | E/O | Switching complete as per the instructions of NLDC AE | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2025-10-13 07:26 | 2025-10-13 09:05 | 0.06875 | E/O | Red hot maintenance in Bhaluka End | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2025-10-16 11:16 | 2025-10-16 12:57 | 0.070139 | E/O | RED HOT | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2025-10-18 06:45 | 2025-10-18 09:56 | 0.13264 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2025-10-23 07:32 | 2025-10-23 08:51 | 0.054861 | E/O | Red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 01:32 |  | Unserved Energy: |  | 151.4333
Dhaka (South) Grid Circle :
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-10-01 02:16 | 2025-10-01 02:55 | 0.027083 | T | General Trip, R,Y,B PH Trip, Zone-1 Trip | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-10-15 12:05 | 2025-10-15 12:42 | 0.025694 | T | Unknown | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-10-02 12:10 | 2025-10-02 13:21 | 0.049306 | T | None | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2025-10-01 02:16 | 2025-10-01 03:23 | 0.046528 | T | Storm and heavy rain | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2025-10-01 02:16 | 2025-10-01 03:23 | 0.046528 | T | Storm and heavy rain | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2025-10-01 02:16 | 2025-10-01 03:23 | 0.046528 | T | Storm and heavy rain | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2025-10-01 02:16 | 2025-10-01 03:23 | 0.046528 | T | Storm and heavy rain | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2025-10-17 12:14 | 2025-10-17 17:08 | 0.20417 | T | due to faulty 21 distance zone =03 R,Y phase,IL1=5.86kA,IL2=4.88kA | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-1 | 2025-10-01 02:16 | 2025-10-01 04:23 | 0.088194 | T | Line 01 trip at Keraniganj source S/S B-phase, O/C, Zone 1, Fault Location -12.45 km. | 23 | 48.6833 | Power interruption
Nawabganj 132/33kV | Keraniganj-2 | 2025-10-01 02:16 | 2025-10-01 04:27 | 0.090972 | T | Line 02 trip at the Keraniganj source S/S, R phase, O/C, Zone 01, Fault location 12.45 km. | 23 | 50.2167 | Power interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2025-10-23 07:56 | 2025-10-23 07:56 | 0 | T | Over Current, Distance Zone 1 | 0 | 0 | No interruption
Maniknagar 132/33kV | Matuail Single Ckt | 2025-10-18 05:57 | 2025-10-18 05:57 | 0 | E/O | Red hot at Matuail ss | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Madunaghat 400KV Ckt-2 | 2025-10-06 11:18 | 2025-10-06 11:52 | 0.023611 | E/O | Forced shutdown due to flushing at DS point. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Madunaghat 400KV Ckt-1 | 2025-10-06 12:39 | 2025-10-06 16:02 | 0.14097 | E/O | Forced shutdown due to flushing at DS point. | 0 | 0 | No interruption
Siddhirganj 132/33kV | Matuail | 2025-10-18 03:01 | 2025-10-18 05:23 | 0.098611 | E/O | Due to red hot at Matuail (DPDC) Substation Ending. | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2025-10-28 11:47 | 2025-10-28 12:00 | 0.0090278 | E/O | Tap change | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2025-10-29 19:16 | 2025-10-29 19:16 | 0 | E/O | NLDC instruction. | 0 | 0 | No interruption
Sonargaon 132/33kV | Bashundhara Line | 2025-10-31 11:30 | 2025-10-31 13:30 | 0.083333 | E/O | Red hot maintenance | 3 | 6 | Power interruption
|  |  | Total : | 1899-12-31 00:39 |  | Unserved Energy: |  | 104.9
Chattogram Grid Circle :
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-01 | 2025-10-10 21:13 | 2025-10-10 22:23 | 0.048611 | T | Thundering | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-02 | 2025-10-10 21:13 | 2025-10-10 22:22 | 0.047917 | T | Thundering | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2025-10-06 17:15 | 2025-10-06 17:21 | 0.0041667 | T | Unexpected | 0 | 0 | No interruption
Baroaulia 132/33kV | KSRM | 2025-10-19 13:18 | 2025-10-19 15:46 | 0.10278 | T | A tree fell across the power line. | 20 | 49.3333 | Power interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2025-10-10 10:42 | 2025-10-10 12:33 | 0.077083 | T | Tripped | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-02 | 2025-10-26 15:34 | 2025-10-27 13:42 | 0.92222 | T | Tripped | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-2 | 2025-10-26 07:44 | 2025-10-26 13:22 | 0.23472 | T | Over Current | 15 | 84.5 | Power interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2025-10-06 11:24 | 2025-10-06 11:59 | 0.024306 | T | Rangamati Ckt-02 tripped due to thundering. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-2 | 2025-10-26 15:34 | 2025-10-27 13:43 | 0.92292 | T | General trip,Zone-01,y-phase fault | 0 | 0 | No interruption
Shikalbaha 230/132kV | Bakulia-1 | 2025-10-10 21:21 | 2025-10-10 21:21 | 0 | T | Tripped | 0 | 0 | No interruption
Baroaulia 132/33kV | KSRM | 2025-10-19 14:13 | 2025-10-19 15:46 | 0.064583 | E/O | A tree fell across the power line. | 20 | 31 | Power interruption
Baroirhat 132/33kV | Hat-1 | 2025-10-21 20:35 | 2025-10-21 21:42 | 0.046528 | E/O | Order by NLDC | 0 | 0 | No interruption | #DIV/0!
Baroirhat 132/33kV | Hat-2 | 2025-10-21 20:36 | 2025-10-21 21:42 | 0.045833 | E/O | Order by NLDC | 0 | 0 | No interruption
KSRM 132/33kV | Baraulia Main | 2025-10-19 13:20 | 2025-10-19 15:48 | 0.10278 | E/O | baraulia incoming feeder trip from baraulia S/S . | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 15:28 |  | Unserved Energy: |  | 164.8333
Cumilla Grid Circle :
Bibiana 400/230kV | Bibi-Kalia Ckt-I | 2025-10-15 10:35 | 2025-10-15 11:17 | 0.029167 | T | EF COM Trip | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Kalia Ckt-I | 2025-10-18 09:55 | 2025-10-18 19:14 | 0.38819 | T | Zone-1 Zcom TRIP AR OPTD EFcom TRIP | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-10-06 13:29 | 2025-10-06 14:22 | 0.036806 | T | Tripped | 21 | 18.55 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2025-10-06 13:29 | 2025-10-06 14:22 | 0.036806 | T | Tripped | 20 | 17.6667 | Power interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-1 | 2025-10-24 06:58 | 2025-10-24 06:58 | 0 | E/O | As per instruction of NLDC | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-2 | 2025-10-24 06:59 | 2025-10-24 06:59 | 0 | E/O | As per instruction of NLDC | 0 | 0 | No interruption
Bibiana 400/230kV | Bibiyana-South | 2025-10-29 15:25 | 2025-10-29 15:25 | 0 | E/O | maintenance at bibiayana south | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-5 section | 2025-10-09 08:07 | 2025-10-09 09:43 | 0.066667 | E/O | Auxiliary transformer fuse maintenance. | 25 | 40 | Power interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-10-09 10:10 | 2025-10-09 17:29 | 0.30486 | E/O | Order by NLDC | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-10-12 09:33 | 2025-10-12 18:58 | 0.39236 | E/O | order by NLDC | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-10-15 09:20 | 2025-10-15 20:55 | 0.48264 | E/O | Order by NLDC | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR1 | 2025-10-18 16:40 | 2025-10-18 18:02 | 0.056944 | E/O | 132/33 KV Tr-01 X-former Emergency shutdown today from 16:40 to 17:40 for Zine pole Remove Work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-10-05 07:38 | 2025-10-09 17:26 | 1900-01-03 09:48 | E/O | Shoutdown for feni 230KV side LILO connection | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla South CKT | 2025-10-08 10:05 | 2025-10-08 17:38 | 0.31458 | E/O | Shutdown was taken by Cumilla south. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 12:25 |  | Unserved Energy: |  | 76.2167
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-10-05 08:33 | 2025-10-05 08:55 | 0.015278 | T | Unknown | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-10-07 15:30 | 2025-10-08 13:50 | 0.93056 | T | 0 | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-2 | 2025-10-08 14:23 | 2025-10-08 16:28 | 0.086806 | T | Due to bad weather. | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-02 | 2025-10-08 14:23 | 2025-10-08 16:27 | 0.086111 | T | None | 0 | 0 | No interruption
Benapole 132/33kV | Jashore-2 | 2025-10-29 15:42 | 2025-10-29 16:30 | 0.033333 | T | Thundering | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Orion | 2025-10-03 11:47 | 2025-10-03 21:47 | 0.41667 | T | Y to N phase Earth fault | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-09 10:52 | 2025-10-09 17:03 | 0.25764 | T | Line Deferential fault. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rupsha Ckt-1 | 2025-10-21 13:22 | 2025-10-21 13:22 | 0 | T | 0 | 0 | 0 | No interruption
Madaripur 132/33kV | Shariatpur CKT-02 | 2025-10-06 18:49 | 2025-10-06 19:29 | 0.027778 | T | lightning | 0 | 0 | No interruption
Shariatpur 132/33kV | Madaripur-Shariatpur CKT-02 | 2025-10-06 18:49 | 2025-10-06 19:31 | 0.029167 | T | Distance Trip(Main Protection Operate) Zone-1 Trip | 0 | 0 | No interruption
Barishal 230/132kV | Bhola Ckt-1 | 2025-10-07 11:23 | 2025-10-07 14:01 | 0.10972 | E/O | Pole discrimincy at Bhola end. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2025-10-20 09:04 | 2025-10-20 11:22 | 0.095833 | E/O | Emergency Maintenance Work at Central SS end. | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-10-08 08:40 | 2025-10-08 13:56 | 0.21944 | E/O | Maintenance work of Bagerhat -Mongla line-1 due to its R-Phase conductor rupture. | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-10-18 05:58 | 2025-10-18 07:41 | 0.071528 | E/O | Red hot at Bagerhat Grid | 12 | 20.6 | Power interruption
Mongla 132/33kV | Bagerhat-Mongla Line-2 | 2025-10-18 05:59 | 2025-10-18 07:41 | 0.070833 | E/O | Red hot maintenance at Bagerhat Grid | 12 | 20.4 | Power interruption
Mongla 132/33kV | 100MW ERBL Solar PS | 2025-10-18 05:59 | 2025-10-18 07:40 | 0.070139 | E/O | Redhot maintenance at Bagerhat grid | 1 | 1.6833 | Power interruption
|  |  | Total : | 1900-01-01 12:30 |  | Unserved Energy: |  | 42.6833
HVDC Grid Circle :
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2025-10-15 17:22 | 2025-10-15 18:32 | 0.048611 | T | SPMD testing work time. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-10-01 07:09 | 2025-10-01 08:49 | 0.069444 | T | None | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-10-01 02:16 | 2025-10-01 02:55 | 0.027083 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-10-15 12:05 | 2025-10-15 12:35 | 0.020833 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | BEN-2 | 2025-10-29 15:42 | 2025-10-29 16:29 | 0.032639 | T | Tripped | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Bghabari-2 | 2025-10-07 11:45 | 2025-10-07 13:05 | 0.055556 | E/O | Red hot maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 0.25417 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2025-10-09 12:56 | 2025-10-09 13:49 | 0.036806 | T | Thundering | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-10-27 21:36 | 2025-10-27 22:34 | 0.040278 | T | Saidpur end 132KV Lightning Arrester blast of B-phase | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-10-10 15:04 | 2025-10-15 18:59 | 1900-01-04 03:55 | T | Tripped | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-10-28 16:11 | 2025-10-30 09:59 | 1899-12-31 17:48 | T | None | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2025-10-04 12:48 | 2025-10-04 13:50 | 0.043056 | T | Thunderstorm | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 2 | 2025-10-31 22:47 | 2025-10-31 22:59 | 0.0083333 | T | Thundering | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-1 | 2025-10-10 15:04 | 2025-10-15 19:00 | 1900-01-04 03:56 | T | Unknown. | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon-1 | 2025-10-05 04:58 | 2025-10-05 05:22 | 0.016667 | T | Tripped | 25 | 10 | Power interruption
Purbasadipur 132/33kV | Thakurgaon Line-2 | 2025-10-05 06:50 | 2025-10-05 07:19 | 0.020139 | T | Heavy rain and thundering. | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2025-10-05 06:57 | 2025-10-05 07:23 | 0.018056 | T | Heavy rain and thundering | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-10-01 08:07 | 2025-10-01 09:51 | 0.072222 | T | tripping | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2025-10-05 10:24 | 2025-10-05 10:42 | 0.0125 | T | Due to heavy rain thundering and lightning. | 10 | 3 | Power interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2025-10-06 11:33 | 2025-10-06 11:43 | 0.0069444 | T | Unknown | 30 | 5 | Power interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-10-01 08:20 | 2025-10-01 08:45 | 0.017361 | T | Tripped | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Jaldhaka CKT-02 | 2025-10-05 08:19 | 2025-10-05 08:50 | 0.021528 | T | Distance Relay, B-phase, Zone-2 | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-01 | 2025-10-27 21:36 | 2025-10-27 22:33 | 0.039583 | T | Lighting Arrestor ( B phase) Burst | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-1 | 2025-10-05 04:58 | 2025-10-05 05:22 | 0.016667 | T | 905B and 920B Trip by Z2 Alarm (47.9km) during heavy thundering. | 12 | 4.8 | Power interruption
Thakurgaon 132/33kV | Panchagar CKT-2 | 2025-10-05 04:58 | 2025-10-05 05:21 | 0.015972 | T | 923B and 920B Trip by Z2 Alarm (47.9km) during heavy thundering. | 12 | 4.6 | Power interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-10-10 18:20 | 2025-10-15 18:59 | 1900-01-04 00:39 | E/O | Repair & Maintenance of Conductor. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-10-16 10:44 | 2025-10-31 23:58 | 1900-01-14 13:14 | E/O | Direction By NLDC | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-1 | 2025-10-10 18:20 | 2025-10-15 19:00 | 1900-01-04 00:40 | E/O | wire disconnected | 0 | 0 | No interruption
Natore 132/33kV | Bogura-1 | 2025-10-25 15:25 | 2025-10-25 16:05 | 0.027778 | E/O | Emergency maint.work | 0 | 0 | No interruption
Natore 132/33kV | Bogura-2 | 2025-10-25 15:25 | 2025-10-25 16:05 | 0.027778 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rahanpur 132/33kV | Rahanpur-2 | 2025-10-17 09:45 | 2025-10-17 17:39 | 0.32917 | E/O | রহনপুর ৪০০কেভি গ্রিড সাইডে শাটডাউন চেয়েছে। | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-01 | 2025-10-30 07:16 | 2025-10-30 14:08 | 0.28611 | E/O | Line LA Replace | 0 | 0 | No interruption
|  |  | Total : | 1900-02-06 17:34 |  | Unserved Energy: |  | 27.4
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-21 18:14 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2025-10-14 09:54 | 2025-10-16 14:58 | 53:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-03 | 2025-10-16 06:15 | 2025-10-16 08:56 | 2:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2025-10-21 12:15 | 2025-10-21 16:54 | 4:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2025-10-22 14:51 | 2025-10-22 15:56 | 1:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 132 kv Bus 01 | 2025-10-23 08:28 | 2025-10-23 17:07 | 8:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2025-10-26 11:44 | 2025-10-26 15:09 | 3:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 132 kv Bus 02 | 2025-10-27 09:41 | 2025-10-27 16:55 | 7:14 | S/O | Anual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-10-13 06:44 | 2025-10-13 12:05 | 5:21 | S/O | Anual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-2(414T) | 2025-10-13 12:16 | 2025-10-13 15:20 | 3:04 | S/O | Anual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-10-25 09:42 | 2025-10-25 14:07 | 4:25 | S/O | Hot spot remove | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-10-29 10:27 | 2025-10-29 14:43 | 4:16 | S/O | 132kV Tr-1 33kV side LV Bushing oil Leakage. | 0 | 0 | No interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2025-10-04 14:26 | 2025-10-04 17:35 | 3:09 | S/O | 33 kv pbs feeder redhot | 0 | 0 | No interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2025-10-13 07:17 | 2025-10-13 10:56 | 3:39 | S/O | Bay extension by PDB | 15 | 54.75 | Power interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2025-10-18 13:17 | 2025-10-18 14:01 | 0:44 | S/O | Red hot pbs feeder no 16 | 30 | 22 | Power interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2025-10-27 08:53 | 2025-10-27 09:30 | 0:37 | S/O | Maintenance works | 30 | 18.5 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2025-10-21 07:11 | 2025-10-21 11:16 | 4:05 | S/O | Redhot maintenance by PBS. | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-4 | 2025-10-15 13:42 | 2025-10-15 14:07 | 0:25 | S/O | Due to replacement of faulty energy meter of incomer. | 30 | 12.5 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-10-18 16:09 | 2025-10-18 17:33 | 1:24 | S/O | Maintenance works | 100 | 140 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-10-26 10:09 | 2025-10-26 17:53 | 7:44 | S/O | Annual Maintanance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/230kV TR2 | 2025-10-27 13:24 | 2025-10-27 16:42 | 3:18 | S/O | Red Hot Maintenance Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-10-28 09:45 | 2025-10-28 17:25 | 7:40 | S/O | Due to annual maintenance . | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-10-29 08:01 | 2025-10-29 08:01 | 0:00 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-10-19 09:24 | 2025-10-19 17:38 | 8:14 | S/O | Shutdown for annual maintenance. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-10-20 09:44 | 2025-10-20 15:47 | 6:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-10-21 09:30 | 2025-10-21 15:24 | 5:54 | S/O | For annual maintenance work | 0 | 0 | No interruption
Kodda 132/33kV | Bus-2 | 2025-10-29 07:22 | 2025-10-29 07:22 | 0:00 | S/O | Maintenance works | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-10-27 11:28 | 2025-10-27 14:54 | 3:26 | S/O | Painting & 33 Kv Bushing Maintanence | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2025-10-10 08:20 | 2025-10-10 11:20 | 3:00 | S/O | 132/33KV NewT3 Transformer (80/120MVA) loop connecting works. | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-10-10 17:30 | 2025-10-10 21:09 | 3:39 | S/O | Maintenance works | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-10-11 08:24 | 2025-10-11 12:08 | 3:44 | S/O | Project development work | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2025-10-20 08:56 | 2025-10-20 13:10 | 4:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2025-10-21 08:45 | 2025-10-21 12:38 | 3:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2025-10-22 09:15 | 2025-10-22 14:42 | 5:27 | S/O | Annual maintenance work | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2025-10-23 08:40 | 2025-10-24 10:55 | 26:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2025-10-05 11:51 | 2025-10-05 13:59 | 2:08 | S/O | Red hot 33KV bus, PBS side | 10 | 21.3333 | Power interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2025-10-31 06:24 | 2025-10-31 08:57 | 2:33 | S/O | Red hot maintenance | 200 | 510 | Power interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2025-10-31 06:41 | 2025-10-31 08:50 | 2:09 | S/O | Red hot maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-2 | 2025-10-31 09:17 | 2025-10-31 15:52 | 6:35 | S/O | Red hot maintenance works. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2025-10-31 09:20 | 2025-10-31 15:41 | 6:21 | S/O | Red hot maintenance work done. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 | 2025-10-23 14:44 | 2025-10-23 16:18 | 1:34 | S/O | 33 kv shakhipur feeder CT Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 09:47 |  | Unserved Energy: |  | 779.0833
Dhaka (South) Grid Circle :
Haripur 230/132kV | Auto TR-2 | 2025-10-15 12:05 | 2025-10-15 14:10 | 2:05 | S/O | High Tempareture Junction Point Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2025-10-16 09:03 | 2025-10-16 12:31 | 3:28 | S/O | High Tempareture Junction Point Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhult | 2025-10-16 13:13 | 2025-10-16 16:40 | 3:27 | S/O | High temperature junction point maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhult | 2025-10-18 14:30 | 2025-10-18 19:12 | 4:42 | S/O | Another side. | 0 | 0 | No interruption
Haripur 230/132kV | Bus-2 | 2025-10-27 12:57 | 2025-10-27 14:04 | 1:07 | S/O | 230 KV Meghnaghat-2 and 210 MW Siddhirganj PS Bay Isolator finger changing work. | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main Bus | 2025-10-13 13:08 | 2025-10-13 14:22 | 1:14 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-10-23 14:31 | 2025-10-23 17:41 | 3:10 | S/O | 132 kv Reserve Bus D/S Maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Main Bus | 2025-10-24 11:10 | 2025-10-25 13:15 | 26:05 | S/O | Maintenance work of Auto TR-2 main bus D/S. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2025-10-09 08:03 | 2025-10-09 12:34 | 4:31 | S/O | Oil filling at 230/132 KV auto Tr-1(Y-B ) Phase main tank conservatory,132KV side B Phase CT top side connector, 132 KV CB Y Phase over temperature. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-2 | 2025-10-21 07:44 | 2025-10-23 12:51 | 53:07 | S/O | oil centrifusing work. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-2 | 2025-10-24 11:10 | 2025-10-24 12:11 | 1:01 | S/O | fingure change | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2025-10-26 11:09 | 2025-10-26 19:50 | 8:41 | S/O | ATR-3, R-Phase Oil leakage Maintenance | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-1 | 2025-10-04 07:17 | 2025-10-04 10:13 | 2:56 | S/O | High Temperature maintenance at CSE pot | 0 | 0 | No interruption
Keranigonj 230/132/33kV | Earthing Trafo-1 | 2025-10-04 07:20 | 2025-10-04 10:13 | 2:53 | S/O | Maint | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-2 | 2025-10-11 07:24 | 2025-10-11 09:33 | 2:09 | S/O | High maintenance work at cse pot. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 400 kV Bus -01 | 2025-10-06 08:31 | 2025-10-06 17:04 | 8:33 | S/O | Project work shutdown. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 400 kV Bus -02 | 2025-10-07 07:31 | 2025-10-07 17:13 | 9:42 | S/O | 400 kV Bus- 02 shutdown for project work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR-1 | 2025-10-10 06:51 | 2025-10-10 11:26 | 4:35 | S/O | For maintenace work | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 01 | 2025-10-14 09:20 | 2025-10-14 15:07 | 5:47 | S/O | 230 kV Bus Section- 1 shutdown instructed by NLDC. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 400 kV Bus -02 | 2025-10-25 07:35 | 2025-10-25 23:54 | 16:19 | S/O | 400 KV Bus-2 shutdown for project work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 400 kV Bus -01 | 2025-10-27 09:41 | 2025-10-27 17:22 | 7:41 | S/O | Shutdown for project work | 0 | 0 | No interruption
Meghnaghat 400/230kV | 400 kV Bus -02 | 2025-10-28 10:12 | 2025-10-28 14:30 | 4:18 | S/O |  | 0 | 0 | No interruption
Motijheel 132/33kV | GT-2 | 2025-10-18 09:28 | 2025-10-18 09:28 | 0:00 | S/O | 132/33 kV GT-2 Maintenance 132 kV Bus-2 Maintenance 33 kV Bus-2 Maintenance 132 kV Line Protective Relay testing at Maniknagar end | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-10-18 16:35 | 2025-10-18 17:17 | 0:42 | S/O | 33 kV Hasnabad feeder redhot maintenance work. | 18 | 12.6 | Power interruption
Shyampur 132/33kV | Bus-2 | 2025-10-13 08:50 | 2025-10-13 09:56 | 1:06 | S/O | Being a red hood in the isolator will work and reserves on Bus-2 will work. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2025-10-06 09:15 | 2025-10-14 16:57 | 199:42 | S/O | Schedule Shutdown by DPDC. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2025-10-31 07:31 | 2025-10-31 12:56 | 5:25 | S/O | Shutdown taken by DPDC. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-10-10 08:21 | 2025-10-10 12:25 | 4:04 | S/O | 33 kv DS Y phase loop change | 42 | 170.8 | Power interruption
Srinagar 132/33kV | Tr-02 | 2025-10-21 22:20 | 2025-10-21 23:32 | 1:12 | S/O | Red hot at 5 no feeder source side maintenance by Mpbs. | 17 | 20.4 | Power interruption
|  |  | Total : | 1900-01-15 05:42 |  | Unserved Energy: |  | 203.8
Chattogram Grid Circle :
Bakulia 132/33kV | T-4 (432T) | 2025-10-09 14:35 | 2025-10-09 17:35 | 3:00 | S/O |  | 0 | 0 | No interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-10-16 19:07 | 2025-10-16 19:48 | 0:41 | S/O | Due to Keranihat PBS feeder bus ds maintenance. | 60 | 41 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-10-22 20:30 | 2025-10-22 22:23 | 1:53 | S/O | Due to Bandarban 33 Kv feeder red hot maintenance work. | 71 | 133.7167 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2025-10-17 07:34 | 2025-10-19 11:17 | 51:43 | S/O | for checking & painting of the tertiary compartment | 0 | 0 | No interruption
Hathazari 230/132/33kV | 132KV MAIN BUS-02 | 2025-10-03 07:12 | 2025-10-03 11:30 | 4:18 | S/O | G2G Project work. | 70 | 301 | Power interruption
Hathazari 230/132/33kV | MT-01 | 2025-10-03 07:13 | 2025-10-03 11:32 | 4:19 | S/O | G2G project work | 40 | 172.6667 | Power interruption
Hathazari 230/132/33kV | MT-03 | 2025-10-03 07:17 | 2025-10-03 11:30 | 4:13 | S/O | G2G project work | 40 | 168.6667 | Power interruption
Hathazari 230/132/33kV | MT-04 | 2025-10-10 06:30 | 2025-10-10 15:46 | 9:16 | S/O | Project Work shutdown | 0 | 0 | No interruption
Hathazari 230/132/33kV | 132KV MAIN BUS-01 | 2025-10-10 07:12 | 2025-10-10 15:40 | 8:28 | S/O | Project Work shutdown | 0 | 0 | No interruption
Hathazari 230/132/33kV | 132KV MAIN BUS-01 | 2025-10-11 08:18 | 2025-10-11 16:00 | 7:42 | S/O | Project Work Shutdown | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-04 | 2025-10-11 08:20 | 2025-10-11 16:00 | 7:40 | S/O | Project Work Shutdown | 0 | 0 | No interruption
Hathazari 230/132/33kV | 230KV MAIN BUS-01 | 2025-10-17 14:35 | 2025-10-17 16:50 | 2:15 | S/O | Dismantling 230kV Conductor | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-10-28 10:32 | 2025-10-28 13:52 | 3:20 | S/O | 33 kv bushing maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-10-05 06:41 | 2025-10-06 22:52 | 40:11 | S/O | Change sf6 breaker form Barauia S/S | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2025-10-05 06:42 | 2025-10-06 22:50 | 40:08 | S/O | Change SF6 breaker from Baraulia S/S | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-03 | 2025-10-05 06:43 | 2025-10-06 22:59 | 40:16 | S/O | Change SF6 breaker from Baraulia S/S | 0 | 0 | No interruption
Rampur 230/132/33 | TR-1 | 2025-10-23 06:49 | 2025-10-23 14:32 | 7:43 | S/O | Annual maitenance | 0 | 0 | No interruption
Rampur 230/132/33 | ATR-01 (706T) | 2025-10-25 07:17 | 2025-10-25 17:25 | 10:08 | S/O | annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 | ATR-02 (716T) | 2025-10-26 06:55 | 2025-10-26 16:14 | 9:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-01 | 2025-10-28 07:43 | 2025-10-28 16:27 | 8:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-02 | 2025-10-29 07:14 | 2025-10-29 12:57 | 5:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 07:00 |  |  |  | 817.05
Cumilla Grid Circle :
Bibiana 400/230kV | ICT-02 | 2025-10-05 11:24 | 2025-10-05 17:44 | 6:20 | S/O | PRD Maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-02 | 2025-10-06 08:42 | 2025-10-06 16:24 | 7:42 | S/O | Project work | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2025-10-09 12:57 | 2025-10-09 13:39 | 0:42 | S/O | Project work | 7 | 4.9 | Power interruption
Chandina 132/33kV | TR-3 | 2025-10-18 09:27 | 2025-10-18 13:49 | 4:22 | S/O | For Maintenance Purpose. | 2 | 8.7333 | Power interruption
Chandpur 132/33kV | 422T(T-5) | 2025-10-13 15:40 | 2025-10-13 18:59 | 3:19 | S/O | Underground cable leakage removing | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2025-10-13 18:59 | 2025-10-13 18:59 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 | 2025-10-03 20:48 | 2025-10-03 21:57 | 1:09 | S/O | Red hot maintenance for PBS | 35 | 40.25 | Power interruption
Chhatak 132/33kV | T-3 | 2025-10-11 11:34 | 2025-10-11 13:16 | 1:42 | S/O | Shutdown for T-3 GCB hydraulic oil leakage problem. | 0 | 0 | No interruption
Chhatak 132/33kV | T-2 | 2025-10-11 13:45 | 2025-10-11 16:58 | 3:13 | S/O | Transformer T-2 shutdown for tap changer maintenance purpose. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-05 | 2025-10-01 15:12 | 2025-10-01 16:32 | 1:20 | S/O | 33KV Bus section-4 DS redhot | 25 | 33.3333 | Power interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-04 12:12 | 2025-10-04 14:17 | 2:05 | S/O | For project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-09 09:57 | 2025-10-09 17:45 | 7:48 | S/O | CNTIC work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Main Bus 1&2 | 2025-10-09 10:18 | 2025-10-09 17:27 | 7:09 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-11 09:55 | 2025-10-11 19:39 | 9:44 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Main Bus 1&2 | 2025-10-11 10:33 | 2025-10-11 19:18 | 8:45 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-12 09:18 | 2025-10-12 19:20 | 10:02 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Main Bus 1&2 | 2025-10-12 09:43 | 2025-10-12 19:00 | 9:17 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-13 09:22 | 2025-10-13 20:22 | 11:00 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Main Bus 1&2 | 2025-10-13 09:43 | 2025-10-13 19:38 | 9:55 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-14 09:30 | 2025-10-14 20:02 | 10:32 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Main Bus 1&2 | 2025-10-14 09:50 | 2025-10-14 19:54 | 10:04 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2025-10-15 09:24 | 2025-10-15 20:40 | 11:16 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Main Bus 1&2 | 2025-10-15 09:52 | 2025-10-15 19:46 | 9:54 | S/O | CNTIC project work | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) | 2025-10-18 09:24 | 2025-10-18 11:35 | 2:11 | S/O | Gas leakage work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-10-25 07:08 | 2025-10-25 09:24 | 2:16 | S/O | Red hot maintenance (PBS work) | 15 | 34 | Power interruption
Feni 132/33kV | T-2(415T) | 2025-10-25 09:15 | 2025-10-25 12:45 | 3:30 | S/O | 413 GCB GAS leakage work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-10-29 07:42 | 2025-10-29 08:42 | 1:00 | S/O | For 33/11 kv T-1 transformer incomming isolator maintenance by bpdb | 38 | 38 | Power interruption
Kachua 230/132/33kV | ATR-2 | 2025-10-15 12:53 | 2025-10-15 16:10 | 3:17 | S/O | Project work | 0 | 0 | No interruption
Kulaura 132/33kV | 132 kV Bus-B | 2025-10-04 11:57 | 2025-10-04 12:59 | 1:02 | S/O | Fen-kul-line-2(line DS Redhot maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-10-08 06:12 | 2025-10-08 08:53 | 2:41 | S/O | Tr-1( A,B) 132KV & 33KV CT Ratio Maintenance | 5 | 13.4167 | Power interruption
Lakshmipur 132/33kV | Transformer-1 | 2025-10-06 11:54 | 2025-10-06 17:16 | 5:22 | S/O | RTCC PANEL PROBLEM | 10 | 53.6667 | Power interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-10-06 17:08 | 2025-10-06 18:27 | 1:19 | S/O | RTCC Panel Announciator Problem | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2025-10-18 09:20 | 2025-10-18 20:08 | 10:48 | S/O | Tapping Line Construction for PBS | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-10-18 09:25 | 2025-10-18 20:19 | 10:54 | S/O | Tapping Line Construction Work by PBS | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2025-10-30 09:36 | 2025-10-30 19:59 | 10:23 | S/O | pdb & pbs work | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-10-30 14:46 | 2025-10-30 16:40 | 1:54 | S/O | PBS Work | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2025-10-07 10:08 | 2025-10-07 10:42 | 0:34 | S/O | Transformer-2, OTI & WTI don't show the correct temperature in SAS. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-11 14:44 | 2025-10-11 18:35 | 3:51 | S/O | Shutdown taken by pbs | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-19 06:32 | 2025-10-19 09:44 | 3:12 | S/O | Red hot maintenance | 50 | 160 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-19 06:32 | 2025-10-19 07:45 | 1:13 | S/O | Red hot maintenance | 25 | 30.4167 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2025-10-24 07:12 | 2025-10-24 09:04 | 1:52 | S/O | Red Hot Maintenance. | 55 | 102.6667 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-25 09:22 | 2025-10-25 14:34 | 5:12 | S/O | Auxiliary Transformer Installation. | 20 | 104 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-27 20:18 | 2025-10-27 22:34 | 2:16 | S/O | Red hot maintenance | 15 | 34 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2025-10-30 15:17 | 2025-10-30 15:48 | 0:31 | S/O | Sutdown Taken By PDB for Red hot maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-10-31 08:01 | 2025-10-31 09:30 | 1:29 | S/O | Maint.work | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2025-10-09 05:22 | 2025-10-09 05:56 | 0:34 | S/O | 33 KV Amborkhana-1 Feeder Fault | 19 | 10.7667 | Power interruption
Sylhet 132/33kV | T2 | 2025-10-09 05:23 | 2025-10-09 09:42 | 4:19 | S/O | 33 KV Amborkhana-1 Feeder Fault | 28 | 120.8667 | Power interruption
|  |  | Total : | 1900-01-08 13:00 |  |  |  | 789.0167
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2025-10-08 07:05 | 2025-10-08 07:21 | 0:16 | S/O | Pbs taken shutdown due to red hot | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2025-10-08 07:06 | 2025-10-08 08:22 | 1:16 | S/O | Pbs taken shutdown due to red hot | 0 | 0 | No interruption
Bagerhat 132/33kV | 132 kV BUS | 2025-10-18 05:44 | 2025-10-18 07:37 | 1:53 | S/O | 132 kV Bhandaria line bus DS B phase red jot maintenance work | 55 | 103.5833 | Power interruption
Barguna 132/33kV | Bus-2 | 2025-10-19 07:22 | 2025-10-19 16:45 | 9:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-1 | 2025-10-20 07:19 | 2025-10-20 17:07 | 9:48 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-1 | 2025-10-21 07:05 | 2025-10-21 17:54 | 10:49 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-2 | 2025-10-22 07:21 | 2025-10-22 17:22 | 10:01 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-2 | 2025-10-23 07:17 | 2025-10-23 16:36 | 9:19 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2025-10-27 06:56 | 2025-10-27 08:16 | 1:20 | S/O | Nolcity 33kV WZPDCL Feeder Red-hot maintenance | 10 | 13.3333 | Power interruption
Barishal 230/132kV | T-5 | 2025-10-13 07:33 | 2025-10-13 17:23 | 9:50 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2025-10-14 07:26 | 2025-10-14 17:21 | 9:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2025-10-15 07:28 | 2025-10-15 16:47 | 9:19 | S/O | Annual maintenance works | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2025-10-16 07:39 | 2025-10-16 16:24 | 8:45 | S/O | Maintenance work 2025 | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 | 2025-10-18 09:38 | 2025-10-18 17:04 | 7:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 | 2025-10-19 08:32 | 2025-10-19 16:10 | 7:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV | ATR-2 | 2025-10-21 08:59 | 2025-10-21 17:09 | 8:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | ATR-2 | 2025-10-22 08:43 | 2025-10-22 16:43 | 8:00 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 230/132kV | ATR-2 | 2025-10-23 07:49 | 2025-10-23 14:16 | 6:27 | S/O | Annual maintenance work 2025 | 0 | 0 | No interruption
Barishal 230/132kV | 230kV BUS | 2025-10-25 08:41 | 2025-10-25 16:05 | 7:24 | S/O | Maintenance work | 0 | 0 | No interruption
Barishal 230/132kV | 230kV BUS | 2025-10-26 08:16 | 2025-10-26 13:11 | 4:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV | 230kV BUS | 2025-10-26 14:55 | 2025-10-26 16:45 | 1:50 | S/O | 230kv Bus-1 shutdown for annual maintenance work. | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2025-10-13 07:37 | 2025-10-13 16:47 | 9:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2025-10-14 07:44 | 2025-10-14 17:42 | 9:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-2 | 2025-10-15 07:27 | 2025-10-15 16:50 | 9:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-2 | 2025-10-16 07:49 | 2025-10-16 15:28 | 7:39 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-1 | 2025-10-04 14:43 | 2025-10-04 16:52 | 2:09 | S/O | Hotspot Maintenance by WZPDCO. | 60 | 129 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-10-20 07:13 | 2025-10-20 09:48 | 2:35 | S/O | 33 kvbus maintenance | 40 | 103.3333 | Power interruption
Goalpara 132/33kV | T1 | 2025-10-15 08:02 | 2025-10-15 15:17 | 7:15 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Goalpara 132/33kV | T1 | 2025-10-16 08:16 | 2025-10-16 15:10 | 6:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-10-20 08:58 | 2025-10-20 15:35 | 6:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-10-21 08:13 | 2025-10-21 17:10 | 8:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2025-10-25 08:06 | 2025-10-25 15:11 | 7:05 | S/O | Yearly Maintanance Works | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2025-10-26 08:12 | 2025-10-26 18:10 | 9:58 | S/O | Annual Maintanance | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2025-10-25 08:06 | 2025-10-25 08:14 | 0:08 | S/O | 33 kv bus-3 shutdown taken by wzpdcl | 16 | 2.1333 | Power interruption
Gollamari 132/33kV | Tr-2 | 2025-10-25 14:44 | 2025-10-25 14:47 | 0:03 | S/O | 33kv bus section-3 shutdown restoration | 16 | 0.8 | Power interruption
Gopalganj 132/33kV | T1 | 2025-10-18 08:22 | 2025-10-18 16:57 | 8:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2025-10-19 08:32 | 2025-10-19 16:44 | 8:12 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2025-10-20 08:19 | 2025-10-20 16:52 | 8:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2025-10-21 08:18 | 2025-10-21 16:03 | 7:45 | S/O | Y/M | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-02 | 2025-10-19 08:32 | 2025-10-19 17:41 | 9:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-02 | 2025-10-20 08:31 | 2025-10-20 20:22 | 11:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-03 | 2025-10-22 08:22 | 2025-10-22 17:17 | 8:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-03 | 2025-10-23 08:50 | 2025-10-23 17:41 | 8:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-04 | 2025-10-26 09:39 | 2025-10-26 17:37 | 7:58 | S/O | annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-04 | 2025-10-27 07:39 | 2025-10-27 17:45 | 10:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-10-28 07:49 | 2025-10-29 18:12 | 34:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-10-11 08:49 | 2025-10-11 15:44 | 6:55 | S/O | for annual maintenance | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-10-12 08:03 | 2025-10-12 15:42 | 7:39 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2025-10-13 07:51 | 2025-10-13 15:57 | 8:06 | S/O | Annual maintenance work | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2025-10-14 08:05 | 2025-10-14 15:53 | 7:48 | S/O | for annual maintenance | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-10-17 09:29 | 2025-10-17 11:21 | 1:52 | S/O | Due to red hot maintenance of 33Kv bus clamp of Khlishpur feeders. | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-10-18 07:47 | 2025-10-18 15:45 | 7:58 | S/O | For annual maintenance | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-10-19 07:49 | 2025-10-19 16:58 | 9:09 | S/O | For annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-10-25 07:59 | 2025-10-25 17:17 | 9:18 | S/O | Annual Maintanance Work | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-10-26 08:14 | 2025-10-26 17:28 | 9:14 | S/O | Annunal maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2025-10-27 07:14 | 2025-10-27 09:32 | 2:18 | S/O | Annual Maintenance. | 10 | 23 | Power interruption
Madaripur 132/33kV | T2-415T | 2025-10-27 10:08 | 2025-10-27 16:53 | 6:45 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Madaripur 132/33kV | T2-415T | 2025-10-28 07:30 | 2025-10-28 18:16 | 10:46 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Madaripur 132/33kV | 33 KV BUS | 2025-10-28 07:40 | 2025-10-28 10:16 | 2:36 | S/O | Madaripur pbs maintenance work. | 16 | 41.6 | Power interruption
Madaripur 132/33kV | T3-426T | 2025-10-29 07:45 | 2025-10-29 16:51 | 9:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | 33 KV BUS | 2025-10-29 07:46 | 2025-10-29 09:52 | 2:06 | S/O | 33 kv bus section-3 shut down taken by Madaripur pbs for manitenance work | 15 | 31.5 | Power interruption
Madaripur 132/33kV | T3-426T | 2025-10-30 07:54 | 2025-10-30 17:12 | 9:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-10-22 08:23 | 2025-10-22 14:09 | 5:46 | S/O | Annul Maintenance | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-10-23 08:20 | 2025-10-23 12:59 | 4:39 | S/O | For Annual Maintenance work. | 0 | 0 | No interruption
Noapara 132/33kV | T-2 | 2025-10-27 08:34 | 2025-10-27 14:34 | 6:00 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Noapara 132/33kV | T-2 | 2025-10-28 08:15 | 2025-10-28 15:50 | 7:35 | S/O | Annual Maintenance | 0 | 0 | No interruption | 14:29
Patuakhali 132/33kV | 405T (T-1) | 2025-10-25 07:21 | 2025-10-25 16:33 | 9:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV | 405T (T-1) | 2025-10-26 07:04 | 2025-10-26 17:17 | 10:13 | S/O | Annual Maintenance-25 | 0 | 0 | No interruption
Patuakhali 132/33kV | 415T (T-2) | 2025-10-27 07:06 | 2025-10-27 16:25 | 9:19 | S/O | Annual Maintenance Work -2025 | 0 | 0 | No interruption
Patuakhali 132/33kV | 415T (T-2) | 2025-10-28 07:09 | 2025-10-28 17:12 | 10:03 | S/O | Annual Maintenance-2025 | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-10-29 07:15 | 2025-10-29 16:42 | 9:27 | S/O | Maintenance work-25 | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-10-30 07:11 | 2025-10-30 16:28 | 9:17 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2025-10-11 08:03 | 2025-10-11 14:08 | 6:05 | S/O | Annual maintence. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2025-10-12 07:44 | 2025-10-12 13:58 | 6:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-2 | 2025-10-13 07:43 | 2025-10-13 14:44 | 7:01 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-2 | 2025-10-14 07:46 | 2025-10-14 13:54 | 6:08 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-3 | 2025-10-15 08:24 | 2025-10-15 14:33 | 6:09 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-3 | 2025-10-16 08:16 | 2025-10-16 14:44 | 6:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajbari 132/33kV | DS - Bus coupler (Bus-1) | 2025-10-18 09:28 | 2025-10-18 15:16 | 5:48 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV | 132 kV Bus-II | 2025-10-19 08:36 | 2025-10-19 13:38 | 5:02 | S/O | For Annual maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV | 132 kV Bus-I | 2025-10-19 13:45 | 2025-10-19 16:07 | 2:22 | S/O | For annual maintenance | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-10-28 10:46 | 2025-10-28 13:24 | 2:38 | S/O | Annual Maintenance. | 15 | 39.5 | Power interruption
Shariatpur 132/33kV | T1-406T | 2025-10-05 08:43 | 2025-10-05 17:20 | 8:37 | S/O | Annual Maintenance(Schedule Shutdown) | 0 | 0 | No interruption
Shariatpur 132/33kV | T1-406T | 2025-10-06 08:08 | 2025-10-06 16:49 | 8:41 | S/O | Annual Maintenence Work. | 0 | 0 | No interruption
Shariatpur 132/33kV | T2-416T | 2025-10-07 08:13 | 2025-10-07 17:03 | 8:50 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Shariatpur 132/33kV | T2-416T | 2025-10-08 08:31 | 2025-10-08 16:42 | 8:11 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Shariatpur 132/33kV | Main Bus - 1 | 2025-10-12 08:16 | 2025-10-12 13:55 | 5:39 | S/O | Annual Maintenance shutdown work | 0 | 0 | No interruption
Shariatpur 132/33kV | Main Bus - 2 | 2025-10-12 14:07 | 2025-10-12 16:46 | 2:39 | S/O | Annual Maintenance shutdown work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-25 20:50 |  | Unserved Energy : |  | 487.7833
HVDC Grid Circle
BIPTC | Block-01, Trafo-02 | 2025-10-06 12:08 | 2025-10-06 16:54 | 4:46 | S/O | Oil leakage in 33/0.4 KV 2 MVA Auxiliary Transformer. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2025-10-11 08:27 | 2025-10-11 17:34 | 9:07 | S/O |  | 20 | 182.3333 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2025-10-11 11:11 | 2025-10-11 14:27 | 3:16 | S/O | auxiliary transformer installation | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2025-10-12 11:01 | 2025-10-12 13:22 | 2:21 | S/O |  | 0 | 0 | No interruption
Jhenaidah 132/33kV | Bus-A | 2025-10-18 06:35 | 2025-10-18 18:15 | 11:40 | S/O | Chuadanga ckt -2 upgradation | 90 | 1050 | Power interruption
Jhenaidah 132/33kV | Bus-B | 2025-10-18 06:37 | 2025-10-18 17:56 | 11:19 | S/O | Maint.works | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Bus1 | 2025-10-16 08:34 | 2025-10-16 14:29 | 5:55 | S/O | Annual maintenance work | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Bus-2 | 2025-10-19 08:25 | 2025-10-19 15:07 | 6:42 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-10-11 09:42 | 2025-10-11 16:46 | 7:04 | S/O | C1 unbalane 60/61 CPR04 | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-10-11 16:11 | 2025-10-11 17:03 | 0:52 | S/O | Tripped by 60/61 C1 unbalane 60/61 instant L3 | 0 | 0 | No interruption
BIPTC | 10CF14 | 2025-10-12 12:01 | 2025-10-12 12:36 | 0:35 | S/O | for emergency maintenance | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-10-13 09:55 | 2025-10-13 13:25 | 3:30 | S/O | for corrective maintenance | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-10-22 11:01 | 2025-10-22 11:23 | 0:22 | S/O | For Corrective Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 19:29 |  | Unserved Energy : |  | 1232.3333
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-10-09 09:37 | 2025-10-09 11:31 | 1:54 | S/O | Red hot maintenance work. | 18 | 34.2 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-10-10 15:10 | 2025-10-10 17:32 | 2:22 | S/O | Maintenance | 27 | 63.9 | Power interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-10-25 08:59 | 2025-10-25 16:52 | 7:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus A | 2025-10-25 09:02 | 2025-10-25 17:08 | 8:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-10-26 09:02 | 2025-10-26 15:39 | 6:37 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-02, 713T | 2025-10-27 09:24 | 2025-10-27 17:25 | 8:01 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus B | 2025-10-27 09:59 | 2025-10-27 16:59 | 7:00 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Main Bus-1 | 2025-10-13 08:30 | 2025-10-14 08:35 | 24:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Main Bus-2 | 2025-10-14 09:12 | 2025-10-15 14:31 | 29:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2025-10-28 12:15 | 2025-10-28 15:24 | 3:09 | S/O | 33 kV feeder extension | 11 | 34.65 | Power interruption
Bogura 132/33kV | Transformer-3 | 2025-10-13 07:40 | 2025-10-13 14:57 | 7:17 | S/O | Junction point temperature high. | 25 | 182.0833 | Power interruption
Bogura 230/132kV | T-03 | 2025-10-28 08:43 | 2025-10-28 16:28 | 7:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | T-03 | 2025-10-29 08:40 | 2025-10-29 15:59 | 7:19 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2025-10-12 09:28 | 2025-10-12 19:39 | 10:11 | S/O | Y phase Conductor Loop Chance | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2025-10-13 09:15 | 2025-10-13 12:41 | 3:26 | S/O | internal wiring cable Checking | 0 | 0 | No interruption
Bogura 400/230kV | ATR-03 | 2025-10-13 14:01 | 2025-10-13 17:17 | 3:16 | S/O | ATR-03 Shutdown due to internal wiring cable checking. | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2025-10-04 08:25 | 2025-10-04 17:57 | 9:32 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Jaldhaka 132/33kV | 416T-2 | 2025-10-05 09:41 | 2025-10-05 17:03 | 7:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV | 416T-2 | 2025-10-06 08:21 | 2025-10-06 16:53 | 8:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV | Bus A | 2025-10-08 09:15 | 2025-10-08 16:30 | 7:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV | Bus B | 2025-10-09 09:05 | 2025-10-09 14:30 | 5:25 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) | 2025-10-27 07:45 | 2025-10-27 16:51 | 9:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) | 2025-10-28 09:15 | 2025-10-28 16:15 | 7:00 | S/O | Annual maintenance. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2025-10-29 07:51 | 2025-10-29 16:53 | 9:02 | S/O | Anual Maintanance | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2025-10-30 10:56 | 2025-10-30 16:47 | 5:51 | S/O |  | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2025-10-05 15:04 | 2025-10-05 16:57 | 1:53 | S/O | Red hot | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 132KV Main bus 1 | 2025-10-11 09:35 | 2025-10-11 15:57 | 6:22 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 132KVMain bus 2 | 2025-10-12 10:21 | 2025-10-12 15:22 | 5:01 | S/O | Annul maintenance Main bus-2 | 0 | 0 | No interruption
Panchagarh 132/33kV | T-1(407T) | 2025-10-11 08:18 | 2025-10-11 16:02 | 7:44 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Panchagarh 132/33kV | T-1(407T) | 2025-10-12 08:19 | 2025-10-12 16:01 | 7:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Panchagarh 132/33kV | T-2(417T) | 2025-10-13 08:07 | 2025-10-13 16:00 | 7:53 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Panchagarh 132/33kV | T-2(417T) | 2025-10-14 08:37 | 2025-10-14 15:32 | 6:55 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2025-10-15 08:20 | 2025-10-15 15:07 | 6:47 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2025-10-16 08:21 | 2025-10-16 16:21 | 8:00 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) | 2025-10-18 08:10 | 2025-10-18 16:11 | 8:01 | S/O | Annual maintenance of T-1 transformer | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) | 2025-10-19 08:24 | 2025-10-19 16:03 | 7:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-4 Transformer | 2025-10-22 08:24 | 2025-10-22 15:38 | 7:14 | S/O | Annual Maitenance | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-10-09 09:15 | 2025-10-09 16:23 | 7:08 | S/O | General checking & inspection | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-10-30 15:02 | 2025-10-30 16:09 | 1:07 | S/O | PBS maintenance work at BUS DS of Banessor feeder | 25 | 27.9167 | Power interruption
Rangpur 132/33kV | T-1(414T) | 2025-10-03 14:57 | 2025-10-03 17:16 | 2:19 | S/O | 33kv Bua section Red hot Maintenance by NESCO | 45 | 104.25 | Power interruption
Rangpur 132/33kV | T-2 (404T) | 2025-10-03 14:57 | 2025-10-03 17:16 | 2:19 | S/O | 33 kv Bus section Red hot Maintenance by NESCO | 45 | 104.25 | Power interruption
Saidpur 132/33kV | TR-5 (434T) | 2025-10-15 10:11 | 2025-10-15 10:57 | 0:46 | S/O | High temperature at T-5 LT CB R phase Upper part maintenance. | 5 | 3.8333 | Power interruption
Saidpur 132/33kV | TR-3 (424T) | 2025-10-16 08:33 | 2025-10-16 14:52 | 6:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | TR-3 (424T) | 2025-10-18 08:38 | 2025-10-18 16:27 | 7:49 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | TR-4 (414T) | 2025-10-19 08:33 | 2025-10-19 15:11 | 6:38 | S/O | QF- GMD-39 and as the instruction of ALDC Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2025-10-20 08:44 | 2025-10-20 15:35 | 6:51 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2025-10-21 08:58 | 2025-10-21 16:13 | 7:15 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2025-10-22 08:35 | 2025-10-22 16:42 | 8:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-1(422T) | 2025-10-06 09:40 | 2025-10-06 17:27 | 7:47 | S/O | For Annual maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-2(412T) | 2025-10-07 09:20 | 2025-10-07 17:47 | 8:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-2(412T) | 2025-10-08 08:30 | 2025-10-08 17:02 | 8:32 | S/O | Annual maintenance. | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-3(432T) | 2025-10-09 08:38 | 2025-10-09 17:09 | 8:31 | S/O | Annual maintenance. | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-3(432T) | 2025-10-11 08:31 | 2025-10-11 16:12 | 7:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-3(432T) | 2025-10-13 11:06 | 2025-10-13 15:48 | 4:42 | S/O | T-3 ট্রান্সফরমারের Self Protection চেক by SPMD Rangpur. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-15 06:14 |  | Unserved Energy : |  | 555.0833
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2218:02 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:October 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Kaliakoir-01 | 2025-10-16 10:32 | 2025-10-16 11:16 | 0:44 | S/O | 230kv Bus 1 Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-10-16 11:30 | 2025-10-16 12:16 | 0:46 | S/O | 230kv Bus-1 Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-10-20 10:16 | 2025-10-20 18:05 | 7:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-10-21 09:18 | 2025-10-21 17:23 | 8:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-10-22 14:31 | 2025-10-22 16:45 | 2:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-01 | 2025-10-26 11:50 | 2025-10-26 15:42 | 3:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2025-10-17 07:06 | 2025-10-17 07:57 | 0:51 | S/O | Remove bird Nest | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2025-10-13 07:25 | 2025-10-13 09:07 | 1:42 | S/O | High temperature minimize. | 40 | 68 | Power interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2025-10-16 11:15 | 2025-10-16 12:59 | 1:44 | S/O | Red hot Sripur end. | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-10-16 13:17 | 2025-10-16 17:40 | 4:23 | S/O | Maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2025-10-18 06:44 | 2025-10-18 09:57 | 3:13 | S/O | Maint.work | 40 | 128.6667 | Power interruption
Bhaluka 132/33kV | Capacitor Bank- 01 | 2025-10-18 13:15 | 2025-10-18 14:04 | 0:49 | S/O | Red hot pbs feeder no 16 | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2025-10-23 07:18 | 2025-10-23 08:51 | 1:33 | S/O | High temperature minimize | 80 | 124 | Power interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2025-10-23 13:15 | 2025-10-23 15:55 | 2:40 | S/O | Temperature maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-10-24 10:14 | 2025-10-24 10:14 | 0:00 | S/O | Mym.grid beaker replacement work | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2025-10-11 08:39 | 2025-10-12 06:06 | 21:27 | S/O | Shutdown taken by SDE NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2025-10-21 09:50 | 2025-10-21 17:23 | 7:33 | S/O | by NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2025-10-26 11:45 | 2025-10-26 15:43 | 3:58 | S/O | NLDC. | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2025-10-24 09:21 | 2025-10-24 11:04 | 1:43 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2025-10-29 07:09 | 2025-10-29 07:09 | 0:00 | S/O | Redhot maintenance | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2025-10-12 09:57 | 2025-10-12 15:43 | 5:46 | S/O | Deadline checking. | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2025-10-13 09:37 | 2025-10-13 15:48 | 6:11 | S/O | Dead line checking | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2025-10-14 09:07 | 2025-10-14 16:43 | 7:36 | S/O | Deadline checking | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2025-10-15 09:14 | 2025-10-15 16:02 | 6:48 | S/O | Annual maintenance RPCL 01 | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2025-10-15 09:14 | 2025-10-15 16:02 | 6:48 | S/O | Annual maintenance RPCL 01 | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2025-10-16 09:07 | 2025-10-16 14:36 | 5:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-2 | 2025-10-25 09:16 | 2025-10-25 15:49 | 6:33 | S/O | Dead line checking | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-2 | 2025-10-26 08:52 | 2025-10-26 15:55 | 7:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-2 | 2025-10-27 09:40 | 2025-10-27 14:49 | 5:09 | S/O | Annual maintenance. | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-2 | 2025-10-29 08:58 | 2025-10-29 08:58 | 0:00 | S/O | Dead line checking | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-RPCL Ckt-1 | 2025-10-13 14:20 | 2025-10-13 14:20 | 0:00 | S/O | Bay upgradation. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2025-10-22 09:38 | 2025-10-23 12:55 | 27:17 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2025-10-26 10:15 | 2025-10-26 10:15 | 0:00 | S/O | Bay upgradation. | 0 | 0 | No interruption
Savar 132/33kV | Capacitor Bank-1 | 2025-10-19 08:24 | 2025-10-19 16:01 | 7:37 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Savar 132/33kV | Capacitor Bank-2 | 2025-10-19 08:24 | 2025-10-19 15:46 | 7:22 | S/O | Annual maintenance work | 0 | 0 | No interruption
Savar 132/33kV | Capacitor Bank-3 | 2025-10-19 08:24 | 2025-10-19 15:47 | 7:23 | S/O | Annual maintenance work | 0 | 0 | No interruption
Savar 132/33kV | Capacitor Bank-2 | 2025-10-21 08:31 | 2025-10-21 12:44 | 4:13 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Capacitor Bank-3 | 2025-10-22 08:57 | 2025-10-22 14:44 | 5:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-1 | 2025-10-31 08:20 | 2025-10-31 11:04 | 2:44 | S/O | ROW | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-2 | 2025-10-31 11:06 | 2025-10-31 12:43 | 1:37 | S/O | Right of Way. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2025-10-07 09:27 | 2025-10-09 20:25 | 58:58 | S/O | Relay Change Work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2025-10-10 14:53 | 2025-10-10 19:42 | 4:49 | S/O | Junction point temperature imcrease | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-10-11 08:50 | 2025-10-12 04:37 | 19:47 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-10-13 09:50 | 2025-10-13 16:38 | 6:48 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-10-14 09:22 | 2025-10-14 16:36 | 7:14 | S/O | annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-10-15 08:54 | 2025-10-15 17:30 | 8:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-10-16 09:22 | 2025-10-16 17:00 | 7:38 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-10-18 07:42 | 2025-10-19 01:22 | 17:40 | S/O | Control Panel Change Work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2025-10-19 09:36 | 2025-10-19 17:17 | 7:41 | S/O | Due to annual maintenance works | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2025-10-20 09:13 | 2025-10-20 17:09 | 7:56 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2025-10-21 09:01 | 2025-10-21 17:04 | 8:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Tongi 80 MW PS | 2025-10-21 10:08 | 2025-10-21 14:52 | 4:44 | S/O | Annual maintenance 80 MW ending side. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2025-10-22 09:07 | 2025-10-22 16:43 | 7:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2025-10-26 09:03 | 2025-10-26 16:39 | 7:36 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2025-10-27 09:31 | 2025-10-27 17:10 | 7:39 | S/O | Annual maintenance work (dead line checking) | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2025-10-28 09:07 | 2025-10-28 17:26 | 8:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2025-10-29 09:25 | 2025-10-29 17:01 | 7:36 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-15 11:09 |  | Unserved Energy: |  | 320.6667
Dhaka (South) Grid Circle :
Fatullah 132/33kV | 132 kV Hasnabad | 2025-10-16 08:36 | 2025-10-24 12:06 | 195:30 | S/O | Maint.work | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Shyampur-1 | 2025-10-25 07:27 | 2025-10-30 14:45 | 127:18 | S/O | Maint.work | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-10-01 08:53 | 2025-10-01 08:53 | 0:00 | S/O | Shutdown requisition from Manikganj grid of Ghorashal Ishwardi ckt-02 due to Dhaka Ashulia Elevated Express work and also re-routing & reconducting for 95 days. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal GIS- AIS Ckt-2 | 2025-10-04 09:59 | 2025-10-04 11:26 | 1:27 | S/O | Emergency work in AIS end (BPDB). | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-2 | 2025-10-27 06:31 | 2025-10-27 09:33 | 3:02 | S/O | For other end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Kamrangirchar Ckt, | 2025-10-11 08:40 | 2025-10-11 19:14 | 10:34 | S/O | High temperature maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Lalbagh Ckt. 3 | 2025-10-18 06:03 | 2025-10-18 16:39 | 10:36 | S/O | High Temperature Maintenance work | 0 | 0 | No interruption
Maniknagar 132/33kV | Motijheel Ckt-1 | 2025-10-11 10:03 | 2025-10-11 17:12 | 7:09 | S/O | Winter Maintenance by DPDC | 0 | 0 | No interruption
Maniknagar 132/33kV | Motijheel Ckt-2 | 2025-10-18 09:56 | 2025-10-18 15:10 | 5:14 | S/O | Annual maintenance and relay test work by DPDC. Shutdown taken by Mr. Raihan Kabir, AE, DPDC. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-SMPCL-02 | 2025-10-24 06:34 | 2025-10-24 20:09 | 13:35 | S/O | Dismantling and reinstallation work of dia-07 | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Haripur-02 | 2025-10-27 06:30 | 2025-10-27 09:34 | 3:04 | S/O | Red hot spot maintenance work at ct clump | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Reliance PP 400KV Ckt-2 | 2025-10-06 15:26 | 2025-10-06 15:26 | 0:00 | S/O | shutdown due to maintenance work at Reliance ckt-2 DS point. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Unique PP 400KV Ckt-1 | 2025-10-22 10:46 | 2025-10-22 13:05 | 2:19 | S/O | Maint.work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Madunaghat 400KV Ckt-1 | 2025-10-25 06:58 | 2025-10-25 17:51 | 10:53 | S/O | Shutdown instructed by NLDC. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2025-10-25 09:35 | 2025-10-25 11:22 | 1:47 | S/O | Shyampur 230 kV ckt-2 shutdown for nut bolt tightness. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2025-10-25 11:28 | 2025-10-25 12:16 | 0:48 | S/O | 230 kV Shyampur ckt- 1 shutdown for DS nut bolt tightness. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-10-27 09:52 | 2025-10-27 17:23 | 7:31 | S/O | Shutdown for project work | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-02 | 2025-10-09 06:52 | 2025-10-09 07:33 | 0:41 | S/O | Maint.work | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-2(E10) | 2025-10-27 08:03 | 2025-10-30 13:54 | 77:51 | S/O | Overhead Transmission Line Reconducting. | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Fatullah-1(E06) | 2025-10-30 08:23 | 2025-10-30 14:44 | 6:21 | S/O | For Shyampur Ckt-1 and Shyampur Ckt-2 Jumparing. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-19 05:40 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Agrabad 132/33kV | Rampur-01 | 2025-10-27 09:22 | 2025-10-27 13:53 | 4:31 | S/O | SF6 Gas Analyzing Test | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2025-10-03 07:24 | 2025-10-03 11:49 | 4:25 | S/O | Hathazari main bus section work at hathazari side. | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-2 | 2025-10-03 07:24 | 2025-10-03 11:49 | 4:25 | S/O | Hathazari main BUS section work at Hathazari side. | 0 | 0 | No interruption
Baroaulia 132/33kV | KSRM | 2025-10-05 06:37 | 2025-10-06 22:42 | 40:05 | S/O | SF6 Breaker change purpose. | 0 | 0 | No interruption
Baroirhat 132/33kV | Feni-1 | 2025-10-06 08:25 | 2025-10-06 14:52 | 6:27 | S/O | Annual maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV | PHP | 2025-10-07 08:48 | 2025-10-07 13:58 | 5:10 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-1 | 2025-10-10 06:16 | 2025-10-11 18:51 | 36:35 | S/O | Due to Annual maintenance work of Hathazari s/s | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2025-10-10 06:17 | 2025-10-11 18:52 | 36:35 | S/O | Due to Annual maintenance work of Hathazari s/s | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-1 | 2025-10-18 08:19 | 2025-10-18 17:22 | 9:03 | S/O | 0 | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2025-10-20 08:29 | 2025-10-20 16:21 | 7:52 | S/O | Annual maintenance work | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-01 | 2025-10-04 09:46 | 2025-10-04 17:52 | 8:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-01 | 2025-10-05 07:54 | 2025-10-05 16:42 | 8:48 | S/O | 0 | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-01 | 2025-10-06 07:48 | 2025-10-06 16:40 | 8:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-01 | 2025-10-07 07:59 | 2025-10-07 16:10 | 8:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-01 | 2025-10-08 08:41 | 2025-10-08 16:45 | 8:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona- Rangamati Ckt-01 | 2025-10-09 08:36 | 2025-10-09 16:12 | 7:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona- Rangamati Ckt-02 | 2025-10-11 08:39 | 2025-10-11 15:09 | 6:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-02 | 2025-10-14 08:17 | 2025-10-14 17:33 | 9:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-02 | 2025-10-15 07:47 | 2025-10-15 17:29 | 9:42 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-02 | 2025-10-16 07:39 | 2025-10-16 16:43 | 9:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-02 | 2025-10-19 07:37 | 2025-10-19 16:59 | 9:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2025-10-17 06:27 | 2025-10-17 10:17 | 3:50 | S/O | this ckt is Dohazari-Patiya-ckt 02 now. SD taken by ESPNER project for Loop maintenance. | 10 | 38.3333 | Power interruption
Dohazari 132/33kV | 100 MW PPP | 2025-10-24 08:21 | 2025-10-24 09:57 | 1:36 | S/O | For high temperature maintenance at B-phase Line DS in clamp. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2025-10-26 08:34 | 2025-10-26 13:20 | 4:46 | S/O | Cox-02 Line Maintenance (Full Load Serve By Cox-01 Line) | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2025-10-17 06:43 | 2025-10-17 11:42 | 4:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2025-10-10 08:08 | 2025-10-10 11:11 | 3:03 | S/O | To remove T connection between juldha and khulshi-3 ckt.at 4 circuit tower at cepz end | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-01 | 2025-10-04 10:04 | 2025-10-04 15:57 | 5:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | Raojan-01 | 2025-10-21 09:45 | 2025-10-21 13:32 | 3:47 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-10-10 08:10 | 2025-10-10 12:05 | 3:55 | S/O | Protection Settings Reshaple at halishahar S/S | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-1 | 2025-10-15 08:17 | 2025-10-15 16:24 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2025-10-16 06:57 | 2025-10-16 14:09 | 7:12 | S/O | Annual maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Baraulia Main | 2025-10-05 06:40 | 2025-10-06 22:47 | 40:07 | S/O | Change SF6 breaker from Baraulia S/S | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-1 | 2025-10-04 09:45 | 2025-10-04 17:51 | 8:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-1 | 2025-10-05 07:59 | 2025-10-05 16:43 | 8:44 | S/O | annual dead line checking | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-1 | 2025-10-06 07:47 | 2025-10-06 16:41 | 8:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-1 | 2025-10-07 07:57 | 2025-10-07 16:09 | 8:12 | S/O | for annual maintenance and deadline checking. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-1 | 2025-10-08 08:33 | 2025-10-08 16:44 | 8:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-1 | 2025-10-10 06:13 | 2025-10-10 15:49 | 9:36 | S/O | Bus Shutdown at Hathazari grid | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-2 | 2025-10-10 06:13 | 2025-10-10 15:49 | 9:36 | S/O | Bus Shutdown at Hathazari Grid | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-1 | 2025-10-11 07:59 | 2025-10-11 16:03 | 8:04 | S/O | S/D Taken by Hathazari Grid Substation for Maintenance Purposes. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-2 | 2025-10-11 07:59 | 2025-10-11 16:03 | 8:04 | S/O | S/D Taken by Hathazari Grid Substation for Maintenance Purposes. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-1 | 2025-10-12 07:49 | 2025-10-12 15:22 | 7:33 | S/O | Annual Maintenance and deadline checking. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-2 | 2025-10-13 07:35 | 2025-10-13 16:48 | 9:13 | S/O | Annual Bay Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-2 | 2025-10-14 08:16 | 2025-10-14 17:34 | 9:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-2 | 2025-10-15 07:33 | 2025-10-15 17:28 | 9:55 | S/O | annual deadline checking | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-2 | 2025-10-16 07:37 | 2025-10-16 16:44 | 9:07 | S/O | Annual Maintenance and deadline checking. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-2 | 2025-10-18 08:05 | 2025-10-18 16:54 | 8:49 | S/O | annual maintenance. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-2 | 2025-10-19 07:36 | 2025-10-19 17:00 | 9:24 | S/O | Annual Maintenance and deadline checking. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-10-31 06:46 | 2025-10-31 20:21 | 13:35 | S/O | For the phile driving work under the drainage improvement project of chattogram city implemented by the bangladesh army. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-10-31 07:03 | 2025-10-31 19:05 | 12:02 | S/O | For the phile driving work under the drainage improvement project of chattogram city implemented by the bangladesh army. | 0 | 0 | No interruption
Mirsorai 230/33kV | BSRM-1 | 2025-10-25 08:30 | 2025-10-25 19:23 | 10:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV | 150 MW Power Station -01 | 2025-10-28 08:39 | 2025-10-28 12:40 | 4:01 | S/O | Annual maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV | 150 MW Power Station -02 | 2025-10-28 12:46 | 2025-10-28 15:47 | 3:01 | S/O | annual maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV | EGCB 75MW Solar Power Station | 2025-10-29 15:26 | 2025-10-29 15:26 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 | Agrabad-1 | 2025-10-27 09:25 | 2025-10-27 13:52 | 4:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangamati 132/33kV | Chandraghona Ckt-01 | 2025-10-09 08:36 | 2025-10-09 16:13 | 7:37 | S/O | Rangamati Chandraghona Ckt-01 taken shutdown due to annual maintenance. | 0 | 0 | No interruption
Rangamati 132/33kV | Chandraghona Ckt-02 | 2025-10-11 08:39 | 2025-10-11 15:10 | 6:31 | S/O | Annual Bay Maintenance. | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-01 | 2025-10-15 08:17 | 2025-10-15 16:13 | 7:56 | S/O | Rangamati-Khagrachori Ckt-01 Taken shutdown due to annual maintenance. | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-02 | 2025-10-16 06:58 | 2025-10-16 14:07 | 7:09 | S/O | Annual Bay Maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV | Interconnection-1 | 2025-10-23 12:23 | 2025-10-23 14:52 | 2:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-22 04:21 |  | Unserved Energy: |  | 38.3333
Cumilla Grid Circle :
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2025-10-12 10:00 | 2025-10-12 13:12 | 3:12 | S/O | Maintenance work at kachua Grid Sub- station. | 0 | 0 | No interruption
Chauddagram 132/33kV | Feni-1 | 2025-10-20 08:44 | 2025-10-20 16:43 | 7:59 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Chauddagram 132/33kV | Cumilla South-1 | 2025-10-23 07:32 | 2025-10-23 16:53 | 9:21 | S/O | Yearly maintenance work | 0 | 0 | No interruption
Chauddagram 132/33kV | Cumilla South-1 | 2025-10-25 07:41 | 2025-10-25 14:49 | 7:08 | S/O | Cumilla South, ckt-1 is under shutdown for yearly maintenance. | 0 | 0 | No interruption
Chauddagram 132/33kV | Cumilla South-1 | 2025-10-27 07:12 | 2025-10-27 15:52 | 8:40 | S/O | Yearly maintenance work | 0 | 0 | No interruption
Chauddagram 132/33kV | Cumilla South-2 | 2025-10-28 07:25 | 2025-10-28 16:48 | 9:23 | S/O | Yearly maintenance work | 0 | 0 | No interruption
Chauddagram 132/33kV | Cumilla South-2 | 2025-10-29 07:47 | 2025-10-29 15:45 | 7:58 | S/O | yearly maintanence. ( Line ) | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2025-10-14 07:17 | 2025-10-14 12:39 | 5:22 | S/O | Shutdown for Red hot maintenance. | 10 | 53.6667 | Power interruption
Chhatak 132/33kV | Sylhet 01 | 2025-10-29 07:22 | 2025-10-29 14:48 | 7:26 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2025-10-30 07:04 | 2025-10-30 16:14 | 9:10 | S/O | 132KV Sylhet - Chhatak ckt -1 Shutdown for Annual maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2025-10-05 07:24 | 2025-10-05 22:56 | 15:32 | S/O | 230kv Feni GIS Grid LILO connection and commissioning work, | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-10-11 09:58 | 2025-10-11 19:21 | 9:23 | S/O | The shutdown has been taken at 09:00 for project work. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-10-13 09:35 | 2025-10-13 19:58 | 10:23 | S/O | Project work in Dagonvhuyan S/s | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-10-14 09:43 | 2025-10-14 19:55 | 10:12 | S/O | For Project work. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-10-29 06:44 | 2025-10-29 17:54 | 11:10 | S/O | Project Work | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2025-10-29 06:44 | 2025-10-29 18:48 | 12:04 | S/O | Project Work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-10-02 07:41 | 2025-10-05 17:37 | 81:56 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-2 | 2025-10-02 07:41 | 2025-10-05 17:33 | 81:52 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2025-10-04 07:09 | 2025-10-05 04:56 | 21:47 | S/O | Ashuganj Ckt-02 Transposition | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2025-10-18 09:31 | 2025-10-19 17:43 | 32:12 | S/O | For work at Shahjibazar 330MW Generation | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Kachua | 2025-10-08 10:05 | 2025-10-08 17:39 | 7:34 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-10-18 07:14 | 2025-10-18 16:06 | 8:52 | S/O | Dead line checking | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-10-19 08:15 | 2025-10-19 17:27 | 9:12 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-10-20 09:08 | 2025-10-20 16:40 | 7:32 | S/O | annual maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-10-21 08:07 | 2025-10-21 14:21 | 6:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-10-22 09:07 | 2025-10-22 16:12 | 7:05 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Chowddagram-1 | 2025-10-23 07:33 | 2025-10-23 16:50 | 9:17 | S/O | Work for Choddagram end | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Chowddagram-1 | 2025-10-25 07:30 | 2025-10-25 14:47 | 7:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Chowddagram-1 | 2025-10-27 07:11 | 2025-10-27 15:51 | 8:40 | S/O | Dead line Checking | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Chowddagram-2 | 2025-10-28 07:24 | 2025-10-28 16:49 | 9:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Chowddagram-2 | 2025-10-29 07:40 | 2025-10-29 15:44 | 8:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2025-10-09 10:04 | 2025-10-09 17:28 | 7:24 | S/O | CNTIC | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-10-11 10:31 | 2025-10-11 19:16 | 8:45 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2025-10-11 10:33 | 2025-10-11 19:27 | 8:54 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-10-12 09:30 | 2025-10-12 18:57 | 9:27 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2025-10-12 09:44 | 2025-10-12 18:58 | 9:14 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-10-13 09:49 | 2025-10-13 19:35 | 9:46 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2025-10-13 09:54 | 2025-10-13 19:57 | 10:03 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-10-14 10:05 | 2025-10-14 19:55 | 9:50 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2025-10-14 10:06 | 2025-10-14 19:56 | 9:50 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2025-10-15 09:46 | 2025-10-15 19:50 | 10:04 | S/O | CNTIC project work | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2025-10-15 09:47 | 2025-10-15 20:52 | 11:05 | S/O | CNTIC project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2025-10-04 11:46 | 2025-10-04 13:03 | 1:17 | S/O | Red hot Maintenance at Kulaura End | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2025-10-25 06:17 | 2025-10-25 10:29 | 4:12 | S/O | B phase armoring. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-1 | 2025-10-29 08:54 | 2025-10-29 14:00 | 5:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-1 | 2025-10-30 09:32 | 2025-10-30 14:49 | 5:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-10-05 07:40 | 2025-10-09 15:05 | 103:25 | S/O | Lilo taping open direct connected to feni 230 kV S/S EEGBPS Project Work. | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-1 | 2025-10-20 08:31 | 2025-10-20 15:24 | 6:53 | S/O | S/D taken for AMS-2025-25 | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-1 | 2025-10-21 09:07 | 2025-10-21 14:41 | 5:34 | S/O | For annual maintenance. | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2025-10-12 10:04 | 2025-10-12 13:10 | 3:06 | S/O | Earth wire loop maintenance | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-1 | 2025-10-01 11:01 | 2025-10-01 15:14 | 4:13 | S/O | shutdown taken by muradnagar for removeing kite | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-2 | 2025-10-04 11:57 | 2025-10-04 12:58 | 1:01 | S/O | Fen-kul-line-2(line DS Redhot maintenance) | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Kosba Ckt-01 | 2025-10-01 10:56 | 2025-10-01 15:12 | 4:16 | S/O | Kite Removed from 'A' Phase. | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2025-10-01 09:31 | 2025-10-01 11:10 | 1:39 | S/O | 86MW Bay B Phase red hot maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | BPDB 60 MW | 2025-10-08 15:15 | 2025-10-08 17:41 | 2:26 | S/O | Bushing Hotspot Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2025-10-25 06:16 | 2025-10-25 10:30 | 4:14 | S/O | Order by NLDC | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2025-10-14 07:21 | 2025-10-14 12:35 | 5:14 | S/O | SD By Chatak Grid SS, Direction by NLDC (299725) | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-10-29 07:23 | 2025-10-29 14:47 | 7:24 | S/O | Due to Yearly Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-10-30 07:07 | 2025-10-30 16:13 | 9:06 | S/O | Annual Maintenance Purpose. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-29 10:07 |  | Unserved Energy: |  | 53.6667
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2025-10-04 14:56 | 2025-10-04 17:20 | 2:24 | S/O | Goalpara Sub station 132 kv BUS insulation resistance test | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-10-05 12:04 | 2025-10-06 20:06 | 32:02 | S/O | Bhandaria Line trip fault check. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2025-10-13 09:55 | 2025-10-13 14:24 | 4:29 | S/O | Orion plant Maintenance Work. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-10-26 09:20 | 2025-10-26 17:03 | 7:43 | S/O | DWZTG project work | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-10-28 09:24 | 2025-10-28 15:38 | 6:14 | S/O | DWZTGE Project piling work | 0 | 0 | No interruption
Barguna 132/33kV | Barguna-Bakergonj 132kv line | 2025-10-18 06:15 | 2025-10-18 14:26 | 8:11 | S/O | Barishal-Patuakhali 230kV Line stringing work. | 16 | 130.9333 | Power interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-10-08 10:38 | 2025-10-08 15:02 | 4:24 | S/O | Shutdown by ALDC | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Capacitor Bank | 2025-10-27 07:10 | 2025-10-28 16:30 | 33:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Capacitor Bank | 2025-10-27 07:10 | 2025-10-28 16:30 | 33:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2025-10-28 07:09 | 2025-10-28 07:09 | 0:00 | S/O | Barishal North to Patuakhali ckt stringing work | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2025-10-23 15:45 | 2025-10-23 17:28 | 1:43 | S/O | Maint.work | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Orion | 2025-10-04 14:47 | 2025-10-04 17:45 | 2:58 | S/O | By the instruction of ALDC, Khulna | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Orion | 2025-10-13 09:50 | 2025-10-13 14:16 | 4:26 | S/O | Broken 132 KV disc insulator Change. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2025-10-18 05:59 | 2025-10-18 07:31 | 1:32 | S/O | S/D TAKEN BY ALDC KHULNA | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2025-10-11 08:58 | 2025-10-11 11:38 | 2:40 | S/O | Due to high temperature maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-1 | 2025-10-11 08:59 | 2025-10-11 11:37 | 2:38 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-24 08:26 | 2025-10-24 20:53 | 12:27 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-25 07:51 | 2025-10-25 18:47 | 10:56 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-26 09:06 | 2025-10-26 19:12 | 10:06 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-27 09:02 | 2025-10-27 19:45 | 10:43 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2025-10-28 07:08 | 2025-10-28 07:08 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-28 09:31 | 2025-10-28 21:05 | 11:34 | S/O | None | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-29 08:30 | 2025-10-29 20:13 | 11:43 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-10-30 08:54 | 2025-10-30 20:14 | 11:20 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -2 | 2025-10-20 09:03 | 2025-10-20 11:30 | 2:27 | S/O | Due to read Hot maintenance | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2025-10-20 09:02 | 2025-10-20 11:52 | 2:50 | S/O | Instructed by ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2025-10-20 09:02 | 2025-10-20 11:52 | 2:50 | S/O | Instructed by ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2025-10-20 12:48 | 2025-10-20 12:48 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-2 | 2025-10-20 12:48 | 2025-10-20 12:48 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2025-10-18 06:15 | 2025-10-18 14:25 | 8:10 | S/O | Stringing work of T-17/3 to T-17/4 Span (G2G project Work ) | 11 | 89.8333 | Power interruption
|  |  | Total : | 1900-01-09 03:10 |  | Unserved Energy: |  | 220.7667
HVDC Grid Circle :
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2025-10-16 14:41 | 2025-10-16 20:58 | 6:17 | S/O | S/D taken by SPMD,Ishurdi. | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2025-10-16 14:41 | 2025-10-16 20:51 | 6:10 | S/O | S/D taken by SPMD,Ishurdi. | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2025-10-22 10:03 | 2025-10-22 18:27 | 8:24 | S/O | S/D taken by SPMD,Ishwardi | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2025-10-22 10:04 | 2025-10-22 18:28 | 8:24 | S/O | S/D taken by SPMD,Ishwardi. | 0 | 0 | No interruption
Chuadanga 132/33kV | Jhenaidah-Chuadanga Ckt-2 | 2025-10-18 06:42 | 2025-10-18 17:58 | 11:16 | S/O | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-10-25 15:28 | 2025-10-25 17:12 | 1:44 | S/O | DS-667S "R'' phase red hot maintenance work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2025-10-27 08:33 | 2025-10-27 15:09 | 6:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2025-10-28 08:24 | 2025-10-28 15:18 | 6:54 | S/O | Maintenance work at Ruppur substation | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2025-10-29 08:14 | 2025-10-29 15:23 | 7:09 | S/O | ANNUAL MAINTENANCE | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-10-01 08:52 | 2025-10-01 08:52 | 0:00 | S/O | 0 | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Jhenaidah (Old) Ckt-1 | 2025-10-18 06:41 | 2025-10-18 17:22 | 10:41 | S/O | Due to Jhenaidah 132kv ss Bus upgradation work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Jhenaidah (Old) Ckt-2 | 2025-10-18 06:42 | 2025-10-18 17:22 | 10:40 | S/O | Due to Jhenaidah 132kv ss Bus upgradation work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Jhenaidah (Old) Ckt-3 | 2025-10-18 06:42 | 2025-10-18 17:22 | 10:40 | S/O | Due to Jhenaidah 132kv ss Bus upgradation work | 0 | 0 | No interruption
Magura 132/33kV | Jhenaidah Ckt. -1 | 2025-10-18 06:43 | 2025-10-18 17:37 | 10:54 | S/O | 132kV Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | 21 | 228.9 | Power interruption
Magura 132/33kV | Jhenaidah Ckt. - 2 | 2025-10-18 06:43 | 2025-10-18 17:32 | 10:49 | S/O | 132kV Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | 21 | 227.15 | Power interruption
Magura 132/33kV | Narail Ckt. - 1 | 2025-10-18 06:44 | 2025-10-18 17:34 | 10:50 | S/O | 132kV Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | 19 | 205.8333 | Power interruption
Magura 132/33kV | Narail Ckt. - 2 | 2025-10-18 06:45 | 2025-10-18 17:35 | 10:50 | S/O | 132kV Jhenaidah-Chuadanga ckt-1 maintenance work & Jhenaidah 132kV Bus Upgration work. | 19 | 205.8333 | Power interruption
Ruppur 132/11kV | 132kv Ishurdi Line-1 | 2025-10-27 08:31 | 2025-10-27 15:12 | 6:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-1 | 2025-10-28 08:25 | 2025-10-28 15:19 | 6:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2025-10-29 08:12 | 2025-10-29 15:27 | 7:15 | S/O | A/M | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 15:08 |  | Unserved Energy: |  | 867.7167
Bogura Grid Circle :
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2025-10-28 07:59 | 2025-10-28 17:09 | 9:10 | S/O | 0 | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-10-30 07:13 | 2025-10-30 14:09 | 6:56 | S/O | saidpur end maintenance work | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-2 | 2025-10-25 09:56 | 2025-10-25 12:59 | 3:03 | S/O | Shutdown taken by Bogura 230/132 KV sub statiuon. | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-1 | 2025-10-05 09:04 | 2025-10-05 16:24 | 7:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | 230KV Main 1 | 2025-10-08 09:17 | 2025-10-08 15:36 | 6:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | 230KV Main 2 | 2025-10-09 09:13 | 2025-10-09 15:22 | 6:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 1 | 2025-10-14 09:02 | 2025-10-14 12:44 | 3:42 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-10-15 09:28 | 2025-10-15 13:20 | 3:52 | S/O | Scada And RTU integration | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-10-15 14:46 | 2025-10-15 16:29 | 1:43 | S/O | SCADA & RTU Integration | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-10-15 17:07 | 2025-10-15 17:27 | 0:20 | S/O | SCADA & RTU Integration | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-2 | 2025-10-21 08:29 | 2025-10-21 17:12 | 8:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-2 | 2025-10-22 08:19 | 2025-10-22 16:28 | 8:09 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bogura 230/132kV | Serajganj Line-2 | 2025-10-23 08:30 | 2025-10-23 16:45 | 8:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-2 | 2025-10-25 09:55 | 2025-10-25 12:58 | 3:03 | S/O | Red-hot Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 1 | 2025-10-25 09:57 | 2025-10-25 12:44 | 2:47 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-10-15 09:29 | 2025-10-15 13:18 | 3:49 | S/O | Bogura -01 (230 kv ckt) Shutdown due to SCADA and RTU upgradation at bogura 230 kv substation. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-10-15 14:46 | 2025-10-15 16:29 | 1:43 | S/O | Bogura -02 (230 kv ckt) Shutdown due to SCADA and RTU upgradation at bogura 230 kv substation. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-10-15 17:07 | 2025-10-15 17:27 | 0:20 | S/O | SCADA upgradation at Bogura 230kV Grid Sub-Station | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2025-10-28 07:49 | 2025-10-28 17:15 | 9:26 | S/O | S/D Taken by ALDC Bogura. For working Barapukuria side. | 0 | 0 | No interruption
Jaldhaka 132/33kV | Capacitor Bank Outdoor (22.5 MVAR) | 2025-10-11 08:48 | 2025-10-11 14:10 | 5:22 | S/O | Anual Maintenance. | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-1 | 2025-10-29 09:50 | 2025-10-29 12:20 | 2:30 | S/O | CB Spring Charging Auxiliary Contact Change (Work done by CCCE) | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-2 | 2025-10-29 10:10 | 2025-10-29 12:32 | 2:22 | S/O | CB Spring Charging Auxiliary Contact Change (Work done by CCCE) | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-02 10:20 | 2025-10-02 17:35 | 7:15 | S/O | Opgw conductor work | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-03 10:14 | 2025-10-03 17:25 | 7:11 | S/O | Opgw change work | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-04 09:31 | 2025-10-04 19:22 | 9:51 | S/O | 132 KV Lalmonirhat - Kurigram change Earth o OPGW | 8 | 78.8 | Power interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-05 08:24 | 2025-10-05 17:16 | 8:52 | S/O | 0 | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-06 06:46 | 2025-10-06 17:35 | 10:49 | S/O | Earthwire change & OPGW installation work | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-07 08:15 | 2025-10-07 17:27 | 9:12 | S/O | Earthwire change and OPGW Installation. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-08 07:36 | 2025-10-08 18:12 | 10:36 | S/O | Earthwire change & OPGW installation work | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-09 08:26 | 2025-10-09 18:38 | 10:12 | S/O | OPGW CHANGE WORK | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-10 08:38 | 2025-10-10 17:52 | 9:14 | S/O | OPGw installation in 132 KV line | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-11 06:15 | 2025-10-11 15:15 | 9:00 | S/O | Project work | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-12 08:40 | 2025-10-12 17:28 | 8:48 | S/O | Opgw project Work. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-13 07:30 | 2025-10-13 18:16 | 10:46 | S/O | 0 | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2025-10-14 08:29 | 2025-10-14 16:45 | 8:16 | S/O | OPGW work | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-10-25 15:28 | 2025-10-25 17:13 | 1:45 | S/O | 0 | 0 | 0 | No interruption
Panchagarh 132/33kV | 132KV Capacitor Bank | 2025-10-23 09:18 | 2025-10-23 16:10 | 6:52 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Rahanpur 132/33kV | Rahanpur-2 | 2025-10-20 11:50 | 2025-10-20 12:24 | 0:34 | S/O | Emergency Maintenance Work In DS | 0 | 0 | No interruption
Rahanpur 132/33kV | Rahanpur-2 | 2025-10-23 15:25 | 2025-10-23 17:10 | 1:45 | S/O | DS QB1 not working in remote. CCCE technician fixing it. | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Chowdala 132 KV Line Ckt-02 | 2025-10-23 15:25 | 2025-10-23 17:09 | 1:44 | S/O | As per instruction of ALDC Bogura | 0 | 0 | No interruption
Saidpur 132/33kV | RPC Bank-01 | 2025-10-08 11:00 | 2025-10-08 12:43 | 1:43 | S/O | Annual maintenances | 0 | 0 | No interruption
Sirajgonj 230 | Bogura -01 | 2025-10-05 09:04 | 2025-10-05 16:25 | 7:21 | S/O | annual shutdown | 0 | 0 | No interruption
Sirajgonj 230 | Bogura -02 | 2025-10-21 08:30 | 2025-10-21 17:26 | 8:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 | Bogura -02 | 2025-10-22 08:41 | 2025-10-22 16:29 | 7:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 | Bogura -02 | 2025-10-23 08:31 | 2025-10-23 16:45 | 8:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV | RPC Indoor-1 | 2025-10-12 09:25 | 2025-10-12 16:30 | 7:05 | S/O | Annual Maintenance (Indoor RPC Plant-01) | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 14:52 |  | Unserved Energy: |  | 78.8
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-04-27 16:27 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October 2025
| Area | Previous Month (September' 2025) |  |  |  | Current Month (October '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 35 | 12 | 30 | 77 | 10 | 19 | 97 | 126
2 | Dhaka (South) Grid Circle. | 23 | 16 | 29 | 68 | 13 | 8 | 49 | 70
3 | Chattogram Grid Circle. | 13 | 14 | 24 | 51 | 13 | 19 | 81 | 113
4 | Cumilla Grid Circle. | 21 | 24 | 53 | 98 | 21 | 18 | 106 | 145
5 | Khulna Grid Circle. | 23 | 15 | 44 | 82 | 14 | 10 | 118 | 142
6 | HVDC Grid Circle | 20 | 12 | 33 | 65 | 15 | 9 | 33 | 57
7 | Bogura Grid Circle. | 33 | 17 | 36 | 86 | 29 | 21 | 100 | 150
8 | Others
9 | Total | 168 | 110 | 249 | 527 | 115 | 104 | 584 | 803
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October 2025
| Area | Previous Month (September' 2025) |  |  |  | Current Month (October '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 834.55 | 371.33 | 1421.1 | 2626.98 | 151.43 | 281.03 | 1099.75 | 1532.21
2 | Dhaka (South) Grid Circle. | 5782.85 | 5728.78 | 192.75 | 11704.38 | 98.9 | 6 | 203.8 | 308.7
3 | Chattogram Grid Circle. | 313.7 | 312.05 | 624.15 | 1249.9 | 157 | 190.37 | 855.38 | 1202.75
4 | Cumilla Grid Circle. | 137.22 | 228.72 | 2304.65 | 2670.59 | 244.64 | 238.5 | 842.69 | 1325.83
5 | Khulna Grid Circle. | 214.67 | 385.79 | 501.59 | 1102.05 | 23 | 87.01 | 708.55 | 818.56
6 | HVDC Grid Circle | 38 | 165.99 | 2730.42 | 2934.41 | 339.35 | 81.98 | 2100.05 | 2521.38
7 | Bogura Grid Circle. | 218.34 | 139.58 | - | 357.92 | 101.77 | 415.31 | 633.88 | 1150.96
8 | Others
9 | Total | 7539.33 | 7332.24 | 7774.66 | 22646.23 | 1116.09 | 1300.2 | 6444.1 | 8860.39
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 5 | 7 | 12 | 1 | 4 | 7 | 1060.11
2 | Dhaka (South) | 5031.6 | - | 3 | 3 | 1 | - | 2 | 203.8
3 | Chattogram | 2042 | 5 | 5 | 10 | 2 | 1 | 7 | 999.58
4 | Khulna | 2434 | 6 | 10 | 16 | 6 |  | 10 | 555.11
5 | HVDC | 5954.3 | 5 | 2 | 7 | - | 2 | 5 | 1653.66
6 | Bogura | 3145.6 | 15 | 8 | 23 | 8 | 1 | 14 | 1044.76
7 | Cumilla | 2981 | 9 | 15 | 24 | 2 | 6 | 16 | 1195.94
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 6712.96
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 100%
3 | Chattogram | 99.98%
4 | Khulna | 99.99%
5 | HVDC | 99.98%
6 | Bogura | 99.97%
7 | Cumilla | 99.97% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | 3 | 6 | - | 3 | 3 | 472.1
2 | Dhaka (South) | 990.29 | - | 3 |  | 3 | - | - | 3 | 104.9
3 | Chattogram | 917 | - | 3 | 1 | 4 | - | - | 4 | 203.16
4 | Khulna | 1238.4 | - | 3 | 2 | 5 |  |  | 5 | 263.45
5 | HVDC | 1325 | - | - | 4 | 4 | - | - | 4 | 867.72
6 | Bogura | 1803.3 | - | 5 | 1 | 6 | 5 | - | 1 | 106.2
7 | Cumilla | 1648.16 | - | 3 | 1 | 4 |  | 2 | 2 | 129.89
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 2147.42
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2025-10-01 | 12 | - | 14 | 15 hr 26 min | 4 | 6 hr 58 min
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:October 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Kishoreganj 132/33kV | 1 | 0.052083 | 18.75
Sreepur 230/132/33kV | 1 | 0.10208 | 88.2
Tangail 132/33kV | 3 | 0.17569 | 174.08
Manikganj 132/33kV | 2 | 1:49 | 78.6
Mirpur 132/33kV | 1 | 0:46 | 72.8333
Bhaluka 132/33kV | 3 | 0.20833 | 95.25
Joydebpur 132/33kV | 1 | 0:25 | 12.5
Kabirpur 132/33kV | 1 | 1:24 | 140
Sherpur 132/33kV | 1 | 2:08 | 21.3333
Sreepur 230/132/33kV | 1 | 2:33 | 510
Bhaluka 132/33kV | 2 | 6:28 | 320.67
Nawabganj 132/33kV | 2 | 0.17917 | 98.9
Sonargaon 132/33kV | 1 | 0.083333 | 6
Narshingdi 132/33kV | 1 | 0.029167 | 12.6
Sonargaon 132/33kV | 1 | 0.16944 | 170.8
Srinagar 132/33kV | 1 | 1:12 | 20.4
Dohazari 132/33kV | 3 | 0:34 | 23.17
Bakulia 132/33kV | 1 | 0.05625 | 27
Dohazari 132/33kV | 1 | 0.043056 | 73.3667
Madunaghat 132/33kV | 1 | 0.16389 | 59
Baroaulia 132/33kV | 1 | 0.10278 | 49.3333
Coxsbazar 132/33kV | 1 | 0.23472 | 84.5
Baroaulia 132/33kV | 1 | 0.064583 | 31
Dohazari 132/33kV | 2 | 0.10694 | 174.72
Hathazari 230/132/33kV | 3 | 12:50 | 642.33
Dohazari 132/33kV | 1 | 3:50 | 38.3333
Brahmanbaria 132/33kV | 2 | 0:50 | 22.42
Daudkandi 132/33kV | 3 | 6:12 | 186
Chowmuhani 132/33kV | 2 | 0.10764 | 87.5
Daudkandi 132/33kV | 1 | 0.091667 | 66
Kachua 230/132/33kV | 1 | 0.125 | 45
Brahmanbaria 132/33kV | 2 | 0.073611 | 36.22
Chandpur 132/33kV | 1 | 1:36 | 40
Chandina 132/33kV | 2 | 5:04 | 13.63
Chauddagram 132/33kV | 3 | 1:09 | 40.25
Cumilla(N) 230/132/33kV | 1 | 1:20 | 33.3333
Feni 132/33kV | 1 | 3:16 | 72
Kulaura 132/33kV | 1 | 0.11181 | 13.4167
Lakshmipur 132/33kV | 1 | 5:22 | 53.6667
Shahjibazar 132/33kV | 5 | 13:45 | 431.08
Sylhet 132/33kV | 2 | 4:53 | 131.63
Chhatak 132/33kV | 1 | 5:22 | 53.6667
Barishal 132/33kV | 2 | 0:09 | 7.67
Patuakhali 132/33kV | 2 | 0:40 | 15.33
Barishal 230/132kV | 1 | 9:31 | 0
Bhandaria 132/33kV | 2 | 4:26 | 44.33
Mongla 132/33kV | 3 | 5:06 | 42.68
Bagerhat 132/33kV | 1 | 1:53 | 103.5833
Barishal 132/33kV | 1 | 1:20 | 13.3333
Faridpur 132/33kV | 2 | 4:44 | 232.33
Gollamari 132/33kV | 2 | 0:11 | 2.93
Madaripur 132/33kV | 3 | 2:36 | 96.1
Satkhira 132/33kV | 1 | 2:38 | 39.5
Barguna 132/33kV | 1 | 8:11 | 130.9333
Patuakhali 132/33kV | 1 | 8:10 | 89.8333
Ishurdi 132/33kV | 1 | 10:17 | 339.35
Bhangura 132/33kV | 2 | 2:38 | 49.93
Jashore 132/33kV | 2 | 2:50 | 32.25
Ishurdi 132/33kV | 1 | 9:07 | 182.3333
Jhenaidah 132/33kV | 1 | 11:40 | 1050
Magura 132/33kV | 4 | 43:23:00 | 867.72
Amnura 132/33kV | 2 | 0:52 | 5.2
Bogura 132/33kV | 2 | 0:40 | 18.67
Niamatpur 132/33kV | 1 | 0:26 | 3.4667
Purbasadipur 132/33kV | 1 | 0:26 | 15.1667
Rajshahi 230/132/33kV | 1 | 0:51 | 31.87
Barapukuria 230/132/33kV | 2 | 4:02 | 92.67
Mithapukur 132/33kV | 2 | 3:08 | 58.91
Niamatpur 132/33kV | 1 | 1:11 | 37.8667
Rangpur 132/33kV | 1 | 4:02 | 201.6667
Saidpur 132/33kV | 1 | 2:01 | 24.2
Panchagarh 132/33kV | 1 | 0:24 | 10
Rangpur 132/33kV | 2 | 0:28 | 8
Thakurgaon 132/33kV | 2 | 0:47 | 9.4
Barapukuria 230/132/33kV | 2 | 4:16 | 98.1
Bog-Sherpur 132/33kV | 1 | 3:09 | 34.65
Bogura 132/33kV | 1 | 7:17 | 182.0833
Rajshahi 132/33kV | 1 | 1:07 | 27.9167
Rangpur 132/33kV | 2 | 4:38 | 208.5
Saidpur 132/33kV | 1 | 0:46 | 3.8333
Lalmonirhat 132/33kV | 1 | 9:51 | 78.8
| 128 | 274:02 | 8860.59
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 13 | 2025-10-02 11:00
2 | AKSML | 164 | 2025-10-28 13:00
3 | Aftabnagar | 42 | 2025-10-19 18:00
4 | Agargaon | 148 | 2025-10-20 13:00
5 | Agrabad | 132 | 2025-10-23 10:00
6 | Amnura | 36 | 2025-10-01 01:00
7 | Ashuganj | 100 | 2025-10-23 00:00
8 | BSRM | 209 | 2025-10-28 00:00
9 | Bagerhat | 89 | 2025-10-23 18:00
10 | Bajitpur | 97 | 2025-10-04 21:00
11 | Bakulia | 105 | 2025-10-28 19:00
12 | Banani | 56 | 2025-10-22 11:00
13 | Bangabhaban | 28 | 2025-10-26 10:00
14 | Barapukuria | 67 | 2025-10-11 18:30
15 | Barguna | 24 | 2025-10-18 19:30
16 | Barishal | 121 | 2025-10-19 18:30
17 | Barishal-230 | 104 | 2025-10-03 21:00
18 | Baroaulia | 77 | 2025-10-28 09:00
19 | Baroirhat | 69 | 2025-10-28 20:00
20 | Bashundhara | 223 | 2025-10-27 15:00
21 | BashundharaCement | 15 | 2025-10-25 21:00
22 | Beanibazar | 88 | 2025-10-17 18:00
23 | Benapole | 70 | 2025-10-06 18:30
24 | Bhaluka | 160 | 2025-10-08 18:30
25 | Bhandaria | 62 | 2025-10-28 22:00
26 | Bhangura | 41 | 2025-10-23 18:00
27 | Bheramara(GK) | 67 | 2025-10-20 19:00
28 | Bhulta | 242 | 2025-10-22 23:00
29 | Bog-Sherpur | 78 | 2025-10-01 02:00
30 | Bogura | 200 | 2025-10-13 14:00
31 | Borhanuddin | 95 | 2025-10-14 21:00
32 | Brahmanbaria | 143 | 2025-10-22 19:30
33 | Cantonment | 170 | 2025-10-23 13:00
34 | Chandina | 40.05 | 2025-10-15 22:00
35 | Chandpur | 92 | 2025-10-04 18:30
36 | Chandraghona | 51 | 2025-10-31 18:00
37 | Chapai | 81 | 2025-10-19 13:00
38 | Charsaidpur | 42 | 2025-10-09 16:00
39 | Chauddagram | 80 | 2025-10-22 18:30
40 | Chhatak | 44 | 2025-10-19 18:30
41 | Chowmuhani | 191 | 2025-10-01 00:00
42 | Chuadanga | 115 | 2025-10-07 18:30
43 | Coxsbazar | 150 | 2025-10-25 18:00
44 | Cumilla(N) | 165 | 2025-10-22 10:00
45 | Cumilla(S) | 174 | 2025-10-21 18:00
46 | Daganbhuiyan | 20 | 2025-10-29 22:00
47 | Daudkandi | 162 | 2025-10-28 19:30
48 | DhakaUniversity | 100 | 2025-10-19 13:00
49 | Dhamrai | 140 | 2025-10-09 18:00
50 | Dhanmondi | 147 | 2025-10-26 13:00
51 | Dohazari | 112 | 2025-10-21 19:30
52 | Faridpur | 179 | 2025-10-01 02:00
53 | Fatullah | 122 | 2025-10-21 16:00
54 | Fenchuganj | 51 | 2025-10-30 19:30
55 | Feni | 136 | 2025-10-21 18:30
56 | GPH | 84 | 2025-10-27 13:00
57 | Ghatail | 88 | 2025-10-17 18:00
58 | Ghorashal | 0 | 2025-10-01 00:00
59 | Ghorashal-230 | 110 | 2025-10-01 00:00
60 | Goalpara | 42 | 2025-10-25 18:00
61 | Gollamari | 104 | 2025-10-08 20:00
62 | Gopalganj | 112 | 2025-10-18 21:00
63 | Gulshan | 138 | 2025-10-20 13:00
64 | Halishahar | 86 | 2025-10-28 11:00
65 | HaripurSBU | 167 | 2025-10-27 12:00
66 | Hasnabad | 110 | 2025-10-27 19:00
67 | Hathazari | 97 | 2025-10-31 18:00
68 | Ishurdi | 80 | 2025-10-21 18:30
69 | Jaldhaka | 84 | 2025-10-01 02:00
70 | Jamalpur | 140 | 2025-10-01 02:00
71 | Jashore | 149 | 2025-10-18 21:00
72 | Jhenaidah | 139 | 2025-10-18 18:30
73 | Joydebpur | 167 | 2025-10-18 18:00
74 | Joypurhat | 66 | 2025-10-28 22:00
75 | Juldah | 21.5 | 2025-10-05 12:00
76 | KSRM | 50 | 2025-10-20 15:00
77 | Kabirpur | 270 | 2025-10-04 18:00
78 | Kachua | 103 | 2025-10-21 18:00
79 | Kallyanpur | 108 | 2025-10-01 00:00
80 | Kalurghat | 55 | 2025-10-15 10:00
81 | Kamrangirchar | 82 | 2025-10-21 18:00
82 | Kaptai | N/A | N/A
83 | Kasba | 41 | 2025-10-15 21:00
84 | Kazla | 110 | 2025-10-30 19:30
85 | Keranigonj | 97 | 2025-10-08 18:30
86 | Khagrachori | 36 | 2025-10-18 18:00
87 | Khulna | 78 | 2025-10-27 13:00
88 | Khulshi | 203 | 2025-10-09 18:00
89 | Kishoreganj | 131 | 2025-10-26 22:00
90 | Kodda | 313 | 2025-10-13 18:30
91 | Kulaura | 56 | 2025-10-23 18:00
92 | Kurigram | 66 | 2025-10-04 18:00
93 | Kushtia | 158 | 2025-10-09 18:30
94 | Laksam | 46 | 2025-10-22 22:00
95 | Lakshmipur | 38 | 2025-10-18 22:00
96 | Lalbag | 72 | 2025-10-19 13:00
97 | Lalmonirhat | 70 | 2025-10-02 21:00
98 | MI_Cement | 18.5 | 2025-10-05 02:00
99 | Madanganj | 51 | 2025-10-23 21:00
100 | Madaripur | 117 | 2025-10-01 02:00
101 | Madartek | 101 | 2025-10-27 23:00
102 | Madunaghat | 62 | 2025-10-13 19:30
103 | Magura | 71 | 2025-10-18 21:00
104 | Mahasthangarh | 92 | 2025-10-01 00:00
105 | Maijdee | 40 | 2025-10-27 21:00
106 | Manikganj | 133 | 2025-10-01 00:00
107 | Maniknagar | 68 | 2025-10-15 13:00
108 | Matarbari | 56 | 2025-10-11 20:00
109 | Matuail | 75 | 2025-10-23 11:00
110 | Metrorail_Motijheel | 42 | 2025-10-14 17:00
111 | Metrorail_Uttara | 20 | 2025-10-29 11:00
112 | Millgate | 136 | 2025-10-19 15:00
113 | Mirpur | 145 | 2025-10-28 12:00
114 | Mirsorai | 20 | 2025-10-16 18:30
115 | Mirzapur | 51 | 2025-10-05 21:00
116 | Mithapukur | 70 | 2025-10-01 02:00
117 | Modern | N/A | N/A
118 | Mogbazar | 107.6 | 2025-10-05 13:00
119 | Mongla | 49 | 2025-10-07 12:00
120 | Motijheel | 77 | 2025-10-27 13:00
121 | Muktagacha | 40 | 2025-10-04 18:00
122 | Munshiganj | 124 | 2025-10-01 00:00
123 | Muradnagar | 45 | 2025-10-15 21:00
124 | Mymensingh | 221 | 2025-10-22 18:00
125 | Naogaon | 140 | 2025-10-01 00:00
126 | Narail | 62 | 2025-10-18 19:00
127 | Narinda | 78 | 2025-10-29 13:00
128 | Narshingdi | 193 | 2025-10-01 00:00
129 | Natore | 153 | 2025-10-11 18:30
130 | Nawabganj | 55 | 2025-10-25 21:00
131 | Netrakona | 149 | 2025-10-23 18:00
132 | New | 62 | 2025-10-28 12:00
133 | Niamatpur | 86 | 2025-10-25 18:30
134 | Noapara | 53 | 2025-10-06 18:00
135 | PHP | 9 | 2025-10-12 06:00
136 | Pabna | 111 | 2025-10-09 18:30
137 | Palashbari | 132 | 2025-10-01 01:00
138 | Panchagarh | 63 | 2025-10-18 18:30
139 | Patiya | 12.6 | 2025-10-01 01:00
140 | Patuakhali | 77 | 2025-10-22 21:00
141 | Payra | 36 | 2025-10-18 18:00
142 | Postogola | 71 | 2025-10-15 13:00
143 | Purbachal | 23 | 2025-10-01 00:00
144 | Purbasadipur | 122 | 2025-10-09 18:30
145 | Rahanpur | 40 | 2025-10-01 02:00
146 | Rahim | 56 | 2025-10-31 03:00
147 | Rajbari | 84 | 2025-10-06 18:30
148 | Rajendrapur | 138 | 2025-10-09 18:00
149 | Rajshahi | 132 | 2025-10-19 13:00
150 | Rajshahi-230 | 102 | 2025-10-07 19:00
151 | Ramganj | 124 | 2025-10-25 18:00
152 | Rampur | 61 | 2025-10-22 20:00
153 | Rangamati | 18 | 2025-10-01 18:30
154 | Rangpur | 149 | 2025-10-08 18:30
155 | Ruppur | 8.6 | 2025-10-07 16:00
156 | SSM | 16 | 2025-10-08 01:00
157 | Saidpur | 110 | 2025-10-23 18:00
158 | Satkhira | 133 | 2025-10-28 22:00
159 | Satmasjid | 107 | 2025-10-23 13:00
160 | Savar | 236 | 2025-10-09 15:00
161 | SevenRings | 21.6 | 2025-10-16 07:00
162 | ShahCement | 32 | 2025-10-20 23:00
163 | Shahjadpur | 94 | 2025-10-21 18:30
164 | Shahjibazar | 135 | 2025-10-31 19:00
165 | Shahmirpur | 68 | 2025-10-14 18:00
166 | Shariatpur | 93 | 2025-10-18 21:00
167 | Sherpur | 150 | 2025-10-01 02:00
168 | Shikalbaha | 40.5 | 2025-10-25 13:00
169 | Shitalakhya | 94.2 | 2025-10-21 16:00
170 | Sholosohor | 52 | 2025-10-16 11:00
171 | Shyampur | 152 | 2025-10-21 12:00
172 | Siddhirganj | 131 | 2025-10-26 18:00
173 | Sirajganj | 120 | 2025-10-21 19:00
174 | Sonargaon | 144 | 2025-10-27 18:30
175 | Sreemongol | 88 | 2025-10-22 22:00
176 | Sreepur | 121 | 2025-10-05 18:00
177 | Srinagar | 52.62 | 2025-10-01 00:00
178 | Sunamganj | 68 | 2025-10-17 22:00
179 | Sylhet | 65 | 2025-10-17 18:00
180 | Sylhet-132 | 154 | 2025-10-14 19:00
181 | TK | 26 | 2025-10-30 18:00
182 | Tangail | 186 | 2025-10-01 01:00
183 | Taraganj | 25 | 2025-10-14 18:00
184 | Thakurgaon | 106 | 2025-10-01 02:00
185 | Tongi | 155 | 2025-10-27 18:00
186 | Ullahpara | 40 | 2025-10-21 18:30
187 | Ullon | 73 | 2025-10-19 18:00
188 | Uttara | 109 | 2025-10-28 13:00
189 | UttaraNew | 80 | 2025-10-18 18:00
190 | Zigatola | 79 | 2025-10-19 18:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: October 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5660.09 | 2025-10-27 | 18:00
Chattogram | 1731.2 | 2025-10-26 | 18:00
Cumilla | 1583.9 | 2025-10-22 | 22:00
Mymensingh | 1160 | 2025-10-01 | 19:00
Sylhet | 689 | 2025-10-23 | 18:00
Khulna | 1803 | 2025-10-27 | 18:30
Barishal | 495 | 2025-10-22 | 21:00
Rajshahi | 1484 | 2025-10-01 | 0:00
Rangpur | 986 | 2025-10-01 | 2:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 388 | 2025-10-13 05:00 | 360 | 2025-10-22 23:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 408 | 2025-10-01 04:00 | 364 | 2025-10-20 16:00
4 | Bibiana | 400 | 392 | 2025-10-03 06:00 | 375 | 2025-10-22 18:30
5 | BIPTC | 400 | 408 | 2025-10-03 11:00 | 394 | 2025-10-07 18:30
6 | Bogura | 400 | 408 | 2025-10-01 08:00 | 366 | 2025-10-24 20:00
7 | Gopalganj | 400 | 402 | 2025-10-03 07:00 | 376 | 2025-10-20 15:00
8 | Kaliakoir | 400 | 383 | 2025-10-10 14:00 | 351 | 2025-10-18 11:00
9 | Korerhat | 400 | N/A | N/A | N/A | N/A
10 | Madunaghat | 400 | 400 | 2025-10-12 19:00 | 381 | 2025-10-05
11 | Meghnaghat | 400 | 395 | 2025-10-23 23:00 | 363 | 2025-10-23 11:00
12 | Payra | 400 | 415 | 2025-10-03 08:00 | 401 | 2025-10-22 18:30
13 | Rahanpur | 400 | 416 | 2025-10-01 07:00 | 381 | 2025-10-22 18:30
14 | Rampal | 400 | 408 | 2025-10-03 08:00 | 380 | 2025-10-17 22:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 233 | 2025-10-03 08:00 | 212 | 2025-10-20 12:00
2 | AKSML | 230 | 238 | 2025-10-13 18:00 | 220 | 2025-10-17 10:00
3 | Aminbazar | 230 | 233 | 2025-10-01 04:00 | 212 | 2025-10-20 12:00
4 | Ashuganj | 230 | 236 | 2025-10-01 05:00 | 212 | 2025-10-23 09:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 239 | 2025-10-31 11:00 | 222 | 2025-10-24 19:30
7 | Barapukuria | 230 | 233 | 2025-10-25 11:00 | 202 | 2025-10-21 18:30
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 237 | 2025-10-10 17:00 | 223 | 2025-10-04 22:00
10 | Bheramara | 230 | 236 | 2025-10-08 22:00 | 221 | 2025-10-01 23:00
11 | Bhulta | 230 | 235 | 2025-10-01 04:00 | 205 | 2025-10-20 16:00
12 | Bibiana | 230 | 233 | 2025-10-31 00:00 | 219 | 2025-10-22 18:30
13 | BIPTC | 230 | 238 | 2025-10-03 12:00 | 221 | 2025-10-09 23:00
14 | Bogura | 230 | 245 | 2025-10-31 10:00 | 223 | 2025-10-20 13:00
15 | Bogura-400 | 230 | 244 | 2025-10-31 10:00 | 223 | 2025-10-21 18:30
16 | Borhanuddin | 230 | 239 | 2025-10-10 16:00 | 229 | 2025-10-04 22:00
17 | BSRM | 230 | 238 | 2025-10-12 18:30 | 214 | 2025-10-24 04:00
18 | Cumilla(N) | 230 | 230 | 2025-10-12 18:30 | 212 | 2025-10-24 00:00
19 | Faridpur | 230 | 236 | 2025-10-01 06:00 | 218 | 2025-10-22 23:00
20 | Fenchuganj | 230 | 234 | 2025-10-13 06:00 | 221 | 2025-10-22 18:30
21 | Ghorashal | 230 | 240 | 2025-10-04 05:00 | 210 | 2025-10-20 13:00
22 | Ghorashal-230 | 230 | 234 | 2025-10-01 05:00 | 206 | 2025-10-20 16:00
23 | Gopalganj | 230 | 244 | 2025-10-04 00:00 | 221 | 2025-10-05
24 | GPH | 230 | 238 | 2025-10-12 18:30 | 220 | 2025-10-24 04:00
25 | Haripur | 230 | 227 | 2025-10-10 17:00 | 209 | 2025-10-20 16:00
26 | Hasnabad | 230 | 229 | 2025-10-01 03:00 | 209 | 2025-10-20 12:00
27 | Hathazari | 230 | 236 | 2025-10-12 17:00 | 220 | 2025-10-24 12:00
28 | Ishurdi | 230 | 239 | 2025-10-31 10:00 | 223 | 2025-10-10 00:00
29 | Jhenaidah | 230 | 235 | 2025-10-30 05:00 | 215 | 2025-10-21 18:30
30 | Kachua | 230 | 235 | 2025-10-12 18:00 | 193 | 2025-10-01 12:00
31 | Kaliakoir | 230 | 239 | 2025-10-01 04:00 | 215 | 2025-10-23 12:00
32 | Keranigonj | 230 | 244 | 2025-10-05 05:00 | 209 | 2025-10-20 12:00
33 | Khulna(S) | 230 | 237 | 2025-10-31 10:00 | 215 | 2025-10-06 22:00
34 | Korerhat | 230 | N/A | N/A | N/A | N/A
35 | Madunaghat | 230 | 239 | 2025-10-12 18:00 | 223 | 2025-10-24 05:00
36 | Madunaghat-400 | 230 | 240 | 2025-10-12 19:00 | 225 | 2025-10-25 15:00
37 | Maniknagar | 230 | 225 | 2025-10-01 06:00 | 206 | 2025-10-22 23:00
38 | Meghnaghat | 230 | 233 | 2025-10-10 17:00 | 215 | 2025-10-22 23:00
39 | Meghnaghat-400 | 230 | 229 | 2025-10-01 04:00 | 211 | 2025-10-23 11:00
40 | Mirsorai | 230 | 240 | 2025-10-05 15:00 | 214 | 2025-10-24 04:00
41 | Rajshahi | 230 | 235 | 2025-10-14 06:00 | 219 | 2025-10-01 13:00
42 | Rampal | 230 | 234 | 2025-10-03 08:00 | 216 | 2025-10-17 22:00
43 | Rampur | 230 | N/A | N/A | N/A | N/A
44 | Rampura | 230 | 235 | 2025-10-03 08:00 | 200 | 2025-10-23 13:00
45 | Shikalbaha | 230 | 240 | 2025-10-12 18:00 | 222 | 2025-10-25 14:00
46 | Shyampur | 230 | 233 | 2025-10-06 00:00 | 210 | 2025-10-20 11:00
47 | Siddhirganj | 230 | 229 | 2025-10-10 18:00 | 209 | 2025-10-22 18:30
48 | Sirajgonj | 230 | 244 | 2025-10-31 17:00 | 229 | 2025-10-22 18:30
49 | Sreepur | 230 | 234 | 2025-10-31 10:00 | 213 | 2025-10-20 13:00
50 | Tongi | 230 | 233 | 2025-10-03 15:00 | 206 | 2025-10-23 12:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 141 | 2025-10-28 06:00 | 121 | 2025-10-15 12:00
2 | Agargaon | 132 | 141 | 2025-10-01 05:00 | 121 | 2025-10-20 13:00
3 | Agrabad | 132 | 137 | 2025-10-13 18:00 | 126 | 2025-10-01 12:00
4 | AKS | 132 | 134 | 2025-10-12 18:00 | 125 | 2025-10-01 12:00
5 | Aminbazar | 132 | 138 | 2025-10-10 13:00 | 123 | 2025-10-18 11:00
6 | Amnura | 132 | 141 | 2025-10-01 07:00 | 126 | 2025-10-03 22:00
7 | Ashuganj | 132 | 142 | 2025-10-01 02:00 | 130 | 2025-10-22 19:00
8 | Bagerhat | 132 | 139 | 2025-10-31 07:00 | 113 | 2025-10-21 18:30
9 | Bajitpur | 132 | 134 | 2025-10-03 16:00 | 115 | 2025-10-20 09:00
10 | Bakulia | 132 | 139 | 2025-10-09 19:00 | 126 | 2025-10-25 14:00
11 | Banani | 132 | 140 | 2025-10-28 06:00 | 120 | 2025-10-09 10:00
12 | Bangabhaban | 132 | 137 | 2025-10-01 03:00 | 123 | 2025-10-20 16:00
13 | Barapukuria | 132 | 142 | 2025-10-30 13:00 | 121 | 2025-10-22 18:00
14 | Barguna | 132 | 141 | 2025-10-06 18:30 | 129 | 2025-10-04 22:00
0 | Barishal | 132 | 140 | 2025-10-12 17:00 | 125 | 2025-10-04 21:00
16 | Barishal-230 | 132 | 138 | 2025-10-12 17:00 | 126 | 2025-10-04 22:00
17 | Baroaulia | 132 | 137 | 2025-10-12 18:00 | 127 | 2025-10-03 10:00
18 | Baroirhat | 132 | 136 | 2025-10-12 18:30 | 123 | 2025-10-24 03:00
19 | Bashundhara | 132 | 140 | 2025-10-28 06:00 | 119 | 2025-10-20 11:00
20 | BashundharaCement | 132 | 138 | 2025-10-10 01:00 | 120 | 2025-10-15 15:00
21 | Beanibazar | 132 | 131 | 2025-10-11 09:00 | 120 | 2025-10-10 22:00
22 | Benapole | 132 | 136 | 2025-10-03 09:00 | 114 | 2025-10-20 11:00
23 | Bhaluka | 132 | 134 | 2025-10-15 17:00 | 118 | 2025-10-20 12:00
24 | Bhandaria | 132 | 135 | 2025-10-10 09:00 | 107 | 2025-10-21 18:30
25 | Bhangura | 132 | 136 | 2025-10-31 09:00 | 126 | 2025-10-22 18:30
26 | Bheramara | 132 | 139 | 2025-10-18 09:00 | 128 | 2025-10-09 23:00
27 | Bheramara(GK) | 132 | 140 | 2025-10-31 10:00 | 127 | 2025-10-09 23:00
28 | Bhulta | 132 | 130 | 2025-10-10 14:00 | 117 | 2025-10-23 16:00
29 | Bog-Sherpur | 132 | 138 | 2025-10-31 10:00 | 124 | 2025-10-22 18:30
30 | Bogura | 132 | 138 | 2025-10-13 18:00 | 125 | 2025-10-23 14:00
31 | Bogura-230 | 132 | 138 | 2025-10-30 09:00 | 126 | 2025-10-20 13:00
32 | Brahmanbaria | 132 | 137 | 2025-10-01 02:00 | 121 | 2025-10-22 19:00
33 | Cantonment | 132 | 141 | 2025-10-01 04:00 | 121 | 2025-10-20 12:00
34 | Chandina | 132 | 135 | 2025-10-01 03:00 | 123 | 2025-10-22 21:00
35 | Chandpur | 132 | 140 | 2025-10-01 02:00 | 116 | 2025-10-01 12:00
36 | Chandraghona | 132 | 139 | 2025-10-08 19:00 | 130 | 2025-10-25 13:00
37 | Chapai | 132 | 140 | 2025-10-01 07:00 | 126 | 2025-10-22 18:30
39 | Charsaidpur | 132 | 133 | 2025-10-01 06:00 | 120 | 2025-10-20 11:00
40 | Chauddagram | 132 | 144 | 2025-10-12 19:30 | 120 | 2025-10-05 09:00
41 | Chhatak | 132 | 130 | 2025-10-02 15:00 | 117 | 2025-10-10 22:00
42 | Chowmuhani | 132 | 136 | 2025-10-12 17:00 | 112 | 2025-10-01 12:00
43 | Chuadanga | 132 | 137 | 2025-10-10 18:00 | 115 | 2025-10-18 13:00
44 | Coxsbazar | 132 | 127 | 2025-10-16 09:00 | 104 | 2025-10-26 11:00
45 | Cumilla(N) | 132 | 134 | 2025-10-01 06:00 | 122 | 2025-10-24 00:00
46 | Cumilla(S) | 132 | 136 | 2025-10-01 03:00 | 118 | 2025-10-22 16:00
47 | Daganbhuiyan | 132 | 135 | 2025-10-01 03:00 | 108 | 2025-10-01 12:00
48 | Daudkandi | 132 | 132 | 2025-10-29 00:00 | 109 | 2025-10-30 15:00
49 | DhakaUniversity | 132 | 139 | 2025-10-25 06:00 | 121 | 2025-10-15 12:00
50 | Dhamrai | 132 | 140 | 2025-10-10 14:00 | 120 | 2025-10-23 16:00
51 | Dhanmondi | 132 | 140 | 2025-10-28 06:00 | 122 | 2025-10-09 10:00
52 | Dohazari | 132 | 134 | 2025-10-15 18:00 | 121 | 2025-10-22 12:00
53 | Faridpur | 132 | 140 | 2025-10-01 07:00 | 129 | 2025-10-04 22:00
54 | Fatullah | 132 | 139 | 2025-10-03 07:00 | 125 | 2025-10-20 11:00
55 | Fenchuganj | 132 | 138 | 2025-10-11 09:00 | 129 | 2025-10-22 19:00
56 | Feni | 132 | 136 | 2025-10-12 17:00 | 109 | 2025-10-01 12:00
57 | Ghatail | 132 | 136 | 2025-10-01 05:00 | 115 | 2025-10-08 18:00
58 | Ghorashal | 132 | 140 | 2025-10-03 06:00 | 120 | 2025-10-26 09:00
59 | Goalpara | 132 | 139 | 2025-10-03 06:00 | 123 | 2025-10-21 18:30
60 | Gollamari | 132 | 139 | 2025-10-03 06:00 | 123 | 2025-10-27 18:00
61 | Gopalganj | 132 | 139 | 2025-10-01 06:00 | 125 | 2025-10-22 18:00
62 | Gopalganj-400 | 132 | 141 | 2025-10-01 07:00 | 128 | 2025-10-25 18:30
63 | Gulshan | 132 | 140 | 2025-10-29 12:00 | 121 | 2025-10-23 09:00
64 | Halishahar | 132 | 137 | 2025-10-12 18:00 | 127 | 2025-10-20 09:00
65 | Haripur | 132 | 133 | 2025-10-01 03:00 | 122 | 2025-10-16 12:00
66 | HaripurSBU | 132 | 133 | 2025-10-01 03:00 | 117 | 2025-10-09 12:00
67 | Hasnabad | 132 | 136 | 2025-10-01 03:00 | 122 | 2025-10-23 12:00
68 | Hathazari | 132 | 137 | 2025-10-03 08:00 | 128 | 2025-10-28 20:00
69 | Ishurdi | 132 | 141 | 2025-10-31 08:00 | 129 | 2025-10-09 23:00
70 | Jaldhaka | 132 | 137 | 2025-10-31 13:00 | 114 | 2025-10-21 18:30
71 | Jamalpur | 132 | 139 | 2025-10-01 06:00 | 112 | 2025-10-26 18:00
72 | Jashore | 132 | 139 | 2025-10-10 08:00 | 115 | 2025-10-20 11:00
73 | Jhenaidah | 132 | 140 | 2025-10-30 06:00 | 119 | 2025-10-09 23:00
74 | Jhenaidah-230 | 132 | 140 | 2025-10-10 08:00 | 124 | 2025-10-23 18:00
75 | Joydebpur | 132 | 145 | 2025-10-05 18:30 | 117 | 2025-10-20 12:00
76 | Joypurhat | 132 | 135 | 2025-10-05 10:00 | 114 | 2025-10-10 22:00
77 | Juldah | 132 | 138 | 2025-10-12 18:00 | 127 | 2025-10-21 09:00
78 | Kabirpur | 132 | 140 | 2025-10-10 14:00 | 116 | 2025-10-20 16:00
79 | Kachua | 132 | 141 | 2025-10-08 17:00 | 121 | 2025-10-03 23:00
80 | Kaliakoir | 132 | 141 | 2025-10-10 14:00 | 123 | 2025-10-23 16:00
81 | Kallyanpur | 132 | 138 | 2025-10-03 01:00 | 122 | 2025-10-20 13:00
82 | Kalurghat | 132 | 138 | 2025-10-12 18:00 | 129 | 2025-10-24 05:00
83 | Kamrangirchar | 132 | 141 | 2025-10-01 03:00 | 121 | 2025-10-18 11:00
84 | Kaptai | 132 | N/A | N/A | N/A | N/A
85 | Kasba | 132 | 132 | 2025-10-01 03:00 | 116 | 2025-10-30 15:00
86 | Kazla | 132 | 136 | 2025-10-01 05:00 | 123 | 2025-10-20 12:00
87 | Keranigonj | 132 | 141 | 2025-10-01 03:00 | 122 | 2025-10-20 13:00
88 | Khagrachori | 132 | 136 | 2025-10-12 18:00 | 128 | 2025-10-24 13:00
89 | Khulna | 132 | 138 | 2025-10-03 08:00 | 121 | 2025-10-27 18:00
90 | Khulna(S) | 132 | 140 | 2025-10-03 09:00 | 124 | 2025-10-21 18:30
91 | Khulshi | 132 | 136 | 2025-10-12 18:00 | 125 | 2025-10-25 13:00
92 | Kishoreganj | 132 | 134 | 2025-10-03 17:00 | 113 | 2025-10-22 19:00
93 | Kodda | 132 | 141 | 2025-10-05 18:30 | 116 | 2025-10-20 12:00
94 | KSRM | 132 | 138 | 2025-10-12 18:00 | 120 | 2025-10-20 12:00
95 | Kulaura | 132 | 137 | 2025-10-11 09:00 | 128 | 2025-10-22 18:30
96 | Kurigram | 132 | 135 | 2025-10-30 14:00 | 114 | 2025-10-21 18:30
97 | Kushtia | 132 | 138 | 2025-10-05 16:00 | 123 | 2025-10-09 23:00
98 | Laksam | 132 | 139 | 2025-10-01 02:00 | 120 | 2025-10-01 11:00
99 | Lakshmipur | 132 | 136 | 2025-10-12 18:30 | 111 | 2025-10-01 12:00
100 | Lalbag | 132 | 140 | 2025-10-01 03:00 | 121 | 2025-10-23 12:00
101 | Lalmonirhat | 132 | 135 | 2025-10-05 11:00 | 115 | 2025-10-22 18:00
102 | Madanganj | 132 | 132 | 2025-10-01 01:00 | 123 | 2025-10-16 09:00
103 | Madaripur | 132 | 139 | 2025-10-01 06:00 | 126 | 2025-10-25 18:00
104 | Madartek | 132 | 139 | 2025-10-30 02:00 | 121 | 2025-10-09 10:00
105 | Madunaghat | 132 | 139 | 2025-10-12 18:00 | 129 | 2025-10-24 02:00
106 | Magura | 132 | 139 | 2025-10-30 06:00 | 120 | 2025-10-22 18:00
107 | Mahasthangarh | 132 | 137 | 2025-10-31 10:00 | 122 | 2025-10-21 18:30
108 | Maijdee | 132 | 136 | 2025-10-12 18:30 | 111 | 2025-10-01 12:00
109 | Manikganj | 132 | 134 | 2025-10-31 08:00 | 115 | 2025-10-22 19:00
110 | Maniknagar | 132 | 138 | 2025-10-01 04:00 | 123 | 2025-10-23 11:00
111 | Matarbari | 132 | 129 | 2025-10-12 18:00 | 106 | 2025-10-24 13:00
112 | Matuail | 132 | 132 | 2025-10-01 03:00 | 120 | 2025-10-20 12:00
113 | Metrorail_Motijheel | 132 | 137 | 2025-10-10 14:00 | 123 | 2025-10-23 11:00
114 | Metrorail_Uttara | 132 | 138 | 2025-10-31 10:00 | 117 | 2025-10-20 16:00
115 | Millgate | 132 | 139 | 2025-10-03 06:00 | 118 | 2025-10-20 16:00
116 | Mirpur | 132 | 137 | 2025-10-01 02:00 | 121 | 2025-10-20 12:00
117 | Mirzapur | 132 | 137 | 2025-10-05 18:00 | 121 | 2025-10-22 22:00
118 | Mithapukur | 132 | 138 | 2025-10-21 20:00 | 120 | 2025-10-20 13:00
119 | MI_Cement | 132 | 135 | 2025-10-12 06:00 | 119 | 2025-10-20 12:00
120 | Modern | 132 | N/A | N/A | N/A | N/A
121 | Mogbazar | 132 | 142 | 2025-10-28 06:00 | 122 | 2025-10-09 10:00
122 | Mongla | 132 | 137 | 2025-10-03 09:00 | 114 | 2025-10-22 18:30
123 | Motijheel | 132 | 137 | 2025-10-01 03:00 | 123 | 2025-10-20 16:00
124 | Muktagacha | 132 | 137 | 2025-10-09 21:00 | 114 | 2025-10-09 21:00
125 | Munshiganj | 132 | 132 | 2025-10-01 04:00 | 119 | 2025-10-20 12:00
126 | Muradnagar | 132 | 134 | 2025-10-01 03:00 | 116 | 2025-10-30 15:00
127 | Mymensingh | 132 | 139 | 2025-10-01 05:00 | 110 | 2025-10-09 21:00
128 | Naogaon | 132 | 135 | 2025-10-01 08:00 | 117 | 2025-10-10 22:00
129 | Narail | 132 | 139 | 2025-10-08 06:00 | 119 | 2025-10-22 18:00
130 | Narinda | 132 | 0 | 2025-10-22 02:00 | 0 | 2025-10-22 02:00
131 | Narshingdi | 132 | 137 | 2025-10-01 03:00 | 114 | 2025-10-18 19:00
132 | Natore | 132 | 136 | 2025-10-03 10:00 | 126 | 2025-10-09 23:00
133 | Nawabganj | 132 | 138 | 2025-10-01 06:00 | 122 | 2025-10-20 12:00
134 | Netrakona | 132 | 128 | 2025-10-11 04:00 | 106 | 2025-10-22 18:30
135 | New | 132 | 139 | 2025-10-03 06:00 | 118 | 2025-10-23 12:00
136 | Niamatpur | 132 | 142 | 2025-10-01 09:00 | 128 | 2025-10-25 18:00
137 | Noapara | 132 | 137 | 2025-10-03 09:00 | 115 | 2025-10-20 11:00
139 | Pabna | 132 | 138 | 2025-10-31 10:00 | 127 | 2025-10-09 23:00
140 | Palashbari | 132 | 135 | 2025-10-05 11:00 | 117 | 2025-10-21 18:30
141 | Panchagarh | 132 | 141 | 2025-10-01 18:00 | 115 | 2025-10-16 07:00
142 | Patiya | 132 | 138 | 2025-10-12 18:00 | 126 | 2025-10-22 12:00
143 | Patuakhali | 132 | 140 | 2025-10-06 18:30 | 130 | 2025-10-22 22:00
144 | Payra | 132 | 139 | 2025-10-01 06:00 | 133 | 2025-10-03 22:00
145 | PHP | 132 | 136 | 2025-10-12 18:30 | 123 | 2025-10-24 00:00
146 | Postogola | 132 | 136 | 2025-10-01 03:00 | 123 | 2025-10-20 12:00
147 | Purbachal | 132 | 140 | 2025-10-28 06:00 | 121 | 2025-10-09 10:00
148 | Purbasadipur | 132 | 137 | 2025-10-01 18:00 | 116 | 2025-10-23 14:00
149 | Rahanpur | 132 | 143 | 2025-10-01 08:00 | 130 | 2025-10-24 20:00
150 | Rahanpur-400 | 132 | 143 | 2025-10-01 07:00 | 131 | 2025-10-20 13:00
151 | Rahim | 132 | 132 | 2025-10-01 04:00 | 121 | 2025-10-16 12:00
152 | Rajbari | 132 | 139 | 2025-10-01 07:00 | 121 | 2025-10-19 20:00
153 | Rajendrapur | 132 | 141 | 2025-10-12 01:00 | 114 | 2025-10-20 09:00
154 | Rajshahi | 132 | 135 | 2025-10-01 07:00 | 126 | 2025-10-03 22:00
155 | Rajshahi-230 | 132 | 135 | 2025-10-14 06:00 | 125 | 2025-10-11 13:00
156 | Ramganj | 132 | 137 | 2025-10-01 02:00 | 112 | 2025-10-01 12:00
157 | Rampur | 132 | 137 | 2025-10-12 18:00 | 125 | 2025-10-25 14:00
158 | Rampura | 132 | 141 | 2025-10-30 03:00 | 121 | 2025-10-23 13:00
159 | Rangamati | 132 | 137 | 2025-10-12 18:00 | 130 | 2025-10-01 12:00
160 | Rangpur | 132 | 138 | 2025-10-30 14:00 | 118 | 2025-10-26 18:00
161 | Ruppur | 132 | 140 | 2025-10-31 09:00 | 130 | 2025-10-09 23:00
162 | Saidpur | 132 | 137 | 2025-10-01 18:00 | 116 | 2025-10-26 07:00
163 | Satkhira | 132 | 138 | 2025-10-03 11:00 | 117 | 2025-10-27 18:00
164 | Satmasjid | 132 | 140 | 2025-10-01 04:00 | 120 | 2025-10-20 13:00
165 | Savar | 132 | 138 | 2025-10-01 02:00 | 120 | 2025-10-18 11:00
166 | SevenRings | 132 | 141 | 2025-10-01 05:00 | 122 | 2025-10-20 09:00
167 | ShahCement | 132 | 133 | 2025-10-01 06:00 | 120 | 2025-10-20 11:00
168 | Shahjadpur | 132 | 139 | 2025-10-03 07:00 | 130 | 2025-10-24 19:30
169 | Shahjibazar | 132 | 137 | 2025-10-11 09:00 | 122 | 2025-10-22 19:00
170 | Shahmirpur | 132 | 139 | 2025-10-12 18:00 | 127 | 2025-10-25 13:00
171 | Shariatpur | 132 | 140 | 2025-10-01 07:00 | 124 | 2025-10-04 23:00
172 | Sherpur | 132 | 138 | 2025-10-05 09:00 | 108 | 2025-10-09 21:00
173 | Shikalbaha | 132 | 127 | 2025-10-15 19:00 | 118 | 2025-10-25 15:00
174 | Shikalbaha-230 | 132 | 140 | 2025-10-12 18:00 | 128 | 2025-10-24 06:00
175 | Shitalakhya | 132 | 135 | 2025-10-12 06:00 | 119 | 2025-10-20 12:00
176 | Sholosohor | 132 | 139 | 2025-10-12 17:00 | 129 | 2025-10-24 06:00
177 | Shyampur | 132 | 140 | 2025-10-01 06:00 | 125 | 2025-10-20 13:00
178 | Shyampur-230 | 132 | 139 | 2025-10-01 05:00 | 124 | 2025-10-20 16:00
179 | Siddhirganj | 132 | 136 | 2025-10-19 20:00 | 121 | 2025-10-20 12:00
180 | Sirajganj | 132 | 137 | 2025-10-31 10:00 | 123 | 2025-10-21 18:30
181 | Sonargaon | 132 | 137 | 2025-10-10 15:00 | 105 | 2025-10-30 15:00
182 | Sreemongol | 132 | 135 | 2025-10-01 05:00 | 123 | 2025-10-22 19:00
183 | Sreepur | 132 | 136 | 2025-10-03 15:00 | 121 | 2025-10-27 15:00
184 | Srinagar | 132 | 139 | 2025-10-01 06:00 | 122 | 2025-10-20 12:00
185 | SSM | 132 | 141 | 2025-10-12 18:30 | 126 | 2025-10-18 19:00
186 | Sunamganj | 132 | 129 | 2025-10-11 10:00 | 114 | 2025-10-10 22:00
187 | Sylhet | 132 | 132 | 2025-10-11 09:00 | 122 | 2025-10-10 22:00
188 | Sylhet-132 | 132 | 132 | 2025-10-11 08:00 | 124 | 2025-10-10 20:00
189 | Tangail | 132 | 137 | 2025-10-05 18:30 | 116 | 2025-10-18 18:00
190 | Taraganj | 132 | 137 | 2025-10-31 21:00 | 116 | 2025-10-21 18:30
191 | Thakurgaon | 132 | 141 | 2025-10-01 18:00 | 112 | 2025-10-22 07:00
192 | TK | 132 | 138 | 2025-10-12 18:00 | 130 | 2025-10-01 12:00
193 | Tongi | 132 | 140 | 2025-10-31 07:00 | 120 | 2025-10-16 17:00
194 | Ullahpara | 132 | 137 | 2025-10-01 07:00 | 125 | 2025-10-21 18:30
195 | Ullon | 132 | 140 | 2025-10-30 03:00 | 121 | 2025-10-20 09:00
196 | Uttara | 132 | 137 | 2025-10-01 02:00 | 120 | 2025-10-20 13:00
197 | UttaraNew | 132 | 138 | 2025-10-31 10:00 | 116 | 2025-10-23 12:00
198 | Zigatola | 132 | 139 | 2025-10-01 03:00 | 122 | 2025-10-20 12:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: October 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 28-10-2025 | 09:00 | 433 | 200 | 91.7227
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 28-10-2025 | 09:00 | 433 | 200 | 91.7227
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 28-10-2025 | 09:00 | 433 | 200 | 91.7227
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 07-10-2025 | 23:00 | 126 | 0 | 38.7692
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 30-10-2025 | 12:00 | 299 | 130 | 62.6997
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 30-10-2025 | 12:00 | 299 | 130 | 62.6997
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 05-10-2025 | 14:00 | 225 | 61 | 44.8312
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 30-10-2025 | 18:00 | 178 | 46 | 35.3553
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 22-10-2025 | 18:30 | 416 | 71 | 56.2687
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 22-10-2025 | 18:30 | 416 | 71 | 56.2687
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 22-10-2025 | 18:30 | 416 | 71 | 56.2687
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 2025-01-10 | 03:00 | 159 | 57 | 51.9718
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 2025-01-10 | 03:00 | 159 | 57 | 51.9718
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 2025-01-10 | 03:00 | 159 | 57 | 51.9718
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 27-10-2025 | 23:00 | 189 | 37 | 25.6784
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 27-10-2025 | 16:00 | 328 | 241 | 78.273
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 09-10-2025 | 10:00 | 293 | 188 | 66.9477
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 29-10-2025 | 06:00 | 298 | 42 | 92.5985
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 29-10-2025 | 06:00 | 298 | 42 | 92.5985
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 25-10-2025 | 15:00 | 394 | 157 | 56.5505
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 16-10-2025 | 00:00 | 394 | 113 | 54.6512
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 16-10-2025 | 00:00 | 394 | 113 | 54.6512
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 29-10-2025 | 22:00 | -459 | 117 | 63.1569
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 29-10-2025 | 22:00 | -459 | 117 | 63.1569
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 |  |  |  |  | 0
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 01-10-2025 | 02:00 | 361 | 53 | 70.1673
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 08-10-2025 | 23:00 | 395 | 40 | 76.35
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 04-10-2025 | 22:00 | 62 | 19 | 19.9526
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 04-10-2025 | 22:00 | 62 | 19 | 19.9526
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 03-10-2025 | 21:00 | 185 | 42 | 36.4822
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 09-10-2025 | 14:00 | 147 | 34 | 29.0155
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 23-10-2025 | 13:00 | 208 | 92 | 75.8126
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 23-10-2025 | 13:00 | 208 | 92 | 75.8126
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 04-10-2025 | 09:00 | 179 | 55 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 04-10-2025 | 09:00 | 179 | 55 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 04-10-2025 | 09:00 | 179 | 55 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 30-10-2025 | 21:00 | 195 | 125 | 77.2082
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 09-10-2025 | 19:30 | 242 | 18 | 80.8895
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 26-10-2025 | 21:00 | 135 | 46 | 47.5406
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 26-10-2025 | 21:00 | 103 | 35 | 48.3485
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 27-10-2025 | 17:00 | 192 | 20 | 85.795
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 20-10-2025 | 23:00 | 182 | 32 | 82.1297
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 27-10-2025 | 17:00 | 234 | 24 | 78.4092
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 22-10-2025 | 15:00 | 178 | 33 | 60.3444
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 19-10-2025 | 13:00 | 173 | 41 | 59.264
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 11-10-2025 | 19:00 | -120 | 34 | 55.4328
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 11-10-2025 | 19:00 | -120 | 34 | 55.4328
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 06-10-2025 | 20:00 | 153 | 21 | 68.6375
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 06-10-2025 | 20:00 | 153 | 21 | 68.6375
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 06-10-2025 | 20:00 | 205 | 34 | 69.2668
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 06-10-2025 | 20:00 | 205 | 34 | 69.2668
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 03-10-2025 | 23:00 | 161 | 50 | 74.9268
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 03-10-2025 | 23:00 | 158 | 49 | 73.5216
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 04-10-2025 | 05:00 | 158 | 46 | 73.1378
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 10-10-2025 | 21:00 | 185 | 82 | 67.4529
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 10-10-2025 | 20:00 | 229 | 106 | 84.1143
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 03-10-2025 | 08:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 20-10-2025 | 06:00 | 100 | 0 | 80
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 15-10-2025 | 14:00 | 133 | 89 | 71.125
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 16-10-2025 | 12:00 | 152 | 86 | 77.6189
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 16-10-2025 | 12:00 | 143 | 90 | 75.0953
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 26-10-2025 | 16:00 | 148 | 50 | 69.4301
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 26-10-2025 | 16:00 | 148 | 50 | 69.4301
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 21-10-2025 | 11:00 | 118 | 58 | 58.4373
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 11-10-2025 | 09:00 | 113 | 40 | 79.9138
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-10-2025 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 11-10-2025 | 09:00 | 113 | 40 | 79.9138
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 10-10-2025 | 13:00 | 92 | 32 | 64.9376
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 11-10-2025 | 19:00 | 98 | 63 | 51.7792
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 11-10-2025 | 19:00 | 98 | 63 | 51.7792
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 09-10-2025 | 23:00 | 93 | 57 | 48.4791
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 27-10-2025 | 18:30 | -223 | 55 | 76.5608
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 27-10-2025 | 18:30 | -223 | 55 | 76.5608
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 12-10-2025 | 04:00 | 198 | 38 | 67.2045
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 11-10-2025 | 09:00 | 230 | 68 | 79.9472
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 04-10-2025 | 10:00 | 213 | 60 | 73.7631
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-10-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 22-10-2025 | 22:00 | 143 | 51 | 67.4766
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 22-10-2025 | 22:00 | 143 | 51 | 67.4766
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 04-10-2025 | 21:00 | 184 | 72 | 65.8618
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 26-10-2025 | 15:00 | 116 | 12 | 38.873
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 26-10-2025 | 15:00 | 116 | 12 | 38.873
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 26-10-2025 | 15:00 | 116 | 12 | 38.873
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 27-10-2025 | 13:00 | 168 | 70 | 60.6667
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 27-10-2025 | 13:00 | 168 | 70 | 60.6667
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 01-10-2025 | 03:00 | -99 | 20 | 33.6667
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 01-10-2025 | 03:00 | -99 | 20 | 33.6667
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 25-10-2025 | 03:00 | 130 | 1 | 43.3346
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 02-10-2025 | 12:00 | 1 | 0 | 0.33333
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 19-10-2025 | 13:00 | 311 | 56 | 70.2226
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 19-10-2025 | 13:00 | 311 | 56 | 70.2226
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 19-10-2025 | 13:00 | 311 | 56 | 70.2226
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 03-10-2025 | 11:00 | 229 | 134 | 88.4414
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 03-10-2025 | 11:00 | 229 | 134 | 88.4414
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 21-10-2025 | 15:00 | 133 | 51 | 47.481
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 21-10-2025 | 15:00 | 133 | 51 | 47.481
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 15-10-2025 | 12:00 | 150 | 36 | 51.4198
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 15-10-2025 | 12:00 | 150 | 36 | 51.4198
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 31-10-2025 | 13:00 | 272 | 93 | 95.8199
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 31-10-2025 | 07:00 | 255 | 79 | 88.9856
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 09-10-2025 | 11:00 | 210 | 36 | 94.6948
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 09-10-2025 | 11:00 | 190 | 45 | 86.7806
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 09-10-2025 | 11:00 | 190 | 45 | 86.7806
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: October 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: October 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-10-01 | 14115.2 | 14115.2 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-01 | 11978.24 | 11978.24 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-02 | 12914 | 12914 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-02 | 11355.89 | 11355.89 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-03 | 12866.05 | 12866.05 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-03 | 10824.92 | 10824.92 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-04 | 14158 | 14158 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-04 | 12684.47 | 12684.47 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-05 | 13156.6 | 13156.6 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-05 | 12467.6 | 12467.6 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-06 | 14417.72 | 14417.72 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-06 | 12735.08 | 12735.08 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-07 | 14428.3 | 14471.15 | 41 | 19:00 Hr. | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-07 | 12797.72 | 12797.72 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-08 | 14734.51 | 14801.51 | 64 | 19:00 Hr. | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-08 | 12885.58 | 12885.58 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-09 | 14696.68 | 14770.96 | 62 | 19:30 Hr. | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-09 | 13044.79 | 13044.79 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-10 | 12934.24 | 12960.37 | 25 | 20:00 Hr. | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-10 | 11832.22 | 11832.22 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-10-11 | 14102.2 | 14151.2 | 47 | 19:00 Hr. | 17 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-11 | 11783.91 | 11783.91 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-12 | 14008.36 | 14351.12 | 328 | 19:30 Hr. | 10 | 0 | 55 | 60 | 0 | 105 | 15 | 43 | 40 | - | 2025-10-12 | 12916.52 | 12916.52 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-13 | 14150.94 | 14449.94 | 286 | 19:30 Hr. | 6 | 0 | 35 | 67 | 0 | 66 | 0 | 65 | 47 | - | 2025-10-13 | 13045.69 | 13045.69 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-14 | 13924.09 | 14272.08 | 333 | 19:00 Hr. | 65 | 15 | 40 | 55 | 20 | 45 | 0 | 55 | 38 | - | 2025-10-14 | 13179.19 | 13194.87 | 15 | 12:00 Hr. | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-15 | 13705.8 | 14269.56 | 450 | 21:00 Hr. | 78 | 22 | 52 | 58 | 40 | 55 | 25 | 68 | 52 | - | 2025-10-15 | 12935.63 | 13144.63 | 200 | 12:00 Hr. | 65 | 10 | 45 | 10 | 10 | 20 | 10 | 20 | 10 | -
2025-10-16 | 14319.66 | 14700.66 | 365 | 20:00 Hr | 70 | 0 | 60 | 100 | 20 | 70 | 10 | 25 | 10 | - | 2025-10-16 | 13301.11 | 13555.11 | 243 | 12:00 Hr. | 148 | 0 | 35 | 60 | 0 | 0 | 0 | 0 | 0 | -
2025-10-17 | 14149.86 | 14210.47 | 58 | 19:00 Hr. | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-17 | 12577.99 | 12577.99 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-18 | 15144.86 | 15250.41 | 101 | 21:00 Hr. | 15 | 0 | 0 | 40 | 0 | 15 | 0 | 0 | 31 | - | 2025-10-18 | 12312.76 | 12333.66 | 20 | 12:00 Hr. | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-19 | 14354.83 | 14950.48 | 570 | 19:30 Hr. | 120 | 30 | 50 | 85 | 40 | 65 | 20 | 85 | 75 | - | 2025-10-19 | 13439.16 | 13575.16 | 130 | 12:00 Hr. | 80 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | -
2025-10-20 | 14767.36 | 15020.36 | 242 | 20:00 Hr | 51 | 0 | 39 | 47 | 24 | 0 | 0 | 39 | 42 | - | 2025-10-20 | 13551.08 | 13853.09 | 289 | 12:00 Hr. | 149 | 10 | 30 | 70 | 30 | 0 | 0 | 0 | 0 | -
2025-10-21 | 15546.26 | 15681.07 | 129 | 19:00 Hr. | 20 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 10 | - | 2025-10-21 | 13404.96 | 13802.96 | 381 | 12:00 Hr. | 176 | 55 | 55 | 30 | 65 | 0 | 0 | 0 | 0 | -
2025-10-22 | 15637.26 | 15801.33 | 157 | 19:00 Hr. | 30 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-22 | 13591.45 | 13853.45 | 251 | 12:00 Hr. | 120 | 0 | 43 | 37 | 51 | 0 | 0 | 0 | 0 | -
2025-10-23 | 15421.7 | 15510.7 | 85 | 19:00 Hr. | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-23 | 13590.93 | 13855.32 | 253 | 12:00 Hr. | 130 | 0 | 33 | 41 | 49 | 0 | 0 | 0 | 0 | -
2025-10-24 | 13867.41 | 13867.41 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-24 | 12326.06 | 12326.06 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-25 | 15236.1 | 15331.1 | 91 | 19:00 Hr. | 9 | 0 | 0 | 49 | 0 | 33 | 0 | 0 | 0 | - | 2025-10-25 | 12643.1 | 12643.1 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-26 | 15575.96 | 15672.1 | 92 | 19:00 Hr. | 12 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-26 | 13866.67 | 13887.57 | 20 | 12:00 Hr. | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-27 | 15644.99 | 15730.68 | 82 | 19:00 Hr. | 12 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-27 | 13844.13 | 13844.13 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-28 | 15206.08 | 15550.12 | 110 | 21:00 Hr. | 0 | 10 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-28 | 13603.5 | 13814.5 | 202 | 12:00 Hr. | 192 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-29 | 14678.1 | 14678.1 | 51 | 19:00 Hr. | 0 | 15 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-29 | 13693.74 | 13822.74 | 123 | 12:00 Hr. | 100 | 10 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | -
2025-10-30 | 14577.7 | 14577.7 | 32 | 18:00 Hr. | 5 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | - | 2025-10-30 | 12616.13 | 12703.13 | 83 | 12:00 Hr. | 60 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-10-31 | 13501 | 13501 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-10-31 | 11627.44 | 11673.42 | 44 | 12:00 Hr. | 15 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: October 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15644.99 | 2025-10-27 | 19:00 Hr.
2 | Maximum Day Peak Genaration | MW | 13866.67 | 2025-10-26 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 15801.33 | 2025-10-22 | 19:00 Hr.
4 | Minimum Generation | MW | 9833.03 | 2025-10-03 | 09:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 14385.22 | - | -
6 | Average of the daily day peak Genaration | MW | 12788.9568 | - | -
7 | Maximum load shed (Evening Peak) | MW | 570 | 2025-10-19 | 19:30 Hr.
8 | Minimum load shed | MW | 0 | 2025-10-01 | 19:00 Hr.
9 | Total nos. of load shed days | Day | 23 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 126.7 | - | -
11 | Total Generation | MkWh | 9668.7856 | - | -
12 | Total Generation by BPDB | MkWh | 1137.6177 | % of total Gen. | 11.77%
13 | Total Generation by IPP | MkWh | 2815.9484 | '' | 29.12%
14 | A) Total Generation by Generation Companies | MkWh | 3978.1653 | '' | 41.14%
| B) Total Generation by REB | MkWh | 46.923 | " | 0.4853%
| C) Total Generation by RENTAL | MkWh | 113.3794 | " | 1.173%
| D) Total Imported from India (BIPTC) | MkWh | 664.6633 | " | 6.874%
| E) Total Imported from Tripura, India (A.C) | MkWh | 48.072 | " | 0.4972%
| F) Total Imported from Nepal | MkWh | 28.272 | " | 0.2924%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 835.7446 | " | 8.644%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3762.6905 | % of total Gen. | 38.92%
| B) Oil | MkWh | 1037.4084 | '' | 10.73%
| C) Hydro | MkWh | 161.6253 | '' | 1.672%
| D) Solar | MkWh | 120.6303 | '' | 1.248%
| E) Coal | MkWh | 3006.767 | '' | 31.1%
| F) BIPTC (Import from India) | MkWh | 664.6633 | '' | 6.874%
| G) A.C (Import from Tripura, India) | MkWh | 48.072 | '' | 0.4972%
| H) Total Imported from Nepal | MkWh | 28.272 | '' | 0.2924%
| I) Adani (Import from India) | MkWh | 835.7446 | '' | 8.644%
| J) Wind | MkWh | 2.9122 | '' | 0.03012%
16 | Maximun of the daily total Generation . | MkWh | 334.6178 | 2025-10-26
17 | Monthly Load factor | % | 83.0661 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 61878.2641 | - | -
| A) Gas | M.Taka | 13472.5643 | - | -
| B) Coal | M.Taka | 18184.0305 | - | -
| C) HFO | M.Taka | 18972.5989 | - | -
| D) HSD | M.Taka | 0.26658 | - | -
| E) Hydro | M.Taka | 16.1625 | - | -
| F) Solar | M.Taka | 1874.8867 | - | -
| G) Total Import | M.Taka | 9314.8362 | - | -
| H) Wind | M.Taka | 42.9184 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2282.164 | 2025-10-16
| A) Gas | M.Taka | 507.168 | 2025-10-04
| B) Coal | M.Taka | 696.864 | 2025-10-22
| C) HFO | M.Taka | 987.1661 | 2025-10-13
| D) HSD | M.Taka | 0.26658 | 2025-10-30 | -
| E) Hydro | M.Taka | 0.5362 | 2025-10-20 | -
| F) Solar | M.Taka | 82.5621 | 2025-10-21 | -
| G) Total Import | M.Taka | 361.4449 | 2025-10-20
| H) Wind | M.Taka | 12.4453 | 2025-10-02
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.2251
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.4143
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 108.9 | 31/10/2025 | 06:00
b) | Actual | FT (MSL) | 103.18 | 31/10/2025 | 06:00
22 | Peak Genaration of October 2024 | MW | 14677 | 2024-10-01 | 20:00
23 | Peak Demand of October 2024 | MW | 15200 | 2024-10-30 | 20:00
24 | Maximum peak Generation recorded upto 31/10/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/10/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/10/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [36 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [11 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [12 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable |  |  | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [43 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [12 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | [18 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [36 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [33 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [10 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [15 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | [21 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [41 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [10 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 |  | 24 |  |  |  |  | 50 | 24 | 24 | 50
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [25 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: October 2025
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 |  |  |  | √ | √ | √ | [5 empty] | √
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | [5 empty] | √ |  | √ | [9 empty] | √ | √
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 |  |  |  |  | √ | √ | [6 empty] | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | √ | √ | √ | √ | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | √ | √ | √ | √ | √ | √ | √ | √
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54 | [12 empty] | √ | √
53 | Anlima Energy Ltd | IPP | HFO | 116 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | [5 empty] | √ | √ | √ |  | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | [5 empty] | √ |  | √ |  |  | √ |  | √ |  |  |  |  | √ | √ | [8 empty] | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | [27 empty] | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | [5 empty] | √ | √ | √ |  |  | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | [26 empty] | √ | √ | √
| Meghnaghat CCPP(Summit)-2 | IPP |  | 583 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | [5 empty] | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622