## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-11-2025 | during | 22-11-2025 | during | 22-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 97.7 | 97.7 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 305 | 338 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 270 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.5 | 53.97 | 53.97 | 53.97 | 53.97
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 30 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 2 | 55 | 55 | 17 | 17 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 13 | 33 | 33 | 33 | 33
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 0 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 88 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 47 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 65 | 162 | 162 | 35 | 108 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 230 | 280 | 718 | 718 | 350 | 350 | FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 816 | 1347.5 | 5220.4 | 5189.4 | 4379.21 | 4421.21
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 16 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 142 | 142 | 140 | 140 | 140 | 140 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 73 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 56 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 28 | 32 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.26 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 531 | 612 | 612 | 582 | 582 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 0 | 4 | 4 | 4 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 290 | 195 | 350 | 350 | 190 | 350 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1148.26 | 1130 | 2556 | 2565.72 | 1817.78 | 1977.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 205 | 200 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 30 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 10 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 60 | 150 | 150 | 125 | 125 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 58 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 80 | 160 | 160 | 106 | 106 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 6 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 47 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 685 | 937 | 2170.4 | 2100.4 | 1895.4 | 1825.4
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-11-2025 | during | 22-11-2025 | during | 22-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 54 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 27.36 | 0 | 45.95 | 0 | 45.95 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 82.36 | 132 | 361.65 | 314 | 302.15 | 254.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 146 | 149 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 27 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 157 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 25 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 341 | 389 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1031 | 897 | 1237 | 1237 | 1159 | 1159
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 696 | 873 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 67 | 164 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 48 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 988 | 975 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1799 | 2012 | 2398 | 2318 | 1637.1 | 1557.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 307 | 435 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 880 | 855 | 992 | 992 | 982 | 982 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.33 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1397.33 | 1515 | 1593 | 1592 | 1450 | 1449
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 35.51 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 135 | 178 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 250 | 344 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.25 | 0 | 5.69 | 0 | 5.69 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 915.06 | 1218 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 38.88 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 62 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1439.7 | 1740 | 3081.56 | 2914.87 | 3008.18 | 2841.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 55 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 105 | 0 | 165.69 | 0 | 165.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 182.2 | 195 | 497.89 | 297 | 483.89 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 8580.85 | 9905.5 | 19115.9 | 18528.39 | 16132.71 | 15768.2
Forecast Scenario (22-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8950 |  | 0 |  | 8950
|  |  |  | 1:00 | 8480 |  | 0 |  | 8480
|  |  |  | 2:00 | 8070 |  | 0 |  | 8070
|  |  |  | 3:00 | 7770 |  | 0 |  | 7770
|  |  |  | 4:00 | 7590 |  | 0 |  | 7590
|  |  |  | 5:00 | 7450 |  | 0 |  | 7450
|  |  |  | 6:00 | 7710 |  | 0 |  | 7710
|  |  |  | 7:00 | 8580 |  | 0 |  | 8580
|  |  |  | 8:00 | 8910 |  | 0 |  | 8910
|  |  |  | 9:00 | 8600 |  | 0 |  | 8600
|  |  |  | 10:00 | 8480 |  | 0 |  | 8480
|  |  |  | 11:00 | 8900 |  | 0 |  | 8900
|  |  |  | 12:00 | 9520 |  | 0 |  | 9520
|  |  |  | 13:00 | 9940 |  | 0 |  | 9940
|  |  |  | 14:00 | 9700 |  | 0 |  | 9700
|  |  |  | 15:00 | 9560 |  | 0 |  | 9560
|  |  |  | 16:00 | 9370 |  | 0 |  | 9370
|  |  |  | 17:00 | 10050 |  | 0 |  | 10050
|  |  |  | 18:00 | 11270 |  | 0 |  | 11270
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11440 |  | 0 |  | 11440
|  |  |  | 19:30 | 11090 |  | 0 |  | 11090
|  |  |  | 20:00 | 11090 |  | 0 |  | 11090
|  |  |  | 21:00 | 10780 |  | 0 |  | 10780
|  |  |  | 22:00 | 10500 |  | 0 |  | 10500
|  |  |  | 23:00 | 10010 |  | 0 |  | 10010
Probable Maximum Temperature: |  |  | 29.00°C
Probable Maximum Demand at Day Peak: |  |  | 9520.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11440.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11440.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 222.72 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:08 hrs on 22-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-11-2025 | [28 empty] | Date: | 21-11-2025 | [28 empty] | Date: | 21-11-2025 | [28 empty] | Date: | 21-11-2025 | [28 empty] | Date: | 21-11-2025 | [14 empty] | Date: | 21-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [14 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 220 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 12 | 0 | 86 | 0 | 37 | 515 | 0 | 0 | 0 | 0 | 65 | 136 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 8 | 350 | 0 | 0 | 10 | 225 | 20 | 0 | 0 | 82 | 0 | 20 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 396 | 0 | 30 | 161 | 0 | 0 | 27 | 30 | 0 | 0 | 158 | 0 | 59 | 19 | 8 | 0 | 0 | 0 | 4383 | 916 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 0 | 1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 453 | 970 | 0 | 5512 | 9895 | 100.45
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 37 | 360 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 504 | 0 | 51 | 0 | 8 | 350 | 0 | 0 | 10 | 226 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 88 | 0 | 0 | 0 | 305 | 0 | 366 | 0 | 30 | 152 | 0 | 0 | 27 | 30 | 0 | 0 | 158 | 0 | 35 | 0 | 7 | 0 | 0 | 0 | 3884 | 916 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.53 | 1100 | 0 | 1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 455 | 920 | 0 | 5461.53 | 9345.53 | 100.44
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 340 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 8 | 350 | 0 | 0 | 10 | 225 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 364 | 0 | 30 | 148 | 0 | 0 | 7 | 20 | 0 | 0 | 158 | 0 | 16 | 0 | 7 | 0 | 0 | 0 | 3778 | 916 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 401 | 855 | 0 | 5144 | 8922 | 100.44
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 335 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 503 | 0 | 51 | 0 | 8 | 380 | 0 | 0 | 10 | 226 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 366 | 0 | 30 | 153 | 0 | 0 | 7 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3787 | 877 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 353 | 850 | 0 | 4907 | 8694 | 100.43
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 335 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 485 | 0 | 51 | 0 | 8 | 390 | 0 | 0 | 10 | 226 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 74 | 0 | 0 | 0 | 315 | 0 | 338 | 0 | 30 | 151 | 0 | 0 | 7 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 3739 | 718 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 353 | 850 | 0 | 4665 | 8404 | 100.43
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 335 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 8 | 390 | 0 | 0 | 10 | 225 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 78 | 0 | 0 | 0 | 305 | 0 | 351 | 0 | 30 | 152 | 0 | 0 | 8 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 3770.5 | 666 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 303 | 850 | 0 | 4521 | 8291.5 | 100.42
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 25 | 338 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 8 | 393 | 0 | 0 | 10 | 203 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 352 | 0 | 30 | 154 | 0 | 0 | 26 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 3888.5 | 636 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 303 | 850 | 0 | 4482 | 8370.5 | 100.42
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 3 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 30 | 338 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 580 | 4 | 51 | 0 | 8 | 395 | 0 | 0 | 10 | 217 | 20 | 0 | 0 | 0 | 0 | 19 | 0 | 68 | 0 | 8 | 0 | 310 | 0 | 372 | 0 | 30 | 154 | 0 | 0 | 27 | 30 | 0 | 0 | 158 | 0 | 0 | 2 | 11 | 0 | 3.91 | 0 | 3954.91 | 634 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 983 | 0 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.68 | 6 | 0 | 0 | 2.24 | 135 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0.18 | 0 | 56 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8 | 0.04 | 0 | 0 | 115 | 110 | 0 | 312 | 850 | 0 | 4547.14 | 8502.05 | 100.41
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 10 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 30 | 340 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 580 | 11 | 51 | 0 | 8 | 393 | 0 | 0 | 10 | 196 | 20 | 0 | 0 | 0 | 0 | 17 | 0 | 66 | 0 | 30 | 0 | 305 | 0 | 343 | 0 | 30 | 157 | 0 | 0 | 27 | 30 | 0 | 0 | 158 | 0 | 57 | 19 | 11 | 1 | 12.79 | 0 | 4015.79 | 674 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 1039 | 0 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.83 | 34 | 0 | 0 | 15.11 | 137 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 1.92 | 0 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 1.7 | 62 | 0.11 | 0 | 0 | 115 | 110 | 0 | 404 | 900 | 0 | 4920.67 | 8936.46 | 100.41
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 19 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2.26 | 86 | 0 | 28 | 290 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 580 | 15 | 10 | 0 | 8 | 300 | 0 | 0 | 10 | 205 | 20 | 0 | 0 | 0 | 0 | 17 | 0 | 68 | 0 | 47 | 0 | 300 | 0 | 341 | 0 | 30 | 146 | 0 | 0 | 27 | 30 | 0 | 0 | 157 | 0 | 24 | 19 | 11 | 1 | 27.36 | 0 | 3762.62 | 696 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 988 | 0 | 915.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.51 | 62 | 0 | 0 | 38.88 | 135 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 3.25 | 0 | 55 | 0 | 19 | 0 | 0 | 0 | 0 | 3.2 | 105 | 0.33 | 0 | 0 | 100 | 110 | 0 | 307 | 880 | 0 | 4818.23 | 8580.85 | 100.4
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 25 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 2.88 | 86 | 0 | 28 | 212 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 582 | 18 | 10 | 0 | 8 | 300 | 0 | 0 | 10 | 197 | 20 | 0 | 0 | 0 | 0 | 17 | 0 | 70 | 0 | 59 | 0 | 310 | 0 | 341 | 0 | 30 | 147 | 0 | 0 | 27 | 30 | 0 | 0 | 158 | 0 | 24 | 19 | 11 | 2 | 37.65 | 0 | 3727.53 | 683 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.01 | 892 | 0 | 829.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.24 | 84 | 0 | 0 | 50.59 | 135 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 4.39 | 0 | 55 | 0 | 28 | 0 | 0 | 0 | 0 | 4.8 | 143 | 0.46 | 0 | 0 | 100 | 110 | 0 | 306 | 800 | 0 | 4656.3 | 8383.83 | 100.4
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 3.19 | 86 | 0 | 26 | 222 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 8 | 350 | 0 | 0 | 7 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 64 | 0 | 0 | 0 | 94 | 0 | 30 | 152 | 0 | 0 | 27 | 30 | 0 | 0 | 160 | 0 | 24 | 19 | 17 | 2 | 42.18 | 0 | 2572.37 | 745 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.88 | 875 | 0 | 817.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.42 | 96 | 0 | 0 | 56.25 | 118 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 5.07 | 0 | 55 | 0 | 32 | 0 | 0 | 0 | 0 | 5.5 | 164 | 0.4 | 0 | 0 | 95 | 110 | 0 | 303 | 800 | 0 | 4811.64 | 7384.01 | 100.39
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 348 | 2 | 0 | 0 | 33 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 40 | 13 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 12 | 3.17 | 86 | 2 | 18 | 196 | 25 | 0 | 0 | 0 | 14 | 142 | 0 | 0 | 0 | 0 | 20 | 20 | 5 | 8 | 393 | 0 | 0 | 0 | 92 | 24 | 7 | 0 | 44 | 0 | 5 | 4 | 90 | 0 | 62 | 0 | 0 | 0 | 114 | 0 | 30 | 160 | 0 | 0 | 70 | 30 | 0 | 0 | 158 | 0 | 56 | 19 | 18 | 2 | 16.21 | 0 | 3135.38 | 916 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.02 | 958 | 0 | 942.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.89 | 98 | 0 | 0 | 36.98 | 91 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.78 | 0 | 55 | 0 | 34 | 0 | 0 | 0 | 0 | 5.4 | 140 | 0.42 | 0 | 0 | 115 | 110 | 0 | 307 | 860 | 0 | 5286.33 | 8421.71 | 100.39
13:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 314 | 17.5 | 0 | 35 | 45 | 95 | 6 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 27 | 52 | 13 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 12 | 12 | 2.88 | 86 | 31 | 0 | 185 | 68 | 0 | 0 | 0 | 99 | 142 | 0 | 0 | 0 | 315 | 18 | 51 | 75 | 8 | 393 | 0 | 0 | 16 | 107 | 37 | 33 | 0 | 118 | 0 | 11 | 46 | 90 | 25 | 58 | 20 | 0 | 0 | 218 | 0 | 30 | 159 | 0 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 56 | 19 | 20 | 2 | 32.02 | 0 | 4339.4 | 916 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.42 | 1043 | 0 | 1116.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.62 | 93 | 0 | 0 | 53.33 | 84 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 4.25 | 0 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 5.5 | 145 | 0.52 | 0 | 0 | 115 | 110 | 0 | 384 | 890 | 0 | 5592.63 | 9932.03 | 100.38
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 224 | 17.5 | 0 | 51 | 0 | 0 | 15 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 19 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 12 | 2.33 | 86 | 0 | 38 | 190 | 0 | 0 | 0 | 0 | 17 | 142 | 0 | 0 | 0 | 395 | 16 | 51 | 30 | 8 | 340 | 0 | 0 | 30 | 150 | 37 | 0 | 0 | 17 | 11 | 11 | 0 | 76 | 0 | 46 | 0 | 0 | 0 | 314 | 0 | 30 | 143 | 0 | 0 | 52 | 30 | 0 | 17 | 159 | 0 | 59 | 19 | 22 | 1 | 36.04 | 0 | 3659.87 | 915 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.53 | 948 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.77 | 80 | 0 | 0 | 42.8 | 65 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 3.11 | 0 | 54 | 0 | 23 | 0 | 0 | 0 | 0 | 4.5 | 123 | 0.41 | 0 | 0 | 120 | 110 | 0 | 305 | 840 | 0 | 5175.12 | 8834.99 | 100.38
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 219 | 15.1 | 0 | 59 | 0 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 14 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 12 | 1.48 | 86 | 0 | 30 | 195 | 0 | 0 | 0 | 0 | 15 | 142 | 0 | 0 | 0 | 427 | 11 | 51 | 0 | 8 | 300 | 0 | 0 | 30 | 111 | 37 | 0 | 0 | 16 | 11 | 11 | 0 | 72 | 0 | 32 | 0 | 0 | 0 | 310 | 0 | 30 | 143 | 16 | 0 | 52 | 30 | 0 | 17 | 157 | 0 | 59 | 19 | 24 | 1 | 21.05 | 0 | 3483.63 | 794 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.8 | 852 | 0 | 964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.64 | 53 | 0 | 0 | 29.03 | 84 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 2.27 | 0 | 54 | 0 | 11 | 0 | 0 | 0 | 0 | 2.5 | 81 | 0.27 | 0 | 0 | 120 | 110 | 0 | 306 | 820 | 0 | 4791.51 | 8275.14 | 100.37
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 240 | 17.5 | 0 | 78 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0.62 | 86 | 0 | 28 | 195 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 420 | 5 | 51 | 0 | 8 | 300 | 0 | 0 | 30 | 121 | 37 | 0 | 0 | 0 | 0 | 13 | 0 | 70 | 0 | 14 | 0 | 0 | 0 | 325 | 0 | 30 | 142 | 16 | 0 | 52 | 30 | 0 | 17 | 157 | 0 | 59 | 19 | 24 | 0 | 7.16 | 0 | 3426.28 | 794 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.21 | 796 | 0 | 939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.78 | 22 | 0 | 0 | 8.92 | 162 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0.79 | 0 | 55 | 0 | 7 | 0 | 0 | 0 | 0 | 1.1 | 27 | 0.11 | 0 | 0 | 115 | 110 | 0 | 306 | 790 | 0 | 4642.91 | 8069.19 | 100.37
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 234 | 17.5 | 0 | 78 | 6 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 86 | 0 | 30 | 195 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 482 | 0 | 51 | 0 | 8 | 300 | 0 | 0 | 30 | 203 | 38 | 0 | 0 | 0 | 0 | 13 | 0 | 70 | 0 | 1 | 0 | 0 | 0 | 337 | 0 | 30 | 152 | 16 | 0 | 55 | 30 | 0 | 17 | 157 | 0 | 59 | 19 | 30 | 0 | 0.2 | 0 | 3650.7 | 779 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | 850 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0 | 0 | 0 | 0.52 | 179 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0.05 | 0 | 55 | 30 | 0 | 8 | 0 | 0 | 0 | 0.1 | 2 | 0.01 | 0 | 0 | 115 | 110 | 0 | 356 | 810 | 0 | 4835.27 | 8485.97 | 100.36
18:00 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 280 | 17.5 | 0 | 88 | 30 | 145 | 0 | 2 | 65 | 0 | 0 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 0 | 35 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 38 | 0 | 86 | 0 | 32 | 195 | 0 | 0 | 16 | 0 | 73 | 142 | 0 | 0 | 0 | 531 | 0 | 51 | 60 | 8 | 393 | 0 | 0 | 30 | 200 | 38 | 6 | 0 | 58 | 0 | 13 | 0 | 80 | 0 | 0 | 0 | 25 | 0 | 389 | 0 | 30 | 149 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 54 | 0 | 0 | 0 | 4443.5 | 873 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 0 | 1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 55 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 435 | 855 | 0 | 5462 | 9905.5 | 100.36
19:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 336 | 17.5 | 0 | 67 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 86 | 0 | 38 | 195 | 0 | 0 | 0 | 0 | 17 | 224 | 0 | 0 | 0 | 531 | 0 | 51 | 18 | 8 | 393 | 0 | 0 | 30 | 206 | 38 | 0 | 0 | 51 | 0 | 20 | 0 | 74 | 0 | 0 | 0 | 25 | 0 | 394 | 0 | 30 | 151 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 54 | 0 | 0 | 0 | 4250.5 | 874 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 0 | 1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 437 | 912 | 0 | 5520 | 9770.5 | 100.35
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 325 | 0 | 0 | 67 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 86 | 0 | 38 | 195 | 0 | 0 | 0 | 0 | 15 | 223 | 0 | 0 | 0 | 530 | 0 | 51 | 0 | 8 | 393 | 0 | 0 | 30 | 199 | 38 | 0 | 0 | 47 | 0 | 20 | 0 | 72 | 0 | 0 | 0 | 45 | 0 | 394 | 0 | 30 | 157 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 64 | 0 | 0 | 0 | 4189 | 874 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 435 | 915 | 0 | 5535 | 9724
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 337 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 38 | 195 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 535 | 0 | 51 | 0 | 8 | 393 | 0 | 0 | 30 | 207 | 38 | 0 | 0 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 80 | 0 | 394 | 0 | 30 | 159 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 64 | 0 | 0 | 0 | 4098 | 874 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 0 | 1224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 35 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 436 | 920 | 0 | 5585 | 9683 | 100.35
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 38 | 195 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 531 | 0 | 51 | 0 | 35 | 393 | 0 | 0 | 32 | 163 | 38 | 0 | 0 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 215 | 0 | 387 | 0 | 30 | 160 | 21 | 0 | 82 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 83 | 0 | 0 | 0 | 4188 | 874 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 0 | 1226.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 320 | 920 | 0 | 5470.95 | 9658.95 | 100.34
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 201 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 570 | 0 | 51 | 0 | 35 | 393 | 0 | 0 | 39 | 195 | 35 | 0 | 0 | 0 | 0 | 20 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 363 | 0 | 30 | 157 | 21 | 0 | 82 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 86 | 0 | 0 | 0 | 4322 | 874 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032 | 0 | 1173.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 304 | 910 | 0 | 5314.07 | 9636.07 | 100.34
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 204 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 505 | 0 | 51 | 0 | 35 | 393 | 0 | 0 | 43 | 180 | 35 | 0 | 0 | 0 | 0 | 20 | 0 | 80 | 0 | 0 | 0 | 295 | 0 | 374 | 0 | 30 | 149 | 17 | 0 | 82 | 30 | 0 | 15 | 158 | 0 | 16 | 8 | 102 | 0 | 0 | 0 | 4170.5 | 874 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934 | 0 | 1063.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 304 | 900 | 0 | 5083.97 | 9254.47 | 100.33
Total KWH | 0 | 178560 | 17760 | 0 | 0 | 0 | 0 | 0 | 8460000 | 0 | 6485660 | 135000 | 0 | 566064 | 157440 | 295320 | 82989 | 15763 | 266400 | 0 | 0 | 0 | 0 | 0 | 37346 | 6945376 | 0 | 0 | 134650 | 109200 | 285000 | 178560 | 0 | 0 | 46418 | 0 | 0 | 0 | 284160 | 22402 | 0 | 0 | 21120 | 151680 | 20188 | 2071200 | 61100 | 657120 | 6218181.82 | 65236 | 0 | 63360 | 0 | 405636 | 3869186 | 0 | 0 | 0 | 11361817 | 139050 | 1139128 | 254254 | 301091 | 8841000 | 0 | 0 | 498240 | 4512000 | 666648 | 76800 | 0 | 487680 | 43680 | 379070 | 58140 | 1831680 | 26909 | 422782 | 19888 | 4548130 | 0 | 7991000 | 0 | 726360 | 3654491 | 323208 | 0 | 1072320 | 662592 | 0 | 301000 | 3315750 | 16560 | 915600 | 304800 | 671040 | 12300 | 251910 | 0 | 94134993.82 | 19737454 | 2863584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483120 | 23345460 | 0 | 23037182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330632 | 639613 | 0 | 0 | 335264 | 3410273 | 0 | 0 | 0 | 0 | 0 | 8569381 | 0 | 28080 | 0 | 1284654 | 172191 | 195670 | 145017 | 0 | 0 | 0 | 35984.16 | 1000800 | 3139 | 0 | 0 | 2717000 | 2677320 | 0 | 8389116 | 21429818.18 | 6000 | 120836752.34 | 214971746.16

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 8580.85 | MW | 09:00 Hr. | Energy Generated |  |  | 214.9717 |  | MKWHr.
| Day Peak Demand |  |  | 8580.85 | MW | 09:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9905.5 | MW | 18:00 Hr. | Energy Demand |  |  | 214.9717 |  | MKWHr.
| Evening Peak Demand |  |  | 9905.5 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29 |  | °C
| Minimum Generation of the Day |  |  | 7384.01 | MW | 11:00 Hr. | Total Gas Supplied |  |  | 681.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 9932.03 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.564 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 22.3546 | 0 | 1.8618 | 0 | 0 | 0.13465 | 0 | 0 | 24.3511 | Gas | 86.7215 | Gas | 309142141.37
| Chattogram Zone |  |  | 4.5263 | 17.58 | 0.83695 | 0 | 2.0712 | 0.15924 | 0 | 0.28416 | 25.4579 | Coal | 72.029 | Coal | 464826178.5568
| Cumilla Zone |  |  | 16.3372 | 0 | 0.96735 | 0 | 0 | 0.42278 | 1.8317 | 0 | 19.559 | HFO | 5.2263 | HFO | 89739371.9
| Mymensingh Zone |  |  | 0.67104 | 0 | 1.237 | 0 | 0 | 0.26421 | 0 | 0 | 2.1722 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 22.5949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5949 | Hydro | 2.0712 | Hydro | 207120
| Khulna Zone |  |  | 2.8636 | 23.3455 | 0 | 0 | 0 | 0.48312 | 19.7375 | 0 | 46.4296 | Solar | 4.0332 | Solar | 64456413.7936
| Barishal Zone |  |  | 5.3943 | 29.8189 | 0.006 | 0 | 0 | 0.003139 | 0 | 0 | 35.2224 | Import | 44.6063 | Import | 263549790.32
| Rajshahi Zone |  |  | 11.9797 | 0 | 0 | 0 | 0 | 1.3336 | 23.0372 | 0 | 36.3504 | Wind | 0.28416 | Wind | 4179993.6
| Rangpur Zone |  |  | 0 | 1.2847 | 0.31721 | 0 | 0 | 1.2325 | 0 | 0 | 2.8343
| Total |  |  | 86.7215 | 72.029 | 5.2263 | 0 | 2.0712 | 4.0332 | 44.6063 | 0.28416 | 214.9717
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 309142141.37 |  | Hydro | 207120
|  |  |  | Coal | 464826178.5568 |  | Solar | 64456413.7936
|  |  |  | HFO | 89739371.9 |  | Import | 263549790.32
|  |  |  | HSD | 0 |  | Wind | 4179993.6
[5 empty] | Total: | 119,61,01,009 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.7375 | Peak Hr Flow | 873.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52175981.85 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.0372 | Peak Hr Flow | 1218.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2374 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.8317 | Peak Hr Flow | 80.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2866 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.6063 | Peak Hr Flow | 2171.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3377
|  |  |  | Chattogram |  | 0 |  | 1163
|  |  |  | Cumilla |  | 0 |  | 899
|  |  |  | Mymensingh |  | 0 |  | 773
|  |  |  | Sylhet |  | 0 |  | 392
|  |  |  | Khulna |  | 0 |  | 1118
|  |  |  | Barishal |  | 0 |  | 276
|  |  |  | Rajshahi |  | 0 |  | 891
|  |  |  | Rangpur |  | 0 |  | 670
|  |  |  | Total |  | 0 |  | 9559
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:06 | 09:44 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to keranihat 33 kv | [7 empty] | 35.0MW load
|  |  | feeder isolator maintenance | [7 empty] | interrup.
| 08:06 | 09:44 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to keranihat 33 kv | [7 empty] | 35.0MW load
|  |  | feeder isolator maintenance | [7 empty] | interrup.
| 08:20 | 12:27 | Goalpara 132/33kV S/S T1 LT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 08:20 | 12:32 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 08:21 | 11:11 | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shahmirpur 132/33kV end Due to For
replacing the spring auxiliary contact of the Sikalbaha ckt-01 C.B.-102B
| 08:24 | 11:44 | Tongi 230/132/33kV S/S T-01 LT Scheduled S/D Due to Oil refill work
| 08:24 | 12:24 | Goalpara 132/33kV S/S T1 HT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 08:24 | 12:25 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 08:25 | 11:44 | Tongi 230/132/33kV S/S T-01 HT Scheduled S/D Due to Oil refill Work
| 08:29 | 12:18 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to None | [7 empty] | 2.0MW load
interrup.
| 08:30 | 12:17 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D | [7 empty] | 2.0MW load
interrup.
| 08:36 | 17:20 | Meghnaghat 400/230kV S/S 230kV BUS Section 02 Scheduled S/D Due to 230 kV Bus Section- 2
shutdown instructed by NLDC
| 09:05 | 17:22 | Meghnaghat 230/132kV S/S Bus2 Project Work S/D Due to project work
| 09:30 | 15:28 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to
Maintenance Work and from Bog-Sherpur 132/33kV end Due to LA Change
| 10:17 | 17:05 | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Rampura 230/132kV end Due to Shutdown
taken by Bhalta Grid.Command by NLDC. and from Bhulta 400/230kV end Due to For installing
OPGW.
| 10:20 | 12:43 | Lakshmipur 132/33kV S/S Lakshmipur-Chowmuhani Circuit 1 Project Work S/D Due to
Development work by project
| 10:20 |  | Barapukuria-Rangpur 132 kV Ckt-1 Project Work S/D from Barapukuria 230/132/33kV end Due
to reconductoring work and from Rangpur 132/33kV end Due to Re conducting
| 10:25 |  | Barapukuria PS 230 KV Main Bus -1 S/D [D/W: To Dismantle Existing Aux Tr Bus & XLPE
Cable Installation]
| 10:38 |  | SS Power Tripped
| 10:38 |  | Bashkhali SS Power Unit-2 tripped at 10:38 hrs.
| 10:38 |  | Ashuganj TSK power plant tripped at 10:38 hrs, and was synchronized at 11:40 hrs.
| 10:38 |  | Bibiyana-3 400 MW CCPP GT was out of sync, at 10:38 hrs and resynchronized at 10:48 hrs.
Also, ST was tripped at 10:38 hrs and was synchronized at 12:30 hrs.
| 10:38 |  | Bhulta-Ghorasal 230 kV Ckt-1 Tripped from Bhulta 400/230kV end showing REL670 relays Due | [7 empty] | 26.31MW load
|  |  | to None | [7 empty] | interrup. Bhulta
400/230kV end
| 10:38 | 11:41 | Bhulta-Haripur 230 kV Ckt-1 Tripped from Haripur 230/132kV end showing N/A relays Due to
Earthquake.
| 10:38 | 12:20 | Haripur 230/132kV S/S Auto TR-1 LT Tripped showing N/A relays Due to Earthquake.
| 10:38 | 11:41 | Haripur 230/132kV S/S Auto TR-1 HT Tripped showing Siprotec(7UT86): Oil level low. relays
Due to Earthquake
| 10:38 |  | Bhulta-Ghorasal 230 kV Ckt-2 Tripped from Bhulta 400/230kV end showing REL670 relays Due | [7 empty] | 26.0MW load
|  |  | to None | [7 empty] | interrup. Bhulta
400/230kV end
| 10:38 | 12:22 | Haripur 230/132kV S/S Bus-2 Tripped showing MVAJ: 86B11,86B12,86B13, 86B14,86B15, 86B16,
86B17, 86B18, 86B19, 86B20. relays Due to Earthquake
| 10:38 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
| 10:39 | 10:46 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 23.0MW load
interrup.
| 10:39 |  | An earthquake of magnitude 5.7 on the Richter scale occurred near Madhabdi, Narsingdi.
| 10:40 |  | Summit Bibiyana-2 CCPP tripped .
| 10:42 |  | Ashuganj 225 MW CCPP ST tripped
| 10:42 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
| 10:46 |  | Sirajgonj 225MW CCPP Unit-1 Tripped with remarks:- ST
| 10:46 |  | Sirajganj 225 MW CCPP Unit-1 ST tripped at 10:46 hrs
| 10:46 | 10:46 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 38.0MW load
interrup.
| 10:48 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 11:23 |  | Haripur 412 MW CCPP, FGMO is ON with remarks:-
| 11:39 |  | Ashuganj Precision power plant tripped at 11:39 hrs
| 11:45 |  | Ashuganj Precision power plant tripped was synchronized at 11:45 hrs.
| 11:46 | 14:18 | Feni 230/132kV S/S ATR-3 HT Forced S/D Due to due to oil leakage of neutral bushing at
230kv side
| 11:46 | 14:18 | Feni 230/132kV S/S ATR-3 LT Forced S/D Due to due to oil leakage of neutral bushing at
230 kv side
| 11:50 | 17:19 | Rangpur 132/33kV S/S Rangpur-GTPS Forced S/D Due to CT Oil leakage
| 12:06 |  | SS Power Synchronized
| 12:18 | 15:56 | Niamatpur 132/33kV S/S Bus-2 Scheduled S/D Due to Annual maintenance.
| 12:18 | 15:56 | Niamatpur 132/33kV S/S Bus-2 Scheduled S/D Due to Annual maintenance.
| 12:30 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- ST
| 13:03 | 14:21 | Feni 230/132kV S/S ATR-2 HT Forced S/D Due to due to oil leakage
| 13:18 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 13:18 |  | Ashuganj 225 MW CCPP was synchronized at 13:18 hrs.
| 13:18 |  | Ashuganj 225 MW ST was sync.
| 14:03 |  | Day Peak Generation: 8417 MW.
| 14:23 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 14:23 |  | Sirajganj 225 MW CCPP Unit-1 ST was sync.
| 14:34 | 16:10 | Fatullah 132/33kV S/S 132 kV Hasnabad Scheduled S/D Due to NLDC
| 14:36 | 16:12 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Scheduled S/D Due to Red Hot maintenance
| 14:46 | 22:30 | Tongi 230/132/33kV S/S T-02 HT Scheduled S/D Due to Due to idmt trip
| 14:46 | 22:25 | Tongi 230/132/33kV S/S T-02 LT Scheduled S/D Due to Due to idmt trip
|  | 15:42 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 is restored.
| 16:43 | 17:08 | Barishal 230/132kV S/S T-4 LT Tripped showing Over current relays Due to Trip due to 33kv | [7 empty] | 20.0MW load
|  |  | Babugang, Banaripara, Rahmatpur fedders trip. | [7 empty] | interrup.
| 16:43 | 17:08 | Barishal 230/132kV S/S T-5 LT Tripped showing Over current relays Due to Trip due to 33kv | [7 empty] | 20.0MW load
|  |  | Babugang, Banaripara, Rahmatpur fedders trip. | [7 empty] | interrup.
|  | 16:58 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
| 17:01 | 17:32 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Scheduled S/D
| 17:40 |  | Summit Bibiyana-2 CCPP GT was synchronized.
| 18:00 |  | Evening Peak Generation is 9905 MW.
|  | 19:13 | Haripur 230/132kV S/S 132KV Bhulta-2 is restored.
| 19:28 |  | Summit Bibiyana-2 CCPP ST was synchronized.
|  | 19:35 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
| 19:38 |  | Kaliakoir 400/132kV 325MVA ATR-3 was switched on.
| 19:46 | 19:54 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Tripped showing Simens 7SJ62 relays Due to | [7 empty] | 12.0MW load
|  |  | টি-১ ৩৩কেভি বাসে সংযুক্ত Chapai ৩৩ কেভি পবিস ফিডারে O/C ,E/F ( নিয়ামতপুর গ্রিড হতে ৪০ | [7 empty] | interrup.
কিমি দুরে ইনশুলেটর ক্র্যাক করে ) এর কারণে গ্রিড এর 33kV T-1 transformer ট্রিপ করে।
| 19:57 |  | Ashuganj-Ghorasal 132kV Ckt-1 and 2 was switched on at 19:57 and 20:05 respectively. Now,
Ghorashal 132kV bus is energized.
| 20:31 |  | Ghorasal-Joydebpur 132kV Ckt-1 and 2 were switched on at 20:31 hrs. Now, Joydebpur is
taking load from Ghorashal SS.
| 20:40 |  | Kaliakoir 400/132kV 325MVA ATR-3 was shut down.
| 00:38 |  | Bhola Nutan Biddut BD LTD Synchronized with remarks:- GT-11
| 01:17 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 06:23 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to For project
work. and from Khulna(S) 230/132kV end Due to None
| 06:59 |  | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance Work.
| 06:59 |  | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance Work.
| 07:05 |  | Amtoli 400KV Bus-1 S/D.
| 07:14 |  | Rampur 230/132/33 S/S Khulshi-2 Scheduled S/D Due to annual maintenance
| 07:15 |  | Meghnaghat 230/132kV S/S Bus2 Project Work S/D Due to Isolator upgradation work
| 07:16 |  | Halishahar-Khulshi 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Annual
maintenance
| 07:23 |  | Saidpur 132/33kV S/S TR-5 (434T) LT Project Work S/D
| 07:24 |  | Saidpur 132/33kV S/S TR-5 (434T) HT Project Work S/D
| 07:39 |  | Saidpur 132/33kV S/S BUS B Project Work S/D
| 07:49 |  | Rajshahi-Rajshahi(New) 132kV Ckt-1 Scheduled S/D from Rajshahi 132/33kV end Due to
Annual Maintenance Work. and from Rajshahi 230/132/33kV end Due to Annual maintenance
| 07:59 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D
| 07:59 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 338 | 8460000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 82989 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6945376 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 135000 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 157440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 2 | 15763 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 37346 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 285000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 178560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 17760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 295320 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 566064 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 47 | 178560 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 65 | 266400 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 134650 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 280 | 6485660 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 35 | 109200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1347.5 | 24351088
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 139050 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 16 | 63360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2071200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 142 | 3869186 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 73 | 405636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 22402 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 21120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 32 | 657120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20188 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 61100 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 151680 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 46418 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 65236 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 531 | 11361817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 284160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 195 | 6218181.82 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1130 | 25457854.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 4512000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8841000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 666648 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 498240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 301091 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1139128 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 60 | 254254 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 19888 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 58 | 487680 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1831680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 26909 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 379070 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 58140 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 43680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 6 | 76800 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 422782 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 937 | 19558990
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 54 | 671040 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 304800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 915600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 16560 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 132 | 2172210
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 726360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3654491 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 662592 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1072320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 3315750 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 301000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 323208 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 25 | 4548130 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 389 | 7991000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 897 | 22594851
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 873 | 19737454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 164 | 2863584 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 483120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 975 | 23345460 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2012 | 46429618
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 435 | 8389116 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2717000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 855 | 21429818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2677320 | GT-11 Shutdown under Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 6000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3139 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1515 | 35222393.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 330632 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 178 | 3410273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 344 | 8569381 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1218 | 23037182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 335264 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 639613 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1740 | 36350425
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1284654 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 145017 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35984.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 172191 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 195670 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1000800 | -
Rangpur Area Total |  |  |  |  | 950 | 195 | 2834316.16
Eastern Grid Total |  |  |  |  | 17383.855 | 4443.5 | 94134993.82
Western Grid Total |  |  |  |  | 10821.56 | 5462 | 120836752.34
National Grid Total |  |  |  |  | 28205.415 | 9905.5 | 214971746.16
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6604.74 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 2954.7 | MW
i) Dhaka area |  |  | 3377.3 |  | MW | i) Khulna area |  |  |  | 1118 | MW
ii) Chattogram area |  |  | 1163 |  | MW | ii) Barishal area |  |  |  | 275.5 | MW
iii) Cumilla area |  |  | 899.44 |  | MW | iii) Rajshahi area |  |  |  | 891.2 | MW
iv) Mymensingh area |  |  | 773 |  | MW | iv) Rangpur area |  |  |  | 670 | MW
v) Sylhet area |  |  | 392 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9559.44 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 18:00 | 67 | Hathazari | 60 | 18:00 | 133 | Niamatpur | 38 | 18:00
2 | AKSML | 154.6 | 09:00 | 68 | Ishurdi | 49 | 18:30 | 134 | Noapara | 27 | 18:30
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 58 | 18:00 | 135 | PHP | 9 | 12:00
4 | Agargaon | 93 | 13:00 | 70 | Jamalpur | 87 | 08:00 | 136 | Pabna | 60 | 18:00
5 | Agrabad | 72 | 18:30 | 71 | Jashore | 97 | 13:00 | 137 | Palashbari | 78 | 18:00
6 | Amnura | 15 | 08:00 | 72 | Jhenaidah | 83 | 18:00 | 138 | Panchagarh | 41 | 18:00
7 | Ashuganj | 59 | 10:00 | 73 | Joydebpur | 78 | 18:30 | 139 | Patiya | 7 | 18:00
8 | BSRM | 195 | 07:00 | 74 | Joypurhat | 38 | 18:00 | 140 | Patuakhali | 41 | 21:00
9 | Bagerhat | 55 | 20:00 | 75 | Juldah | 12 | 00:00 | 141 | Payra | 22 | 21:00
10 | Bajitpur | 55 | 18:30 | 76 | KSRM | 16 | 03:00 | 142 | Postogola | 47 | 00:00
11 | Bakulia | 58 | 13:00 | 77 | Kabirpur | 153 | 13:00 | 143 | Purbachal | 27 | 13:00
12 | Banani | 24.2 | 12:00 | 78 | Kachua | 54 | 13:00 | 144 | Purbasadipur | 95 | 18:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 78 | 13:00 | 145 | Rahanpur | 20 | 18:00
14 | Barapukuria | 40 | 08:00 | 80 | Kalurghat | 36 | 00:00 | 146 | Rahim | 43 | 03:00
15 | Barguna | 14 | 19:30 | 81 | Kamrangirchar | 57 | 00:00 | 147 | Rajbari | 50 | 18:00
16 | Barishal | 85 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 88 | 12:00
17 | Barishal-230 | 64 | 13:00 | 83 | Kasba | 25 | 13:00 | 149 | Rajshahi | 62 | 18:00
18 | Baroaulia | 50 | 12:00 | 84 | Kazla | 81 | 00:00 | 150 | Rajshahi-230 | 70 | 13:00
19 | Baroirhat | 36 | 18:00 | 85 | Keranigonj | 49 | 00:00 | 151 | Ramganj | 74 | 13:00
20 | Bashundhara | 155 | 12:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 35 | 12:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 52 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 19:00 | 88 | Khulshi | 146 | 14:00 | 154 | Rangpur | 99 | 13:00
23 | Benapole | 42 | 13:00 | 89 | Kishoreganj | 78 | 13:00 | 155 | Ruppur | 3 | 15:00
24 | Bhaluka | 108 | 13:00 | 90 | Kodda | 202 | 00:00 | 156 | SSM | 15 | 02:00
25 | Bhandaria | 36 | 21:00 | 91 | Kulaura | 31 | 18:00 | 157 | Saidpur | 63 | 13:00
26 | Bhangura | 22 | 18:00 | 92 | Kurigram | 44 | 18:00 | 158 | Satkhira | 81 | 18:00
27 | Bheramara(GK) | 38 | 18:00 | 93 | Kushtia | 89 | 13:00 | 159 | Satmasjid | 78 | 13:00
28 | Bhulta | 195 | 00:00 | 94 | Laksam | 20 | 00:00 | 160 | Savar | 122 | 00:00
29 | Bog-Sherpur | 52 | 18:00 | 95 | Lakshmipur | 19 | 19:00 | 161 | SevenRings | 12.93 | 04:00
30 | Bogura | 101 | 18:30 | 96 | Lalbag | 54 | 00:00 | 162 | ShahCement | 30 | 00:00
31 | Borhanuddin | 61 | 21:00 | 97 | Lalmonirhat | 40 | 18:00 | 163 | Shahjadpur | 46 | 18:00
32 | Brahmanbaria | 92 | 13:00 | 98 | MI_Cement | 17.9 | 02:00 | 164 | Shahjibazar | 72 | 21:00
33 | Cantonment | 78 | 12:00 | 99 | Madanganj | 31 | 18:00 | 165 | Shahmirpur | 41.5 | 00:00
34 | Chandina | 12.05 | 11:00 | 100 | Madaripur | 66 | 21:00 | 166 | Shariatpur | 58 | 13:00
35 | Chandpur | 50 | 13:00 | 101 | Madartek | 70 | 13:00 | 167 | Sherpur | 94 | 08:00
36 | Chandraghona | 28 | 18:00 | 102 | Madunaghat | 35 | 13:00 | 168 | Shikalbaha | 17 | 03:00
37 | Chapai | 42 | 18:00 | 103 | Magura | 43 | 18:00 | 169 | Shitalakhya | 43.6 | 12:00
38 | Charsaidpur | 38 | 08:00 | 104 | Mahasthangarh | 46 | 17:00 | 170 | Sholosohor | 32 | 00:00
39 | Chauddagram | 47 | 13:00 | 105 | Maijdee | 25 | 18:00 | 171 | Shyampur | 124 | 00:00
40 | Chhatak | 23 | 13:00 | 106 | Manikganj | 83 | 21:00 | 172 | Siddhirganj | 74 | 00:00
41 | Chowmuhani | 101 | 20:00 | 107 | Maniknagar | 42 | 00:00 | 173 | Sirajganj | 68 | 18:00
42 | Chuadanga | 68 | 13:00 | 108 | Matarbari | 40 | 13:00 | 174 | Sonargaon | 113 | 00:00
43 | Coxsbazar | 105 | 18:00 | 109 | Matuail | 52.2 | 00:00 | 175 | Sreemongol | 55 | 18:00
44 | Cumilla(N) | 78 | 13:00 | 110 | Metrorail_Motijheel | 28 | 19:30 | 176 | Sreepur | 70 | 00:00
45 | Cumilla(S) | 112 | 12:00 | 111 | Metrorail_Uttara | 1 | 00:00 | 177 | Srinagar | 35.85 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 64 | 00:00 | 178 | Sunamganj | 37 | 18:30
47 | Daudkandi | 102 | 18:00 | 113 | Mirpur | 114 | 13:00 | 179 | Sylhet | 40 | 13:00
48 | DhakaUniversity | 32 | 13:00 | 114 | Mirsorai | 22 | 13:00 | 180 | Sylhet-132 | 78 | 13:00
49 | Dhamrai | 94 | 00:00 | 115 | Mirzapur | 34 | 18:00 | 181 | TK | 18 | 18:00
50 | Dhanmondi | 82.2 | 13:00 | 116 | Mithapukur | 40 | 18:00 | 182 | Tangail | 116 | 13:00
51 | Dohazari | 72 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 13 | 09:00
52 | Faridpur | 95 | 18:00 | 118 | Mogbazar | 60.3 | 13:00 | 184 | Tasnim | 30 | 00:00
53 | Fatullah | 83 | 00:00 | 119 | Mongla | 27 | 00:00 | 185 | Thakurgaon | 70 | 18:30
54 | Fenchuganj | 26 | 18:00 | 120 | Motijheel | 25 | 13:00 | 186 | Tongi | 95 | 00:00
55 | Feni | 79 | 13:00 | 121 | Muktagacha | 24 | 08:00 | 187 | Ullahpara | 24 | 18:00
56 | GPH | 96 | 06:00 | 122 | Munshiganj | 77 | 13:00 | 188 | Ullon | 53 | 13:00
57 | Ghatail | 54 | 18:00 | 123 | Muradnagar | 25 | 19:00 | 189 | Uttara | 64 | 12:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 132 | 13:00 | 190 | UttaraNew | 30 | 12:00
59 | Ghorashal-230 | 76 | 01:00 | 125 | Naogaon | 81 | 19:30 | 191 | Zigatola | 58 | 13:00
60 | Goalpara | 21 | 22:00 | 126 | Narail | 39 | 18:00
61 | Gollamari | 80 | 13:00 | 127 | Narinda | 42 | 13:00
62 | Gopalganj | 71 | 18:00 | 128 | Narshingdi | 129 | 00:00
63 | Gulshan | 66 | 12:00 | 129 | Natore | 89 | 18:30
64 | Halishahar | 52 | 00:00 | 130 | Nawabganj | 33.2 | 13:00
65 | HaripurSBU | 129 | 00:00 | 131 | Netrakona | 96 | 18:00
66 | Hasnabad | 69 | 13:00 | 132 | New | 48 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9895 | 0 |  | 9895
1:00 | 9345.53 | 0 |  | 9345.53
2:00 | 8922 | 0 |  | 8922
3:00 | 8694 | 0 |  | 8694
4:00 | 8404 | 0 |  | 8404
5:00 | 8291.5 | 0 |  | 8291.5
6:00 | 8370.5 | 0 |  | 8370.5
7:00 | 8502.05 | 0 |  | 8502.05
8:00 | 8936.46 | 0 |  | 8936.46
9:00 | 8580.85 | 0 |  | 8580.85
10:00 | 8383.83 | 0 |  | 8383.83
11:00 | 7384.01 | 0 |  | 7384.01
12:00 | 8421.71 | 0 |  | 8421.71
13:00 | 9932.03 | 0 |  | 9932.03
14:00 | 8834.99 | 0 |  | 8834.99
15:00 | 8275.14 | 0 |  | 8275.14
16:00 | 8069.19 | 0 |  | 8069.19
17:00 | 8485.97 | 0 |  | 8485.97
18:00 | 9905.5 | 0 |  | 9905.5
19:00 | 9770.5 | 0 |  | 9770.5
19:30 | 9724 | 0 |  | 9724
20:00 | 9683 | 0 |  | 9683
21:00 | 9658.95 | 0 |  | 9658.95
22:00 | 9636.07 | 0 |  | 9636.07
23:00 | 9254.47 | 0 |  | 9254.47
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 21-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2675 | 989 | 916 | 0 | 88 | 1241 | 86 | 3624 | 0 | 0 | 249 | 0 | 0 | 27 | 0 | DAILY ENERGY CURVE
00:30 | 2651.5 | 985 | 916 | 0 | 88 | 1188 | 86 | 3509 | 29.265 | 0 | 142 | 0 | 0 | 25.5 | 0 | 21-11-2025
01:00 | 2628 | 981 | 916 | 0 | 88 | 1135 | 86 | 3394 | 58.53 | 0 | 35 | 0 | 0 | 24 | 0
01:30 | 2621.5 | 948 | 916 | 0 | 86 | 1080 | 86 | 3316 | 29.265 | 0 | 25.5 | 0 | 0 | 25.5 | 0 | Energy Generated | 214.9717 |  | MKWHr
02:00 | 2615 | 915 | 916 | 0 | 84 | 1025 | 86 | 3238 | 0 | 0 | 16 | 0 | 0 | 27 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2636.5 | 920 | 896.5 | 0 | 82 | 973 | 86 | 3182 | 0 | 0 | 8 | 0 | 0 | 24 | 0 | Total Energy Requirement | 214.9717 |  | MKWHr
03:00 | 2658 | 925 | 877 | 0 | 80 | 921 | 86 | 3126 | 0 | 0 | 0 | 0 | 0 | 21 | 0
03:30 | 2628.5 | 926.5 | 797.5 | 0 | 77 | 914 | 86 | 3100 | 0 | 0 | 0 | 0 | 0 | 19.5 | 0
04:00 | 2599 | 928 | 718 | 0 | 74 | 907 | 86 | 3074 | 0 | 0 | 0 | 0 | 0 | 18 | 0
04:30 | 2619.5 | 924.25 | 692 | 0 | 76 | 870.5 | 86 | 3062 | 0 | 0 | 0 | 0 | 0 | 17.5 | 0
05:00 | 2640 | 920.5 | 666 | 0 | 78 | 834 | 86 | 3050 | 0 | 0 | 0 | 0 | 0 | 17 | 0
05:30 | 2623 | 944 | 651 | 0 | 74 | 838 | 86 | 3092.5 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0
06:00 | 2606 | 967.5 | 636 | 0 | 70 | 842 | 86 | 3135 | 0 | 0 | 0 | 0 | 0 | 28 | 0
06:30 | 2648 | 972.75 | 635 | 0 | 69 | 850 | 86 | 3127 | 22.525 | 0 | 1 | 0 | 0 | 25 | 0
07:00 | 2690 | 978 | 634 | 0 | 68 | 858 | 86 | 3119 | 45.05 | 0 | 2 | 0 | 0 | 22 | 0
07:30 | 2638 | 978.5 | 654 | 0 | 67 | 884.5 | 86 | 3218.5 | 137.755 | 0 | 39 | 0 | 0 | 16 | 0
08:00 | 2586 | 979 | 674 | 0 | 66 | 911 | 86 | 3318 | 230.46 | 0 | 76 | 0 | 0 | 10 | 0
08:30 | 2464.5 | 938.5 | 685 | 0 | 67 | 913.03 | 86 | 3209 | 328.625 | 0 | 59.5 | 0 | 0 | 7.5 | 0
09:00 | 2343 | 898 | 696 | 0 | 68 | 915.06 | 86 | 3100 | 426.79 | 0 | 43 | 0 | 0 | 5 | 0
09:30 | 2339 | 903.5 | 689.5 | 0 | 69 | 872.435 | 86 | 2973.5 | 499.405 | 0 | 43 | 0 | 0 | 7 | 0
10:00 | 2335 | 909 | 683 | 0 | 70 | 829.81 | 86 | 2847 | 572.02 | 0 | 43 | 0 | 0 | 9 | 0
10:30 | 2241 | 742.5 | 714 | 0 | 73 | 823.465 | 86 | 2551 | 594.955 | 0 | 43 | 0 | 0 | 15 | 0
11:00 | 2147 | 576 | 745 | 0 | 76 | 817.12 | 86 | 2255 | 617.89 | 0 | 43 | 0 | 0 | 21 | 0
11:30 | 2272 | 664 | 830.5 | 0 | 83 | 879.98 | 86 | 2315.5 | 585.38 | 36.5 | 131.5 | 0 | 0 | 18.5 | 0
12:00 | 2397 | 752 | 916 | 0 | 90 | 942.84 | 86 | 2376 | 552.87 | 73 | 220 | 0 | 0 | 16 | 0
12:30 | 2453 | 757 | 916 | 0 | 90 | 1029.915 | 86 | 2624 | 556.705 | 103 | 544.25 | 0 | 0 | 17 | 0
13:00 | 2509 | 762 | 916 | 0 | 90 | 1116.99 | 86 | 2872 | 560.54 | 133 | 868.5 | 0 | 0 | 18 | 0
13:30 | 2488.5 | 721 | 915.5 | 0 | 83 | 1066.495 | 86 | 2802 | 529.015 | 75 | 601 | 0 | 0 | 16 | 0
14:00 | 2468 | 680 | 915 | 0 | 76 | 1016 | 86 | 2732 | 497.49 | 17 | 333.5 | 0 | 0 | 14 | 0
14:30 | 2447 | 681.5 | 854.5 | 0 | 74 | 990 | 86 | 2693 | 410.765 | 17 | 285.8 | 0 | 0 | 15.5 | 0
15:00 | 2426 | 683 | 794 | 0 | 72 | 964 | 86 | 2654 | 324.04 | 17 | 238.1 | 0 | 0 | 17 | 0
15:30 | 2493 | 693 | 794 | 0 | 71 | 951.5 | 86 | 2608 | 224.865 | 17 | 219.3 | 0 | 0 | 14.5 | 0
16:00 | 2560 | 703 | 794 | 0 | 70 | 939 | 86 | 2562 | 125.69 | 17 | 200.5 | 0 | 0 | 12 | 0
16:30 | 2670.5 | 707.5 | 786.5 | 0 | 70 | 982 | 86 | 2655 | 66.08 | 28.5 | 219.5 | 0 | 0 | 6 | 0
17:00 | 2781 | 712 | 779 | 0 | 70 | 1025 | 86 | 2748 | 6.47 | 40 | 238.5 | 0 | 0 | 0 | 0
17:30 | 2819 | 762.5 | 826 | 0 | 75 | 1121.5 | 86 | 2897 | 3.235 | 84.5 | 521 | 0 | 0 | 0 | 0
18:00 | 2857 | 813 | 873 | 0 | 80 | 1218 | 86 | 3046 | 0 | 129 | 803.5 | 0 | 0 | 0 | 0
18:30 | 2970.5 | 848.5 | 873.5 | 0 | 77 | 1220.5 | 86 | 3085.5 | 0 | 97 | 579.5 | 0 | 0 | 0 | 0
19:00 | 3084 | 884 | 874 | 0 | 74 | 1223 | 86 | 3125 | 0 | 65 | 355.5 | 0 | 0 | 0 | 0
19:30 | 3067 | 899 | 874 | 0 | 72 | 1220 | 86 | 3160 | 0 | 32 | 314 | 0 | 0 | 0 | 0
20:00 | 3111 | 948 | 874 | 0 | 84 | 1224 | 86 | 3198 | 0 | 0 | 158 | 0 | 0 | 0 | 0
20:30 | 3122.5 | 1024 | 874 | 0 | 84 | 1225.475 | 86 | 3137 | 0 | 0 | 118 | 0 | 0 | 0 | 0
21:00 | 3134 | 1100 | 874 | 0 | 84 | 1226.95 | 86 | 3076 | 0 | 0 | 78 | 0 | 0 | 0 | 0
21:30 | 3108 | 1145 | 874 | 0 | 83 | 1200.01 | 86 | 3073.5 | 0 | 0 | 78 | 0 | 0 | 0 | 0
22:00 | 3082 | 1190 | 874 | 0 | 82 | 1173.07 | 86 | 3071 | 0 | 0 | 78 | 0 | 0 | 0 | 0
22:30 | 3071.5 | 1177.25 | 874 | 0 | 81 | 1118.52 | 86 | 2986 | 0 | 0 | 51 | 0 | 0 | 0 | 0
23:00 | 3061 | 1164.5 | 874 | 0 | 80 | 1063.97 | 86 | 2901 | 0 | 0 | 24 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4383 | 5512 | 9895 | DAILY GENERATION CURVE
00:30 | 4133.5 | 5486.765 | 9620.265
01:00 | 3884 | 5461.53 | 9345.53 | 21-11-2025
01:30 | 3831 | 5302.765 | 9133.765
02:00 | 3778 | 5144 | 8922
02:30 | 3782.5 | 5025.5 | 8808
03:00 | 3787 | 4907 | 8694
03:30 | 3763 | 4786 | 8549
04:00 | 3739 | 4665 | 8404
04:30 | 3754.75 | 4593 | 8347.75
05:00 | 3770.5 | 4521 | 8291.5
05:30 | 3829.5 | 4501.5 | 8331
06:00 | 3888.5 | 4482 | 8370.5
06:30 | 3921.705 | 4514.57 | 8436.275
07:00 | 3954.91 | 4547.14 | 8502.05
07:30 | 3985.35 | 4733.905 | 8719.255
08:00 | 4015.79 | 4920.67 | 8936.46
08:30 | 3889.205 | 4869.45 | 8758.655
09:00 | 3762.62 | 4818.23 | 8580.85
09:30 | 3745.075 | 4737.265 | 8482.34
10:00 | 3727.53 | 4656.3 | 8383.83
10:30 | 3149.95 | 4733.97 | 7883.92
11:00 | 2572.37 | 4811.64 | 7384.01
11:30 | 2853.875 | 5048.985 | 7902.86
12:00 | 3135.38 | 5286.33 | 8421.71
12:30 | 3737.39 | 5439.48 | 9176.87
13:00 | 4339.4 | 5592.63 | 9932.03
13:30 | 3999.635 | 5383.875 | 9383.51
14:00 | 3659.87 | 5175.12 | 8834.99
14:30 | 3571.75 | 4983.315 | 8555.065
15:00 | 3483.63 | 4791.51 | 8275.14
15:30 | 3454.955 | 4717.21 | 8172.165
16:00 | 3426.28 | 4642.91 | 8069.19
16:30 | 3538.49 | 4739.09 | 8277.58
17:00 | 3650.7 | 4835.27 | 8485.97
17:30 | 4047.1 | 5148.635 | 9195.735
18:00 | 4443.5 | 5462 | 9905.5
18:30 | 4347 | 5491 | 9838
19:00 | 4250.5 | 5520 | 9770.5
19:30 | 4189 | 5535 | 9724
20:00 | 4098 | 5585 | 9683
20:30 | 4143 | 5527.975 | 9670.975 |  | Executive Engineer
21:00 | 4188 | 5470.95 | 9658.95 |  | Network Operation Division
21:30 | 4255 | 5392.51 | 9647.51
22:00 | 4322 | 5314.07 | 9636.07
22:30 | 4246.25 | 5199.02 | 9445.27
23:00 | 4170.5 | 5083.97 | 9254.47

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 395 | 06:00 | 383 | 00:00 | Meghnaghat | 395 | 06:00 | 385 | 00:00
Ashuganj | 403 | 6:00 | 392 | 12:00 | Payra | 414 | 05:00 | 409 | 00:00
Bhulta | 399 | 06:00 | 387 | 00:00 | Rahanpur | 414 | 04:00 | 404 | 13:00
Bibiana | 398 | 23:00 | 388 | 11:00 | Rampal | 411 | 05:00 | 398 | 13:00
BIPTC | 407 | 05:00 | 389 | 12:00
Bogura | 406 | 04:00 | 393 | 00:00
Gopalganj | 406 | 06:00 | 392 | 13:00
Kaliakoir | 392 | 18:00 | 382 | 00:00
Korerhat | 402 | 06:00 | 395 | 00:00
Madunaghat | 400 | 07:00 | 389 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 05:00 | 230 | 00:00 | Kachua | 236 | 13:00 | 227 | 20:00
AKSML | 238 | 13:00 | 228 | 11:00 | Kaliakoir | 238 | 18:00 | 229 | 00:00
Aminbazar | 239 | 06:00 | 230 | 00:00 | Keranigonj | 235 | 06:00 | 228 | 00:00
Ashuganj | 232 | 04:00 | 224 | 17:00 | Khulna(S) | 240 | 06:00 | 231 | 13:00
Ashuganj-400 | 232 | 6:00 | 222 | 12:00 | Korerhat | 236 | 18:00 | 232 | 20:00
Baghabari | 236 | 06:00 | 226 | 12:00 | Madunaghat | 236 | 06:00 | 229 | 11:00
Barapukuria | 223 | 05:00 | 217 | 00:00 | Madunaghat-400 | 237 | 07:00 | 230 | 23:00
Barapukuria-230 | 223 | 5:00 | 218 | 23:00 | Maniknagar | 230 | 18:00 | 224 | 00:00
Barishal | 240 | 04:00 | 233 | 12:00 | Meghnaghat | 239 | 06:00 | 232 | 00:00
Bheramara | 235 | 15:00 | 225 | 12:00 | Meghnaghat-400 | 234 | 06:00 | 226 | 00:00
Bhulta | 232 | 06:00 | 225 | 00:00 | Mirsorai | 239 | 13:00 | 228 | 20:00
Bibiana | 237 | 05:00 | 229 | 11:00 | Rajshahi | 235 | 15:00 | 224 | 13:00
BIPTC | 238 | 04:00 | 225 | 13:00 | Rampal | 238 | 06:00 | 228 | 13:00
Bogura | 235 | 04:00 | 228 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 235 | 04:00 | 227 | 00:00 | Rampura | 230 | 05:00 | 223 | 00:00
Borhanuddin | 241 | 23:00 | 237 | 13:00 | Shikalbaha | 235 | 07:00 | 228 | 11:00
BSRM | 237 | 13:00 | 228 | 00:00 | Shyampur | 234 | 06:00 | 222 | 23:00
Cumilla(N) | 234 | 06:00 | 225 | 11:00 | Siddhirganj | 231 | 15:00 | 225 | 00:00
Faridpur | 240 | 06:00 | 137 | 02:00 | Sirajgonj | 240 | 06:00 | 234 | 00:00
Fenchuganj | 238 | 18:00 | 230 | 01:00 | Sreepur | 230 | 05:00 | 224 | 00:00
Feni | N/A | N/A | N/A | N/A | Tongi | 237 | 18:00 | 226 | 01:00
Ghorashal | 235 | 01:00 | 235 | 01:00
Ghorashal-230 | 236 | 14:00 | 222 | 00:00
Gopalganj | 240 | 06:00 | 231 | 13:00
GPH | 237 | 13:00 | 231 | 00:00
Haripur | 232 | 06:00 | 226 | 00:00
Hasnabad | 236 | 06:00 | 227 | 00:00
Hathazari | 235 | 03:00 | 230 | 22:00
Ishurdi | 238 | 04:00 | 228 | 13:00
Jhenaidah | 237 | 04:00 | 224 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 130 | 00:00 | Lalbag | 137 | 05:00 | 132 | 00:00
Agargaon | 138 | 06:00 | 133 | 00:00 | Lalmonirhat | 132 | 03:00 | 122 | 12:00
Agrabad | 135 | 07:00 | 132 | 01:00 | Madanganj | 135 | 11:00 | 132 | 00:00
AKS | 134 | 08:00 | 131 | 11:00 | Madaripur | 138 | 05:00 | 134 | 13:00
Aminbazar | 138 | 05:00 | 134 | 01:00 | Madartek | 133 | 01:00 | 129 | 02:00
Amnura | 138 | 03:00 | 130 | 12:00 | Madunaghat | 137 | 06:00 | 135 | 00:00
Ashuganj | 142 | 05:00 | 138 | 11:00 | Magura | 139 | 03:00 | 130 | 13:00
Bagerhat | 137 | 05:00 | 130 | 11:00 | Mahasthangarh | 134 | 04:00 | 129 | 00:00
Bajitpur | 136 | 04:00 | 132 | 00:00 | Maijdee | 133 | 06:00 | 129 | 20:00
Bakulia | 137 | 05:00 | 134 | 00:00 | Manikganj | 136 | 18:00 | 131 | 00:00
Banani | 134 | 04:00 | 129 | 12:00 | Maniknagar | 139 | 05:00 | 132 | 00:00
Bangabhaban | 137 | 05:00 | 133 | 00:00 | Matarbari | 137 | 18:00 | 122 | 19:00
Barapukuria | 137 | 05:00 | 130 | 08:00 | Matuail | 136 | 11:00 | 131 | 00:00
Barguna | 135 | 03:00 | 133 | 12:00 | Metrorail_Motijheel | 139 | 05:00 | 132 | 00:00
Barishal | 138 | 04:00 | 134 | 12:00 | Metrorail_Uttara | 137 | 18:00 | 132 | 00:00
Barishal-230 | 139 | 05:00 | 133 | 12:00 | Millgate | 139 | 18:00 | 132 | 00:00
Baroaulia | 137 | 08:00 | 133 | 00:00 | Mirpur | 138 | 03:00 | 132 | 12:00
Baroirhat | 136 | 06:00 | 132 | 14:00 | Mirzapur | 132 | 11:00 | 126 | 07:00
Bashundhara | 134 | 04:00 | 127 | 22:00 | Mithapukur | 135 | 05:00 | 128 | 08:00
BashundharaCement | 135 | 11:00 | 132 | 00:00 | MI_Cement | 135 | 06:00 | 130 | 00:00
Beanibazar | 134 | 05:00 | 131 | 00:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 137 | 04:00 | 123 | 13:00 | Mogbazar | 137 | 03:00 | 130 | 12:00
Bhaluka | 133 | 05:00 | 128 | 00:00 | Mongla | 137 | 06:00 | 130 | 13:00
Bhandaria | 135 | 03:00 | 132 | 12:00 | Motijheel | 137 | 05:00 | 133 | 00:00
Bhangura | 136 | 06:00 | 132 | 00:00 | Muktagacha | 133 | 22:00 | 119 | 07:00
Bheramara | 139 | 23:00 | 133 | 13:00 | Munshiganj | 135 | 18:00 | 129 | 00:00
Bheramara(GK) | 139 | 23:00 | 133 | 13:00 | Muradnagar | 135 | 06:00 | 132 | 00:00
Bhulta | 130 | 07:00 | 126 | 10:00 | Mymensingh | 133 | 22:00 | 115 | 07:00
Bog-Sherpur | 136 | 06:00 | 131 | 00:00 | Naogaon | 133 | 06:00 | 128 | 00:00
Bogura | 135 | 05:00 | 131 | 00:00 | Narail | 139 | 04:00 | 124 | 09:00
Bogura-230 | 135 | 04:00 | 130 | 13:00 | Narinda | 139 | 5:00 | 132 | 0:00
Brahmanbaria | 135 | 18:00 | 130 | 00:00 | Narshingdi | 136 | 23:00 | 126 | 00:00
Cantonment | 138 | 06:00 | 133 | 00:00 | Natore | 135 | 15:00 | 130 | 13:00
Chandina | 138 | 06:00 | 127 | 04:00 | Nawabganj | 138 | 18:00 | 132 | 00:00
Chandpur | 139 | 13:00 | 132 | 14:00 | Netrakona | 131 | 23:00 | 125 | 00:00
Chandraghona | 138 | 00:00 | 136 | 01:00 | New | 141 | 12:00 | 133 | 00:00
Chapai | 138 | 05:00 | 133 | 19:00 | Niamatpur | 138 | 06:00 | 134 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 06:00 | 131 | 00:00 | Noapara | 138 | 06:00 | 126 | 13:00
Chauddagram | 135 | 05:00 | 132 | 11:00 | Pabna | 137 | 15:00 | 133 | 12:00
Chhatak | 133 | 03:00 | 129 | 00:00 | Palashbari | 132 | 04:00 | 126 | 21:00
Chowmuhani | 133 | 18:00 | 130 | 02:00 | Panchagarh | 138 | 17:00 | 130 | 13:00
Chuadanga | 139 | 23:00 | 131 | 12:00 | Patiya | 139 | 00:00 | 132 | 20:00
Coxsbazar | 128 | 08:00 | 122 | 18:00 | Patuakhali | 136 | 00:00 | 134 | 01:00
Cumilla(N) | 138 | 06:00 | 133 | 20:00 | Payra | 137 | 05:00 | 134 | 13:00
Cumilla(S) | 136 | 08:00 | 126 | 12:00 | PHP | 135 | 18:00 | 130 | 12:00
Daganbhuiyan | 135 | 06:00 | 131 | 14:00 | Postogola | 136 | 16:00 | 132 | 00:00
Daudkandi | 133 | 06:00 | 129 | 00:00 | Purbachal | 134 | 04:00 | 128 | 13:00
DhakaUniversity | 134 | 03:00 | 129 | 13:00 | Purbasadipur | 134 | 04:00 | 125 | 08:00
Dhamrai | 137 | 18:00 | 133 | 00:00 | Rahanpur | 139 | 05:00 | 136 | 00:00
Dhanmondi | 137 | 06:00 | 129 | 13:00 | Rahanpur-400 | 139 | 03:00 | 136 | 00:00
Dohazari | 134 | 06:00 | 127 | 11:00 | Rahim | 136 | 18:00 | 131 | 00:00
Faridpur | 139 | 06:00 | 135 | 00:00 | Rajbari | 139 | 04:00 | 133 | 13:00
Fatullah | 138 | 05:00 | 129 | 00:00 | Rajendrapur | 133 | 05:00 | 126 | 19:00
Fenchuganj | 139 | 16:00 | 136 | 09:00 | Rajshahi | 136 | 15:00 | 130 | 12:00
Feni | 133 | 06:00 | 130 | 14:00 | Rajshahi-230 | 135 | 04:00 | 130 | 12:00
Feni-230 | N/A | N/A | N/A | N/A | Ramganj | 134 | 04:00 | 129 | 20:00
Ghatail | 132 | 22:00 | 120 | 07:00 | Rampur | 135 | 13:00 | 131 | 11:00
Ghorashal | 140 | 03:00 | 136 | 20:00 | Rampura | 134 | 05:00 | 129 | 00:00
Goalpara | 139 | 04:00 | 131 | 13:00 | Rangamati | 137 | 05:00 | 134 | 11:00
Gollamari | 138 | 04:00 | 133 | 13:00 | Rangpur | 134 | 04:00 | 129 | 09:00
Gopalganj | 138 | 04:00 | 133 | 13:00 | Ruppur | 139 | 15:00 | 135 | 00:00
Gopalganj-400 | 140 | 06:00 | 132 | 15:00 | Saidpur | 134 | 15:00 | 125 | 13:00
Gulshan | 134 | 05:00 | 129 | 00:00 | Satkhira | 137 | 03:00 | 130 | 13:00
Halishahar | 137 | 18:00 | 134 | 00:00 | Satmasjid | 137 | 05:00 | 132 | 00:00
Haripur | 136 | 06:00 | 131 | 00:00 | Savar | 137 | 18:00 | 132 | 00:00
HaripurSBU | 136 | 06:00 | 132 | 00:00 | SevenRings | 140 | 05:00 | 136 | 00:00
Hasnabad | 136 | 05:00 | 131 | 00:00 | ShahCement | 135 | 06:00 | 131 | 00:00
Hathazari | 138 | 03:00 | 135 | 12:00 | Shahjadpur | 139 | 15:00 | 136 | 11:00
Ishurdi | 140 | 04:00 | 134 | 13:00 | Shahjibazar | 137 | 18:00 | 131 | 00:00
Jaldhaka | 132 | 04:00 | 125 | 08:00 | Shahmirpur | 137 | 07:00 | 134 | 00:00
Jamalpur | 132 | 14:00 | 112 | 07:00 | Shariatpur | 138 | 05:00 | 132 | 13:00
Jashore | 138 | 06:00 | 125 | 13:00 | Sherpur | 126 | 14:00 | 108 | 07:00
Jhenaidah | 141 | 06:00 | 124 | 12:00 | Shikalbaha | 126 | 02:00 | 123 | 00:00
Jhenaidah-230 | 141 | 04:00 | 132 | 13:00 | Shikalbaha-230 | 138 | 07:00 | 133 | 11:00
Joydebpur | 140 | 04:00 | 128 | 13:00 | Shitalakhya | 136 | 20:00 | 130 | 00:00
Joypurhat | 133 | 05:00 | 128 | 00:00 | Sholosohor | 137 | 04:00 | 135 | 00:00
Juldah | 137 | 08:00 | 132 | 11:00 | Shyampur | 137 | 06:00 | 133 | 00:00
Kabirpur | 137 | 18:00 | 130 | 12:00 | Shyampur-230 | 139 | 05:00 | 134 | 00:00
Kachua | 138 | 06:00 | 134 | 20:00 | Siddhirganj | 136 | 05:00 | 132 | 00:00
Kaliakoir | 138 | 06:00 | 133 | 00:00 | Sirajganj | 135 | 15:00 | 131 | 12:00
Kallyanpur | 138 | 06:00 | 134 | 00:00 | Sonargaon | 135 | 16:00 | 130 | 00:00
Kalurghat | 138 | 07:00 | 135 | 00:00 | Sreemongol | 137 | 22:00 | 132 | 00:00
Kamrangirchar | 137 | 18:00 | 132 | 00:00 | Sreepur | 135 | 03:00 | 130 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 04:00 | 132 | 00:00
Kasba | 135 | 04:00 | 132 | 00:00 | SSM | 140 | 03:00 | 138 | 11:00
Kazla | 136 | 05:00 | 132 | 00:00 | Sunamganj | 131 | 04:00 | 129 | 00:00
Keranigonj | 137 | 05:00 | 132 | 00:00 | Sylhet | 134 | 05:00 | 131 | 12:00
Khagrachori | 136 | 05:00 | 132 | 11:00 | Sylhet-132 | 133 | 06:00 | 131 | 00:00
Khulna | 137 | 16:00 | 131 | 13:00 | Tangail | 130 | 11:00 | 124 | 00:00
Khulna(S) | 139 | 04:00 | 133 | 13:00 | Taraganj | 134 | 05:00 | 126 | 21:00
Khulshi | 135 | 18:00 | 130 | 11:00 | Tasnim | 135 | 15:00 | 130 | 00:00
Kishoreganj | 135 | 10:00 | 132 | 12:00 | Thakurgaon | 136 | 17:00 | 125 | 08:00
Kodda | 135 | 06:00 | 127 | 00:00 | TK | 138 | 12:00 | 134 | 05:00
KSRM | 137 | 06:00 | 135 | 00:00 | Tongi | 141 | 18:00 | 134 | 01:00
Kulaura | 139 | 05:00 | 135 | 13:00 | Ullahpara | 136 | 05:00 | 133 | 00:00
Kurigram | 131 | 05:00 | 123 | 08:00 | Ullon | 134 | 04:00 | 129 | 13:00
Kushtia | 135 | 04:00 | 127 | 13:00 | Uttara | 137 | 05:00 | 133 | 00:00
Laksam | 139 | 18:30 | 133 | 20:00 | UttaraNew | 137 | 18:00 | 132 | 00:00
Lakshmipur | 134 | 05:00 | 130 | 20:00 | Zigatola | 137 | 05:00 | 133 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division