## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-11-2025 | during | 23-11-2025 | during | 23-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Electrical fault due to Earthquape
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 368 | 363 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 25 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.5 | 53.97 | 53.97 | 53.97 | 53.97 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 0 | 0 | 17 | 17 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 0 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 8 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 15 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 17 | 162 | 162 | 35 | 108 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 20 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 69 | 0 | 584 | 584 | 420 | 420 | ST maint
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Under maint
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 314 | 323 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1177 | 1335.5 | 5124.9 | 5091.9 | 3959.71 | 4048.71
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 208 | 187 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 100 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 48 | 56 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 8 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.92 | 0 | 3.27 | 0 | 3.27 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 30 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 26 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 15 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 420 | 585 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 21 | 4 | 5 | 4 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 350 | 350 | 350 | 350 | 355 | 355 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1110.92 | 1542 | 2642.99 | 2632.72 | 2099.77 | 2089.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 194 | 187 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 33 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 2 | 47 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 36 | 85 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 25 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 56 | 150 | 150 | 125 | 125 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 109 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 90 | 92 | 160 | 160 | 106 | 106 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 16 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 17 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 48 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 833 | 1103 | 2170.4 | 2100.4 | 1895.4 | 1825.4
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-11-2025 | during | 23-11-2025 | during | 23-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 95 | 82 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.26 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 175.26 | 177 | 360.7 | 314 | 301.2 | 254.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 159 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 51 | 81 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 155 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 20 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 393 | 385 | 385 | 366 | 366 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1138 | 1198 | 1231 | 1231 | 1178 | 1178
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 866 | 886 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 312 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 786 | 1088 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2035 | 2224 | 2390 | 2312 | 1635.1 | 1557.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 305 | 502 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 545 | 870 | 992 | 992 | 932 | 932 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.42 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1185.42 | 1707 | 1593 | 1593 | 1400 | 1400
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 183 | 189 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.53 | 0 | 5.04 | 0 | 5.04 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 829.16 | 1283.49 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.45 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1627.14 | 1886.49 | 3080.91 | 2915.87 | 2546.13 | 2381.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 54 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 143 | 0 | 181.82 | 0 | 181.82 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 234.6 | 214 | 534.02 | 317 | 500.02 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 9516.34 | 11386.99 | 19127.92 | 18507.89 | 15515.33 | 15017.3
Forecast Scenario (23-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9920 |  | 0 |  | 9920
|  |  |  | 1:00 | 9420 |  | 0 |  | 9420
|  |  |  | 2:00 | 9090 |  | 0 |  | 9090
|  |  |  | 3:00 | 8790 |  | 0 |  | 8790
|  |  |  | 4:00 | 8520 |  | 0 |  | 8520
|  |  |  | 5:00 | 8490 |  | 0 |  | 8490
|  |  |  | 6:00 | 8660 |  | 0 |  | 8660
|  |  |  | 7:00 | 9460 |  | 0 |  | 9460
|  |  |  | 8:00 | 9940 |  | 0 |  | 9940
|  |  |  | 9:00 | 9900 |  | 0 |  | 9900
|  |  |  | 10:00 | 9850 |  | 0 |  | 9850
|  |  |  | 11:00 | 10200 |  | 0 |  | 10200
|  |  |  | 12:00 | 10770 |  | 0 |  | 10770
|  |  |  | 13:00 | 11010 |  | 0 |  | 11010
|  |  |  | 14:00 | 10600 |  | 0 |  | 10600
|  |  |  | 15:00 | 10560 |  | 0 |  | 10560
|  |  |  | 16:00 | 10390 |  | 0 |  | 10390
|  |  |  | 17:00 | 10730 |  | 0 |  | 10730
|  |  |  | 18:00 | 11990 |  | 0 |  | 11990
|  |  |  | 18:30 | 11700 |  | 0 |  | 11700
|  |  |  | 19:00 | 11520 |  | 0 |  | 11520
|  |  |  | 19:30 | 11240 |  | 0 |  | 11240
|  |  |  | 20:00 | 11150 |  | 0 |  | 11150
|  |  |  | 21:00 | 11020 |  | 0 |  | 11020
|  |  |  | 22:00 | 10530 |  | 0 |  | 10530
|  |  |  | 23:00 | 10120 |  | 0 |  | 10120
Probable Maximum Temperature: |  |  | 28.20°C
Probable Maximum Demand at Day Peak: |  |  | 10770.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 11990.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11990.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 242.63 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 09:47 hrs on 23-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-11-2025 | [28 empty] | Date: | 22-11-2025 | [28 empty] | Date: | 22-11-2025 | [28 empty] | Date: | 22-11-2025 | [28 empty] | Date: | 22-11-2025 | [14 empty] | Date: | 22-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 198 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 502 | 0 | 51 | 0 | 35 | 393 | 0 | 0 | 44 | 178 | 38 | 0 | 0 | 0 | 0 | 18 | 0 | 78 | 0 | 0 | 0 | 300 | 0 | 356 | 0 | 30 | 150 | 17 | 0 | 82 | 30 | 0 | 15 | 158 | 0 | 16 | 8 | 103 | 0 | 0 | 0 | 4155.5 | 888 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 0 | 919.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 305 | 860 | 0 | 4880.66 | 9036.16 | 100.33
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 200 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 420 | 0 | 51 | 0 | 35 | 340 | 0 | 0 | 38 | 189 | 38 | 0 | 0 | 0 | 0 | 18 | 0 | 74 | 0 | 0 | 0 | 300 | 0 | 335 | 0 | 30 | 146 | 17 | 0 | 41 | 30 | 0 | 15 | 158 | 0 | 8 | 8 | 109 | 0 | 0 | 0 | 3887.5 | 819 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 844 | 0 | 851.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 131 | 0 | 305 | 700 | 0 | 4604.18 | 8491.68 | 100.32
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10.5 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42 | 197 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 420 | 0 | 51 | 0 | 35 | 300 | 0 | 0 | 10 | 188 | 38 | 0 | 0 | 0 | 0 | 18 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 332 | 0 | 30 | 150 | 17 | 0 | 41 | 30 | 0 | 15 | 158 | 0 | 8 | 0 | 110 | 0 | 0 | 0 | 3876.5 | 672 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 832.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 210 | 0 | 306 | 600 | 0 | 4365.9 | 8242.4 | 100.32
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10.5 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 200 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 320 | 0 | 5 | 0 | 8 | 300 | 0 | 0 | 10 | 186 | 10 | 0 | 0 | 0 | 0 | 16 | 0 | 68 | 0 | 0 | 0 | 300 | 0 | 332 | 0 | 30 | 150 | 17 | 0 | 8 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3517.5 | 672 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 839.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 272 | 500 | 0 | 4187.07 | 7704.57 | 100.31
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 0 | 0 | 10.5 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 201 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 330 | 0 | 5 | 0 | 8 | 250 | 0 | 0 | 10 | 189 | 10 | 0 | 0 | 0 | 0 | 16 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 342 | 0 | 30 | 151 | 17 | 0 | 7 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3451.5 | 673 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769 | 0 | 848.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 272 | 500 | 0 | 4181.06 | 7632.56 | 100.31
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 0 | 0 | 10.5 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 200 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 8 | 250 | 0 | 0 | 4 | 198 | 10 | 0 | 0 | 0 | 0 | 16 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 363 | 0 | 30 | 153 | 17 | 0 | 7 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3435.5 | 673 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 0 | 835.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 273 | 500 | 0 | 4113.66 | 7549.16 | 100.3
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11.5 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 200 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 8 | 350 | 0 | 0 | 2 | 198 | 10 | 0 | 0 | 0 | 0 | 16 | 0 | 70 | 0 | 0 | 0 | 315 | 0 | 354 | 0 | 30 | 159 | 17 | 0 | 7 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3660.5 | 672 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 836.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 273 | 500 | 0 | 4189.4 | 7849.9 | 100.3
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 0 | 10 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.16 | 86 | 0 | 42 | 198 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 430 | 3 | 5 | 0 | 13 | 393 | 0 | 0 | 3 | 203 | 18 | 0 | 0 | 0 | 0 | 16 | 0 | 70 | 0 | 6 | 0 | 315 | 0 | 371 | 0 | 30 | 160 | 17 | 0 | 41 | 20 | 0 | 15 | 158 | 0 | 16 | 3 | 111 | 0 | 1.84 | 0 | 4023 | 862 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 800 | 0 | 850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 6 | 0 | 0 | 2.96 | 187 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 56 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 10 | 0.03 | 0 | 0 | 115 | 180 | 0 | 274 | 556 | 0 | 4608.56 | 8631.56 | 100.29
08:00 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.71 | 86 | 0 | 18 | 200 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 420 | 9 | 20 | 0 | 43 | 400 | 0 | 0 | 21 | 184 | 34 | 0 | 0 | 0 | 0 | 16 | 0 | 76 | 0 | 22 | 0 | 315 | 0 | 341 | 0 | 30 | 160 | 17 | 0 | 76 | 30 | 0 | 15 | 158 | 0 | 47 | 19 | 111 | 1 | 14.08 | 0 | 4204.79 | 832 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 840 | 0 | 832.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.14 | 31 | 0 | 0 | 16.19 | 183 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 1.67 | 0 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 1.6 | 55 | 0.12 | 0 | 0 | 115 | 220 | 0 | 300 | 560 | 0 | 4756.7 | 8961.49 | 100.29
09:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 327 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.94 | 86 | 0 | 8 | 200 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 420 | 14 | 5 | 0 | 20 | 285 | 0 | 0 | 36 | 186 | 38 | 0 | 0 | 0 | 0 | 16 | 0 | 76 | 0 | 40 | 0 | 305 | 0 | 353 | 0 | 30 | 151 | 17 | 0 | 7 | 20 | 0 | 15 | 158 | 0 | 56 | 19 | 111 | 1 | 27.02 | 0 | 4012.96 | 832 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 804 | 0 | 829.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.02 | 58 | 0 | 0 | 35.45 | 171 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 2.85 | 0 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 3.4 | 112 | 0.25 | 0 | 0 | 115 | 180 | 0 | 305 | 550 | 0 | 4805.08 | 8818.04 | 100.28
10:00 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 296 | 0 | 0 | 30 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 25 | 0 | 22 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 86 | 0 | 10 | 200 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 420 | 17 | 5 | 0 | 8 | 250 | 0 | 0 | 0 | 190 | 10 | 0 | 0 | 0 | 0 | 16 | 0 | 80 | 0 | 54 | 0 | 300 | 0 | 353 | 0 | 30 | 153 | 0 | 0 | 7 | 20 | 0 | 15 | 159 | 0 | 16 | 19 | 108 | 2 | 37.06 | 0 | 3836.57 | 841 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 760 | 0 | 832.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.89 | 80 | 0 | 0 | 45.46 | 174 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 3.82 | 0 | 55 | 0 | 24 | 0 | 0 | 0 | 0 | 4.7 | 133 | 0.36 | 0 | 0 | 100 | 180 | 0 | 305 | 500 | 0 | 4676.77 | 8513.34 | 100.28
11:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 306 | 0 | 0 | 15 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 25 | 0 | 21 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2.82 | 86 | 0 | 10 | 195 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 423 | 19 | 5 | 0 | 8 | 250 | 0 | 0 | 0 | 197 | 10 | 0 | 0 | 0 | 0 | 16 | 0 | 84 | 0 | 64 | 0 | 315 | 0 | 369 | 0 | 30 | 158 | 0 | 0 | 7 | 20 | 0 | 15 | 158 | 0 | 16 | 19 | 99 | 2 | 42.06 | 0 | 3953.88 | 842 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 780 | 0 | 831.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.29 | 97 | 0 | 0 | 53.93 | 181 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 4.16 | 0 | 55 | 0 | 28 | 0 | 0 | 0 | 0 | 5.4 | 146 | 0.42 | 0 | 0 | 100 | 180 | 0 | 302 | 500 | 0 | 4894.53 | 8848.41 | 100.27
12:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 314 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 20 | 0 | 21 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 2.92 | 86 | 0 | 12 | 350 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 420 | 18 | 25 | 0 | 36 | 393 | 0 | 0 | 2 | 194 | 34 | 0 | 0 | 0 | 0 | 11 | 0 | 90 | 0 | 48 | 0 | 315 | 0 | 386 | 0 | 30 | 163 | 0 | 0 | 51 | 20 | 0 | 15 | 158 | 0 | 16 | 19 | 95 | 2 | 43.26 | 0 | 4434.18 | 866 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 786 | 0 | 829.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 95 | 0 | 0 | 47.45 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.53 | 0 | 55 | 0 | 31 | 0 | 0 | 0 | 0 | 5.6 | 143 | 0.42 | 0 | 0 | 115 | 220 | 0 | 305 | 545 | 0 | 5082.16 | 9516.34 | 100.27
13:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 315 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 24 | 0 | 19 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 9 | 2.67 | 86 | 0 | 17 | 350 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 515 | 17 | 51 | 0 | 50 | 393 | 0 | 0 | 22 | 193 | 37 | 0 | 0 | 0 | 0 | 11 | 0 | 84 | 0 | 63 | 0 | 320 | 0 | 376 | 0 | 30 | 162 | 16 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 16 | 19 | 82 | 2 | 18.2 | 0 | 4644.87 | 865 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 850 | 0 | 882.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.26 | 92 | 0 | 0 | 32.22 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.11 | 0 | 54 | 0 | 10 | 0 | 0 | 0 | 0 | 5.3 | 101 | 0.36 | 0 | 0 | 115 | 220 | 0 | 334 | 600 | 0 | 5136.2 | 9781.07 | 100.26
14:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 290 | 10 | 0 | 15 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 23 | 0 | 26 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 12 | 2.09 | 86 | 0 | 12 | 350 | 0 | 0 | 0 | 0 | 13 | 208 | 0 | 0 | 0 | 520 | 13 | 51 | 0 | 70 | 350 | 0 | 0 | 41 | 187 | 37 | 0 | 0 | 11 | 0 | 11 | 0 | 94 | 0 | 50 | 0 | 305 | 0 | 351 | 0 | 30 | 149 | 20 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 35 | 19 | 82 | 1 | 30.6 | 0 | 4588.69 | 865 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.88 | 876 | 0 | 926.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.13 | 76 | 0 | 0 | 32.54 | 181 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 3.83 | 0 | 54 | 0 | 20 | 0 | 0 | 0 | 0 | 4.8 | 110 | 0.35 | 0 | 0 | 115 | 180 | 0 | 302 | 560 | 0 | 5004.44 | 9593.13 | 100.26
15:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 300 | 17.5 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 15 | 0 | 28 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 12 | 1.43 | 86 | 0 | 6 | 350 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 522 | 9 | 51 | 0 | 70 | 350 | 0 | 0 | 45 | 185 | 37 | 0 | 0 | 0 | 0 | 11 | 0 | 90 | 0 | 32 | 0 | 300 | 0 | 382 | 0 | 30 | 143 | 20 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 35 | 19 | 82 | 1 | 20.69 | 0 | 4529.62 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 871 | 0 | 860.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.44 | 51 | 0 | 0 | 28.05 | 175 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.53 | 0 | 54 | 0 | 14 | 0 | 0 | 0 | 0 | 2.8 | 80 | 0.2 | 0 | 0 | 115 | 180 | 0 | 303 | 560 | 0 | 4831.33 | 9360.95 | 100.25
16:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 301 | 17.5 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 7 | 0 | 28 | 3 | 0 | 68 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 0.55 | 86 | 0 | 4 | 350 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 480 | 4 | 51 | 0 | 16 | 393 | 0 | 0 | 21 | 194 | 37 | 0 | 0 | 0 | 0 | 11 | 0 | 88 | 0 | 13 | 0 | 320 | 0 | 404 | 0 | 30 | 155 | 20 | 0 | 23 | 30 | 0 | 15 | 158 | 0 | 35 | 19 | 82 | 0 | 7.68 | 0 | 4433.73 | 889 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 801 | 0 | 840.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.82 | 22 | 0 | 0 | 9.4 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.91 | 0 | 54 | 0 | 6 | 0 | 0 | 0 | 0 | 1.1 | 30 | 0.08 | 0 | 0 | 115 | 220 | 0 | 304 | 590 | 0 | 4748.91 | 9182.64 | 100.25
17:00 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 282 | 17.5 | 0 | 31 | 0 | 15 | 4 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 17 | 28 | 8 | 0 | 0 | 7 | 32 | 0 | 0 | 13 | 0 | 0 | 0 | 26 | 12 | 0 | 86 | 4 | 11 | 350 | 15 | 0 | 4 | 3 | 22 | 188 | 0 | 0 | 0 | 570 | 0 | 51 | 20 | 26 | 393 | 0 | 0 | 22 | 180 | 37 | 4 | 0 | 12 | 0 | 11 | 17 | 92 | 0 | 1 | 0 | 315 | 0 | 371 | 0 | 30 | 158 | 20 | 0 | 81 | 30 | 0 | 15 | 155 | 5 | 56 | 19 | 82 | 0 | 0.19 | 0 | 4736.69 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 895 | 0 | 984.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0 | 0 | 0 | 0.56 | 194 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0.05 | 0 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 0 | 115 | 220 | 0 | 304 | 680 | 0 | 5057.32 | 9794.01 | 100.24
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 323 | 17.5 | 0 | 70 | 0 | 95 | 25 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 0 | 26 | 32 | 0 | 0 | 21 | 0 | 0 | 0 | 38 | 38 | 0 | 86 | 30 | 8 | 350 | 15 | 0 | 18 | 8 | 100 | 187 | 0 | 0 | 0 | 585 | 0 | 51 | 56 | 85 | 393 | 0 | 0 | 47 | 187 | 33 | 17 | 0 | 109 | 0 | 16 | 17 | 92 | 0 | 0 | 0 | 315 | 0 | 393 | 0 | 30 | 159 | 20 | 0 | 81 | 30 | 0 | 15 | 155 | 17 | 59 | 19 | 82 | 0 | 0 | 0 | 5355.5 | 886 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 1283.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 502 | 870 | 0 | 6031.49 | 11386.99 | 100.24
19:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 316 | 17.5 | 0 | 70 | 0 | 45 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 28.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 38 | 0 | 86 | 0 | 19 | 350 | 0 | 0 | 19 | 0 | 34 | 187 | 0 | 0 | 0 | 585 | 0 | 51 | 10 | 130 | 393 | 0 | 0 | 47 | 186 | 38 | 0 | 108 | 100 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 343 | 0 | 30 | 147 | 20 | 0 | 81 | 30 | 0 | 15 | 155 | 0 | 59 | 19 | 84 | 0 | 0 | 0 | 5064 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 1429.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 54 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 448 | 940 | 0 | 6023.35 | 11087.35 | 100.23
19:30 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 317 | 17.5 | 0 | 70 | 0 | 45 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 28.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 38 | 0 | 86 | 0 | 17 | 350 | 0 | 0 | 19 | 0 | 30 | 181 | 0 | 0 | 0 | 585 | 0 | 51 | 0 | 135 | 393 | 0 | 0 | 47 | 183 | 38 | 0 | 108 | 92 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 333 | 0 | 30 | 144 | 20 | 0 | 81 | 30 | 0 | 15 | 155 | 0 | 59 | 19 | 86 | 0 | 0 | 0 | 4994 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 1424.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 54 | 50 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 401 | 960 | 0 | 5947.99 | 10941.99
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 315 | 0 | 0 | 50 | 0 | 45 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 28.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 38 | 0 | 86 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 586 | 0 | 51 | 0 | 142 | 393 | 0 | 0 | 47 | 189 | 38 | 0 | 108 | 51 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 335 | 0 | 30 | 149 | 20 | 0 | 81 | 30 | 0 | 15 | 155 | 0 | 59 | 19 | 90 | 0 | 0 | 0 | 4888.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 1430.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 353 | 970 | 0 | 5871.94 | 10760.44 | 100.23
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 28.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 23 | 350 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 585 | 0 | 51 | 0 | 81 | 340 | 0 | 0 | 47 | 204 | 37 | 0 | 109 | 0 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 315 | 0 | 365 | 0 | 30 | 157 | 20 | 0 | 81 | 30 | 0 | 15 | 155 | 0 | 35 | 0 | 91 | 0 | 0 | 0 | 4553.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 353 | 960 | 0 | 5949 | 10502.5 | 100.22
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 26 | 350 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 582 | 0 | 51 | 0 | 35 | 340 | 0 | 0 | 48 | 197 | 32 | 0 | 110 | 0 | 0 | 20 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 354 | 0 | 30 | 153 | 20 | 0 | 81 | 30 | 0 | 16 | 155 | 0 | 35 | 0 | 91 | 0 | 0 | 0 | 4435 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071 | 0 | 1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 305 | 915 | 0 | 5755 | 10190 | 100.22
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 26 | 350 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 534 | 0 | 51 | 0 | 8 | 355 | 0 | 0 | 45 | 194 | 35 | 0 | 111 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 390 | 0 | 30 | 146 | 21 | 0 | 33 | 30 | 0 | 15 | 156 | 0 | 35 | 0 | 86 | 0 | 0 | 0 | 4353 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 923 | 0 | 1332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 305 | 895 | 0 | 5437 | 9790 | 100.21
Total KWH | 0 | 78720 | 169440 | 0 | 0 | 0 | 0 | 0 | 8593200 | 0 | 7613680 | 104400 | 0 | 384192 | 0 | 245640 | 37965 | 133953 | 417600 | 0 | 0 | 0 | 0 | 0 | 73180 | 7275530 | 0 | 0 | 150855 | 20400 | 460200 | 99720 | 0 | 1048636.36 | 52691 | 55200 | 0 | 0 | 133920 | 0 | 0 | 0 | 71040 | 169920 | 17879 | 2051160 | 71930 | 421920 | 6669090.91 | 21745 | 0 | 58080 | 15134.4 | 267636 | 4586033 | 0 | 0 | 0 | 11209089 | 122175 | 889544 | 128800 | 986909 | 8326500 | 0 | 0 | 592320 | 4667000 | 705456 | 37440 | 560294 | 430560 | 0 | 367930 | 28500 | 1937280 | 0 | 389536 | 0 | 7537500 | 0 | 8809000 | 0 | 710280 | 3695891 | 416208 | 0 | 1157760 | 634368 | 0 | 358000 | 4321000 | 27720 | 714000 | 266400 | 2239680 | 11300 | 254250 | 0 | 104103380.67 | 19936727 | 6509664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466560 | 21076360 | 0 | 23792727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337776 | 614930 | 0 | 0 | 316496 | 4232000 | 0 | 0 | 0 | 0 | 0 | 8826981 | 0 | 24900 | 0 | 1254545 | 235225 | 178593 | 149337 | 0 | 0 | 0 | 33805.68 | 912240 | 2557 | 0 | 0 | 2612000 | 4847010 | 0 | 7561368 | 16634181.82 | 0 | 120555983.5 | 224659364.17

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9516.34 | MW | 12:00 Hr. | Energy Generated |  |  | 224.6594 |  | MKWHr.
| Day Peak Demand |  |  | 9516.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.092 |  | MKWHr.
| Evening Peak Generation |  |  | 11386.99 | MW | 18:00 Hr. | Energy Demand |  |  | 224.7514 |  | MKWHr.
| Evening Peak Demand |  |  | 11386.99 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 7549.16 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 756.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 11386.99 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.314 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.091 | 0 | 1.6655 | 0 | 0 | 0.15085 | 0 | 0 | 26.9073 | Gas | 104.1022 | Gas | 369059500.2812
| Chattogram Zone |  |  | 5.008 | 17.8782 | 0.78338 | 0 | 2.0512 | 0.14005 | 0 | 0.13392 | 25.9946 | Coal | 64.4046 | Coal | 414982552.6213
| Cumilla Zone |  |  | 17.096 | 0 | 0.6253 | 0 | 0 | 0.38954 | 1.9373 | 0 | 20.0481 | HFO | 4.4668 | HFO | 75700433.438
| Mymensingh Zone |  |  | 2.2397 | 0 | 1.0081 | 0 | 0 | 0.26555 | 0 | 0 | 3.5133 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.64 | Hydro | 2.0512 | Hydro | 205116
| Khulna Zone |  |  | 6.5097 | 21.0764 | 0 | 0 | 0 | 0.46656 | 19.9367 | 0 | 47.9893 | Solar | 3.8339 | Solar | 61234267.3928
| Barishal Zone |  |  | 7.459 | 24.1955 | 0 | 0 | 0 | 0.002557 | 0 | 0 | 31.6571 | Import | 45.6667 | Import | 270691896.84
| Rajshahi Zone |  |  | 13.059 | 0 | 0 | 0 | 0 | 1.2941 | 23.7927 | 0 | 38.1458 | Wind | 0.13392 | Wind | 1969963.2
| Rangpur Zone |  |  | 0 | 1.2545 | 0.38456 | 0 | 0 | 1.1246 | 0 | 0 | 2.7637
| Total |  |  | 104.1022 | 64.4046 | 4.4668 | 0 | 2.0512 | 3.8339 | 45.6667 | 0.13392 | 224.6594
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 369059500.2812 |  | Hydro | 205116
|  |  |  | Coal | 414982552.6213 |  | Solar | 61234267.3928
|  |  |  | HFO | 75700433.438 |  | Import | 270691896.84
|  |  |  | HSD | 0 |  | Wind | 1969963.2
[5 empty] | Total: | 119,38,43,729 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.9367 | Peak Hr Flow | 886.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50209854.57 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.7927 | Peak Hr Flow | 1283.49 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2556 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.9373 | Peak Hr Flow | 92.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2788 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.6667 | Peak Hr Flow | 2261.49 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4269
|  |  |  | Chattogram |  | 0 |  | 1260
|  |  |  | Cumilla |  | 0 |  | 959
|  |  |  | Mymensingh |  | 0 |  | 887
|  |  |  | Sylhet |  | 0 |  | 430
|  |  |  | Khulna |  | 0 |  | 1275
|  |  |  | Barishal |  | 0 |  | 316
|  |  |  | Rajshahi |  | 0 |  | 989
|  |  |  | Rangpur |  | 0 |  | 758
|  |  |  | Total |  | 0 |  | 11143
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:14 | 12:27 | Narail 132/33kV S/S Auxiliary TR 1 LT Scheduled S/D Due to Annual Maintenance of 132 kV
Buber Section-1
| 08:14 | 12:26 | Narail 132/33kV S/S Auxiliary TR 1 HT Scheduled S/D Due to Annual Maintenance of 132 kV
Buber Section-1
| 08:15 |  | Bropukuria - P.Sadipur 230kv Ckt 01-S/D.
| 08:18 | 16:33 | Bhulta 132/33kV S/S GT1 LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 50.0MW load
interrup.
| 08:20 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to Annual
Maintenance. and from Bogura 230/132kV end Due to Annual Maintenance Work
| 08:22 | 15:51 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual maintenance
| 08:25 | 16:22 | Rahanpur 400/132kV S/S AT-01 LT Scheduled S/D
| 08:26 | 16:22 | Rahanpur 400/132kV S/S AT-01 HT Scheduled S/D
| 08:30 | 15:49 | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to Annual maintenance work
| 08:32 | 15:50 | Rajbari 132/33kV S/S Bheramara-2 Scheduled S/D Due to Annual maintenance work
| 08:33 | 15:57 | Baghabari-Ishurdi 230 kV Ckt-2 Scheduled S/D from Ishurdi 230/132kV end Due to Due to
Annual Maintenance.
| 08:34 | 12:16 | Narail 132/33kV S/S 132 kV Busbar Scheduled S/D Due to Annual Maintenance of 132 kV Buber
Section-1
| 08:35 | 17:16 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance by PBS | [7 empty] | 10.0MW load
interrup.
| 08:35 | 17:32 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Gopalganj 400/132kVend.
| 08:36 | 16:34 | Bhulta 132/33kV S/S GT1 HT Scheduled S/D Due to Annual Maintanance | [7 empty] | 50.0MW load
interrup.
| 08:36 | 15:51 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to Annual
maintenance
| 08:37 | 14:55 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end Due to
Kishoreganj s/s end annual maintenance
| 08:38 | 14:54 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to
Annual maintenance
| 08:40 | 13:41 | Narshingdi 132/33kV S/S T-4 LT Scheduled S/D Due to Annual Maintenance
| 08:40 | 13:45 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to Annual Maintenance
| 08:44 | 17:14 | Amnura-Rajshahi 132kV Ckt-1 Scheduled S/D from Amnura 132/33kV end Due to Annual
Maintenance, Clearance ALDC, Bogura
| 08:44 | 17:15 | Amnura 132/33kV S/S Amnura - 100MW PPP Scheduled S/D Due to Annual Maintenance, Clearance
ALDC, Bogura
| 08:44 | 17:14 | Amnura 132/33kV S/S Bus-2 Scheduled S/D Due to Annual Maintenance, Clearance ALDC, Bogura
| 08:45 |  | Niamotpur 132 kv Bus 1 S/D.
| 08:47 | 17:15 | Amnura 132/33kV S/S T-1 (406T) HT Scheduled S/D Due to Annual Maintenance, Clearance
ALDC, Bogura
| 08:47 | 17:04 | Amnura 132/33kV S/S T-2 (416T) HT Scheduled S/D Due to Annual Maintenance, Clearance
ALDC, Bogura
| 08:51 | 15:59 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Scheduled S/D Due to Annual
Maintenance
| 08:52 | 15:58 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Annual
Maintenance
| 08:53 | 15:59 | Baghabari-Ishurdi 230 kV Ckt-2 Scheduled S/D from Baghabari 230/132kV end Due to Annual
Maintenance
| 08:59 | 14:37 | Kaliakoir 400/230/132kV S/S 132kV Bus 1 Forced S/D Due to maintenance
| 09:00 | 16:43 | Amnura-Chapainawabganj-132kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to S/D
Taken by Amnura grid. and from Amnura 132/33kV end Due to Annual Maintenance, Clearance
ALDC, Bogura
| 09:01 | 16:44 | Amnura 132/33kV S/S Bus-33KV Scheduled S/D Due to Annual Maintenance, Clearance ALDC,
Bogura
| 09:01 | 16:44 | Amnura 132/33kV S/S T-3 (426T) HT Scheduled S/D Due to Annual Maintenance, Clearance
ALDC, Bogura
| 09:02 | 18:02 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
| 09:02 | 16:43 | Amnura 132/33kV S/S Bus-1 Scheduled S/D Due to Annual Maintenance, Clearance ALDC, Bogura
| 09:11 | 18:01 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-01 Scheduled S/D Due to Line checking
| 09:11 | 17:12 | Hathazari 230/132/33kV S/S T-02 HT Scheduled S/D Due to Annual Maintenance
| 09:13 | 17:05 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar
132/33kV end Due to Annual Maintenance. and from Keranigonj 230/132/33kV end Due to
Annual maintenance work
| 09:18 | 15:36 | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Satkhira 132/33kV end Due to Yearly
Maintenance Work. and from Khulna(S) 230/132kV end Due to Annual Maintenance work
| 09:27 | 10:44 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Forced S/D Due to SPMD work at Amtoli end.
| 09:30 | 15:18 | Kodda 132/33kV S/S Tr-1 (406T) LT Scheduled S/D Due to Maintenance Wirk
| 09:30 | 15:18 | Kodda 132/33kV S/S Tr-1 (406T) HT Scheduled S/D Due to Maintenance
| 09:31 | 16:14 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance
|  | 09:38 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 09:39 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
| 09:40 |  | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end.
| 09:40 |  | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end.
| 09:41 | 17:01 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to Annual maintenance
| 09:41 | 17:01 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to Annual maintenance
| 09:41 | 17:01 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to Annual maintenance
| 09:41 | 17:01 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to Annual Maintenance
| 09:46 | 15:49 | Jashore 132/33kV S/S JH-1(L2) Scheduled S/D Due to Annual Maintenance
| 09:47 | 15:49 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to Annual Maintenance.
| 09:53 | 17:12 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to Due to 33kV bus maintenance by
Nilphamari PBS
| 09:53 | 17:11 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to Due to 33kV bus maintenance by
Nilphamari PBS
| 10:00 |  | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Due to
earthquake fault
| 10:00 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
|  | 10:08 | Saidpur 132/33kV S/S BUS B is restored.
| 10:10 | 18:22 | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to From Other End.
|  | 10:25 | Saidpur 132/33kV S/S TR-5 (434T) HT is restored.
|  | 10:26 | Saidpur 132/33kV S/S TR-5 (434T) LT is restored.
| 10:37 | 17:10 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Scheduled shutdown
| 10:44 | 16:20 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Control cable change
| 10:47 | 16:19 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Control cable change
| 10:55 | 11:40 | Saidpur 132/33kV S/S BUS A Project Work S/D Due to CCCE Project work.
| 10:55 | 11:40 | Saidpur 132/33kV S/S BUS A Project Work S/D Due to CCCE Project work.
| 11:16 | 17:01 | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Rampura 230/132kV end Due to Bhulta 230KV
CKt-4 shutdown due to OPGW install for Bhulta-Rupshi 132kV Transmission line by OFCN.
Bhulta SS taken the shutdown by NLDC in request of OFCN for safety puspose. and from
Bhulta 400/230kV end Due to For OPGW Installation.
| 11:20 | 16:16 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 Scheduled S/D
| 12:00 |  | Day Peak Generation: 9513 MW.
| 12:15 | 14:01 | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Wz maintenance work
| 12:16 | 13:59 | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to Wz maintenance work
|  | 12:25 | Narail 132/33kV S/S TR1 (403-T) HT is restored.
|  | 12:26 | Narail 132/33kV S/S TR1 (403-T) LT is restored.
| 12:50 | 13:05 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Tripped showing Simens 7SJ62 relays Due to | [7 empty] | 12.0MW load
|  |  | টি-১ ৩৩কেভি বাসে সংযুক্ত Chapai ৩৩ কেভি পবিস ফিডারে O/C ,E/F এর কারণে গ্রিড এর 33kV T-1 | [7 empty] | interrup.
transformer ট্রিপ করে।
|  | 13:52 | Halishahar-Khulshi 132kV Ckt-2 is restored.
| 14:06 |  | Barapukuria[ 14:06 ]---P.sadipur [ 14:12 ] 230 KV Ckt -1 Syn and Bus-A Energized [First
Time], P.sadipur 230 KV Bus Coupler Breaker Closed [14:17] [First Time Charged],
P.sadipur [ 14:23 ]------Barapukuria [Last Ganty] 230 KV Ckt -2 Syn with Bus-B [First
Time].
| 14:52 |  | Niamotpur 132 kv Bus-1 Syn
|  | 15:06 | Chhatak 132/33kV S/S T-2 LT is restored.
|  | 15:06 | Chhatak 132/33kV S/S T-2 HT is restored.
|  | 15:32 | Chandpur 132/33kV S/S 100MW(GT) Power Plant Incomer (T4) is restored.
| 16:39 |  | Unique Meghnaghat Power 584 MW CCPP GT was shut down.
| 16:39 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
|  | 16:46 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 16:46 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
| 16:49 |  | Purboshadipur 230 kV Bus-1 and Bus-2 were charged at 14:12 hrs and 14:17 hrs respectively
for the first time through the Barapukuria–Purboshadipur 230 kV
Ckt-1. Barapukuria–Purboshadipur 230 kV Ckt-2 was charged from Purboshadipur end at
14:23 hrs. Also, 230/132 kV T-1 and T-2 transformers were charged from 230 kV end at
16:39 hrs and 16:49 hrs respectively for the first time.
|  | 16:49 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
| 16:50 |  | 16:39--->Purbasadipur 230/132 kV T1-Syn[230 KV Side, First Time],
16:49--->Purbasadipur 230/132 kV T2-Syn[230 KV Side, First Time]
|  | 16:57 | Meghnaghat 230/132kV S/S Bus2 is restored.
|  | 17:13 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT is restored.
|  | 17:14 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT is restored.
|  | 17:15 | KSRM 132/33kV S/S Transformer-01 HT is restored.
| 17:15 | 17:28 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent protection relay & Earth
fault. relays Due to 33kV Nawabganj feeder fault
| 18:00 |  | Evening Peak Generation: 11369 MW.
| 18:34 | 19:29 | Kabirpur -Kodda 132kV Ckt-1 Forced S/D from Kabirpur 132/33kV end Due to Poly removing
of Kabirpur-kadda ckt-1(Tower no 26)
| 05:00 |  | Minimum Generation: 7868 MW.
| 06:14 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Project Work S/D from Khulna(S) 230/132kV end Due to
Project Work at Central SS end. and from Khulna (C) end Due to Work for project
| 07:00 |  | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D
| 07:01 |  | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance.
| 07:02 |  | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance.
| 07:03 |  | Rajbari 132/33kV S/S Bheramara-2 Scheduled S/D
| 07:13 |  | Joydebpur 132/33kV S/S GT-2 HT Scheduled S/D
| 07:17 |  | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Scheduled S/D Due to Annual maintenance
work (Bay Equipment's)
| 07:23 |  | Meghnaghat 400/230kV S/S 230kV BUS Section 02 Scheduled S/D Due to 230 kV Bus- 01
shutdown instructed by NLDC.
| 07:32 |  | Meghnaghat 230/132kV S/S Bus2 Project Work S/D Due to Isolator upgradation.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 363 | 8593200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 25 | 37965 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7275530 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 104400 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 133953 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 73180 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 460200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 8 | 99720 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 169440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 245640 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 384192 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 78720 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 417600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 150855 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 1048636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 323 | 7613680 | FGMO
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 20400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1335.5 | 26907311.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 15134.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 122175 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 58080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2051160 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 187 | 4586033 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 100 | 267636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 71040 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 421920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 55200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 30 | 71930 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 169920 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 26 | 52691 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 15 | 21745 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 585 | 11209089 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 21 | 133920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 350 | 6669090.91 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1542 | 25994643.31
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 187 | 4667000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8326500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 705456 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 592320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 85 | 986909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 889544 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 56 | 128800 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 560294 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 109 | 430560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 92 | 1937280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 367930 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 28500 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 37440 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 389536 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1103 | 20048069
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 82 | 2239680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 266400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 714000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 254250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 27720 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 177 | 3513350
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 710280 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 159 | 3695891 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 634368 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1157760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 155 | 4321000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 358000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 416208 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7537500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 393 | 8809000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1198 | 27640007
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 886 | 19936727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6509664 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 466560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1088 | 21076360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2224 | 47989311
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 502 | 7561368 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2612000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 870 | 16634181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 4847010 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2557 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1707 | 31657116.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 337776 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 189 | 4232000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8826981 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24900 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1283.49 | 23792727 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 316496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 614930 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1886.49 | 38145810
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1254545 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 149337 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33805.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 235225 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 178593 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 912240 | -
Rangpur Area Total |  |  |  |  | 950 | 214 | 2763745.68
Eastern Grid Total |  |  |  |  | 17383.855 | 5355.5 | 104103380.67
Western Grid Total |  |  |  |  | 10821.56 | 6031.49 | 120555983.5
National Grid Total |  |  |  |  | 28205.415 | 11386.99 | 224659364.17
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7805.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3337.1 | MW
i) Dhaka area |  |  | 4268.65 |  | MW | i) Khulna area |  |  |  | 1274.8 | MW
ii) Chattogram area |  |  | 1260.4 |  | MW | ii) Barishal area |  |  |  | 315.5 | MW
iii) Cumilla area |  |  | 959.42 |  | MW | iii) Rajshahi area |  |  |  | 988.8 | MW
iv) Mymensingh area |  |  | 887 |  | MW | iv) Rangpur area |  |  |  | 758 | MW
v) Sylhet area |  |  | 430 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11142.57 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 19:30 | 67 | Hathazari | 59 | 18:00 | 133 | Niamatpur | 43 | 18:00
2 | AKSML | 162.8 | 12:00 | 68 | Ishurdi | 53 | 19:30 | 134 | Noapara | 40 | 18:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jaldhaka | 62 | 18:00 | 135 | PHP | 9 | 16:00
4 | Agargaon | 92 | 13:00 | 70 | Jamalpur | 96 | 18:00 | 136 | Pabna | 68 | 18:00
5 | Agrabad | 78 | 18:00 | 71 | Jashore | 97 | 13:00 | 137 | Palashbari | 80 | 18:00
6 | Amnura | 18 | 18:00 | 72 | Jhenaidah | 94 | 18:00 | 138 | Panchagarh | 42 | 18:00
7 | Ashuganj | 63 | 13:00 | 73 | Joydebpur | 106 | 12:00 | 139 | Patiya | 7 | 21:00
8 | BSRM | 199 | 04:00 | 74 | Joypurhat | 44 | 18:00 | 140 | Patuakhali | 43 | 20:00
9 | Bagerhat | 65 | 18:00 | 75 | Juldah | 12 | 11:00 | 141 | Payra | 24 | 21:00
10 | Bajitpur | 60 | 18:30 | 76 | KSRM | 19 | 21:00 | 142 | Postogola | 54 | 13:00
11 | Bakulia | 64 | 18:00 | 77 | Kabirpur | 187 | 16:00 | 143 | Purbachal | 28 | 13:00
12 | Banani | 28.6 | 14:00 | 78 | Kachua | 57 | 18:30 | 144 | Purbasadipur | 102 | 18:00
13 | Bangabhaban | 7 | 10:00 | 79 | Kallyanpur | 75 | 13:00 | 145 | Rahanpur | 22 | 18:00
14 | Barapukuria | 49 | 18:00 | 80 | Kalurghat | 42 | 12:00 | 146 | Rahim | 22 | 16:00
15 | Barguna | 14 | 18:30 | 81 | Kamrangirchar | 64 | 18:30 | 147 | Rajbari | 63 | 18:00
16 | Barishal | 88 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 104 | 18:00
17 | Barishal-230 | 64 | 18:00 | 83 | Kasba | 22 | 14:00 | 149 | Rajshahi | 66 | 18:00
18 | Baroaulia | 56 | 12:00 | 84 | Kazla | 91 | 13:00 | 150 | Rajshahi-230 | 70 | 13:00
19 | Baroirhat | 48 | 18:00 | 85 | Keranigonj | 66 | 19:00 | 151 | Ramganj | 76 | 13:00
20 | Bashundhara | 135 | 18:00 | 86 | Khagrachori | 22 | 18:30 | 152 | Rampur | 32 | 18:00
21 | BashundharaCement | 7 | 18:00 | 87 | Khulna | 47 | 19:00 | 153 | Rangamati | 14 | 18:00
22 | Beanibazar | 52 | 18:00 | 88 | Khulshi | 158 | 14:00 | 154 | Rangpur | 105 | 18:00
23 | Benapole | 42 | 18:00 | 89 | Kishoreganj | 88 | 18:00 | 155 | Ruppur | 2.2 | 15:00
24 | Bhaluka | 130 | 17:00 | 90 | Kodda | 261 | 18:00 | 156 | SSM | 1 | 22:00
25 | Bhandaria | 39 | 20:00 | 91 | Kulaura | 31 | 18:00 | 157 | Saidpur | 89 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 48 | 18:00 | 158 | Satkhira | 88 | 18:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | Kushtia | 108 | 18:00 | 159 | Satmasjid | 80 | 18:00
28 | Bhulta | 185 | 18:30 | 94 | Laksam | 26 | 13:00 | 160 | Savar | 170 | 09:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 19 | 20:00 | 161 | SevenRings | 13.16 | 20:00
30 | Bogura | 116 | 18:00 | 96 | Lalbag | 60 | 18:00 | 162 | ShahCement | 25 | 23:00
31 | Borhanuddin | 63 | 20:00 | 97 | Lalmonirhat | 44 | 18:00 | 163 | Shahjadpur | 53 | 18:00
32 | Brahmanbaria | 87 | 19:00 | 98 | MI_Cement | 15.3 | 00:00 | 164 | Shahjibazar | 83 | 18:00
33 | Cantonment | 95 | 14:00 | 99 | Madanganj | 36 | 18:00 | 165 | Shahmirpur | 50 | 18:00
34 | Chandina | 8.47 | 17:00 | 100 | Madaripur | 69 | 20:00 | 166 | Shariatpur | 56 | 20:00
35 | Chandpur | 52 | 18:30 | 101 | Madartek | 68 | 13:00 | 167 | Sherpur | 100 | 18:00
36 | Chandraghona | 26 | 18:00 | 102 | Madunaghat | 39 | 18:00 | 168 | Shikalbaha | 19 | 12:00
37 | Chapai | 47.5 | 03:00 | 103 | Magura | 51 | 18:00 | 169 | Shitalakhya | 64.7 | 12:00
38 | Charsaidpur | 26 | 00:00 | 104 | Mahasthangarh | 48 | 18:00 | 170 | Sholosohor | 39 | 12:00
39 | Chauddagram | 49 | 13:00 | 105 | Maijdee | 26 | 18:00 | 171 | Shyampur | 129 | 10:00
40 | Chhatak | 22 | 18:00 | 106 | Manikganj | 88 | 18:00 | 172 | Siddhirganj | 103 | 12:00
41 | Chowmuhani | 109 | 18:00 | 107 | Maniknagar | 44 | 13:00 | 173 | Sirajganj | 78 | 18:00
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 40 | 18:00 | 174 | Sonargaon | 110 | 18:00
43 | Coxsbazar | 109 | 18:00 | 109 | Matuail | 60 | 12:00 | 175 | Sreemongol | 57 | 18:00
44 | Cumilla(N) | 83 | 19:00 | 110 | Metrorail_Motijheel | 17 | 17:00 | 176 | Sreepur | 87 | 18:00
45 | Cumilla(S) | 120 | 18:30 | 111 | Metrorail_Uttara | 6 | 18:00 | 177 | Srinagar | 30.6 | 14:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 90 | 12:00 | 178 | Sunamganj | 40 | 18:00
47 | Daudkandi | 108 | 18:00 | 113 | Mirpur | 118 | 18:00 | 179 | Sylhet | 34 | 18:00
48 | DhakaUniversity | 54 | 13:00 | 114 | Mirsorai | 9 | 10:00 | 180 | Sylhet-132 | 86 | 18:00
49 | Dhamrai | 106 | 09:00 | 115 | Mirzapur | 37 | 18:00 | 181 | TK | 24 | 18:00
50 | Dhanmondi | 91.6 | 14:00 | 116 | Mithapukur | 44 | 18:00 | 182 | Tangail | 132 | 18:30
51 | Dohazari | 75 | 19:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 15 | 07:00
52 | Faridpur | 115 | 18:30 | 118 | Mogbazar | 66.1 | 12:00 | 184 | Tasnim | 28 | 00:00
53 | Fatullah | 103 | 12:00 | 119 | Mongla | 27 | 18:00 | 185 | Thakurgaon | 78 | 18:00
54 | Fenchuganj | 25 | 18:00 | 120 | Motijheel | 30 | 13:00 | 186 | Tongi | 102 | 11:00
55 | Feni | 74 | 18:00 | 121 | Muktagacha | 28 | 17:00 | 187 | Ullahpara | 27 | 18:00
56 | GPH | 94 | 02:00 | 122 | Munshiganj | 74 | 13:00 | 188 | Ullon | 53 | 14:00
57 | Ghatail | 60 | 18:00 | 123 | Muradnagar | 25 | 18:00 | 189 | Uttara | 63 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 130 | 18:00 | 190 | UttaraNew | 27 | 13:00
59 | Ghorashal-230 | 78 | 19:00 | 125 | Naogaon | 77 | 13:00 | 191 | Zigatola | 55 | 13:00
60 | Goalpara | 24 | 13:00 | 126 | Narail | 42 | 18:30
61 | Gollamari | 76 | 13:00 | 127 | Narinda | 58 | 13:00
62 | Gopalganj | 79 | 18:00 | 128 | Narshingdi | 155 | 19:00
63 | Gulshan | 78 | 13:00 | 129 | Natore | 100 | 18:00
64 | Halishahar | 60 | 12:00 | 130 | Nawabganj | 31.2 | 19:30
65 | HaripurSBU | 134 | 09:00 | 131 | Netrakona | 99 | 18:00
66 | Hasnabad | 70 | 13:00 | 132 | New | 60 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9036.16 | 0 |  | 9036.16
1:00 | 8491.68 | 0 |  | 8491.68
2:00 | 8242.4 | 0 |  | 8242.4
3:00 | 7704.57 | 0 |  | 7704.57
4:00 | 7632.56 | 0 |  | 7632.56
5:00 | 7549.16 | 0 |  | 7549.16
6:00 | 7849.9 | 0 |  | 7849.9
7:00 | 8631.56 | 0 |  | 8631.56
8:00 | 8961.49 | 0 |  | 8961.49
9:00 | 8818.04 | 0 |  | 8818.04
10:00 | 8513.34 | 0 |  | 8513.34
11:00 | 8848.41 | 0 |  | 8848.41
12:00 | 9516.34 | 0 |  | 9516.34
13:00 | 9781.07 | 26 |  | 9808.07
14:00 | 9593.13 | 0 |  | 9593.13
15:00 | 9360.95 | 22 |  | 9383.95
16:00 | 9182.64 | 21 |  | 9204.59
17:00 | 9794.01 | 23 |  | 9818.05
18:00 | 11386.99 | 0 |  | 11386.99
19:00 | 11087.35 | 0 |  | 11087.35
19:30 | 10941.99 | 0 |  | 10941.99
20:00 | 10760.44 | 0 |  | 10760.44
21:00 | 10502.5 | 0 |  | 10502.5
22:00 | 10190 | 0 |  | 10190
23:00 | 9790 | 0 |  | 9790
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4155.5 | 4880.66 | 9036.16 | DAILY GENERATION CURVE
00:30 | 4021.5 | 4742.42 | 8763.92
01:00 | 3887.5 | 4604.18 | 8491.68 | 22-11-2025
01:30 | 3882 | 4485.04 | 8367.04
02:00 | 3876.5 | 4365.9 | 8242.4
02:30 | 3697 | 4276.485 | 7973.485
03:00 | 3517.5 | 4187.07 | 7704.57
03:30 | 3484.5 | 4184.065 | 7668.565
04:00 | 3451.5 | 4181.06 | 7632.56
04:30 | 3443.5 | 4147.36 | 7590.86
05:00 | 3435.5 | 4113.66 | 7549.16
05:30 | 3548 | 4151.53 | 7699.53
06:00 | 3660.5 | 4189.4 | 7849.9
06:30 | 3841.75 | 4398.98 | 8240.73
07:00 | 4023 | 4608.56 | 8631.56
07:30 | 4113.895 | 4682.63 | 8796.525
08:00 | 4204.79 | 4756.7 | 8961.49
08:30 | 4108.875 | 4780.89 | 8889.765
09:00 | 4012.96 | 4805.08 | 8818.04
09:30 | 3924.765 | 4740.925 | 8665.69
10:00 | 3836.57 | 4676.77 | 8513.34
10:30 | 3895.225 | 4785.65 | 8680.875
11:00 | 3953.88 | 4894.53 | 8848.41
11:30 | 4194.03 | 4988.345 | 9182.375
12:00 | 4434.18 | 5082.16 | 9516.34
12:30 | 4539.525 | 5109.18 | 9648.705
13:00 | 4644.87 | 5136.2 | 9781.07
13:30 | 4616.78 | 5070.32 | 9687.1
14:00 | 4588.69 | 5004.44 | 9593.13
14:30 | 4559.155 | 4917.885 | 9477.04
15:00 | 4529.62 | 4831.33 | 9360.95
15:30 | 4481.675 | 4790.12 | 9271.795
16:00 | 4433.73 | 4748.91 | 9182.64
16:30 | 4585.21 | 4903.115 | 9488.325
17:00 | 4736.69 | 5057.32 | 9794.01
17:30 | 5046.095 | 5544.405 | 10590.5
18:00 | 5355.5 | 6031.49 | 11386.99
18:30 | 5209.75 | 6027.42 | 11237.17
19:00 | 5064 | 6023.35 | 11087.35
19:30 | 4994 | 5947.99 | 10941.99
20:00 | 4888.5 | 5871.94 | 10760.44
20:30 | 4721 | 5910.47 | 10631.47 |  | Executive Engineer
21:00 | 4553.5 | 5949 | 10502.5 |  | Network Operation Division
21:30 | 4494.25 | 5852 | 10346.25
22:00 | 4435 | 5755 | 10190
22:30 | 4394 | 5596 | 9990
23:00 | 4353 | 5437 | 9790

## En-Curve
QF-LDC-12
Date | 22-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3053 | 1176.5 | 888 | 0 | 78 | 919.66 | 86 | 2811 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3012.5 | 1163 | 853.5 | 0 | 76 | 885.42 | 86 | 2667.5 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22-11-2025
01:00 | 2972 | 1149.5 | 819 | 0 | 74 | 851.18 | 86 | 2524 | 0 | 0 | 16 | 0 | 0 | 0 | 0
01:30 | 2950 | 1217.5 | 745.5 | 0 | 69 | 842.04 | 86 | 2445 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | Energy Generated | 224.6594 |  | MKWHr
02:00 | 2928 | 1285.5 | 672 | 0 | 64 | 832.9 | 86 | 2366 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | Energy not Served | 0.092 |  | MKWHr
02:30 | 2905 | 1163 | 672 | 0 | 66 | 835.985 | 86 | 2241.5 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | Total Energy Requirement | 224.7514 |  | MKWHr
03:00 | 2882 | 1040.5 | 672 | 0 | 68 | 839.07 | 86 | 2117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2840 | 1036.5 | 672.5 | 0 | 68 | 843.565 | 86 | 2122 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2798 | 1032.5 | 673 | 0 | 68 | 848.06 | 86 | 2127 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2768 | 1030 | 673 | 0 | 68 | 841.86 | 86 | 2124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2738 | 1027.5 | 673 | 0 | 68 | 835.66 | 86 | 2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2834 | 1074 | 672.5 | 0 | 69 | 836.03 | 86 | 2128 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2930 | 1120.5 | 672 | 0 | 70 | 836.4 | 86 | 2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 3050 | 1168.75 | 767 | 0 | 70 | 843.2 | 86 | 2224.5 | 21.28 | 0 | 9.5 | 0 | 0 | 0.5 | 0
07:00 | 3170 | 1217 | 862 | 0 | 70 | 850 | 86 | 2314 | 42.56 | 0 | 19 | 0 | 0 | 1 | 0
07:30 | 3169.5 | 1263.5 | 847 | 0 | 73 | 841.49 | 86 | 2344.5 | 122.535 | 3.5 | 42.5 | 0 | 0 | 3 | 0
08:00 | 3169 | 1310 | 832 | 0 | 76 | 832.98 | 86 | 2375 | 202.51 | 7 | 66 | 0 | 0 | 5 | 0
08:30 | 3075 | 1233.5 | 832 | 0 | 76 | 831.045 | 86 | 2354.5 | 307.22 | 20.5 | 71 | 0 | 0 | 3 | 0
09:00 | 2981 | 1157 | 832 | 0 | 76 | 829.11 | 86 | 2334 | 411.93 | 34 | 76 | 0 | 0 | 1 | 0
09:30 | 2861.5 | 1111 | 836.5 | 0 | 78 | 830.825 | 86 | 2287 | 474.365 | 20 | 80 | 0 | 0 | 0.5 | 0
10:00 | 2742 | 1065 | 841 | 0 | 80 | 832.54 | 86 | 2240 | 536.8 | 6 | 84 | 0 | 0 | 0 | 0
10:30 | 2829 | 1079.5 | 841.5 | 0 | 82 | 831.935 | 86 | 2247.5 | 574.44 | 11 | 93 | 0 | 0 | 5 | 0
11:00 | 2916 | 1094 | 842 | 0 | 84 | 831.33 | 86 | 2255 | 612.08 | 16 | 102 | 0 | 0 | 10 | 0
11:30 | 3070.5 | 1166.5 | 854 | 0 | 87 | 830.245 | 86 | 2358 | 599.13 | 16 | 103 | 0 | 0 | 12 | 0
12:00 | 3225 | 1239 | 866 | 0 | 90 | 829.16 | 86 | 2461 | 586.18 | 16 | 104 | 0 | 0 | 14 | 0
12:30 | 3204.5 | 1295 | 865.5 | 0 | 87 | 856.055 | 86 | 2582 | 535.15 | 16 | 108.5 | 0 | 0 | 13 | 13
13:00 | 3184 | 1351 | 865 | 0 | 84 | 882.95 | 86 | 2703 | 484.12 | 16 | 113 | 0 | 0 | 12 | 26
13:30 | 3086 | 1327 | 865 | 0 | 89 | 904.93 | 86 | 2682.5 | 476.67 | 16 | 141 | 0 | 0 | 13 | 13
14:00 | 2988 | 1303 | 865 | 0 | 94 | 926.91 | 86 | 2662 | 469.22 | 16 | 169 | 0 | 0 | 14 | 0
14:30 | 2988.5 | 1303 | 865.5 | 0 | 92 | 893.61 | 86 | 2661 | 397.68 | 16 | 161.25 | 0 | 0 | 12.5 | 11
15:00 | 2989 | 1303 | 866 | 0 | 90 | 860.31 | 86 | 2660 | 326.14 | 16 | 153.5 | 0 | 0 | 11 | 22
15:30 | 3071.5 | 1272 | 877.5 | 0 | 89 | 850.455 | 86 | 2619.5 | 226.84 | 16 | 153.5 | 0 | 0 | 9.5 | 21.5
16:00 | 3154 | 1241 | 889 | 0 | 88 | 840.6 | 86 | 2579 | 127.54 | 16 | 153.5 | 0 | 0 | 8 | 21
16:30 | 3144 | 1237 | 888.5 | 0 | 90 | 912.315 | 86 | 2716 | 66.51 | 27 | 310.5 | 0 | 0 | 10.5 | 22
17:00 | 3134 | 1233 | 888 | 0 | 92 | 984.03 | 86 | 2853 | 5.48 | 38 | 467.5 | 0 | 0 | 13 | 23
17:30 | 3151.5 | 1283 | 887 | 0 | 92 | 1133.76 | 86 | 3151 | 2.74 | 44 | 742.5 | 0 | 0 | 17 | 11.5
18:00 | 3169 | 1333 | 886 | 0 | 92 | 1283.49 | 86 | 3449 | 0 | 50 | 1017.5 | 0 | 0 | 21 | 0
18:30 | 3163.5 | 1345.25 | 886.5 | 0 | 91 | 1356.42 | 86 | 3467.5 | 0 | 33 | 791 | 0 | 0 | 17 | 0
19:00 | 3158 | 1357.5 | 887 | 0 | 90 | 1429.35 | 86 | 3486 | 0 | 16 | 564.5 | 0 | 0 | 13 | 0
19:30 | 3103 | 1353.5 | 887 | 0 | 90 | 1424.99 | 86 | 3456 | 0 | 16 | 511.5 | 0 | 0 | 14 | 0
20:00 | 3150 | 1371.5 | 887 | 0 | 94 | 1430.94 | 86 | 3419 | 0 | 0 | 314 | 0 | 0 | 8 | 0
20:30 | 3169.5 | 1357 | 887 | 0 | 92 | 1438.97 | 86 | 3422 | 0 | 0 | 174.5 | 0 | 0 | 4.5 | 0
21:00 | 3189 | 1342.5 | 887 | 0 | 90 | 1447 | 86 | 3425 | 0 | 0 | 35 | 0 | 0 | 1 | 0
21:30 | 3139 | 1306.75 | 887.5 | 0 | 86 | 1455 | 86 | 3350.5 | 0 | 0 | 35 | 0 | 0 | 0.5 | 0
22:00 | 3089 | 1271 | 888 | 0 | 82 | 1463 | 86 | 3276 | 0 | 0 | 35 | 0 | 0 | 0 | 0
22:30 | 3095.5 | 1237 | 887.5 | 0 | 83 | 1397.5 | 86 | 3168.5 | 0 | 0 | 35 | 0 | 0 | 0 | 0
23:00 | 3102 | 1203 | 887 | 0 | 84 | 1332 | 86 | 3061 | 0 | 0 | 35 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 03:00 | 384 | 21:00 | Meghnaghat | 400 | 05:00 | 386 | 21:00
Ashuganj | 403 | 6:00 | 390 | 13:00 | Payra | 417 | 04:00 | 410 | 18:00
Bhulta | 400 | 02:00 | 384 | 12:00 | Rahanpur | 415 | 05:00 | 398 | 20:00
Bibiana | 401 | 04:00 | 393 | 13:00 | Rampal | 413 | 02:00 | 400 | 20:00
BIPTC | 407 | 03:00 | 389 | 17:00
Bogura | 407 | 04:00 | 385 | 21:00
Gopalganj | 409 | 02:00 | 396 | 19:00
Kaliakoir | 398 | 03:00 | 381 | 21:00
Korerhat | 404 | 03:00 | 394 | 12:00
Madunaghat | 400 | 03:00 | 392 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 03:00 | 231 | 12:00 | Kachua | 235 | 18:00 | 224 | 12:00
AKSML | 238 | 03:00 | 229 | 12:00 | Kaliakoir | 240 | 02:00 | 230 | 21:00
Aminbazar | 240 | 05:00 | 231 | 21:00 | Keranigonj | 238 | 02:00 | 228 | 21:00
Ashuganj | 234 | 00:00 | 227 | 12:00 | Khulna(S) | 241 | 01:00 | 230 | 18:00
Ashuganj-400 | 234 | 00:00 | 227 | 12:00 | Korerhat | 238 | 05:00 | 231 | 13:00
Baghabari | 236 | 00:00 | 227 | 18:30 | Madunaghat | 237 | 06:00 | 232 | 12:00
Barapukuria | 223 | 05:00 | 211 | 20:00 | Madunaghat-400 | 238 | 03:00 | 232 | 13:00
Barapukuria-230 | 223 | 05:00 | 211 | 20:00 | Maniknagar | 233 | 03:00 | 224 | 12:00
Barishal | 243 | 02:00 | 236 | 13:00 | Meghnaghat | 240 | 07:00 | 233 | 19:30
Bheramara | 236 | 00:00 | 225 | 18:00 | Meghnaghat-400 | 236 | 06:00 | 227 | 12:00
Bhulta | 234 | 02:00 | 225 | 12:00 | Mirsorai | 234 | 01:00 | 227 | 12:00
Bibiana | 238 | 03:00 | 231 | 11:00 | Rajshahi | 237 | 04:00 | 223 | 18:00
BIPTC | 238 | 00:00 | 225 | 18:00 | Rampal | 239 | 02:00 | 229 | 13:00
Bogura | 236 | 03:00 | 224 | 20:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 235 | 03:00 | 224 | 19:00 | Rampura | 234 | 06:00 | 223 | 12:00
Borhanuddin | 244 | 02:00 | 240 | 18:00 | Shikalbaha | 236 | 18:00 | 230 | 12:00
BSRM | 234 | 01:00 | 226 | 12:00 | Shyampur | 237 | 04:00 | 227 | 14:00
Cumilla(N) | 233 | 04:00 | 226 | 11:00 | Siddhirganj | 234 | 05:00 | 229 | 19:00
Faridpur | 242 | 03:00 | 233 | 18:30 | Sirajgonj | 241 | 04:00 | 233 | 19:00
Fenchuganj | 238 | 02:00 | 232 | 13:00 | Sreepur | 231 | 00:00 | 224 | 11:00
Feni | N/A | N/A | N/A | N/A | Tongi | 236 | 07:00 | 228 | 21:00
Ghorashal | N/A | N/A | N/A | N/A
Ghorashal-230 | 232 | 05:00 | 214 | 19:00
Gopalganj | 242 | 02:00 | 234 | 12:00
GPH | 235 | 00:00 | 229 | 13:00
Haripur | 235 | 06:00 | 226 | 12:00
Hasnabad | 238 | 18:30 | 226 | 03:00
Hathazari | 235 | 04:00 | 228 | 15:00
Ishurdi | 239 | 00:00 | 227 | 18:00
Jhenaidah | 237 | 00:00 | 224 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 128 | 13:00 | Lalbag | 140 | 04:00 | 132 | 12:00
Agargaon | 139 | 02:00 | 133 | 12:00 | Lalmonirhat | 132 | 03:00 | 122 | 19:00
Agrabad | 136 | 03:00 | 131 | 12:00 | Madanganj | 136 | 06:00 | 131 | 11:00
AKS | 134 | 01:00 | 131 | 12:00 | Madaripur | 139 | 09:00 | 135 | 12:00
Aminbazar | 139 | 01:00 | 133 | 15:00 | Madartek | 135 | 04:00 | 129 | 12:00
Amnura | 138 | 02:00 | 130 | 20:00 | Madunaghat | 138 | 05:00 | 134 | 12:00
Ashuganj | 141 | 01:00 | 138 | 11:00 | Magura | 140 | 00:00 | 130 | 18:00
Bagerhat | 138 | 04:00 | 128 | 18:00 | Mahasthangarh | 134 | 04:00 | 126 | 20:00
Bajitpur | 136 | 00:00 | 123 | 12:00 | Maijdee | 134 | 03:00 | 129 | 13:00
Bakulia | 139 | 06:00 | 133 | 12:00 | Manikganj | 137 | 03:00 | 132 | 12:00
Banani | 136 | 04:00 | 127 | 13:00 | Maniknagar | 139 | 04:00 | 131 | 13:00
Bangabhaban | 139 | 05:00 | 132 | 12:00 | Matarbari | 132 | 17:00 | 121 | 13:00
Barapukuria | 137 | 05:00 | 127 | 20:00 | Matuail | 137 | 02:00 | 132 | 12:00
Barguna | 137 | 04:00 | 133 | 18:00 | Metrorail_Motijheel | 139 | 04:00 | 131 | 13:00
Barishal | 139 | 05:00 | 135 | 12:00 | Metrorail_Uttara | 141 | 03:00 | 133 | 12:00
Barishal-230 | 140 | 02:00 | 135 | 18:00 | Millgate | 142 | 04:00 | 134 | 12:00
Baroaulia | 136 | 01:00 | 132 | 16:00 | Mirpur | 139 | 03:00 | 132 | 21:00
Baroirhat | 137 | 06:00 | 131 | 13:00 | Mirzapur | 135 | 02:00 | 128 | 21:00
Bashundhara | 136 | 03:00 | 128 | 12:00 | Mithapukur | 134 | 04:00 | 125 | 20:00
BashundharaCement | 136 | 06:00 | 131 | 11:00 | MI_Cement | 137 | 02:00 | 129 | 12:00
Beanibazar | 134 | 04:00 | 131 | 15:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 137 | 03:00 | 121 | 13:00 | Mogbazar | 137 | 03:00 | 130 | 12:00
Bhaluka | 134 | 00:00 | 127 | 13:00 | Mongla | 137 | 04:00 | 128 | 18:00
Bhandaria | 139 | 08:00 | 132 | 18:30 | Motijheel | 139 | 05:00 | 132 | 12:00
Bhangura | 136 | 04:00 | 131 | 18:00 | Muktagacha | 136 | 15:00 | 127 | 18:00
Bheramara | 139 | 00:00 | 135 | 18:00 | Munshiganj | 135 | 06:00 | 130 | 12:00
Bheramara(GK) | 139 | 00:00 | 135 | 18:00 | Muradnagar | 136 | 08:00 | 132 | 12:00
Bhulta | 132 | 09:00 | 125 | 18:30 | Mymensingh | 137 | 16:00 | 126 | 13:00
Bog-Sherpur | 136 | 04:00 | 129 | 18:00 | Naogaon | 133 | 03:00 | 123 | 18:00
Bogura | 136 | 04:00 | 128 | 20:00 | Narail | 140 | 02:00 | 130 | 18:00
Bogura-230 | 135 | 02:00 | 128 | 19:00 | Narinda | 139 | 04:00 | 131 | 13:00
Brahmanbaria | 136 | 00:00 | 131 | 11:00 | Narshingdi | 137 | 03:00 | 123 | 18:00
Cantonment | 139 | 02:00 | 132 | 21:00 | Natore | 136 | 01:00 | 130 | 18:00
Chandina | 138 | 00:00 | 133 | 13:00 | Nawabganj | 140 | 05:00 | 132 | 12:00
Chandpur | 140 | 18:00 | 130 | 13:00 | Netrakona | 130 | 01:00 | 124 | 05:00
Chandraghona | 138 | 03:00 | 134 | 12:00 | New | 140 | 03:00 | 134 | 12:00
Chapai | 138 | 01:00 | 133 | 19:30 | Niamatpur | 139 | 02:00 | 132 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 137 | 05:00 | 131 | 12:00 | Noapara | 139 | 04:00 | 131 | 08:00
Chauddagram | 136 | 01:00 | 131 | 13:00 | Pabna | 139 | 04:00 | 133 | 18:30
Chhatak | 132 | 00:00 | 128 | 23:00 | Palashbari | 132 | 01:00 | 122 | 20:00
Chowmuhani | 134 | 03:00 | 128 | 13:00 | Panchagarh | 139 | 18:30 | 126 | 16:00
Chuadanga | 140 | 00:00 | 130 | 18:00 | Patiya | 136 | 04:00 | 133 | 00:00
Coxsbazar | 126 | 05:00 | 120 | 16:00 | Patuakhali | 137 | 02:00 | 134 | 09:00
Cumilla(N) | 138 | 05:00 | 133 | 12:00 | Payra | 137 | 02:00 | 134 | 18:00
Cumilla(S) | 138 | 04:00 | 126 | 12:00 | PHP | 136 | 02:00 | 131 | 16:00
Daganbhuiyan | 136 | 04:00 | 131 | 12:00 | Postogola | 137 | 01:00 | 131 | 12:00
Daudkandi | 135 | 02:00 | 129 | 21:00 | Purbachal | 136 | 04:00 | 128 | 13:00
DhakaUniversity | 136 | 03:00 | 129 | 12:00 | Purbasadipur | 133 | 04:00 | 121 | 20:00
Dhamrai | 139 | 02:00 | 129 | 12:00 | Rahanpur | 139 | 01:00 | 133 | 19:30
Dhanmondi | 136.4 | 05:00 | 128 | 13:00 | Rahanpur-400 | 139 | 00:00 | 134 | 19:00
Dohazari | 134 | 08:00 | 127 | 12:00 | Rahim | 137 | 04:00 | 131 | 13:00
Faridpur | 140 | 03:00 | 135 | 18:00 | Rajbari | 140 | 02:00 | 134 | 13:00
Fatullah | 141 | 04:00 | 131 | 12:00 | Rajendrapur | 134 | 01:00 | 128 | 12:00
Fenchuganj | 140 | 06:00 | 137 | 13:00 | Rajshahi | 136 | 01:00 | 130 | 18:00
Feni | 134 | 08:00 | 130 | 16:00 | Rajshahi-230 | 137 | 04:00 | 129 | 13:00
Feni-230 | N/A | N/A | N/A | N/A | Ramganj | 135 | 19:00 | 128 | 13:00
Ghatail | 133 | 03:00 | 125 | 18:00 | Rampur | 135 | 01:00 | 132 | 12:00
Ghorashal | 136 | 00:00 | 130 | 12:00 | Rampura | 136 | 06:00 | 129 | 12:00
Goalpara | 141 | 03:00 | 132 | 13:00 | Rangamati | 138 | 06:00 | 134 | 13:00
Gollamari | 140 | 04:00 | 132 | 18:00 | Rangpur | 133 | 05:00 | 124 | 20:00
Gopalganj | 140 | 03:00 | 133 | 18:00 | Ruppur | 139 | 00:00 | 134 | 18:00
Gopalganj-400 | 141 | 03:00 | 136 | 12:00 | Saidpur | 133 | 10:00 | 123 | 20:00
Gulshan | 135 | 03:00 | 129 | 12:00 | Satkhira | 139 | 04:00 | 128 | 13:00
Halishahar | 137 | 07:00 | 123 | 12:00 | Satmasjid | 139 | 05:00 | 132 | 13:00
Haripur | 137 | 02:00 | 133 | 12:00 | Savar | 137 | 01:00 | 131 | 21:00
HaripurSBU | 137 | 02:00 | 133 | 13:00 | SevenRings | 139 | 03:00 | 130 | 12:00
Hasnabad | 137 | 03:00 | 131 | 12:00 | ShahCement | 137 | 05:00 | 131 | 12:00
Hathazari | 137 | 03:00 | 134 | 15:00 | Shahjadpur | 140 | 03:00 | 135 | 13:00
Ishurdi | 140 | 00:00 | 135 | 18:00 | Shahjibazar | 138 | 00:00 | 132 | 11:00
Jaldhaka | 133 | 10:00 | 120 | 20:00 | Shahmirpur | 137 | 06:00 | 133 | 12:00
Jamalpur | 135 | 09:00 | 120 | 07:00 | Shariatpur | 140 | 03:00 | 134 | 18:00
Jashore | 137 | 00:00 | 122 | 12:00 | Sherpur | 133 | 09:00 | 118 | 07:00
Jhenaidah | 142 | 03:00 | 122 | 18:00 | Shikalbaha | 126 | 05:00 | 122 | 12:00
Jhenaidah-230 | 142 | 04:00 | 133 | 13:00 | Shikalbaha-230 | 138 | 03:00 | 134 | 12:00
Joydebpur | 134 | 00:00 | 126 | 12:00 | Shitalakhya | 137 | 02:00 | 129 | 12:00
Joypurhat | 133 | 02:00 | 122 | 18:00 | Sholosohor | 137 | 00:00 | 134 | 12:00
Juldah | 137 | 05:00 | 133 | 12:00 | Shyampur | 137 | 03:00 | 135 | 11:00
Kabirpur | 139 | 08:00 | 129 | 21:00 | Shyampur-230 | 141 | 04:00 | 135 | 14:00
Kachua | 139 | 18:00 | 132 | 12:00 | Siddhirganj | 138 | 03:00 | 132 | 21:00
Kaliakoir | 141 | 04:00 | 133 | 12:00 | Sirajganj | 135 | 02:00 | 128 | 19:00
Kallyanpur | 139 | 04:00 | 134 | 12:00 | Sonargaon | 135 | 00:00 | 132 | 12:00
Kalurghat | 137 | 00:00 | 134 | 21:00 | Sreemongol | 138 | 00:00 | 133 | 11:00
Kamrangirchar | 140 | 06:00 | 133 | 12:00 | Sreepur | 135 | 00:00 | 130 | 14:00
Kaptai | 136 | 1:00 | 132 | 12:00 | Srinagar | 139 | 04:00 | 132 | 12:00
Kasba | 136 | 02:00 | 132 | 12:00 | SSM | 140 | 00:00 | 135 | 12:00
Kazla | 138 | 06:00 | 131 | 13:00 | Sunamganj | 132 | 05:00 | 128 | 17:00
Keranigonj | 140 | 04:00 | 133 | 11:00 | Sylhet | 135 | 05:00 | 132 | 11:00
Khagrachori | 137 | 02:00 | 133 | 13:00 | Sylhet-132 | 133 | 00:00 | 131 | 10:00
Khulna | 138 | 06:00 | 131 | 14:00 | Tangail | 132 | 04:00 | 125 | 18:00
Khulna(S) | 140 | 01:00 | 132 | 18:00 | Taraganj | 133 | 03:00 | 123 | 20:00
Khulshi | 135 | 00:00 | 131 | 12:00 | Tasnim | 135 | 00:00 | 132 | 12:00
Kishoreganj | 136 | 00:00 | 128 | 12:00 | Thakurgaon | 140 | 18:30 | 123 | 20:00
Kodda | 133 | 01:00 | 126 | 12:00 | TK | 138 | 04:00 | 134 | 12:00
KSRM | 138 | 00:00 | 133 | 12:00 | Tongi | 141 | 04:00 | 136 | 21:00
Kulaura | 140 | 08:00 | 136 | 11:00 | Ullahpara | 137 | 03:00 | 130 | 18:00
Kurigram | 130 | 04:00 | 119 | 19:30 | Ullon | 136 | 03:00 | 128 | 13:00
Kushtia | 136 | 02:00 | 128 | 18:00 | Uttara | 140 | 04:00 | 131 | 21:00
Laksam | 138 | 03:00 | 130 | 13:00 | UttaraNew | 141 | 03:00 | 133 | 12:00
Lakshmipur | 135 | 03:00 | 130 | 13:00 | Zigatola | 139 | 02:00 | 132 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division