## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-11-2025 | during | 24-11-2025 | during | 24-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Electrical fault due to Earthquake
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 362 | 304 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 228 | 160 | 335 | 335 | 335 | 335 | Under maint.
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 28.3 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 27.5 | 27.5 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 24 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 2 | 160 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 55 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 87.5 | 87.5 | 87.5 | 87.5 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 162 | 162 | 35 | 108 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | Under maint.
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 314 | 418 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 10 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1026.5 | 1414.8 | 4754.9 | 4722.9 | 4052.74 | 4142.74
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 23 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 46 | 90 | 90 | 90 | 90 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 148 | 141 | 225 | 225 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 5 | 46 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 56 | 40 | 48 | 40 | 48 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 9 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.16 | 0 | 2.92 | 0 | 2.92 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 24 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 22 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 590 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 14 | 9 | 12 | 9 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 350 | 350 | 350 | 350 | 355 | 355 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1215.16 | 1449 | 3257.64 | 3251.72 | 2623.42 | 2617.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 194 | 176 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 37 | 0 | 0 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 25 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 76 | 53 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 3 | 76 | 150 | 150 | 125 | 125 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 17 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 108 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 4 | 62 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 88 | 100 | 160 | 160 | 94 | 94 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 17 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1071 | 1128 | 2442.51 | 2372.51 | 1883.4 | 1813.4
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-11-2025 | during | 24-11-2025 | during | 24-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 86 | 84 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 50 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 38.29 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 195.29 | 178 | 361.1 | 314 | 301.6 | 254.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 166 | 157 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 80 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 158 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 14 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 345 | 385 | 385 | 366 | 366 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1176 | 1151 | 1236 | 1236 | 1183 | 1183
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 862 | 861 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 334 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 856 | 1035 | 0 | 0 | 1148 | 1148 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2130 | 2146 | 2387 | 2312 | 2780.1 | 2705.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 305 | 504 | 0 | 0 | 0 | 0 | Machine Problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 760 | 910 | 1085.32 | 1085.32 | 992 | 992 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 220 | 220 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.56 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1290.56 | 1639 | 1576.32 | 1576.32 | 1460 | 1460
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 53.6 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 175 | 182 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 358 | 380 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 47 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.18 | 0 | 5.59 | 0 | 5.59 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1071 | 1378.58 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.52 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 82 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1795.3 | 2009.58 | 3081.46 | 2914.87 | 2986.68 | 2820.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 55 | 55 | 55 | 55 | 55 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 161 | 0 | 161 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 233.6 | 195 | 513.2 | 317 | 479.2 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 10133.41 | 11310.38 | 19610.13 | 19017.32 | 17750.14 | 17279.33
Forecast Scenario (24-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9380 |  | 0 |  | 9380
|  |  |  | 1:00 | 8810 |  | 0 |  | 8810
|  |  |  | 2:00 | 8410 |  | 0 |  | 8410
|  |  |  | 3:00 | 8200 |  | 0 |  | 8200
|  |  |  | 4:00 | 7920 |  | 0 |  | 7920
|  |  |  | 5:00 | 7860 |  | 0 |  | 7860
|  |  |  | 6:00 | 8150 |  | 0 |  | 8150
|  |  |  | 7:00 | 8950 |  | 0 |  | 8950
|  |  |  | 8:00 | 9500 |  | 0 |  | 9500
|  |  |  | 9:00 | 9440 |  | 0 |  | 9440
|  |  |  | 10:00 | 9400 |  | 0 |  | 9400
|  |  |  | 11:00 | 9760 |  | 0 |  | 9760
|  |  |  | 12:00 | 10130 |  | 0 |  | 10130
|  |  |  | 13:00 | 10550 |  | 0 |  | 10550
|  |  |  | 14:00 | 10060 |  | 0 |  | 10060
|  |  |  | 15:00 | 9910 |  | 0 |  | 9910
|  |  |  | 16:00 | 9750 |  | 0 |  | 9750
|  |  |  | 17:00 | 10230 |  | 0 |  | 10230
|  |  |  | 18:00 | 11310 |  | 0 |  | 11310
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 10910 |  | 0 |  | 10910
|  |  |  | 19:30 | 10750 |  | 0 |  | 10750
|  |  |  | 20:00 | 10660 |  | 0 |  | 10660
|  |  |  | 21:00 | 10520 |  | 0 |  | 10520
|  |  |  | 22:00 | 10200 |  | 0 |  | 10200
|  |  |  | 23:00 | 9780 |  | 0 |  | 9780
Probable Maximum Temperature: |  |  | 27.50°C
Probable Maximum Demand at Day Peak: |  |  | 10130.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11310.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11310.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 229.79 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:05 hrs on 24-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-11-2025 | [28 empty] | Date: | 23-11-2025 | [28 empty] | Date: | 23-11-2025 | [28 empty] | Date: | 23-11-2025 | [28 empty] | Date: | 23-11-2025 | [14 empty] | Date: | 23-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [14 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 2 | 350 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 530 | 0 | 51 | 0 | 8 | 360 | 0 | 0 | 20 | 187 | 38 | 0 | 110 | 0 | 0 | 20 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 375 | 0 | 30 | 153 | 21 | 0 | 33 | 30 | 0 | 15 | 158 | 0 | 24 | 0 | 90 | 0 | 0 | 0 | 4288 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 896 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 302 | 800 | 0 | 5099 | 9387 | 100.21
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 15 | 350 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 470 | 0 | 51 | 0 | 8 | 360 | 0 | 0 | 20 | 184 | 38 | 0 | 110 | 0 | 0 | 20 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 365 | 0 | 30 | 151 | 17 | 0 | 33 | 30 | 0 | 15 | 158 | 0 | 16 | 0 | 110 | 0 | 0 | 0 | 4194.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 0 | 940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 302 | 600 | 0 | 4620 | 8814.5 | 100.2
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 15 | 320 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 425 | 0 | 5 | 0 | 8 | 360 | 0 | 0 | 8 | 195 | 5 | 0 | 110 | 0 | 0 | 17 | 0 | 78 | 0 | 0 | 0 | 305 | 0 | 390 | 0 | 30 | 151 | 17 | 0 | 8 | 30 | 0 | 15 | 157 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 3921.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 303 | 550 | 0 | 4492 | 8413.5 | 100.2
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 318 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 390 | 0 | 5 | 0 | 8 | 300 | 0 | 0 | 5 | 198 | 5 | 0 | 110 | 0 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 347 | 0 | 30 | 151 | 17 | 0 | 8 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3783.5 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799 | 0 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 303 | 500 | 0 | 4425 | 8208.5 | 100.19
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 318 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 304 | 0 | 5 | 0 | 8 | 260 | 0 | 0 | 5 | 192 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 341 | 0 | 30 | 154 | 17 | 0 | 8 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3579.5 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 302 | 500 | 0 | 4349 | 7928.5 | 100.19
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 5 | 318 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 305 | 0 | 5 | 0 | 8 | 240 | 0 | 0 | 5 | 199 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 72 | 0 | 0 | 0 | 270 | 0 | 341 | 0 | 30 | 155 | 17 | 0 | 8 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3547.5 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 302 | 500 | 0 | 4321 | 7868.5 | 100.18
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 6 | 318 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 305 | 0 | 5 | 0 | 8 | 330 | 0 | 0 | 5 | 200 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 66 | 0 | 0 | 0 | 270 | 0 | 363 | 0 | 30 | 165 | 17 | 0 | 8 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3711.5 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 783 | 0 | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 180 | 0 | 302 | 500 | 0 | 4438 | 8149.5 | 100.18
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 2 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.16 | 86 | 0 | 21 | 350 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 428 | 0 | 15 | 0 | 8 | 395 | 0 | 0 | 12 | 197 | 31 | 0 | 110 | 0 | 0 | 17 | 0 | 68 | 0 | 6 | 0 | 320 | 0 | 402 | 0 | 30 | 165 | 17 | 0 | 51 | 30 | 0 | 15 | 157 | 0 | 2 | 2 | 110 | 0 | 2.92 | 0 | 4307.58 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 816 | 0 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.04 | 6 | 0 | 0 | 3.31 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.27 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 8 | 0.04 | 0 | 0 | 115 | 220 | 0 | 303 | 516 | 0 | 4644.96 | 8952.54 | 100.17
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 10 | 0 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.59 | 86 | 0 | 13 | 350 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 505 | 9 | 51 | 0 | 8 | 393 | 0 | 0 | 43 | 192 | 34 | 0 | 109 | 0 | 0 | 17 | 0 | 82 | 0 | 25 | 0 | 310 | 0 | 362 | 0 | 30 | 155 | 17 | 0 | 51 | 30 | 0 | 15 | 157 | 0 | 57 | 19 | 94 | 1 | 13.83 | 0 | 4446.92 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 942 | 0 | 1037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.96 | 30 | 0 | 0 | 13.91 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.31 | 0 | 52 | 0 | 7 | 0 | 0 | 0 | 0 | 1.6 | 44 | 0.16 | 0 | 0 | 115 | 110 | 0 | 304 | 650 | 0 | 5058.94 | 9505.86 | 100.17
09:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 18 | 0 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2.07 | 86 | 0 | 8 | 350 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 500 | 15 | 51 | 0 | 8 | 393 | 0 | 0 | 43 | 187 | 36 | 0 | 109 | 0 | 0 | 12 | 0 | 74 | 0 | 44 | 0 | 310 | 0 | 347 | 0 | 30 | 150 | 17 | 0 | 53 | 30 | 0 | 15 | 158 | 0 | 47 | 8 | 88 | 1 | 25.86 | 0 | 4277.43 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 953 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.36 | 57 | 0 | 0 | 31.49 | 183 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 2.55 | 0 | 52 | 0 | 15 | 0 | 0 | 0 | 0 | 3.4 | 87 | 0.32 | 0 | 0 | 115 | 110 | 0 | 304 | 695 | 0 | 5163.12 | 9440.55 | 100.16
10:00 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 24 | 0 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.69 | 86 | 0 | 8 | 350 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 500 | 18 | 51 | 0 | 16 | 393 | 0 | 0 | 43 | 190 | 33 | 0 | 108 | 0 | 0 | 12 | 0 | 80 | 0 | 56 | 0 | 305 | 0 | 349 | 0 | 30 | 148 | 17 | 0 | 53 | 30 | 0 | 15 | 158 | 0 | 45 | 8 | 88 | 2 | 34.54 | 0 | 4268.73 | 862 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 882 | 0 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.11 | 76 | 0 | 0 | 43.98 | 172 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 3.66 | 0 | 52 | 0 | 24 | 0 | 0 | 0 | 0 | 4.7 | 119 | 0.47 | 0 | 0 | 115 | 110 | 0 | 303 | 695 | 0 | 5137.92 | 9406.65 | 100.16
11:00 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 26 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3.01 | 86 | 0 | 10 | 350 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 540 | 20 | 51 | 0 | 50 | 393 | 0 | 0 | 43 | 195 | 33 | 0 | 107 | 0 | 0 | 13 | 0 | 90 | 0 | 61 | 0 | 310 | 0 | 367 | 0 | 30 | 156 | 17 | 0 | 78 | 30 | 0 | 15 | 158 | 0 | 45 | 8 | 87 | 2 | 37.96 | 0 | 4539.97 | 862 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 859 | 0 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.63 | 87 | 0 | 0 | 50.88 | 176 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 4.18 | 0 | 53 | 0 | 28 | 0 | 0 | 0 | 0 | 5.2 | 143 | 0.53 | 0 | 0 | 115 | 110 | 0 | 304 | 700 | 0 | 5223.42 | 9763.39 | 100.16
12:00 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 314 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 29 | 0 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 3.16 | 86 | 0 | 9 | 350 | 0 | 0 | 0 | 0 | 5 | 148 | 0 | 0 | 0 | 580 | 20 | 51 | 3 | 76 | 393 | 0 | 0 | 43 | 194 | 38 | 0 | 105 | 4 | 0 | 13 | 0 | 88 | 0 | 63 | 0 | 315 | 0 | 367 | 0 | 30 | 166 | 17 | 0 | 78 | 30 | 0 | 15 | 158 | 0 | 50 | 19 | 86 | 2 | 38.29 | 0 | 4683.95 | 862 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 856 | 0 | 1071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6 | 82 | 0 | 0 | 51.52 | 175 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 4.18 | 0 | 53 | 0 | 30 | 0 | 0 | 0 | 0 | 5.6 | 145 | 0.56 | 0 | 0 | 115 | 110 | 0 | 305 | 760 | 0 | 5449.46 | 10133.41 | 100.15
13:00 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 306 | 14.5 | 0 | 0 | 0 | 145 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 28 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 24 | 0 | 0 | 12 | 2.84 | 86 | 0 | 17 | 350 | 0 | 0 | 26 | 0 | 49 | 148 | 0 | 0 | 0 | 570 | 18 | 51 | 73 | 100 | 393 | 0 | 0 | 45 | 185 | 36 | 0 | 105 | 69 | 0 | 13 | 0 | 98 | 0 | 58 | 0 | 310 | 0 | 352 | 0 | 30 | 161 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 86 | 2 | 38.13 | 0 | 5074.97 | 862 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 853 | 0 | 1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.41 | 81 | 0 | 0 | 41.06 | 175 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 3.77 | 0 | 54 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 140 | 0.5 | 0 | 0 | 115 | 110 | 0 | 304 | 797 | 0 | 5481.74 | 10556.71 | 100.14
14:00 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 232 | 17.5 | 0 | 0 | 0 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 21 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 32 | 0 | 0 | 12 | 2.23 | 86 | 0 | 12 | 350 | 0 | 0 | 19 | 0 | 17 | 141 | 0 | 0 | 0 | 580 | 15 | 51 | 30 | 103 | 393 | 0 | 0 | 44 | 197 | 34 | 0 | 105 | 17 | 16 | 13 | 0 | 102 | 0 | 50 | 0 | 310 | 0 | 406 | 0 | 30 | 151 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 84 | 1 | 30.71 | 0 | 4803.94 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 851 | 0 | 1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.67 | 70 | 0 | 0 | 30.59 | 171 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 2.28 | 0 | 54 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 104 | 0.37 | 0 | 0 | 115 | 110 | 0 | 303 | 791 | 0 | 5258.91 | 10062.85 | 100.14
15:00 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 243 | 17.5 | 0 | 6 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 9 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 32 | 0 | 0 | 12 | 1.39 | 86 | 0 | 6 | 350 | 0 | 0 | 19 | 0 | 16 | 142 | 0 | 0 | 0 | 580 | 10 | 51 | 10 | 100 | 393 | 0 | 0 | 44 | 193 | 36 | 0 | 105 | 16 | 17 | 13 | 0 | 98 | 0 | 33 | 0 | 315 | 0 | 396 | 0 | 30 | 148 | 21 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 84 | 1 | 15.36 | 0 | 4692.25 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 851 | 0 | 1075.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 0 | 0 | 22.14 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.1 | 0 | 53 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 66 | 0.26 | 0 | 0 | 115 | 110 | 0 | 302 | 800 | 0 | 5224.01 | 9916.26 | 100.13
16:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 411 | 17.5 | 0 | 17 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 6 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 0 | 12 | 0.57 | 86 | 0 | 8 | 350 | 0 | 0 | 19 | 0 | 15 | 142 | 0 | 0 | 0 | 580 | 4 | 51 | 10 | 53 | 393 | 0 | 0 | 44 | 196 | 34 | 0 | 106 | 16 | 16 | 13 | 0 | 90 | 0 | 14 | 0 | 310 | 0 | 406 | 0 | 30 | 150 | 21 | 0 | 80 | 30 | 0 | 13 | 158 | 0 | 59 | 19 | 84 | 0 | 6.25 | 0 | 4781.32 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 765 | 0 | 1069.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.95 | 20 | 0 | 0 | 8.59 | 191 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.66 | 0 | 53 | 0 | 5 | 0 | 0 | 0 | 0 | 0.9 | 27 | 0.1 | 0 | 0 | 115 | 110 | 0 | 305 | 750 | 0 | 4972.77 | 9754.09 | 100.13
17:00 | 0 | 9 | 24 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 418 | 35 | 5 | 17 | 0 | 80 | 4 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 17 | 20 | 22 | 0 | 0 | 3 | 16 | 0 | 0 | 21 | 33 | 42 | 10 | 12 | 24 | 0 | 86 | 2 | 15 | 350 | 0 | 0 | 19 | 0 | 17 | 142 | 0 | 0 | 0 | 590 | 0 | 51 | 26 | 58 | 393 | 0 | 0 | 44 | 184 | 35 | 0 | 107 | 18 | 0 | 13 | 0 | 92 | 0 | 1 | 0 | 325 | 0 | 366 | 0 | 30 | 159 | 21 | 0 | 80 | 30 | 0 | 14 | 158 | 6 | 59 | 19 | 84 | 0 | 0.07 | 0 | 5023.07 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 842 | 0 | 1157.06 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.78 | 0 | 28 | 0 | 0.38 | 189 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0.04 | 0 | 53 | 35 | 0 | 20 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 0 | 115 | 110 | 0 | 353 | 780 | 0 | 5215.37 | 10238.44 | 100.12
18:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 418 | 28.3 | 35 | 55 | 0 | 160 | 30 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 160 | 0 | 0 | 0 | 10 | 27.5 | 22 | 0 | 0 | 22 | 16 | 0 | 0 | 14 | 33 | 56 | 17 | 38 | 24 | 0 | 46 | 24 | 9 | 350 | 0 | 0 | 23 | 0 | 46 | 141 | 0 | 0 | 0 | 590 | 0 | 51 | 76 | 53 | 393 | 0 | 0 | 25 | 176 | 37 | 17 | 108 | 62 | 0 | 13 | 0 | 100 | 0 | 0 | 17 | 315 | 0 | 345 | 0 | 30 | 157 | 22 | 0 | 80 | 30 | 0 | 14 | 158 | 17 | 59 | 18 | 84 | 0 | 0 | 0 | 5320.8 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 0 | 1378.58 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 55 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 504 | 910 | 0 | 5989.58 | 11310.38 | 100.12
19:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 480 | 0 | 0 | 0 | 0 | 110 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 180 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 36 | 0 | 46 | 0 | 15 | 350 | 0 | 0 | 32 | 0 | 62 | 142 | 0 | 0 | 0 | 585 | 0 | 51 | 35 | 53 | 393 | 0 | 0 | 25 | 188 | 32 | 0 | 107 | 68 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 370 | 0 | 30 | 146 | 22 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 59 | 18 | 84 | 0 | 0 | 0 | 4940 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 1465.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 443 | 1050 | 0 | 5976.56 | 10916.56 | 100.11
19:30 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 500 | 0 | 0 | 0 | 0 | 45 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 180 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 24 | 350 | 0 | 0 | 19 | 0 | 40 | 142 | 0 | 0 | 0 | 581 | 0 | 51 | 0 | 53 | 393 | 0 | 0 | 25 | 190 | 35 | 0 | 107 | 30 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 383 | 0 | 30 | 150 | 22 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 35 | 18 | 89 | 0 | 0 | 0 | 4758 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 1473.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 56 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 400 | 1080 | 0 | 5997.28 | 10755.28 | 100.11
20:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 509 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 180 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 30 | 350 | 0 | 0 | 0 | 0 | 33 | 142 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 53 | 393 | 0 | 0 | 25 | 194 | 35 | 0 | 108 | 34 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 393 | 0 | 30 | 157 | 22 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 35 | 18 | 89 | 0 | 0 | 0 | 4695 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 1476.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 368 | 1085 | 0 | 5973.44 | 10668.44 | 100.11
21:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 38 | 0 | 46 | 0 | 29 | 350 | 0 | 0 | 0 | 0 | 31 | 142 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 45 | 393 | 0 | 0 | 19 | 192 | 35 | 0 | 109 | 34 | 0 | 20 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 390 | 0 | 30 | 167 | 22 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 16 | 18 | 94 | 0 | 0 | 0 | 4635 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 0 | 1460.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 56 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 357 | 1085 | 0 | 5889.76 | 10524.76 | 100.1
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 29 | 350 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 535 | 0 | 51 | 0 | 45 | 393 | 0 | 0 | 15 | 181 | 35 | 0 | 110 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 350 | 0 | 30 | 147 | 22 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 16 | 18 | 90 | 0 | 0 | 0 | 4328 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1023 | 0 | 1379.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 57 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 302 | 1060 | 0 | 5690.78 | 10018.78 | 100.1
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 30 | 350 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 635 | 0 | 51 | 0 | 45 | 330 | 0 | 0 | 15 | 184 | 35 | 0 | 110 | 0 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 305 | 0 | 317 | 0 | 30 | 147 | 22 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 16 | 18 | 89 | 0 | 0 | 0 | 4285 | 861 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 884 | 0 | 1312.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 302 | 1010 | 0 | 5417.08 | 9702.08 | 100.09
Total KWH | 0 | 24960 | 353280 | 0 | 0 | 0 | 0 | 0 | 8665200 | 0 | 8521620 | 129960 | 52200 | 150624 | 0 | 582862 | 35209 | 134597 | 253440 | 0 | 0 | 0 | 0 | 0 | 65523 | 5523348 | 0 | 0 | 172077 | 24000 | 453000 | 532080 | 0 | 0 | 40145 | 30109 | 0 | 0 | 252960 | 62182 | 226944 | 31472 | 46080 | 196800 | 18480 | 1791500 | 59380 | 341280 | 8298181.82 | 0 | 0 | 191520 | 0 | 343745 | 3447069 | 0 | 0 | 0 | 12299999 | 118125 | 1008984 | 351272 | 970181 | 8871000 | 0 | 0 | 643200 | 4726000 | 718632 | 46080 | 2443274 | 406080 | 55440 | 373110 | 0 | 2061120 | 0 | 415464 | 16768 | 7442000 | 0 | 9022000 | 0 | 727800 | 3716591 | 461568 | 0 | 1376640 | 681216 | 0 | 347000 | 3708000 | 27360 | 805200 | 266400 | 2191680 | 10050 | 236750 | 0 | 107596811.82 | 20932364 | 6768576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488880 | 21185454 | 0 | 26187272 | 0 | 0 | 0 | 0 | 99744 | 0 | 0 | 0 | 0 | 291340 | 568310 | 31202 | 0 | 300000 | 4202727 | 0 | 0 | 0 | 0 | 0 | 8955781 | 0 | 24720 | 0 | 1284654 | 276053 | 170150 | 115987 | 0 | 0 | 0 | 18564.84 | 878400 | 3305 | 0 | 0 | 2696000 | 3476660 | 0 | 7757652 | 18936727.27 | 0 | 125650523.11 | 233247334.93

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10133.41 | MW | 12:00 Hr. | Energy Generated |  |  | 233.2473 |  | MKWHr.
| Day Peak Demand |  |  | 10133.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11310.38 | MW | 18:00 Hr. | Energy Demand |  |  | 233.2473 |  | MKWHr.
| Evening Peak Demand |  |  | 11310.38 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29.1 |  | °C
| Minimum Generation of the Day |  |  | 7868.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 761.95 |  | MMCFD
| Maximum Generation of the Day |  |  | 11310.38 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.4145 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.6952 | 0 | 1.8067 | 0 | 0 | 0.17208 | 0 | 0 | 25.674 | Gas | 103.0122 | Gas | 365058249.66
| Chattogram Zone |  |  | 3.7883 | 20.5982 | 1.2284 | 0 | 1.7915 | 0.13661 | 0 | 0.25296 | 27.796 | Coal | 69.7627 | Coal | 447596046.2075
| Cumilla Zone |  |  | 19.7544 | 0 | 0.87564 | 0 | 0 | 0.41546 | 2.0611 | 0 | 23.1066 | HFO | 5.5326 | HFO | 94150026.97
| Mymensingh Zone |  |  | 2.1917 | 0 | 1.099 | 0 | 0 | 0.2468 | 0 | 0 | 3.5374 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.4828 | Hydro | 1.7915 | Hydro | 179150
| Khulna Zone |  |  | 6.7686 | 21.1855 | 0 | 0 | 0 | 0.48888 | 20.9324 | 0 | 49.3753 | Solar | 3.7146 | Solar | 59273849.5664
| Barishal Zone |  |  | 6.1727 | 26.6944 | 0 | 0 | 0 | 0.003305 | 0 | 0 | 32.8703 | Import | 49.1808 | Import | 292941112.52
| Rajshahi Zone |  |  | 13.1585 | 0 | 0.13095 | 0 | 0 | 1.1844 | 26.1873 | 0 | 40.6611 | Wind | 0.25296 | Wind | 3721041.6
| Rangpur Zone |  |  | 0 | 1.2847 | 0.39204 | 0 | 0 | 1.0671 | 0 | 0 | 2.7438
| Total |  |  | 103.0122 | 69.7627 | 5.5326 | 0 | 1.7915 | 3.7146 | 49.1808 | 0.25296 | 233.2473
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 365058249.66 |  | Hydro | 179150
|  |  |  | Coal | 447596046.2075 |  | Solar | 59273849.5664
|  |  |  | HFO | 94150026.97 |  | Import | 292941112.52
|  |  |  | HSD | 0 |  | Wind | 3721041.6
[5 empty] | Total: | 126,29,19,476 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9324 | Peak Hr Flow | 861.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51870012.37 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.1873 | Peak Hr Flow | 1378.58 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2547 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.0611 | Peak Hr Flow | 100.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2754 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.1808 | Peak Hr Flow | 2339.58 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4288
|  |  |  | Chattogram |  | 0 |  | 1167
|  |  |  | Cumilla |  | 0 |  | 940
|  |  |  | Mymensingh |  | 0 |  | 849
|  |  |  | Sylhet |  | 0 |  | 403
|  |  |  | Khulna |  | 0 |  | 1263
|  |  |  | Barishal |  | 0 |  | 313
|  |  |  | Rajshahi |  | 0 |  | 970
|  |  |  | Rangpur |  | 0 |  | 738
|  |  |  | Total |  | 0 |  | 10931
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 16:10 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to Annual Maintenance
| 08:10 | 16:10 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to Annual Maintenance
| 08:10 | 16:10 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to Annual Maintenance
| 08:10 | 16:08 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to Annual Maintenance
| 08:15 | 16:53 | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance Work
| 08:16 | 16:41 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Gopalganj 400/132kV end Due to Annual Maintenance
| 08:21 | 15:41 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to
Annual Maintanence
| 08:22 | 15:40 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to
Annual Maintanence
| 08:23 | 17:56 | Rahanpur 400/132kV S/S AT-01 LT Scheduled S/D
| 08:23 | 17:55 | Rahanpur 400/132kV S/S AT-01 HT Scheduled S/D
| 08:23 | 21:31 | Bhulta-Haripur 230 kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to CT changing
work. and from Bhulta 400/230kV end Due to Annual.Maintenance
| 08:25 | 16:55 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
Maintenance on Bay equipment of Uttara sector-18 ckt.
| 08:26 | 17:13 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Scheduled S/D from Rajshahi 230/132/33kV end Due to
Annual Maintenance. and from Rajshahi 132/33kV end Due to Annual Maintenance Work.
| 08:33 | 13:57 | Maijdee 132/33kV S/S TR-01 HT Scheduled S/D Due to Silicon painting work, top surface of
GIS building
| 08:35 | 17:17 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Control cable change
| 08:38 | 17:15 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Control cable change
| 08:42 | 16:48 | Baroaulia 132/33kV S/S T2(415T) HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 20.0MW load
interrup.
| 08:44 | 15:01 | Agargaon-Bhasantek 132kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to Annual
Maintenance.
| 08:52 | 14:42 | Noapara 132/33kV S/S BUS-B Scheduled S/D
| 08:52 | 16:08 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 08:54 | 17:56 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
| 08:55 | 17:55 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-01 Scheduled S/D Due to Annual maintenance
| 09:03 | 18:00 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to Annual Maintenance
| 09:03 | 18:01 | Jashore 132/33kV S/S JH-1(L2) Scheduled S/D Due to Annual Maintanance
| 09:07 | 16:05 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to AM
| 09:07 | 15:15 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Scheduled S/D Due to Annual
Maintenance
| 09:08 | 15:13 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Annual
Maintenance
| 09:19 | 15:42 | BIPTC S/S 10CF15 Scheduled S/D Due to Annual Maintenance
| 09:20 | 15:24 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end Due to
AnnaulMaintenanceend at Kishoreganj S/S
| 09:20 | 16:22 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance on Bay equipment of
Uttara sector-18 ckt
| 09:20 | 16:48 | Baghabari-Ishurdi 230 kV Ckt-2 Scheduled S/D from Ishurdi 230/132kV end Due to A/M and
from Baghabari 230/132kV end Due to Annual Maintenance
| 09:21 | 15:22 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to
Annual Maintenance
| 09:24 | 15:33 | Bhangura 132/33kV S/S Tr-1(403T) LT Scheduled S/D Due to বাৎসরিক মেরামত
| 09:25 | 15:31 | Bhangura 132/33kV S/S Tr-1(403T) HT Scheduled S/D Due to বাৎসরিক মেরামত
| 09:59 | 14:27 | Kodda 132/33kV S/S Tr-1 (406T) LT Scheduled S/D Due to AM
| 09:59 | 14:27 | Kodda 132/33kV S/S Tr-1 (406T) HT Scheduled S/D Due to AM
| 10:38 | 15:53 | Bogura 400/230kV S/S 230 KV BUS-B (B1-B2) Scheduled S/D Due to Annual Maintenance
| 10:47 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:- FGMO Mode Active 10:41
| 10:57 | 19:33 | New Tongi S/S Bus-1 Scheduled S/D Due to Annual Maintanance.
| 11:02 | 15:44 | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to For Relay test
| 11:02 | 19:27 | New Tongi-Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to S/D taken
by new tongi grid
| 11:09 | 17:16 | BIPTC S/S Block-01, Trafo-02 HT Scheduled S/D Due to Oil Leakage Rectification at 2MVA
Auxiliary Transformer
| 13:50 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:- FGMO off 13.49
|  | 14:16 | Chhatak 132/33kV S/S T-2 HT is restored.
|  | 14:17 | Chhatak 132/33kV S/S T-2 LT is restored.
|  | 15:35 | Joydebpur 132/33kV S/S GT-2 HT is restored.
|  | 16:13 | Meghnaghat 230/132kV S/S Bus2 is restored.
| 16:26 |  | P.Sadipur 230/132kv S/S 132KV GIS BUS C-SYN (First Time).
| 16:31 |  | P.Sadipur 230/132kv S/S 132KV GIS BUS B-SYN (First Time).
| 16:36 |  | P.Sadipur 230/132kv S/S 132KV GIS BUS A-SYN (First Time).
|  | 16:48 | Rajbari 132/33kV S/S Bheramara-2 is restored.
|  | 16:48 | Rajbari 132/33kV S/S Bheramara-1 is restored.
|  | 16:50 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 16:50 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 16:53 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
|  | 17:32 | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 is restored.
|  | 17:34 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 is restored.
| 18:00 |  | Evening peak Generation is 11309 MW
| 18:00 |  | Evening Peak Generation: 11309 MW.
| 23:07 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:- FGMO mode active 23:00
| 02:46 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:- FGMO Mode OFF 2.:41
| 03:21 |  | Siddhirganj 335 MW CCPP GT was forced shutdown due to steam leakage.
| 05:00 |  | Minimum Generation: 7828 MW.
| 06:27 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to For project
work and from Khulna(S) 230/132kV end Due to Annual Maintenance
| 06:45 |  | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D
| 07:00 |  | Chandpur 132/33kV S/S 200KVA Aux. T-1 LT Scheduled S/D Due to MAINTAINACE
|  | 07:00 | Chandpur 132/33kV S/S 200KVA Aux. T-2 LT is restored.
| 07:02 |  | Bhulta-Rampura 230 kV Ckt-3 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance.
| 07:03 |  | Narail 132/33kV S/S TR1 (403-T) LT Project Work S/D Due to 33 kv bay extension work | [7 empty] | 20.0MW load
interrup.
| 07:04 |  | Narail 132/33kV S/S TR1 (403-T) HT Project Work S/D Due to 33 kv bay extension work | [7 empty] | 20.0MW load
interrup.
| 07:07 |  | Chandpur 132/33kV S/S 33 kV T-1 Section Scheduled S/D Due to MAINTAINACE | [7 empty] | 6.0MW load
interrup.
| 07:07 |  | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to MAINTAINACE | [7 empty] | 4.0MW load
interrup.
| 07:07 |  | Chandpur 132/33kV S/S 402T (T-01) HT Scheduled S/D Due to MAINTAINACE | [7 empty] | 6.0MW load
interrup.
| 07:08 |  | Chandpur 132/33kV S/S 33 kV T-2 section Scheduled S/D Due to MAINTAINACE | [7 empty] | 4.0MW load
interrup.
| 07:08 |  | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to MAINTAINACE
| 07:15 |  | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to Annual Maintenance Purpose.
| 07:15 |  | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to Annual Maintenance Purpose.
| 07:21 |  | Bhulta-Rampura 230 kV Ckt-3 Scheduled S/D from Bhulta 400/230kV end Due to Scheduled S/D
| 07:29 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to Annual
Maintenance
| 07:41 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Kachua 230/132/33kV end Due to Due to
Annual maintenance.
| 07:49 |  | Baghabari 230/132kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
| 07:52 |  | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to Annual maintenance.
| 07:53 |  | Rajbari 132/33kV S/S Bheramara-2 Scheduled S/D Due to Annual maintenance.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Electrical fault due to Earthquape
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 304 | 8665200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 35209 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 160 | 5523348 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 28.3 | 129960 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 134597 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 65523 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 27.5 | 453000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 532080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 353280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 582862 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 55 | 150624 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 24960 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 253440 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 172077 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 52200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 418 | 8521620 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 10 | 24000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1414.8 | 25673980
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 118125 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 23 | 191520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1791500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 141 | 3447069 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 46 | 343745 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 56 | 226944 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 62182 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 46080 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 341280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 30109 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 31472 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 24 | 59380 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 196800 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 22 | 40145 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 590 | 12299999 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 252960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 350 | 8298181.82 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1449 | 27795971.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 176 | 4726000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8871000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 718632 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 25 | 643200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 53 | 970181 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1008984 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 76 | 351272 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 17 | 16768 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2443274 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 62 | 406080 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 100 | 2061120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 373110 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 55440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 46080 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 415464 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1128 | 23106605
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 84 | 2191680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 266400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 805200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 236750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 27360 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 178 | 3537440
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 727800 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3716591 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 681216 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1376640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3708000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 14 | 347000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 461568 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7442000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 345 | 9022000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Gas shortage
Sylhet Area Total |  |  |  |  | 2325 | 1151 | 27482815
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 861 | 20932364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6768576 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 488880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1035 | 21185454 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2146 | 49375274
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 504 | 7757652 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2696000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 910 | 18936727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 3476660 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3305 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1639 | 32870344.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 291340 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4202727 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 380 | 8955781 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 31202 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 47 | 99744 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1378.58 | 26187272 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 300000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 568310 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2009.58 | 40661096
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1284654 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 115987 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 18564.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 276053 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 170150 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 878400 | -
Rangpur Area Total |  |  |  |  | 950 | 195 | 2743808.84
Eastern Grid Total |  |  |  |  | 17383.855 | 5320.8 | 107596811.82
Western Grid Total |  |  |  |  | 10821.56 | 5989.58 | 125650523.11
National Grid Total |  |  |  |  | 28205.415 | 11310.38 | 233247334.93
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7646.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3284.4 | MW
i) Dhaka area |  |  | 4288.08 |  | MW | i) Khulna area |  |  |  | 1263 | MW
ii) Chattogram area |  |  | 1166.6 |  | MW | ii) Barishal area |  |  |  | 313 | MW
iii) Cumilla area |  |  | 939.8 |  | MW | iii) Rajshahi area |  |  |  | 970.4 | MW
iv) Mymensingh area |  |  | 849 |  | MW | iv) Rangpur area |  |  |  | 738 | MW
v) Sylhet area |  |  | 403 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10930.88 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 15:00 | 67 | Hathazari | 58 | 18:00 | 133 | Niamatpur | 39 | 18:00
2 | AKSML | 156.7 | 14:00 | 68 | Ishurdi | 56 | 18:00 | 134 | Noapara | 42 | 18:00
3 | Aftabnagar | 30 | 13:00 | 69 | Jaldhaka | 53 | 18:00 | 135 | PHP | 8 | 00:00
4 | Agargaon | 98 | 13:00 | 70 | Jamalpur | 85 | 08:00 | 136 | Pabna | 68 | 18:00
5 | Agrabad | 66 | 11:00 | 71 | Jashore | 96 | 13:00 | 137 | Palashbari | 76 | 18:00
6 | Amnura | 16 | 07:00 | 72 | Jhenaidah | 95 | 18:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 57 | 01:00 | 73 | Joydebpur | 107 | 18:00 | 139 | Patiya | 7 | 19:30
8 | BSRM | 202 | 00:00 | 74 | Joypurhat | 43 | 18:00 | 140 | Patuakhali | 43 | 19:30
9 | Bagerhat | 65 | 18:00 | 75 | Juldah | 14 | 16:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 56 | 18:00 | 76 | KSRM | 18 | 13:00 | 142 | Postogola | 56 | 13:00
11 | Bakulia | 64 | 18:00 | 77 | Kabirpur | 180 | 16:00 | 143 | Purbachal | 29 | 13:00
12 | Banani | 35 | 13:00 | 78 | Kachua | 56 | 20:00 | 144 | Purbasadipur | 98 | 18:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 75 | 14:00 | 145 | Rahanpur | 20 | 19:00
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 42 | 18:00 | 146 | Rahim | 44 | 17:00
15 | Barguna | 14 | 18:00 | 81 | Kamrangirchar | 66 | 17:00 | 147 | Rajbari | 59 | 18:00
16 | Barishal | 90 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 106 | 18:00
17 | Barishal-230 | 64 | 18:00 | 83 | Kasba | 22 | 13:00 | 149 | Rajshahi | 63 | 18:00
18 | Baroaulia | 48 | 22:00 | 84 | Kazla | 74 | 22:00 | 150 | Rajshahi-230 | 62 | 12:00
19 | Baroirhat | 48 | 18:00 | 85 | Keranigonj | 72 | 13:00 | 151 | Ramganj | 76 | 18:00
20 | Bashundhara | 139 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 32 | 18:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulna | 57 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 19:00 | 88 | Khulshi | 184 | 14:00 | 154 | Rangpur | 104 | 18:00
23 | Benapole | 38 | 07:00 | 89 | Kishoreganj | 83 | 18:30 | 155 | Ruppur | 3.4 | 16:00
24 | Bhaluka | 123 | 19:00 | 90 | Kodda | 246 | 12:00 | 156 | SSM | 2 | 00:00
25 | Bhandaria | 37 | 19:30 | 91 | Kulaura | 27 | 18:00 | 157 | Saidpur | 91 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 46 | 18:00 | 158 | Satkhira | 88 | 18:00
27 | Bheramara(GK) | 39 | 18:30 | 93 | Kushtia | 109 | 18:00 | 159 | Satmasjid | 83 | 13:00
28 | Bhulta | 207 | 12:00 | 94 | Laksam | 20 | 02:00 | 160 | Savar | 164 | 10:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 24 | 20:00 | 161 | SevenRings | 13.44 | 21:00
30 | Bogura | 113 | 19:00 | 96 | Lalbag | 62 | 13:00 | 162 | ShahCement | 25 | 00:00
31 | Borhanuddin | 63 | 20:00 | 97 | Lalmonirhat | 42 | 18:00 | 163 | Shahjadpur | 55 | 18:00
32 | Brahmanbaria | 89 | 18:00 | 98 | MI_Cement | 4.3 | 03:00 | 164 | Shahjibazar | 78 | 18:00
33 | Cantonment | 100 | 14:00 | 99 | Madanganj | 35 | 18:00 | 165 | Shahmirpur | 40 | 00:00
34 | Chandina | 8.63 | 17:00 | 100 | Madaripur | 70 | 21:00 | 166 | Shariatpur | 54 | 20:00
35 | Chandpur | 51 | 19:00 | 101 | Madartek | 66 | 18:00 | 167 | Sherpur | 100 | 08:00
36 | Chandraghona | 26 | 17:00 | 102 | Madunaghat | 37 | 18:30 | 168 | Shikalbaha | 19 | 18:00
37 | Chapai | 48 | 12:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 70 | 12:00
38 | Charsaidpur | 35 | 16:00 | 104 | Mahasthangarh | 48 | 18:00 | 170 | Sholosohor | 35 | 15:00
39 | Chauddagram | 47 | 17:00 | 105 | Maijdee | 23 | 00:00 | 171 | Shyampur | 132 | 12:00
40 | Chhatak | 21 | 17:00 | 106 | Manikganj | 92 | 18:00 | 172 | Siddhirganj | 98 | 12:00
41 | Chowmuhani | 104 | 19:30 | 107 | Maniknagar | 43 | 13:00 | 173 | Sirajganj | 82 | 18:30
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 36 | 18:00 | 174 | Sonargaon | 112 | 10:00
43 | Coxsbazar | 97 | 18:00 | 109 | Matuail | 56.4 | 18:30 | 175 | Sreemongol | 56 | 18:00
44 | Cumilla(N) | 77 | 00:00 | 110 | Metrorail_Motijheel | 33 | 11:00 | 176 | Sreepur | 89 | 15:00
45 | Cumilla(S) | 125 | 18:00 | 111 | Metrorail_Uttara | 7 | 09:00 | 177 | Srinagar | 30.6 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 84 | 12:00 | 178 | Sunamganj | 38 | 18:00
47 | Daudkandi | 106 | 19:30 | 113 | Mirpur | 115.5 | 12:00 | 179 | Sylhet | 33 | 14:00
48 | DhakaUniversity | 58 | 13:00 | 114 | Mirsorai | 11 | 16:00 | 180 | Sylhet-132 | 85 | 18:00
49 | Dhamrai | 116 | 18:00 | 115 | Mirzapur | 37 | 17:00 | 181 | TK | 17 | 22:00
50 | Dhanmondi | 96 | 13:00 | 116 | Mithapukur | 42 | 18:00 | 182 | Tangail | 124 | 18:00
51 | Dohazari | 74 | 19:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 16 | 16:00
52 | Faridpur | 111 | 18:00 | 118 | Mogbazar | 70 | 13:00 | 184 | Tasnim | 28 | 16:00
53 | Fatullah | 102 | 16:00 | 119 | Mongla | 32 | 15:00 | 185 | Thakurgaon | 75 | 18:00
54 | Fenchuganj | 24 | 19:00 | 120 | Motijheel | 31 | 13:00 | 186 | Tongi | 97 | 11:00
55 | Feni | 71 | 18:00 | 121 | Muktagacha | 26 | 18:00 | 187 | Ullahpara | 25 | 18:00
56 | GPH | 17 | 00:00 | 122 | Munshiganj | 73 | 00:00 | 188 | Ullon | 52 | 13:00
57 | Ghatail | 58 | 18:30 | 123 | Muradnagar | 25 | 18:30 | 189 | Uttara | 65 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 126 | 18:00 | 190 | UttaraNew | 30 | 13:00
59 | Ghorashal-230 | 74 | 17:00 | 125 | Naogaon | 80 | 18:00 | 191 | Zigatola | 56 | 12:00
60 | Goalpara | 24 | 13:00 | 126 | Narail | 41 | 18:00
61 | Gollamari | 70 | 12:00 | 127 | Narinda | 60 | 13:00
62 | Gopalganj | 77 | 18:00 | 128 | Narshingdi | 138 | 19:00
63 | Gulshan | 84 | 13:00 | 129 | Natore | 97 | 18:30
64 | Halishahar | 61 | 13:00 | 130 | Nawabganj | 30 | 21:00
65 | HaripurSBU | 141 | 16:00 | 131 | Netrakona | 101 | 18:00
66 | Hasnabad | 70 | 13:00 | 132 | New | 66.8 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9387 | 0 |  | 9387
1:00 | 8814.5 | 0 |  | 8814.5
2:00 | 8413.5 | 0 |  | 8413.5
3:00 | 8208.5 | 0 |  | 8208.5
4:00 | 7928.5 | 0 |  | 7928.5
5:00 | 7868.5 | 0 |  | 7868.5
6:00 | 8149.5 | 0 |  | 8149.5
7:00 | 8952.54 | 0 |  | 8952.54
8:00 | 9505.86 | 0 |  | 9505.86
9:00 | 9440.55 | 0 |  | 9440.55
10:00 | 9406.65 | 0 |  | 9406.65
11:00 | 9763.39 | 0 |  | 9763.39
12:00 | 10133.41 | 0 |  | 10133.41
13:00 | 10556.71 | 0 |  | 10556.71
14:00 | 10062.85 | 0 |  | 10062.85
15:00 | 9916.26 | 0 |  | 9916.26
16:00 | 9754.09 | 0 |  | 9754.09
17:00 | 10238.44 | 0 |  | 10238.44
18:00 | 11310.38 | 0 |  | 11310.38
19:00 | 10916.56 | 0 |  | 10916.56
19:30 | 10755.28 | 0 |  | 10755.28
20:00 | 10668.44 | 0 |  | 10668.44
21:00 | 10524.76 | 0 |  | 10524.76
22:00 | 10018.78 | 0 |  | 10018.78
23:00 | 9702.08 | 0 |  | 9702.08
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4288 | 5099 | 9387 | DAILY GENERATION CURVE
00:30 | 4241.25 | 4859.5 | 9100.75
01:00 | 4194.5 | 4620 | 8814.5 | 23-11-2025
01:30 | 4058 | 4556 | 8614
02:00 | 3921.5 | 4492 | 8413.5
02:30 | 3852.5 | 4458.5 | 8311
03:00 | 3783.5 | 4425 | 8208.5
03:30 | 3681.5 | 4387 | 8068.5
04:00 | 3579.5 | 4349 | 7928.5
04:30 | 3563.5 | 4335 | 7898.5
05:00 | 3547.5 | 4321 | 7868.5
05:30 | 3629.5 | 4379.5 | 8009
06:00 | 3711.5 | 4438 | 8149.5
06:30 | 4009.54 | 4541.48 | 8551.02
07:00 | 4307.58 | 4644.96 | 8952.54
07:30 | 4377.25 | 4851.95 | 9229.2
08:00 | 4446.92 | 5058.94 | 9505.86
08:30 | 4362.175 | 5111.03 | 9473.205
09:00 | 4277.43 | 5163.12 | 9440.55
09:30 | 4273.08 | 5150.52 | 9423.6
10:00 | 4268.73 | 5137.92 | 9406.65
10:30 | 4404.35 | 5180.67 | 9585.02
11:00 | 4539.97 | 5223.42 | 9763.39
11:30 | 4611.96 | 5336.44 | 9948.4
12:00 | 4683.95 | 5449.46 | 10133.41
12:30 | 4879.46 | 5465.6 | 10345.06
13:00 | 5074.97 | 5481.74 | 10556.71
13:30 | 4939.455 | 5370.325 | 10309.78
14:00 | 4803.94 | 5258.91 | 10062.85
14:30 | 4748.095 | 5241.46 | 9989.555
15:00 | 4692.25 | 5224.01 | 9916.26
15:30 | 4736.785 | 5098.39 | 9835.175
16:00 | 4781.32 | 4972.77 | 9754.09
16:30 | 4902.195 | 5094.07 | 9996.265
17:00 | 5023.07 | 5215.37 | 10238.44
17:30 | 5171.935 | 5602.475 | 10774.41
18:00 | 5320.8 | 5989.58 | 11310.38
18:30 | 5130.4 | 5983.07 | 11113.47
19:00 | 4940 | 5976.56 | 10916.56
19:30 | 4758 | 5997.28 | 10755.28
20:00 | 4695 | 5973.44 | 10668.44
20:30 | 4665 | 5931.6 | 10596.6 |  | Executive Engineer
21:00 | 4635 | 5889.76 | 10524.76 |  | Network Operation Division
21:30 | 4481.5 | 5790.27 | 10271.77
22:00 | 4328 | 5690.78 | 10018.78
22:30 | 4306.5 | 5553.93 | 9860.43
23:00 | 4285 | 5417.08 | 9702.08

## En-Curve
QF-LDC-12
Date | 23-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3100 | 1150 | 887 | 0 | 86 | 1120 | 86 | 2933 | 0 | 0 | 24 | 0 | 0 | 1 | 0 | DAILY ENERGY CURVE
00:30 | 3094 | 1141.75 | 887 | 0 | 81 | 1030 | 86 | 2759 | 0 | 0 | 20 | 0 | 0 | 2 | 0 | 23-11-2025
01:00 | 3088 | 1133.5 | 887 | 0 | 76 | 940 | 86 | 2585 | 0 | 0 | 16 | 0 | 0 | 3 | 0
01:30 | 3053.5 | 1090.5 | 887 | 0 | 77 | 889 | 86 | 2520 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | Energy Generated | 233.2473 |  | MKWHr
02:00 | 3019 | 1047.5 | 887 | 0 | 78 | 838 | 86 | 2455 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2971.5 | 1045 | 874.5 | 0 | 79 | 839.5 | 86 | 2410 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | Total Energy Requirement | 233.2473 |  | MKWHr
03:00 | 2924 | 1042.5 | 862 | 0 | 80 | 841 | 86 | 2365 | 0 | 0 | 0 | 0 | 0 | 8 | 0
03:30 | 2859.5 | 1040 | 862 | 0 | 74 | 838.5 | 86 | 2297.5 | 0 | 0 | 0 | 0 | 0 | 11 | 0
04:00 | 2795 | 1037.5 | 862 | 0 | 68 | 836 | 86 | 2230 | 0 | 0 | 0 | 0 | 0 | 14 | 0
04:30 | 2766 | 1025.5 | 862 | 0 | 70 | 844 | 86 | 2232 | 0 | 0 | 0 | 0 | 0 | 13 | 0
05:00 | 2737 | 1013.5 | 862 | 0 | 72 | 852 | 86 | 2234 | 0 | 0 | 0 | 0 | 0 | 12 | 0
05:30 | 2862.5 | 1019 | 861.5 | 0 | 69 | 852.5 | 86 | 2247 | 0 | 0 | 0 | 0 | 0 | 11.5 | 0
06:00 | 2988 | 1024.5 | 861 | 0 | 66 | 853 | 86 | 2260 | 0 | 0 | 0 | 0 | 0 | 11 | 0
06:30 | 3139.5 | 1128 | 861.5 | 0 | 67 | 873.5 | 86 | 2362.5 | 19.52 | 0 | 2 | 0 | 0 | 11.5 | 0
07:00 | 3291 | 1231.5 | 862 | 0 | 68 | 894 | 86 | 2465 | 39.04 | 0 | 4 | 0 | 0 | 12 | 0
07:30 | 3244.5 | 1193 | 861.5 | 0 | 75 | 965.5 | 86 | 2634 | 117.2 | 0 | 40 | 0 | 0 | 12.5 | 0
08:00 | 3198 | 1154.5 | 861 | 0 | 82 | 1037 | 86 | 2803 | 195.36 | 0 | 76 | 0 | 0 | 13 | 0
08:30 | 3134 | 1093 | 861.5 | 0 | 78 | 1028.5 | 86 | 2828.5 | 288.705 | 1 | 65.5 | 0 | 0 | 8.5 | 0
09:00 | 3070 | 1031.5 | 862 | 0 | 74 | 1020 | 86 | 2854 | 382.05 | 2 | 55 | 0 | 0 | 4 | 0
09:30 | 3052.5 | 1027.5 | 862 | 0 | 77 | 971.5 | 86 | 2818 | 449.6 | 12 | 62.5 | 0 | 0 | 5 | 0
10:00 | 3035 | 1023.5 | 862 | 0 | 80 | 923 | 86 | 2782 | 517.15 | 22 | 70 | 0 | 0 | 6 | 0
10:30 | 3075 | 1099.75 | 862 | 0 | 85 | 924.5 | 86 | 2794 | 553.77 | 32 | 61.5 | 0 | 0 | 11.5 | 0
11:00 | 3115 | 1176 | 862 | 0 | 90 | 926 | 86 | 2806 | 590.39 | 42 | 53 | 0 | 0 | 17 | 0
11:30 | 3125.5 | 1208.75 | 862 | 0 | 89 | 998.5 | 86 | 2855 | 598.15 | 42 | 68 | 0 | 0 | 15.5 | 0
12:00 | 3136 | 1241.5 | 862 | 0 | 88 | 1071 | 86 | 2904 | 605.91 | 42 | 83 | 0 | 0 | 14 | 0
12:30 | 3138.5 | 1250 | 862 | 0 | 93 | 1072 | 86 | 2916 | 578.81 | 54 | 283.25 | 0 | 0 | 11.5 | 0
13:00 | 3141 | 1258.5 | 862 | 0 | 98 | 1073 | 86 | 2928 | 551.71 | 66 | 483.5 | 0 | 0 | 9 | 0
13:30 | 3101 | 1215 | 862 | 0 | 100 | 1072.5 | 86 | 2928.5 | 494.78 | 70 | 370 | 0 | 0 | 10 | 0
14:00 | 3061 | 1171.5 | 862 | 0 | 102 | 1072 | 86 | 2929 | 437.85 | 74 | 256.5 | 0 | 0 | 11 | 0
14:30 | 3094 | 1162.25 | 862 | 0 | 100 | 1073.755 | 86 | 2932.5 | 356.55 | 74 | 240 | 0 | 0 | 8.5 | 0
15:00 | 3127 | 1153 | 862 | 0 | 98 | 1075.51 | 86 | 2936 | 275.25 | 74 | 223.5 | 0 | 0 | 6 | 0
15:30 | 3136.5 | 1213 | 861.5 | 0 | 94 | 1072.54 | 86 | 2869.5 | 197.635 | 69 | 228 | 0 | 0 | 7.5 | 0
16:00 | 3146 | 1273 | 861 | 0 | 90 | 1069.57 | 86 | 2803 | 120.02 | 64 | 232.5 | 0 | 0 | 9 | 0
16:30 | 3113.5 | 1304.5 | 861.5 | 0 | 91 | 1113.315 | 86 | 2885.5 | 62.7 | 108.5 | 354.75 | 0 | 0 | 15 | 0
17:00 | 3081 | 1336 | 862 | 0 | 92 | 1157.06 | 86 | 2968 | 5.38 | 153 | 477 | 0 | 0 | 21 | 0
17:30 | 2994 | 1319.25 | 861.5 | 0 | 96 | 1267.82 | 66 | 3206 | 2.69 | 166 | 777.65 | 0 | 0 | 17.5 | 0
18:00 | 2907 | 1302.5 | 861 | 0 | 100 | 1378.58 | 46 | 3444 | 0 | 179 | 1078.3 | 0 | 0 | 14 | 0
18:30 | 2924 | 1316.25 | 861 | 0 | 98 | 1422.07 | 46 | 3506 | 0 | 97.5 | 828.65 | 0 | 0 | 14 | 0
19:00 | 2941 | 1330 | 861 | 0 | 96 | 1465.56 | 46 | 3568 | 0 | 16 | 579 | 0 | 0 | 14 | 0
19:30 | 2998 | 1368 | 861 | 0 | 98 | 1473.28 | 46 | 3558 | 0 | 16 | 329 | 0 | 0 | 8 | 0
20:00 | 3008 | 1385 | 862 | 0 | 98 | 1476.44 | 46 | 3533 | 0 | 8 | 245 | 0 | 0 | 7 | 0
20:30 | 2993 | 1406 | 861.5 | 0 | 95 | 1468.6 | 46 | 3502.5 | 0 | 8 | 208.5 | 0 | 0 | 7.5 | 0
21:00 | 2978 | 1427 | 861 | 0 | 92 | 1460.76 | 46 | 3472 | 0 | 8 | 172 | 0 | 0 | 8 | 0
21:30 | 2935.5 | 1386.5 | 861.5 | 0 | 88 | 1420.27 | 46 | 3399.5 | 0 | 4 | 120.5 | 0 | 0 | 10 | 0
22:00 | 2893 | 1346 | 862 | 0 | 84 | 1379.78 | 46 | 3327 | 0 | 0 | 69 | 0 | 0 | 12 | 0
22:30 | 2848 | 1322 | 861.5 | 0 | 89 | 1345.93 | 46 | 3282.5 | 0 | 0 | 51.5 | 0 | 0 | 14 | 0
23:00 | 2803 | 1298 | 861 | 0 | 94 | 1312.08 | 46 | 3238 | 0 | 0 | 34 | 0 | 0 | 16 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 04:00 | 379 | 12:00 | Meghnaghat | 399 | 04:00 | 379 | 12:00
Ashuganj | 403 | 6:00 | 383 | 12:00 | Payra | 416 | 04:00 | 409 | 18:30
Bhulta | 399 | 04:00 | 377 | 12:00 | Rahanpur | 414 | 03:00 | 398 | 19:00
Bibiana | 400 | 02:00 | 390 | 12:00 | Rampal | 415 | 04:00 | 400 | 12:00
BIPTC | 405 | 03:00 | 396 | 11:00
Bogura | 407 | 04:00 | 387 | 19:00
Gopalganj | 409 | 04:00 | 394 | 12:00
Kaliakoir | 396 | 04:00 | 375 | 16:00
Korerhat | 405 | 06:00 | 389.56 | 12:00
Madunaghat | 399 | 04:00 | 390 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 225 | 12:00 | Kachua | 236 | 18:00 | 221 | 11:00
AKSML | 237 | 01:00 | 228 | 11:00 | Kaliakoir | 240 | 04:00 | 226 | 15:00
Aminbazar | 239 | 05:00 | 226 | 12:00 | Keranigonj | 238 | 04:00 | 223 | 12:00
Ashuganj | 233 | 01:00 | 225 | 11:00 | Khulna(S) | 240 | 04:00 | 232 | 12:00
Ashuganj-400 | 233 | 01:00 | 225 | 11:00 | Korerhat | 238 | 04:00 | 229 | 16:00
Baghabari | 236 | 02:00 | 228 | 18:00 | Madunaghat | 237 | 05:00 | 231 | 12:00
Barapukuria | 225 | 04:00 | 213 | 19:00 | Madunaghat-400 | 237 | 04:00 | 232 | 12:00
Barapukuria-230 | 225 | 04:00 | 213 | 19:00 | Maniknagar | 233 | 03:00 | 218 | 12:00
Barishal | 243 | 02:00 | 236 | 12:00 | Meghnaghat | 238 | 00:00 | 227 | 12:00
Bheramara | 236 | 05:00 | 225 | 12:00 | Meghnaghat-400 | 235 | 04:00 | 221 | 12:00
Bhulta | 233 | 03:00 | 218 | 12:00 | Mirsorai | 236 | 04:00 | 225 | 11:00
Bibiana | 237 | 03:00 | 229 | 12:00 | Rajshahi | 235 | 05:00 | 225 | 12:00
BIPTC | 238 | 04:00 | 226 | 12:00 | Rampal | 239 | 05:00 | 229 | 12:00
Bogura | 236 | 04:00 | 224 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 235 | 04:00 | 225 | 19:00 | Rampura | 232 | 04:00 | 216 | 12:00
Borhanuddin | 244 | 01:00 | 239 | 12:00 | Shikalbaha | 234 | 05:00 | 229 | 11:00
BSRM | 234 | 04:00 | 225 | 12:00 | Shyampur | 236 | 04:00 | 222 | 12:00
Cumilla(N) | 234 | 06:00 | 223 | 12:00 | Siddhirganj | 232 | 01:00 | 220 | 12:00
Faridpur | 242 | 04:00 | 233 | 12:00 | Sirajgonj | 240 | 04:00 | 233 | 19:00
Fenchuganj | 238 | 07:00 | 232 | 12:00 | Sreepur | 231 | 04:00 | 224 | 15:00
Feni | 234 | 6:00 | 223 | 11:00 | Tongi | 234 | 04:00 | 223 | 15:00
Ghorashal | 0 | 00:00 | N/A | N/A
Ghorashal-230 | 231 | 04:00 | 216 | 12:00
Gopalganj | 242 | 04:00 | 233 | 12:00
GPH | 236 | 04:00 | 232 | 00:00
Haripur | 234 | 04:00 | 219 | 12:00
Hasnabad | 237 | 03:00 | 222 | 12:00
Hathazari | 235 | 18:00 | 227 | 12:00
Ishurdi | 239 | 05:00 | 228 | 12:00
Jhenaidah | 238 | 05:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 02:00 | 124 | 12:00 | Lalbag | 139 | 04:00 | 128 | 12:00
Agargaon | 139 | 04:00 | 129 | 12:00 | Lalmonirhat | 131 | 06:00 | 122 | 08:00
Agrabad | 136 | 04:00 | 132 | 11:00 | Madanganj | 136 | 05:00 | 130 | 10:00
AKS | 134 | 04:00 | 131 | 02:00 | Madaripur | 139 | 05:00 | 135 | 12:00
Aminbazar | 139 | 05:00 | 130 | 11:00 | Madartek | 135 | 03:00 | 124 | 16:00
Amnura | 138 | 02:00 | 130 | 12:00 | Madunaghat | 138 | 05:00 | 134 | 12:00
Ashuganj | 140 | 00:00 | 138 | 11:00 | Magura | 140 | 05:00 | 132 | 12:00
Bagerhat | 137 | 03:00 | 129 | 18:00 | Mahasthangarh | 133 | 03:00 | 127 | 19:00
Bajitpur | 137 | 04:00 | 133 | 18:00 | Maijdee | 135 | 04:00 | 128 | 12:00
Bakulia | 137 | 18:00 | 133 | 11:00 | Manikganj | 137 | 06:00 | 125 | 15:00
Banani | 135 | 02:00 | 124 | 12:00 | Maniknagar | 138 | 05:00 | 129 | 12:00
Bangabhaban | 138 | 04:00 | 128 | 12:00 | Matarbari | 129 | 04:00 | 122 | 18:00
Barapukuria | 138 | 04:00 | 129 | 08:00 | Matuail | 136.7 | 05:00 | 127 | 12:00
Barguna | 136 | 03:00 | 133 | 18:00 | Metrorail_Motijheel | 138 | 05:00 | 129 | 12:00
Barishal | 139 | 01:00 | 135 | 12:00 | Metrorail_Uttara | 139 | 01:00 | 129 | 12:00
Barishal-230 | 140 | 02:00 | 134 | 13:00 | Millgate | 141 | 03:00 | 129 | 15:00
Baroaulia | 138 | 06:00 | 132 | 15:00 | Mirpur | 138 | 03:00 | 129 | 12:00
Baroirhat | 135 | 03:00 | 131 | 10:00 | Mirzapur | 136 | 04:00 | 128 | 19:30
Bashundhara | 136 | 04:00 | 124 | 12:00 | Mithapukur | 135 | 06:00 | 124 | 08:00
BashundharaCement | 136 | 05:00 | 130 | 10:00 | MI_Cement | 136 | 04:00 | 125.1 | 12:00
Beanibazar | 133 | 01:00 | 130 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 138 | 04:00 | 122 | 12:00 | Mogbazar | 137 | 03:00 | 125 | 12:00
Bhaluka | 132 | 05:00 | 127 | 19:00 | Mongla | 137 | 05:00 | 129 | 18:00
Bhandaria | 138 | 03:00 | 132 | 13:00 | Motijheel | 138 | 04:00 | 128 | 12:00
Bhangura | 135 | 01:00 | 131 | 13:00 | Muktagacha | 136 | 08:00 | 128 | 21:00
Bheramara | 140 | 03:00 | 135 | 12:00 | Munshiganj | 135 | 04:00 | 125 | 12:00
Bheramara(GK) | 140 | 04:00 | 136 | 12:00 | Muradnagar | 137 | 04:00 | 128 | 12:00
Bhulta | 130 | 01:00 | 123 | 12:00 | Mymensingh | 136 | 10:00 | 125 | 05:00
Bog-Sherpur | 136 | 04:00 | 128 | 19:00 | Naogaon | 132 | 05:00 | 126 | 08:00
Bogura | 136 | 04:00 | 128 | 19:00 | Narail | 140 | 03:00 | 131 | 12:00
Bogura-230 | 135 | 03:00 | 128 | 19:00 | Narinda | 0 | 00:00 | N/A | N/A
Brahmanbaria | 135 | 06:00 | 132 | 11:00 | Narshingdi | 135 | 01:00 | 122 | 12:00
Cantonment | 139 | 04:00 | 129 | 12:00 | Natore | 136 | 06:00 | 131 | 12:00
Chandina | 139 | 04:00 | 131 | 12:00 | Nawabganj | 139 | 04:00 | 128 | 12:00
Chandpur | 138 | 18:00 | 132 | 11:00 | Netrakona | 129 | 01:00 | 124 | 18:30
Chandraghona | 139 | 06:00 | 134 | 12:00 | New | 140 | 06:00 | 130 | 15:00
Chapai | 139 | 03:00 | 132 | 19:30 | Niamatpur | 139 | 04:00 | 133 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 136 | 02:00 | 126 | 12:00 | Noapara | 139 | 03:00 | 131 | 12:00
Chauddagram | 137 | 02:00 | 130 | 11:00 | Pabna | 139 | 04:00 | 133 | 12:00
Chhatak | 132 | 01:00 | 128 | 00:00 | Palashbari | 131 | 04:00 | 122 | 08:00
Chowmuhani | 133 | 04:00 | 128 | 11:00 | Panchagarh | 137 | 04:00 | 121 | 08:00
Chuadanga | 139 | 04:00 | 130 | 12:00 | Patiya | 137 | 18:00 | 133 | 00:00
Coxsbazar | 128 | 08:00 | 122 | 17:00 | Patuakhali | 136 | 04:00 | 134 | 00:00
Cumilla(N) | 138 | 06:00 | 131 | 12:00 | Payra | 137 | 07:00 | 134 | 13:00
Cumilla(S) | 139 | 04:00 | 126 | 08:00 | PHP | 136 | 05:00 | 130 | 12:00
Daganbhuiyan | 136 | 04:00 | 130 | 11:00 | Postogola | 137 | 04:00 | 127 | 12:00
Daudkandi | 134 | 02:00 | 126 | 12:00 | Purbachal | 136 | 03:00 | 124 | 12:00
DhakaUniversity | 136 | 02:00 | 125 | 12:00 | Purbasadipur | 132 | 04:00 | 123 | 08:00
Dhamrai | 138 | 05:00 | 128 | 15:00 | Rahanpur | 139 | 05:00 | 133 | 18:30
Dhanmondi | 136 | 05:00 | 128 | 12:00 | Rahanpur-400 | 139 | 02:00 | 134 | 19:00
Dohazari | 134 | 05:00 | 128 | 12:00 | Rahim | 136 | 05:00 | 127 | 12:00
Faridpur | 140 | 03:00 | 134 | 12:00 | Rajbari | 140 | 03:00 | 134 | 12:00
Fatullah | 140 | 03:00 | 125 | 12:00 | Rajendrapur | 135 | 05:00 | 128 | 10:00
Fenchuganj | 140 | 04:00 | 136 | 11:00 | Rajshahi | 135 | 04:00 | 130 | 12:00
Feni | 136 | 04:00 | 130 | 11:00 | Rajshahi-230 | 136 | 04:00 | 130 | 12:00
Feni-230 | 137 | 5:00 | 131 | 11:00 | Ramganj | 135 | 01:00 | 129 | 12:00
Ghatail | 133 | 14:00 | 127 | 07:00 | Rampur | 136 | 03:00 | 131 | 11:00
Ghorashal | 136 | 08:00 | 131 | 12:00 | Rampura | 135 | 04:00 | 124 | 12:00
Goalpara | 140 | 03:00 | 132 | 12:00 | Rangamati | 138 | 06:00 | 134 | 11:00
Gollamari | 139 | 03:00 | 133 | 12:00 | Rangpur | 132 | 01:00 | 124 | 07:00
Gopalganj | 139 | 02:00 | 133 | 12:00 | Ruppur | 140 | 06:00 | 135 | 12:00
Gopalganj-400 | 141 | 03:00 | 135 | 12:00 | Saidpur | 134 | 05:00 | 125 | 08:00
Gulshan | 135 | 05:00 | 124 | 12:00 | Satkhira | 138 | 04:00 | 130 | 18:00
Halishahar | 137 | 04:00 | 133 | 11:00 | Satmasjid | 139 | 04:00 | 129 | 12:00
Haripur | 137 | 04:00 | 127 | 12:00 | Savar | 137 | 05:00 | 128 | 12:00
HaripurSBU | 137 | 04:00 | 127 | 12:00 | SevenRings | 136 | 04:00 | 131 | 12:00
Hasnabad | 136 | 05:00 | 128 | 15:00 | ShahCement | 136 | 02:00 | 126 | 12:00
Hathazari | 138 | 17:00 | 134 | 12:00 | Shahjadpur | 140 | 03:00 | 135 | 12:00
Ishurdi | 141 | 04:00 | 136 | 12:00 | Shahjibazar | 136 | 07:00 | 134 | 00:00
Jaldhaka | 131 | 03:00 | 119 | 08:00 | Shahmirpur | 137 | 02:00 | 134 | 01:00
Jamalpur | 134 | 11:00 | 119 | 21:00 | Shariatpur | 140 | 03:00 | 134 | 12:00
Jashore | 138 | 05:00 | 123 | 12:00 | Sherpur | 132 | 11:00 | 115 | 07:00
Jhenaidah | 141 | 03:00 | 124 | 13:00 | Shikalbaha | 127 | 18:00 | 122 | 11:00
Jhenaidah-230 | 142 | 04:00 | 133 | 12:00 | Shikalbaha-230 | 138 | 03:00 | 134 | 11:00
Joydebpur | 135 | 08:00 | 128 | 11:00 | Shitalakhya | 136 | 04:00 | 125.1 | 12:00
Joypurhat | 131 | 03:00 | 124 | 13:00 | Sholosohor | 138 | 05:00 | 134 | 11:00
Juldah | 138 | 18:00 | 133 | 11:00 | Shyampur | 137 | 08:00 | 130 | 12:00
Kabirpur | 137 | 06:00 | 127 | 15:00 | Shyampur-230 | 140 | 03:00 | 131 | 12:00
Kachua | 139 | 03:00 | 131 | 11:00 | Siddhirganj | 136 | 01:00 | 128 | 12:00
Kaliakoir | 140 | 04:00 | 131 | 14:00 | Sirajganj | 135 | 04:00 | 128 | 19:00
Kallyanpur | 138 | 04:00 | 130 | 11:00 | Sonargaon | 135 | 03:00 | 126 | 12:00
Kalurghat | 138 | 18:00 | 134 | 00:00 | Sreemongol | 136 | 01:00 | 134 | 11:00
Kamrangirchar | 138 | 01:00 | 128 | 12:00 | Sreepur | 136 | 04:00 | 130 | 16:00
Kaptai | 140 | 4:00 | 136 | 12:00 | Srinagar | 139 | 03:00 | 128 | 12:00
Kasba | 136 | 03:00 | 128 | 12:00 | SSM | 140 | 00:00 | 139 | 10:00
Kazla | 138 | 05:00 | 129 | 12:00 | Sunamganj | 131 | 02:00 | 128 | 14:00
Keranigonj | 139 | 04:00 | 129 | 12:00 | Sylhet | 135 | 05:00 | 131 | 12:00
Khagrachori | 138 | 04:00 | 133 | 11:00 | Sylhet-132 | 133 | 02:00 | 130 | 15:00
Khulna | 138 | 06:00 | 131 | 12:00 | Tangail | 132 | 04:00 | 126 | 19:30
Khulna(S) | 140 | 04:00 | 133 | 12:00 | Taraganj | 133 | 05:00 | 122 | 08:00
Khulshi | 135 | 03:00 | 130 | 12:00 | Tasnim | 134 | 03:00 | 127 | 12:00
Kishoreganj | 135 | 06:00 | 131 | 12:00 | Thakurgaon | 137 | 18:30 | 119 | 08:00
Kodda | 133 | 02:00 | 125 | 11:00 | TK | 138 | 06:00 | 133 | 11:00
KSRM | 138 | 03:00 | 133 | 12:00 | Tongi | 141 | 04:00 | 131 | 15:00
Kulaura | 139 | 02:00 | 136 | 11:00 | Ullahpara | 137 | 02:00 | 131 | 18:30
Kurigram | 131 | 02:00 | 118 | 08:00 | Ullon | 135 | 05:00 | 124 | 16:00
Kushtia | 137 | 03:00 | 129 | 12:00 | Uttara | 139 | 00:00 | 129 | 16:00
Laksam | 138 | 05:00 | 131 | 11:00 | UttaraNew | 139 | 01:00 | 129 | 12:00
Lakshmipur | 135 | 07:00 | 129 | 11:00 | Zigatola | 139 | 04:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division