## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-11-2025 | [28 empty] | Date: | 24-11-2025 | [28 empty] | Date: | 24-11-2025 | [28 empty] | Date: | 24-11-2025 | [28 empty] | Date: | 24-11-2025 | [14 empty] | Date: | 24-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 32 | 350 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 620 | 0 | 51 | 0 | 45 | 330 | 0 | 0 | 15 | 183 | 37 | 0 | 110 | 0 | 0 | 20 | 0 | 92 | 0 | 0 | 0 | 300 | 0 | 317 | 0 | 30 | 147 | 20 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 16 | 0 | 89 | 0 | 0 | 0 | 4240.5 | 861 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 877 | 0 | 1163.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 251 | 900 | 0 | 5157.5 | 9398 | 100.09
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 32 | 350 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 606 | 0 | 5 | 0 | 45 | 330 | 0 | 0 | 15 | 188 | 38 | 0 | 110 | 0 | 0 | 20 | 0 | 78 | 0 | 0 | 0 | 300 | 0 | 326 | 0 | 30 | 148 | 16 | 0 | 41 | 30 | 0 | 15 | 157 | 0 | 8 | 0 | 108 | 0 | 0 | 0 | 4170.5 | 861 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 883.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 251 | 700 | 0 | 4562.19 | 8732.69 | 100.08
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 610 | 0 | 5 | 0 | 8 | 280 | 0 | 0 | 7 | 189 | 5 | 0 | 110 | 0 | 0 | 20 | 0 | 72 | 0 | 0 | 0 | 305 | 0 | 329 | 0 | 30 | 149 | 16 | 0 | 8 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 3978.5 | 861 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 849.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 252 | 550 | 0 | 4369.94 | 8348.44 | 100.08
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 350 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 8 | 280 | 0 | 0 | 5 | 191 | 5 | 0 | 110 | 0 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 339 | 0 | 30 | 150 | 16 | 0 | 8 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3913.5 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 836.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 252 | 500 | 0 | 4200.93 | 8114.43 | 100.07
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 605 | 0 | 5 | 0 | 8 | 260 | 0 | 0 | 5 | 190 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 72 | 0 | 0 | 0 | 310 | 0 | 326 | 0 | 30 | 154 | 16 | 0 | 8 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3678.5 | 862 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 830.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 252 | 500 | 0 | 4158.17 | 7836.67 | 100.07
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 602 | 0 | 5 | 0 | 8 | 260 | 0 | 0 | 5 | 190 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 74 | 0 | 0 | 0 | 305 | 0 | 336 | 0 | 30 | 120 | 16 | 0 | 8 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3652.5 | 861 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 845.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 254 | 500 | 0 | 4176.87 | 7829.37 | 100.06
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 655 | 0 | 5 | 0 | 8 | 260 | 0 | 0 | 5 | 188 | 5 | 0 | 113 | 0 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 333 | 0 | 30 | 132 | 16 | 0 | 8 | 30 | 0 | 15 | 157 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3831.5 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 843.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 254 | 510 | 0 | 4250.42 | 8081.92 | 100.06
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0.39 | 46 | 0 | 29 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 807 | 0 | 20 | 0 | 8 | 350 | 0 | 0 | 15 | 193 | 35 | 0 | 111 | 0 | 0 | 11 | 0 | 74 | 0 | 7 | 0 | 310 | 0 | 341 | 0 | 30 | 153 | 16 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 6 | 19 | 111 | 0 | 2.81 | 0 | 4448.7 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.69 | 836 | 0 | 838.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 5 | 0 | 0 | 2.52 | 167 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0.22 | 0 | 53 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 6 | 0.03 | 0 | 0 | 120 | 110 | 0 | 253 | 615 | 0 | 4491.27 | 8939.97 | 100.05
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1.33 | 46 | 0 | 17 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 872 | 10 | 51 | 0 | 42 | 393 | 0 | 0 | 44 | 188 | 38 | 0 | 110 | 0 | 0 | 11 | 0 | 72 | 0 | 30 | 0 | 315 | 0 | 362 | 0 | 30 | 156 | 16 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 28 | 19 | 98 | 1 | 14.06 | 0 | 4768.89 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 861 | 0 | 843.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.32 | 24 | 0 | 0 | 13.24 | 172 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 1.25 | 0 | 55 | 30 | 8 | 0 | 0 | 0 | 0 | 1.5 | 19 | 0.11 | 0 | 0 | 120 | 110 | 0 | 253 | 695 | 0 | 4755.75 | 9524.64 | 100.05
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2.21 | 46 | 0 | 14 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 801 | 15 | 51 | 0 | 53 | 350 | 0 | 0 | 45 | 186 | 35 | 0 | 110 | 0 | 0 | 11 | 0 | 72 | 0 | 50 | 0 | 305 | 0 | 357 | 0 | 30 | 152 | 16 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 35 | 8 | 87 | 1 | 26.55 | 0 | 4661.26 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 819 | 0 | 834.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.65 | 50 | 0 | 0 | 30.61 | 173 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 2.56 | 0 | 53 | 35 | 16 | 0 | 0 | 0 | 0 | 3 | 57 | 0.25 | 0 | 0 | 120 | 110 | 0 | 255 | 650 | 0 | 4736.95 | 9398.21 | 100.05
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 512 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.89 | 46 | 0 | 14 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 650 | 18 | 51 | 0 | 53 | 320 | 0 | 33 | 46 | 184 | 35 | 0 | 108 | 0 | 0 | 13 | 0 | 80 | 0 | 62 | 0 | 300 | 0 | 358 | 0 | 30 | 140 | 16 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 24 | 19 | 88 | 2 | 38.54 | 0 | 4487.93 | 861 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 776 | 0 | 830.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.54 | 74 | 0 | 0 | 46.15 | 159 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 3.82 | 0 | 54 | 35 | 26 | 0 | 0 | 0 | 0 | 4.4 | 137 | 0.35 | 0 | 0 | 100 | 110 | 0 | 254 | 620 | 0 | 4787.3 | 9275.23 | 100.04
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 25 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3.25 | 46 | 0 | 11 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 520 | 0 | 51 | 0 | 53 | 350 | 0 | 80 | 46 | 195 | 35 | 0 | 106 | 0 | 0 | 13 | 0 | 74 | 0 | 69 | 0 | 310 | 0 | 378 | 0 | 30 | 144 | 16 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 35 | 19 | 87 | 2 | 42.9 | 0 | 4554.15 | 870 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 793 | 0 | 841.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 0 | 0 | 55.21 | 164 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 4.72 | 0 | 54 | 35 | 31 | 0 | 0 | 0 | 0 | 5 | 158 | 0.41 | 0 | 0 | 100 | 110 | 0 | 254 | 629 | 0 | 4980.36 | 9534.51 | 100.03
12:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 27 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3.27 | 46 | 0 | 15 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 585 | 0 | 51 | 0 | 45 | 393 | 0 | 80 | 45 | 198 | 35 | 0 | 105 | 0 | 0 | 14 | 0 | 98 | 0 | 66 | 0 | 315 | 0 | 381 | 0 | 30 | 153 | 16 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 45 | 19 | 84 | 2 | 43.13 | 0 | 4891.4 | 871 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 840 | 0 | 844.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 88 | 0 | 0 | 55.56 | 170 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 5.03 | 0 | 54 | 35 | 32 | 0 | 0 | 0 | 0 | 5.3 | 163 | 0.55 | 0 | 0 | 100 | 110 | 0 | 254 | 675 | 0 | 5136.22 | 10027.62 | 100.03
13:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 614 | 0 | 0 | 6 | 0 | 15 | 4 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 25 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.03 | 46 | 0 | 14 | 350 | 0 | 0 | 3 | 0 | 29 | 135 | 0 | 0 | 0 | 580 | 17 | 51 | 2 | 8 | 393 | 0 | 58 | 33 | 189 | 35 | 0 | 105 | 39 | 0 | 14 | 0 | 98 | 0 | 62 | 0 | 325 | 0 | 369 | 0 | 30 | 161 | 16 | 0 | 80 | 30 | 0 | 15 | 156 | 0 | 56 | 19 | 84 | 2 | 40.21 | 0 | 4910.24 | 871 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 930 | 0 | 931.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 78 | 0 | 0 | 52.78 | 173 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 4.94 | 0 | 55 | 0 | 30 | 0 | 0 | 0 | 0 | 5 | 150 | 0.47 | 0 | 0 | 115 | 110 | 0 | 285 | 803 | 0 | 5400.9 | 10311.14 | 100.02
14:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 538 | 17 | 0 | 15 | 0 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 97 | 0 | 21 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2.41 | 46 | 0 | 8 | 350 | 0 | 0 | 18 | 0 | 34 | 135 | 0 | 0 | 0 | 578 | 16 | 51 | 12 | 8 | 350 | 0 | 33 | 20 | 187 | 34 | 0 | 106 | 34 | 0 | 14 | 0 | 104 | 0 | 51 | 0 | 310 | 0 | 366 | 0 | 30 | 157 | 16 | 0 | 80 | 30 | 0 | 15 | 156 | 0 | 56 | 19 | 84 | 2 | 34.31 | 0 | 4713.72 | 887 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 908 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 75 | 0 | 0 | 43.29 | 167 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 3.7 | 0 | 55 | 0 | 22 | 0 | 0 | 0 | 0 | 4.1 | 125 | 0.39 | 0 | 0 | 115 | 110 | 0 | 283 | 845 | 0 | 5322.48 | 10036.2 | 100.02
15:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 486 | 17.5 | 0 | 16 | 0 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 97 | 0 | 14 | 0 | 27.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1.6 | 46 | 0 | 9 | 350 | 0 | 0 | 18 | 0 | 33 | 135 | 0 | 0 | 0 | 575 | 12 | 51 | 12 | 8 | 345 | 0 | 40 | 20 | 184 | 33 | 0 | 105 | 33 | 5 | 14 | 0 | 100 | 0 | 34 | 0 | 305 | 0 | 365 | 0 | 30 | 154 | 16 | 0 | 80 | 30 | 0 | 15 | 157 | 0 | 56 | 19 | 83 | 1 | 21.5 | 0 | 4645.1 | 887 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 893 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 44 | 0 | 0 | 29.19 | 164 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 2.68 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 2.7 | 82 | 0.25 | 0 | 0 | 115 | 110 | 0 | 281 | 850 | 0 | 5179.82 | 9824.92 | 100.01
16:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 502 | 17.5 | 0 | 16 | 0 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 98 | 0 | 6 | 0 | 27.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24 | 0.68 | 86 | 0 | 4 | 350 | 0 | 0 | 19 | 0 | 31 | 135 | 0 | 0 | 0 | 780 | 0 | 51 | 12 | 8 | 330 | 0 | 55 | 7 | 182 | 34 | 0 | 105 | 31 | 8 | 8 | 0 | 96 | 0 | 14 | 0 | 310 | 0 | 364 | 0 | 30 | 156 | 16 | 0 | 80 | 30 | 0 | 15 | 157 | 0 | 58 | 19 | 83 | 0 | 8.11 | 0 | 4827.09 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 900 | 0 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 0 | 0 | 10.66 | 166 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 1.02 | 0 | 55 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 32 | 0.1 | 0 | 0 | 115 | 110 | 0 | 283 | 850 | 0 | 4958.78 | 9785.87 | 100.01
17:00 | 0 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 513 | 17.5 | 0 | 15 | 0 | 40 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 98 | 0 | 1 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 24 | 0 | 12 | 24 | 0.01 | 86 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 32 | 135 | 0 | 0 | 0 | 889 | 0 | 51 | 26 | 8 | 305 | 0 | 51 | 5 | 191 | 34 | 0 | 106 | 33 | 0 | 14 | 0 | 94 | 0 | 1 | 29 | 320 | 0 | 369 | 0 | 30 | 159 | 20 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 84 | 0 | 0.22 | 0 | 5105.73 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 948 | 0 | 1055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59 | 1 | 0 | 0 | 0.57 | 172 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0.06 | 0 | 55 | 45 | 0 | 5 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 0 | 115 | 110 | 0 | 341 | 880 | 0 | 5223.23 | 10328.96 | 100
18:00 | 0 | 38 | 17 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 450 | 17.5 | 0 | 29 | 15 | 145 | 7 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 330 | 40 | 0 | 0 | 17 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 17 | 48 | 0 | 38 | 36 | 0 | 86 | 0 | 2 | 350 | 0 | 0 | 0 | 0 | 35 | 134 | 0 | 0 | 0 | 880 | 0 | 51 | 50 | 0 | 315 | 0 | 51 | 0 | 188 | 29 | 12 | 108 | 69 | 0 | 14 | 0 | 106 | 0 | 0 | 38 | 305 | 0 | 358 | 0 | 30 | 150 | 20 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 84 | 0 | 0 | 0 | 5529.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 0 | 1320 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 55 | 50 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 408 | 1030 | 0 | 5961 | 11490.5 | 100
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 448 | 0 | 0 | 49 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 24 | 0 | 86 | 0 | 24 | 350 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 937 | 0 | 51 | 0 | 0 | 375 | 0 | 14 | 0 | 190 | 29 | 0 | 109 | 0 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 300 | 0 | 391 | 0 | 30 | 143 | 20 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 84 | 0 | 0 | 0 | 5080 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 55 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 398 | 1045 | 0 | 5807 | 10887 | 99.99
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 430 | 0 | 0 | 60 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 7 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 38 | 0 | 86 | 0 | 25 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 937 | 0 | 51 | 0 | 0 | 360 | 0 | 14 | 0 | 191 | 29 | 0 | 109 | 0 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 385 | 0 | 30 | 144 | 20 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 84 | 0 | 0 | 0 | 5063 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 1193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 402 | 1080 | 0 | 5776 | 10839
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 430 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 0 | 86 | 0 | 28 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 928 | 0 | 51 | 0 | 0 | 365 | 0 | 18 | 0 | 188 | 29 | 0 | 109 | 0 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 380 | 0 | 30 | 146 | 20 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 85 | 0 | 0 | 0 | 4960 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 1160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 55 | 35 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 406 | 1085 | 0 | 5729 | 10689 | 99.99
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 432 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 33 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 988 | 0 | 51 | 0 | 0 | 365 | 0 | 33 | 0 | 188 | 26 | 0 | 110 | 0 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 375 | 0 | 30 | 149 | 20 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 89 | 0 | 0 | 0 | 4967 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 1061.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 408 | 1085 | 0 | 5614.11 | 10581.11 | 99.98
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 350 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 1034 | 0 | 51 | 0 | 0 | 360 | 0 | 40 | 0 | 188 | 31 | 0 | 110 | 0 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 360 | 0 | 30 | 147 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 89 | 0 | 0 | 0 | 4936 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 0 | 969.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 304 | 1010 | 0 | 5237.85 | 10173.85 | 99.98
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 350 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 1011 | 0 | 51 | 0 | 0 | 335 | 0 | 55 | 0 | 192 | 29 | 0 | 110 | 0 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 377 | 0 | 30 | 144 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 8 | 8 | 89 | 0 | 0 | 0 | 4868 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 851 | 0 | 818.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 304 | 900 | 0 | 4798.49 | 9666.49 | 99.97
Total KWH | 0 | 278400 | 148320 | 0 | 0 | 0 | 0 | 0 | 8409600 | 0 | 11695040 | 93960 | 0 | 249984 | 4320 | 295822 | 30934 | 133461 | 367200 | 0 | 0 | 0 | 0 | 0 | 31290 | 2778610 | 652000 | 0 | 170730 | 30000 | 471600 | 520560 | 0 | 0 | 0 | 0 | 0 | 0 | 268800 | 20495 | 50160 | 0 | 45120 | 177600 | 21238 | 1279240 | 0 | 446400 | 8501818.18 | 0 | 0 | 75360 | 0 | 257599 | 3227887 | 0 | 0 | 0 | 17874543 | 93825 | 1011384 | 199054 | 418181.82 | 8122400 | 0 | 674000 | 374400 | 4657000 | 666936 | 25920 | 2475545 | 326880 | 22680 | 374499 | 0 | 2053440 | 0 | 450800 | 48192 | 7477500 | 0 | 8852000 | 0 | 721800 | 3503945 | 437856 | 0 | 1562880 | 670080 | 0 | 357000 | 4303800 | 0 | 813600 | 288000 | 2167680 | 11900 | 273250 | 0 | 112044519 | 20712000 | 6854112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481680 | 21018180 | 0 | 22476524.93 | 0 | 0 | 0 | 0 | 47904 | 0 | 0 | 0 | 0 | 292224 | 557630 | 24355 | 0 | 344992 | 3937182 | 0 | 0 | 0 | 0 | 0 | 8571054 | 0 | 29700 | 0 | 1274618 | 388710 | 189254 | 127401 | 0 | 0 | 0 | 32094.84 | 939600 | 2979 | 0 | 0 | 2655000 | 2757790 | 0 | 7027885.3 | 19210181.82 | 0 | 119953051.89 | 231997570.89

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-11-2025 | during | 25-11-2025 | during | 25-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 354 | 332 | 400.75 | 400.75 | 381 | 381 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 7 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 98 | 40 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.5 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 15 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 23 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 17 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 29 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 38 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 35 | 162 | 162 | 35 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 644 | 450 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1251 | 1551.5 | 5285.4 | 5255.4 | 2654.99 | 2764.99
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 86 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 135 | 134 | 130 | 130 | 0 | 0 | DP High
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 35 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 48 | 40 | 48 | 40 | 48 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 15 | 2 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.27 | 0 | 3.16 | 0 | 3.16 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 50 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 110 | 110 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 585 | 880 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 13 | 1 | 7 | 1 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 350 | 350 | 350 | 350 | 355 | 355 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1138.27 | 1639 | 3114.88 | 3111.72 | 2425.66 | 2422.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 198 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 80 | 51 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 315 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 29 | 46.7 | 46.7 | 46.7 | 46.7 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 125 | 125 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 108 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 69 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 98 | 106 | 160 | 160 | 102 | 102 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 12 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1130 | 1031 | 2489.21 | 2419.21 | 2210.21 | 2140.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-11-2025 | during | 25-11-2025 | during | 25-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 84 | 84 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.13 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 193.13 | 162 | 361.7 | 314 | 302.2 | 254.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 150 | 163 | 163 | 0 | 0 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 157 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 20 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 381 | 358 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1179 | 1146 | 1236 | 1236 | 1011 | 1011
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 871 | 887 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 342 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 840 | 1083 | 0 | 0 | 1148 | 1148 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2132 | 2220 | 2390 | 2312 | 2783.1 | 2705.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 254 | 408 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 675 | 1030 | 1085.32 | 1085.32 | 1022 | 1022 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 220 | 220 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1139.55 | 1663 | 1576.32 | 1576.32 | 1490 | 1490
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 47 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 170 | 167 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 365 | 402 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 30 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.03 | 0 | 4.8 | 0 | 4.8 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 844.78 | 1320 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.56 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 88 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1575.37 | 1940 | 3086.67 | 2920.87 | 2551.89 | 2386.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 55 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 33 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.3 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 163 | 0 | 161.21 | 0 | 161.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 289.3 | 138 | 493.41 | 297 | 479.41 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 10027.62 | 11490.5 | 20033.59 | 19442.52 | 15908.46 | 15457.39
Forecast Scenario (25-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9390 |  | 0 |  | 9390
|  |  |  | 1:00 | 8730 |  | 0 |  | 8730
|  |  |  | 2:00 | 8340 |  | 0 |  | 8340
|  |  |  | 3:00 | 8110 |  | 0 |  | 8110
|  |  |  | 4:00 | 7830 |  | 0 |  | 7830
|  |  |  | 5:00 | 7820 |  | 0 |  | 7820
|  |  |  | 6:00 | 8080 |  | 0 |  | 8080
|  |  |  | 7:00 | 8940 |  | 0 |  | 8940
|  |  |  | 8:00 | 9520 |  | 0 |  | 9520
|  |  |  | 9:00 | 9390 |  | 0 |  | 9390
|  |  |  | 10:00 | 9270 |  | 0 |  | 9270
|  |  |  | 11:00 | 9530 |  | 0 |  | 9530
|  |  |  | 12:00 | 10020 |  | 0 |  | 10020
|  |  |  | 13:00 | 10310 |  | 0 |  | 10310
|  |  |  | 14:00 | 10030 |  | 0 |  | 10030
|  |  |  | 15:00 | 9820 |  | 0 |  | 9820
|  |  |  | 16:00 | 9780 |  | 0 |  | 9780
|  |  |  | 17:00 | 10320 |  | 0 |  | 10320
|  |  |  | 18:00 | 11490 |  | 0 |  | 11490
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 10880 |  | 0 |  | 10880
|  |  |  | 19:30 | 10830 |  | 0 |  | 10830
|  |  |  | 20:00 | 10680 |  | 0 |  | 10680
|  |  |  | 21:00 | 10580 |  | 0 |  | 10580
|  |  |  | 22:00 | 10170 |  | 0 |  | 10170
|  |  |  | 23:00 | 9750 |  | 0 |  | 9750
Probable Maximum Temperature: |  |  | 28.00°C
Probable Maximum Demand at Day Peak: |  |  | 10020.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11490.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11490.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 228.78 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:31 hrs on 25-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10027.62 | MW | 12:00 Hr. | Energy Generated |  |  | 231.9976 |  | MKWHr.
| Day Peak Demand |  |  | 10027.62 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11490.5 | MW | 18:00 Hr. | Energy Demand |  |  | 231.9976 |  | MKWHr.
| Evening Peak Demand |  |  | 11490.5 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 7829.37 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 771.25 |  | MMCFD
| Maximum Generation of the Day |  |  | 11490.5 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.374 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.5274 | 0 | 1.6637 | 0 | 0 | 0.17073 | 0 | 0 | 26.3618 | Gas | 101.8057 | Gas | 361880372.9094
| Chattogram Zone |  |  | 3.6743 | 26.3764 | 0.62633 | 0 | 1.2792 | 0.11506 | 0 | 0.2688 | 32.3401 | Coal | 74.9072 | Coal | 474601528.9582
| Cumilla Zone |  |  | 18.7743 | 0 | 0.62273 | 0 | 0 | 0.4508 | 2.0534 | 0 | 21.9013 | HFO | 4.6027 | HFO | 78209980.24
| Mymensingh Zone |  |  | 2.1677 | 0 | 1.1016 | 0 | 0 | 0.28515 | 0 | 0 | 3.5544 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.8869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.8869 | Hydro | 1.2792 | Hydro | 127924
| Khulna Zone |  |  | 6.8541 | 21.0182 | 0 | 0 | 0 | 0.48168 | 20.712 | 0 | 49.066 | Solar | 3.8919 | Solar | 62153597.0464
| Barishal Zone |  |  | 5.4128 | 26.2381 | 0 | 0 | 0 | 0.002979 | 0 | 0 | 31.6538 | Import | 45.242 | Import | 265838235.8579
| Rajshahi Zone |  |  | 12.5082 | 0 | 0.072259 | 0 | 0 | 1.2245 | 22.4765 | 0 | 36.2816 | Wind | 0.2688 | Wind | 3954048
| Rangpur Zone |  |  | 0 | 1.2746 | 0.51611 | 0 | 0 | 1.1609 | 0 | 0 | 2.9517
| Total |  |  | 101.8057 | 74.9072 | 4.6027 | 0 | 1.2792 | 3.8919 | 45.242 | 0.2688 | 231.9976
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 361880372.9094 |  | Hydro | 127924
|  |  |  | Coal | 474601528.9582 |  | Solar | 62153597.0464
|  |  |  | HFO | 78209980.24 |  | Import | 265838235.8579
|  |  |  | HSD | 0 |  | Wind | 3954048
[5 empty] | Total: | 124,67,65,687 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.712 | Peak Hr Flow | 887.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47684914.93 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.4765 | Peak Hr Flow | 1320.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2541 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.0534 | Peak Hr Flow | 106.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2639 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.242 | Peak Hr Flow | 2313.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4360
|  |  |  | Chattogram |  | 0 |  | 1233
|  |  |  | Cumilla |  | 0 |  | 965
|  |  |  | Mymensingh |  | 0 |  | 883
|  |  |  | Sylhet |  | 0 |  | 401
|  |  |  | Khulna |  | 0 |  | 1252
|  |  |  | Barishal |  | 0 |  | 304
|  |  |  | Rajshahi |  | 0 |  | 974
|  |  |  | Rangpur |  | 0 |  | 728
|  |  |  | Total |  | 0 |  | 11100
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:04 | 19:02 | Rampur 230/132/33 S/S Halishahar-1 Scheduled S/D Due to annual maintenance
| 08:05 | 17:45 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to
Annual maintenance
| 08:05 | 17:45 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to
Annual maintenance
| 08:07 | 19:01 | Halishahar-Khulshi 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end Due to due to
annual bay maintenance work.
| 08:10 | 17:45 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to
Annual maintenance
| 08:13 | 15:32 | Rajshahi-Rajshahi(New) 132kV Ckt-2 Scheduled S/D from Rajshahi 132/33kV end Due to
Annual Maintenance Work.
| 08:13 | 15:30 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from Rajshahi 230/132/33kV end Due
to Annual Maintenance
|  | 08:14 | Narail 132/33kV S/S TR1 (403-T) HT is restored.
| 08:14 | 15:59 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
| 08:15 | 15:11 | Maijdee 132/33kV S/S Tr-02 HT Scheduled S/D Due to Silicon paint work on top surface of
GIS building.
|  | 08:15 | Narail 132/33kV S/S TR1 (403-T) LT is restored.
| 08:25 | 16:34 | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to Annual
maintenance work and from Naogaon 132/33kV end Due to Annual maintanence.
| 08:25 | 16:57 | Rahanpur 400/132kV S/S AT-02 LT Scheduled S/D Due to Due to maintenance work.
| 08:26 | 16:56 | Rahanpur 400/132kV S/S AT-02 HT Scheduled S/D Due to Due to maintenance work.
| 08:31 | 16:09 | Bibiana 400/230kV S/S ICT-02 LT Scheduled S/D
| 08:31 | 16:08 | Bibiana 400/230kV S/S ICT-02 HT Scheduled S/D
| 08:48 | 19:41 | Baghabari 230/132kV S/S Auxiliary X-Former-01(Turtiary) Scheduled S/D Due to Annual
Maintenance
| 08:49 | 17:26 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to T-3 Transformer waring change work.
| 08:49 | 19:41 | Baghabari 230/132kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
|  | 08:50 | Chandpur 132/33kV S/S 412T (T-2) HT is restored.
| 08:51 | 17:08 | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
|  | 08:51 | Chandpur 132/33kV S/S 412T (T-2) LT is restored.
|  | 08:52 | Chandpur 132/33kV S/S 33 kV T-2 section is restored.
|  | 08:52 | Chandpur 132/33kV S/S 33 kV T-1 Section is restored.
|  | 08:52 | Chandpur 132/33kV S/S 402T (T-01) HT is restored.
| 08:52 | 09:03 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Kaliakoir end work
|  | 08:52 | Chandpur 132/33kV S/S 33 kV T-2 section is restored.
| 08:52 | 09:03 | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Kaliakoir end work
| 08:52 | 16:30 | Jashore 132/33kV S/S JH-1(L2) Scheduled S/D Due to Annual Maintenance
| 08:52 | 17:25 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to T-3 Transformer waring change work.
|  | 08:52 | Chandpur 132/33kV S/S 200KVA Aux. T-1 LT is restored.
| 08:53 | 15:07 | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw Scheduled S/D Due to Annual Maintenance Work.
| 08:54 |  | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to Annual Maintenance Work.
| 08:54 | 16:30 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to Annual Maintenance
| 08:54 | 17:07 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-02 Scheduled S/D Due to Annual maintenance
| 08:56 | 16:25 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
Maintenance
| 09:01 | 15:00 | Aminbazar-Manikgonj PP 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance
| 09:05 | 14:14 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Scheduled S/D Due to Corrective Maintenance
Work.
| 09:11 | 14:12 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Scheduled S/D Due to Corrective Maintenance
Work.
| 09:11 | 14:38 | Noapara 132/33kV S/S BUS-B Scheduled S/D
| 09:21 | 16:41 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual Maintenance
| 09:40 | 15:57 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to Annual Maintenance.
| 09:40 | 15:57 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to Annual Maintenance.
| 09:45 | 16:13 | BIPTC S/S 10CF16 Scheduled S/D
| 09:56 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 10:15 | 16:23 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to
Annual maintenance
| 10:19 | 16:24 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end.
| 10:35 | 16:56 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to Hand over shift duty to the
next shift in-charge with healthy condition.
| 10:35 | 16:55 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to Annual Maintenance
| 10:38 | 16:55 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to Hand over shift duty to the
next shift in-charge with healthy condition.
| 10:38 | 16:55 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to Hand over shift duty to the
next shift in-charge with healthy condition.
| 11:07 | 16:05 | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to Yearly Maintenance
| 11:29 |  | Bheramara 410 MW CCPP, FGMO is ON with remarks:- FGMO activated at 10:39 hrs on
24.11.2025
| 11:30 | 14:04 | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Measurement for painting work
| 11:30 | 14:05 | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to Measurement for painting work
|  | 12:09 | Ghorasal-Tongi 230kV Ckt-1 is restored.
|  | 13:02 | Sylhet 132/33kV S/S T1 LT is restored.
|  | 13:02 | Sylhet 132/33kV S/S T1 HT is restored.
|  | 15:00 | Aminbazar-Manikgonj PP 132kV Ckt-2 is restored.
|  | 15:07 | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw is restored.
|  | 16:26 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
| 16:58 | 17:32 | Halishahar 132/33kV S/S 405T(TR-1) HT Scheduled S/D Due to Due to pdb cable insulation
faliure.
|  | 17:22 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
| 18:00 |  | Evening peak Generation is 11490 MW
|  | 18:11 | Ghorasal-Tongi 230kV Ckt-2 is restored.
| 19:07 | 19:37 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Work by
kaliakoir grid SS.
|  | 19:18 | Bhulta-Rampura 230 kV Ckt-3 is restored.
|  | 19:18 | Bhulta-Rampura 230 kV Ckt-3 is restored.
| 19:40 | 20:02 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Work done
by kaliakoir grid SS.
|  | 19:41 | Baghabari 230/132kV S/S T-1 HT is restored.
|  | 20:36 | Rangpur 132/33kV S/S Rangpur-GTPS is restored.
| 21:22 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:- FGMO Off at 15:01 as per NLDC demand.
| 21:35 |  | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Forced S/D Due to 113 no. Tower fault work
| 21:38 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Kurigram 132/33kV end Due to Emergency
tower maintanance.
| 01:27 |  | Mahasthangar-Palashbari 132kV Ckt-1 Tripped from Mahasthangarh 132/33kV end showing
Distance Protection P443 relays Due to Conductor broken
| 05:00 |  | Minimum Generation: 7706 MW.
| 06:26 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 07:00 |  | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D
| 07:16 |  | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to Annunal maintenance .
| 07:16 |  | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to Annunal maintenance .
| 07:34 |  | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) LT Scheduled S/D Due to Annual
Maintenance.
| 07:36 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to Annual
maintenance. and from Kachua 230/132/33kV end Due to Yearly maintenance.
| 07:36 |  | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) HT Scheduled S/D Due to Annual
Maintenance.
| 07:45 |  | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
maintenance.
| 07:59 |  | Rampur 230/132/33 S/S Halishahar-2 Scheduled S/D Due to Annual maintenance of bay
equipment in Halishahar Grid SS.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Electrical fault due to Earthquape
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 332 | 8409600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 7 | 30934 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 40 | 652000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 2778610 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 93960 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 4320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 133461 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 31290 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 471600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 520560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 148320 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 295822 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 29 | 249984 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 38 | 278400 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 367200 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 170730 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 450 | 11695040 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 30000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1551.5 | 26361831
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 93825 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 75360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 1279240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 134 | 3227887 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 35 | 257599 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 50160 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 20495 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 45120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 446400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 177600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 880 | 17874543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 268800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 350 | 8501818.18 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1639 | 32340085.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 188 | 4657000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 51 | 674000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 315 | 8122400 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 29 | 666936 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 374400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 418181.82 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1011384 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 199054 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 48192 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2475545 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 69 | 326880 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 106 | 2053440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 374499 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 22680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 12 | 25920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 450800 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1031 | 21901311.82
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 84 | 2167680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 288000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 813600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 273250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 162 | 3554430
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 721800 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3503945 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 670080 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1562880 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 4303800 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 357000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 437856 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7477500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 358 | 8852000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1146 | 27886861
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 887 | 20712000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6854112 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 481680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1083 | 21018180 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2220 | 49065972
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 408 | 7027885.3 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2655000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1030 | 19210181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2757790 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2979 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1663 | 31653836.12
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 292224 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 167 | 3937182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 402 | 8571054 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 24355 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 30 | 47904 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1320 | 22476524.93 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 344992 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 557630 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1940 | 36281565.93
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1274618 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 33 | 127401 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32094.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 388710 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189254 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 939600 | -
Rangpur Area Total |  |  |  |  | 950 | 138 | 2951677.84
Eastern Grid Total |  |  |  |  | 17383.855 | 5529.5 | 112044519
Western Grid Total |  |  |  |  | 10821.56 | 5961 | 119953051.89
National Grid Total |  |  |  |  | 28205.415 | 11490.5 | 231997570.89
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7842.66 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3257.5 | MW
i) Dhaka area |  |  | 4360.36 |  | MW | i) Khulna area |  |  |  | 1252.4 | MW
ii) Chattogram area |  |  | 1233.3 |  | MW | ii) Barishal area |  |  |  | 303.5 | MW
iii) Cumilla area |  |  | 965 |  | MW | iii) Rajshahi area |  |  |  | 973.6 | MW
iv) Mymensingh area |  |  | 883 |  | MW | iv) Rangpur area |  |  |  | 728 | MW
v) Sylhet area |  |  | 401 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11100.16 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 23:00 | 67 | Hathazari | 56 | 18:00 | 133 | Niamatpur | 42 | 18:00
2 | AKSML | 141 | 13:00 | 68 | Ishurdi | 56 | 18:00 | 134 | Noapara | 41 | 18:00
3 | Aftabnagar | 30 | 18:00 | 69 | Jaldhaka | 52 | 18:00 | 135 | PHP | 8 | 07:00
4 | Agargaon | 94 | 13:00 | 70 | Jamalpur | 88 | 18:00 | 136 | Pabna | 67 | 18:00
5 | Agrabad | 66 | 18:00 | 71 | Jashore | 91 | 13:00 | 137 | Palashbari | 82 | 18:00
6 | Amnura | 16 | 20:00 | 72 | Jhenaidah | 96 | 18:00 | 138 | Panchagarh | 44 | 18:00
7 | Ashuganj | 61 | 13:00 | 73 | Joydebpur | 111 | 13:00 | 139 | Patiya | 6.8 | 18:00
8 | BSRM | 199 | 20:00 | 74 | Joypurhat | 46 | 18:00 | 140 | Patuakhali | 43 | 21:00
9 | Bagerhat | 62 | 18:00 | 75 | Juldah | 16 | 09:00 | 141 | Payra | 20 | 00:00
10 | Bajitpur | 56 | 20:00 | 76 | KSRM | 15 | 11:00 | 142 | Postogola | 52 | 13:00
11 | Bakulia | 63 | 18:00 | 77 | Kabirpur | 190 | 18:00 | 143 | Purbachal | 29 | 13:00
12 | Banani | 34.8 | 13:00 | 78 | Kachua | 56 | 18:00 | 144 | Purbasadipur | 96 | 08:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kallyanpur | 72 | 14:00 | 145 | Rahanpur | 21 | 18:00
14 | Barapukuria | 44 | 18:00 | 80 | Kalurghat | 40 | 15:00 | 146 | Rahim | 48 | 11:00
15 | Barguna | 14 | 19:30 | 81 | Kamrangirchar | 64 | 13:00 | 147 | Rajbari | 55 | 18:00
16 | Barishal | 87 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 107 | 18:00
17 | Barishal-230 | 64 | 18:00 | 83 | Kasba | 22 | 18:00 | 149 | Rajshahi | 63 | 21:00
18 | Baroaulia | 57 | 15:00 | 84 | Kazla | 90 | 13:00 | 150 | Rajshahi-230 | 68 | 13:00
19 | Baroirhat | 47 | 18:00 | 85 | Keranigonj | 63 | 18:00 | 151 | Ramganj | 64 | 17:00
20 | Bashundhara | 130 | 12:00 | 86 | Khagrachori | 26 | 18:00 | 152 | Rampur | 38 | 18:00
21 | BashundharaCement | 8 | 12:00 | 87 | Khulna | 54 | 18:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 171 | 12:00 | 154 | Rangpur | 106 | 18:00
23 | Benapole | 46 | 18:00 | 89 | Kishoreganj | 83 | 18:00 | 155 | Ruppur | 3.2 | 10:00
24 | Bhaluka | 125 | 17:00 | 90 | Kodda | 251 | 18:30 | 156 | SSM | 2 | 04:00
25 | Bhandaria | 36 | 21:00 | 91 | Kulaura | 30 | 18:00 | 157 | Saidpur | 92 | 18:00
26 | Bhangura | 22 | 18:00 | 92 | Kurigram | 48 | 18:00 | 158 | Satkhira | 85 | 07:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | Kushtia | 109 | 18:00 | 159 | Satmasjid | 80 | 12:00
28 | Bhulta | 192 | 19:00 | 94 | Laksam | 21 | 18:00 | 160 | Savar | 168 | 18:00
29 | Bog-Sherpur | 50 | 00:00 | 95 | Lakshmipur | 24 | 18:00 | 161 | SevenRings | 14.57 | 19:30
30 | Bogura | 119 | 18:30 | 96 | Lalbag | 60 | 18:00 | 162 | ShahCement | 22 | 00:00
31 | Borhanuddin | 64 | 21:00 | 97 | Lalmonirhat | 38 | 18:30 | 163 | Shahjadpur | 56 | 19:00
32 | Brahmanbaria | 90 | 18:00 | 98 | MI_Cement | 15.5 | 15:00 | 164 | Shahjibazar | 78 | 21:00
33 | Cantonment | 100 | 13:00 | 99 | Madanganj | 38 | 13:00 | 165 | Shahmirpur | 42 | 18:00
34 | Chandina | 10 | 18:00 | 100 | Madaripur | 67 | 19:00 | 166 | Shariatpur | 54 | 20:00
35 | Chandpur | 50 | 18:00 | 101 | Madartek | 66 | 19:00 | 167 | Sherpur | 102 | 18:00
36 | Chandraghona | 26 | 18:30 | 102 | Madunaghat | 40 | 18:00 | 168 | Shikalbaha | 22 | 14:00
37 | Chapai | 43 | 13:00 | 103 | Magura | 44 | 18:00 | 169 | Shitalakhya | 72.2 | 12:00
38 | Charsaidpur | 39 | 13:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 36 | 18:00
39 | Chauddagram | 44 | 17:00 | 105 | Maijdee | 23 | 21:00 | 171 | Shyampur | 122 | 11:00
40 | Chhatak | 23 | 18:30 | 106 | Manikganj | 92 | 18:00 | 172 | Siddhirganj | 98 | 16:00
41 | Chowmuhani | 104 | 18:00 | 107 | Maniknagar | 46 | 14:00 | 173 | Sirajganj | 79 | 18:30
42 | Chuadanga | 72 | 18:00 | 108 | Matarbari | 35 | 18:00 | 174 | Sonargaon | 109 | 16:00
43 | Coxsbazar | 104 | 17:00 | 109 | Matuail | 59 | 18:00 | 175 | Sreemongol | 54 | 18:30
44 | Cumilla(N) | 85 | 19:30 | 110 | Metrorail_Motijheel | 18 | 19:30 | 176 | Sreepur | 85 | 18:00
45 | Cumilla(S) | 129 | 18:00 | 111 | Metrorail_Uttara | 8 | 16:00 | 177 | Srinagar | 30.2 | 21:00
46 | Daganbhuiyan | 0 | 02:00 | 112 | Millgate | 94 | 12:00 | 178 | Sunamganj | 40 | 18:00
47 | Daudkandi | 108 | 18:30 | 113 | Mirpur | 118 | 13:00 | 179 | Sylhet | 35 | 18:00
48 | DhakaUniversity | 54 | 12:00 | 114 | Mirsorai | 9 | 10:00 | 180 | Sylhet-132 | 84 | 18:00
49 | Dhamrai | 102 | 16:00 | 115 | Mirzapur | 39 | 17:00 | 181 | TK | 17 | 12:00
50 | Dhanmondi | 93 | 12:00 | 116 | Mithapukur | 42 | 18:00 | 182 | Tangail | 122 | 18:00
51 | Dohazari | 69 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 15 | 18:00
52 | Faridpur | 113 | 18:00 | 118 | Mogbazar | 69.6 | 15:00 | 184 | Tasnim | 27 | 16:00
53 | Fatullah | 107 | 12:00 | 119 | Mongla | 40 | 12:00 | 185 | Thakurgaon | 75 | 18:00
54 | Fenchuganj | 25 | 18:00 | 120 | Motijheel | 29 | 13:00 | 186 | Tongi | 98 | 11:00
55 | Feni | 69 | 18:00 | 121 | Muktagacha | 26 | 07:00 | 187 | Ullahpara | 26 | 18:00
56 | GPH | 12 | 04:00 | 122 | Munshiganj | 76 | 00:00 | 188 | Ullon | 49 | 18:00
57 | Ghatail | 60 | 07:00 | 123 | Muradnagar | 25 | 18:00 | 189 | Uttara | 63 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 133 | 18:00 | 190 | UttaraNew | 29 | 13:00
59 | Ghorashal-230 | 81 | 18:30 | 125 | Naogaon | 79 | 18:00 | 191 | Zigatola | 53 | 13:00
60 | Goalpara | 24 | 13:00 | 126 | Narail | 46 | 18:00
61 | Gollamari | 78 | 13:00 | 127 | Narinda | 64 | 13:00
62 | Gopalganj | 74.4 | 18:30 | 128 | Narshingdi | 139 | 19:30
63 | Gulshan | 90 | 13:00 | 129 | Natore | 98 | 18:00
64 | Halishahar | 60 | 16:00 | 130 | Nawabganj | 28.8 | 20:00
65 | HaripurSBU | 140 | 12:00 | 131 | Netrakona | 108 | 18:00
66 | Hasnabad | 72 | 12:00 | 132 | New | 62 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9398 | 0 |  | 9398
1:00 | 8732.69 | 0 |  | 8732.69
2:00 | 8348.44 | 0 |  | 8348.44
3:00 | 8114.43 | 0 |  | 8114.43
4:00 | 7836.67 | 0 |  | 7836.67
5:00 | 7829.37 | 0 |  | 7829.37
6:00 | 8081.92 | 0 |  | 8081.92
7:00 | 8939.97 | 0 |  | 8939.97
8:00 | 9524.64 | 0 |  | 9524.64
9:00 | 9398.21 | 0 |  | 9398.21
10:00 | 9275.23 | 0 |  | 9275.23
11:00 | 9534.51 | 0 |  | 9534.51
12:00 | 10027.62 | 0 |  | 10027.62
13:00 | 10311.14 | 0 |  | 10311.14
14:00 | 10036.2 | 0 |  | 10036.2
15:00 | 9824.92 | 0 |  | 9824.92
16:00 | 9785.87 | 0 |  | 9785.87
17:00 | 10328.96 | 0 |  | 10328.96
18:00 | 11490.5 | 0 |  | 11490.5
19:00 | 10887 | 0 |  | 10887
19:30 | 10839 | 0 |  | 10839
20:00 | 10689 | 0 |  | 10689
21:00 | 10581.11 | 0 |  | 10581.11
22:00 | 10173.85 | 0 |  | 10173.85
23:00 | 9666.49 | 0 |  | 9666.49
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4240.5 | 5157.5 | 9398 | DAILY GENERATION CURVE
00:30 | 4205.5 | 4859.845 | 9065.345
01:00 | 4170.5 | 4562.19 | 8732.69 | 24-11-2025
01:30 | 4074.5 | 4466.065 | 8540.565
02:00 | 3978.5 | 4369.94 | 8348.44
02:30 | 3946 | 4285.435 | 8231.435
03:00 | 3913.5 | 4200.93 | 8114.43
03:30 | 3796 | 4179.55 | 7975.55
04:00 | 3678.5 | 4158.17 | 7836.67
04:30 | 3665.5 | 4167.52 | 7833.02
05:00 | 3652.5 | 4176.87 | 7829.37
05:30 | 3742 | 4213.645 | 7955.645
06:00 | 3831.5 | 4250.42 | 8081.92
06:30 | 4140.1 | 4370.845 | 8510.945
07:00 | 4448.7 | 4491.27 | 8939.97
07:30 | 4608.795 | 4623.51 | 9232.305
08:00 | 4768.89 | 4755.75 | 9524.64
08:30 | 4715.075 | 4746.35 | 9461.425
09:00 | 4661.26 | 4736.95 | 9398.21
09:30 | 4574.595 | 4762.125 | 9336.72
10:00 | 4487.93 | 4787.3 | 9275.23
10:30 | 4521.04 | 4883.83 | 9404.87
11:00 | 4554.15 | 4980.36 | 9534.51
11:30 | 4722.775 | 5058.29 | 9781.065
12:00 | 4891.4 | 5136.22 | 10027.62
12:30 | 4900.82 | 5268.56 | 10169.38
13:00 | 4910.24 | 5400.9 | 10311.14
13:30 | 4811.98 | 5361.69 | 10173.67
14:00 | 4713.72 | 5322.48 | 10036.2
14:30 | 4679.41 | 5251.15 | 9930.56
15:00 | 4645.1 | 5179.82 | 9824.92
15:30 | 4736.095 | 5069.3 | 9805.395
16:00 | 4827.09 | 4958.78 | 9785.87
16:30 | 4966.41 | 5091.005 | 10057.415
17:00 | 5105.73 | 5223.23 | 10328.96
17:30 | 5317.615 | 5592.115 | 10909.73
18:00 | 5529.5 | 5961 | 11490.5
18:30 | 5304.75 | 5884 | 11188.75
19:00 | 5080 | 5807 | 10887
19:30 | 5063 | 5776 | 10839
20:00 | 4960 | 5729 | 10689
20:30 | 4963.5 | 5671.555 | 10635.055 |  | Executive Engineer
21:00 | 4967 | 5614.11 | 10581.11 |  | Network Operation Division
21:30 | 4951.5 | 5425.98 | 10377.48
22:00 | 4936 | 5237.85 | 10173.85
22:30 | 4902 | 5018.17 | 9920.17
23:00 | 4868 | 4798.49 | 9666.49

## En-Curve
QF-LDC-12
Date | 24-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2857 | 1294.5 | 861 | 0 | 92 | 1163.5 | 46 | 3055 | 0 | 0 | 16 | 0 | 0 | 13 | 0 | DAILY ENERGY CURVE
00:30 | 2876.5 | 1254.5 | 861 | 0 | 85 | 1023.345 | 46 | 2888 | 0 | 0 | 12 | 0 | 0 | 19 | 0 | 24-11-2025
01:00 | 2896 | 1214.5 | 861 | 0 | 78 | 883.19 | 46 | 2721 | 0 | 0 | 8 | 0 | 0 | 25 | 0
01:30 | 2849.5 | 1169.5 | 861 | 0 | 75 | 866.565 | 46 | 2647 | 0 | 0 | 4 | 0 | 0 | 22 | 0 | Energy Generated | 231.9976 |  | MKWHr
02:00 | 2803 | 1124.5 | 861 | 0 | 72 | 849.94 | 46 | 2573 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2757.5 | 1088 | 861.5 | 0 | 71 | 843.435 | 46 | 2544 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | Total Energy Requirement | 231.9976 |  | MKWHr
03:00 | 2712 | 1051.5 | 862 | 0 | 70 | 836.93 | 46 | 2515 | 0 | 0 | 0 | 0 | 0 | 21 | 0
03:30 | 2576 | 1051 | 862 | 0 | 71 | 833.55 | 46 | 2515.5 | 0 | 0 | 0 | 0 | 0 | 20.5 | 0
04:00 | 2440 | 1050.5 | 862 | 0 | 72 | 830.17 | 46 | 2516 | 0 | 0 | 0 | 0 | 0 | 20 | 0
04:30 | 2443.5 | 1031 | 861.5 | 0 | 73 | 838.02 | 46 | 2517 | 0 | 0 | 0 | 0 | 0 | 23 | 0
05:00 | 2447 | 1011.5 | 861 | 0 | 74 | 845.87 | 46 | 2518 | 0 | 0 | 0 | 0 | 0 | 26 | 0
05:30 | 2506.5 | 1034 | 861.5 | 0 | 72 | 844.645 | 46 | 2562 | 0 | 0 | 0 | 0 | 0 | 29 | 0
06:00 | 2566 | 1056.5 | 862 | 0 | 70 | 843.42 | 46 | 2606 | 0 | 0 | 0 | 0 | 0 | 32 | 0
06:30 | 2666 | 1208 | 862 | 0 | 72 | 841.04 | 46 | 2760 | 17.905 | 0 | 12.5 | 0 | 0 | 25.5 | 0
07:00 | 2766 | 1359.5 | 862 | 0 | 74 | 838.66 | 46 | 2914 | 35.81 | 0 | 25 | 0 | 0 | 19 | 0
07:30 | 2813.5 | 1429.5 | 861.5 | 0 | 73 | 840.995 | 46 | 3000 | 102.31 | 0 | 51 | 0 | 0 | 14.5 | 0
08:00 | 2861 | 1499.5 | 861 | 0 | 72 | 843.33 | 46 | 3086 | 168.81 | 0 | 77 | 0 | 0 | 10 | 0
08:30 | 2791 | 1469.5 | 861 | 0 | 72 | 839.105 | 46 | 3007 | 258.32 | 8.5 | 100 | 0 | 0 | 9 | 0
09:00 | 2721 | 1439.5 | 861 | 0 | 72 | 834.88 | 46 | 2928 | 347.83 | 17 | 123 | 0 | 0 | 8 | 0
09:30 | 2695.5 | 1409 | 861 | 0 | 76 | 832.46 | 46 | 2816 | 446.26 | 21 | 126.5 | 0 | 0 | 7 | 0
10:00 | 2670 | 1378.5 | 861 | 0 | 80 | 830.04 | 46 | 2704 | 544.69 | 25 | 130 | 0 | 0 | 6 | 0
10:30 | 2791 | 1406.75 | 865.5 | 0 | 77 | 835.53 | 46 | 2652 | 572.09 | 25 | 127 | 0 | 0 | 7 | 0
11:00 | 2912 | 1435 | 870 | 0 | 74 | 841.02 | 46 | 2600 | 599.49 | 25 | 124 | 0 | 0 | 8 | 0
11:30 | 2992.5 | 1483 | 870.5 | 0 | 86 | 842.9 | 46 | 2679 | 608.165 | 38 | 129 | 0 | 0 | 6 | 0
12:00 | 3073 | 1531 | 871 | 0 | 98 | 844.78 | 46 | 2758 | 616.84 | 51 | 134 | 0 | 0 | 4 | 0
12:30 | 3055.5 | 1499.5 | 871 | 0 | 98 | 888.245 | 46 | 2880.5 | 600.635 | 51 | 177 | 0 | 0 | 2 | 0
13:00 | 3038 | 1468 | 871 | 0 | 98 | 931.71 | 46 | 3003 | 584.43 | 51 | 220 | 0 | 0 | 0 | 0
13:30 | 2985 | 1397 | 879 | 0 | 101 | 922.855 | 46 | 3011 | 537.315 | 51 | 243.5 | 0 | 0 | 0 | 0
14:00 | 2932 | 1326 | 887 | 0 | 104 | 914 | 46 | 3019 | 490.2 | 51 | 267 | 0 | 0 | 0 | 0
14:30 | 2941.5 | 1312.25 | 887 | 0 | 102 | 914 | 46 | 3011.5 | 404.56 | 42.5 | 269.25 | 0 | 0 | 0 | 0
15:00 | 2951 | 1298.5 | 887 | 0 | 100 | 914 | 46 | 3004 | 318.92 | 34 | 271.5 | 0 | 0 | 0 | 0
15:30 | 2905.5 | 1300.15 | 887 | 0 | 98 | 911 | 66 | 3111 | 220.745 | 25.5 | 278.5 | 0 | 0 | 2 | 0
16:00 | 2860 | 1301.8 | 887 | 0 | 96 | 908 | 86 | 3218 | 122.57 | 17 | 285.5 | 0 | 0 | 4 | 0
16:30 | 2901 | 1316.4 | 887 | 0 | 95 | 981.5 | 86 | 3340.5 | 65.515 | 46.5 | 332.5 | 0 | 0 | 5.5 | 0
17:00 | 2942 | 1331 | 887 | 0 | 94 | 1055 | 86 | 3463 | 8.46 | 76 | 379.5 | 0 | 0 | 7 | 0
17:30 | 3038.5 | 1279.5 | 887 | 0 | 100 | 1187.5 | 86 | 3634.5 | 4.23 | 143.5 | 539 | 0 | 0 | 10 | 0
18:00 | 3135 | 1228 | 887 | 0 | 106 | 1320 | 86 | 3806 | 0 | 211 | 698.5 | 0 | 0 | 13 | 0
18:30 | 3129.5 | 1235 | 887 | 0 | 100 | 1289.5 | 86 | 3838 | 0 | 126.5 | 484.25 | 0 | 0 | 13 | 0
19:00 | 3124 | 1242 | 887 | 0 | 94 | 1259 | 86 | 3870 | 0 | 42 | 270 | 0 | 0 | 13 | 0
19:30 | 3100 | 1236 | 887 | 0 | 94 | 1193 | 86 | 3920 | 0 | 32 | 280 | 0 | 0 | 11 | 0
20:00 | 3095 | 1236 | 887 | 0 | 96 | 1160 | 86 | 3917 | 0 | 0 | 205 | 0 | 0 | 7 | 0
20:30 | 3104 | 1243.5 | 887 | 0 | 95 | 1110.555 | 66 | 3949 | 0 | 0 | 176 | 0 | 0 | 4 | 0
21:00 | 3113 | 1251 | 887 | 0 | 94 | 1061.11 | 46 | 3981 | 0 | 0 | 147 | 0 | 0 | 1 | 0
21:30 | 3097.5 | 1237 | 887 | 0 | 92 | 1015.48 | 46 | 3884.5 | 0 | 0 | 112.5 | 0 | 0 | 5.5 | 0
22:00 | 3082 | 1223 | 887 | 0 | 90 | 969.85 | 46 | 3788 | 0 | 0 | 78 | 0 | 0 | 10 | 0
22:30 | 3089.5 | 1228 | 887 | 0 | 90 | 894.17 | 46 | 3629.5 | 0 | 0 | 47 | 0 | 0 | 9 | 0
23:00 | 3097 | 1233 | 887 | 0 | 90 | 818.49 | 46 | 3471 | 0 | 0 | 16 | 0 | 0 | 8 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 04:00 | 382 | 12:00 | Meghnaghat | 396 | 04:00 | 382 | 12:00
Ashuganj | 401 | 5:00 | 385 | 12:00 | Payra | 417 | 06:00 | 409 | 18:00
Bhulta | 397 | 05:00 | 378 | 12:00 | Rahanpur | 415 | 04:00 | 401 | 18:30
Bibiana | 400 | 01:00 | 389 | 16:00 | Rampal | 415 | 05:00 | 399 | 13:00
BIPTC | 405 | 00:00 | 392 | 18:00
Bogura | 408 | 04:00 | 389 | 18:00
Gopalganj | 409 | 04:00 | 394 | 18:30
Kaliakoir | 393 | 05:00 | 376 | 12:00
Korerhat | 404 | 06:00 | 392 | 12:00
Madunaghat | 402 | 03:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 04:00 | 227 | 12:00 | Kachua | 238 | 04:00 | 229 | 12:00
AKSML | 239 | 05:00 | 229 | 12:00 | Kaliakoir | 239 | 04:00 | 227 | 12:00
Aminbazar | 260 | 19:00 | 227 | 12:00 | Keranigonj | 237 | 05:00 | 224 | 12:00
Ashuganj | 233 | 05:00 | 226 | 19:00 | Khulna(S) | 242 | 04:00 | 231 | 18:00
Ashuganj-400 | 233 | 05:00 | 226 | 19:00 | Korerhat | 238 | 03:00 | 230 | 12:00
Baghabari | 236 | 01:00 | 228 | 18:00 | Madunaghat | 238 | 04:00 | 231 | 12:00
Barapukuria | 225 | 03:00 | 213 | 18:00 | Madunaghat-400 | 239 | 04:00 | 232 | 12:00
Barapukuria-230 | 225 | 03:00 | 213 | 18:00 | Maniknagar | 230 | 03:00 | 219 | 12:00
Barishal | 243 | 05:00 | 235 | 18:00 | Meghnaghat | 238 | 05:00 | 227 | 12:00
Bheramara | 236 | 04:00 | 225 | 18:00 | Meghnaghat-400 | 234 | 04:00 | 222 | 12:00
Bhulta | 232 | 04:00 | 220 | 12:00 | Mirsorai | 236 | 06:00 | 227 | 12:00
Bibiana | 236 | 03:00 | 228 | 12:00 | Rajshahi | 236 | 03:00 | 224 | 18:00
BIPTC | 239 | 04:00 | 226 | 18:00 | Rampal | 239 | 04:00 | 228 | 13:00
Bogura | 237 | 05:00 | 226 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 236 | 04:00 | 225 | 18:00 | Rampura | 231 | 04:00 | 218 | 12:00
Borhanuddin | 244 | 02:00 | 240 | 12:00 | Shikalbaha | 236 | 03:00 | 230 | 11:00
BSRM | 236 | 06:00 | 226 | 12:00 | Shyampur | 235 | 04:00 | 222 | 12:00
Cumilla(N) | 231 | 06:00 | 224 | 12:00 | Siddhirganj | 231 | 01:00 | 217 | 02:00
Faridpur | 242 | 03:00 | 233 | 12:00 | Sirajgonj | 240 | 04:00 | 234 | 18:00
Fenchuganj | 237 | 04:00 | 232 | 12:00 | Sreepur | 230 | 04:00 | 222 | 18:00
Feni | 234 | 06:00 | 224 | 12:00 | Tongi | 236 | 05:00 | 226 | 11:00
Ghorashal | 0 | 00:00 | N/A | N/A
Ghorashal-230 | 232 | 04:00 | 215 | 18:30
Gopalganj | 242 | 03:00 | 234 | 12:00
GPH | 235 | 03:00 | 224 | 10:00
Haripur | 232 | 03:00 | 220 | 12:00
Hasnabad | 236 | 03:00 | 223 | 12:00
Hathazari | 236 | 07:00 | 229 | 12:00
Ishurdi | 240 | 05:00 | 228 | 18:00
Jhenaidah | 238 | 04:00 | 226 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 01:00 | 126 | 11:00 | Lalbag | 139 | 05:00 | 129 | 12:00
Agargaon | 138 | 02:00 | 130 | 12:00 | Lalmonirhat | 132 | 05:00 | 124 | 08:00
Agrabad | 137 | 05:00 | 132 | 12:00 | Madanganj | 133 | 01:00 | 128 | 12:00
AKS | 135 | 04:00 | 130 | 11:00 | Madaripur | 139 | 03:00 | 135 | 13:00
Aminbazar | 139 | 06:00 | 131 | 12:00 | Madartek | 134 | 02:00 | 124 | 12:00
Amnura | 138 | 05:00 | 130 | 18:00 | Madunaghat | 138 | 01:00 | 134 | 12:00
Ashuganj | 140 | 00:00 | 138 | 12:00 | Magura | 140 | 02:00 | 132 | 12:00
Bagerhat | 137 | 04:00 | 128 | 18:00 | Mahasthangarh | 135 | 04:00 | 127 | 18:00
Bajitpur | 137 | 06:00 | 132 | 18:00 | Maijdee | 135 | 04:00 | 129 | 12:00
Bakulia | 138 | 03:00 | 133 | 19:00 | Manikganj | 137 | 04:00 | 128 | 15:00
Banani | 134 | 03:00 | 125 | 12:00 | Maniknagar | 137 | 04:00 | 127 | 13:00
Bangabhaban | 138 | 05:00 | 128 | 12:00 | Matarbari | 129 | 01:00 | 121 | 16:00
Barapukuria | 138 | 03:00 | 130 | 18:00 | Matuail | 136 | 04:00 | 128 | 12:00
Barguna | 136 | 05:00 | 133 | 12:00 | Metrorail_Motijheel | 137 | 04:00 | 127 | 13:00
Barishal | 139 | 04:00 | 135 | 12:00 | Metrorail_Uttara | 137 | 01:00 | 131 | 12:00
Barishal-230 | 140 | 03:00 | 135 | 12:00 | Millgate | 140 | 03:00 | 131 | 12:00
Baroaulia | 138 | 06:00 | 132 | 13:00 | Mirpur | 138 | 04:00 | 130 | 16:00
Baroirhat | 136 | 03:00 | 131 | 12:00 | Mirzapur | 136 | 05:00 | 128 | 11:00
Bashundhara | 135 | 03:00 | 125 | 12:00 | Mithapukur | 134 | 05:00 | 126 | 18:00
BashundharaCement | 133 | 01:00 | 128 | 12:00 | MI_Cement | 135.8 | 04:00 | 13.5 | 05:00
Beanibazar | 134 | 04:00 | 131 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 139 | 03:00 | 123 | 12:00 | Mogbazar | 136 | 02:00 | 125 | 13:00
Bhaluka | 134 | 08:00 | 127 | 17:00 | Mongla | 137 | 06:00 | 128 | 12:00
Bhandaria | 137 | 04:00 | 130 | 14:00 | Motijheel | 138 | 05:00 | 128 | 12:00
Bhangura | 137 | 06:00 | 131 | 18:00 | Muktagacha | 138 | 09:00 | 128 | 18:00
Bheramara | 140 | 02:00 | 135 | 18:00 | Munshiganj | 135 | 04:00 | 126 | 12:00
Bheramara(GK) | 140 | 04:00 | 135 | 18:00 | Muradnagar | 136 | 05:00 | 125 | 04:00
Bhulta | 130 | 03:00 | 124 | 11:00 | Mymensingh | 138 | 09:00 | 124 | 18:00
Bog-Sherpur | 136 | 03:00 | 129 | 18:00 | Naogaon | 134 | 05:00 | 126 | 13:00
Bogura | 135 | 05:00 | 129 | 18:00 | Narail | 142 | 05:00 | 132 | 12:00
Bogura-230 | 136 | 05:00 | 129 | 18:00 | Narinda | 136 | 05:00 | 125 | 04:00
Brahmanbaria | 135 | 01:00 | 132 | 12:00 | Narshingdi | 136 | 01:00 | 123 | 12:00
Cantonment | 138 | 02:00 | 130 | 12:00 | Natore | 136 | 01:00 | 130 | 18:00
Chandina | 138 | 03:00 | 132 | 12:00 | Nawabganj | 138 | 03:00 | 130 | 12:00
Chandpur | 138 | 08:00 | 133 | 12:00 | Netrakona | 131 | 00:00 | 123 | 18:00
Chandraghona | 139 | 06:00 | 134 | 12:00 | New | 141 | 06:00 | 132 | 15:00
Chapai | 138 | 04:00 | 133 | 18:00 | Niamatpur | 139 | 06:00 | 133 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 02:00 | 127 | 12:00 | Noapara | 139 | 05:00 | 131 | 12:00
Chauddagram | 136 | 01:00 | 131 | 11:00 | Pabna | 139 | 03:00 | 132 | 18:00
Chhatak | 133 | 06:00 | 128 | 17:00 | Palashbari | 132 | 04:00 | 124 | 18:00
Chowmuhani | 133 | 06:00 | 128 | 13:00 | Panchagarh | 137 | 04:00 | 127 | 18:00
Chuadanga | 141 | 06:00 | 129 | 12:00 | Patiya | 138 | 06:00 | 133 | 11:00
Coxsbazar | 130 | 05:00 | 121 | 13:00 | Patuakhali | 136 | 09:00 | 133 | 18:30
Cumilla(N) | 137 | 06:00 | 132 | 12:00 | Payra | 137 | 07:00 | 134 | 13:00
Cumilla(S) | 137 | 06:00 | 126 | 14:00 | PHP | 136 | 03:00 | 130 | 13:00
Daganbhuiyan | 136 | 04:00 | 130 | 12:00 | Postogola | 137 | 06:00 | 128 | 12:00
Daudkandi | 133 | 04:00 | 127 | 12:00 | Purbachal | 135 | 03:00 | 125 | 12:00
DhakaUniversity | 135 | 05:00 | 125 | 12:00 | Purbasadipur | 134 | 03:00 | 124 | 18:00
Dhamrai | 137 | 05:00 | 128 | 11:00 | Rahanpur | 139 | 05:00 | 134 | 18:00
Dhanmondi | 137 | 04:00 | 129 | 12:00 | Rahanpur-400 | 140 | 06:00 | 135 | 18:00
Dohazari | 136 | 06:00 | 129 | 13:00 | Rahim | 135 | 02:00 | 128 | 12:00
Faridpur | 140 | 03:00 | 134 | 17:00 | Rajbari | 140 | 03:00 | 134 | 12:00
Fatullah | 140 | 05:00 | 126 | 12:00 | Rajendrapur | 134 | 04:00 | 127 | 18:00
Fenchuganj | 140 | 06:00 | 137 | 12:00 | Rajshahi | 137 | 06:00 | 131 | 12:00
Feni | 135 | 04:00 | 130 | 11:00 | Rajshahi-230 | 136 | 03:00 | 130 | 18:00
Feni-230 | 137 | 05:00 | 131 | 12:00 | Ramganj | 135 | 04:00 | 129 | 12:00
Ghatail | 133 | 05:00 | 126 | 18:00 | Rampur | 137 | 09:00 | 133 | 11:00
Ghorashal | 135 | 01:00 | 132 | 11:00 | Rampura | 134 | 02:00 | 125 | 12:00
Goalpara | 139 | 04:00 | 132 | 12:00 | Rangamati | 139 | 06:00 | 133 | 12:00
Gollamari | 140 | 05:00 | 132 | 12:00 | Rangpur | 134 | 03:00 | 126 | 21:00
Gopalganj | 140 | 03:00 | 134 | 12:00 | Ruppur | 140 | 04:00 | 135 | 18:00
Gopalganj-400 | 142 | 06:00 | 136 | 12:00 | Saidpur | 134 | 04:00 | 124 | 18:00
Gulshan | 134 | 04:00 | 124 | 12:00 | Satkhira | 139 | 05:00 | 130 | 18:00
Halishahar | 138 | 06:00 | 132 | 12:00 | Satmasjid | 138 | 03:00 | 130 | 06:00
Haripur | 136 | 03:00 | 128 | 12:00 | Savar | 137 | 04:00 | 129 | 12:00
HaripurSBU | 136 | 05:00 | 128 | 12:00 | SevenRings | 136 | 03:00 | 130 | 17:00
Hasnabad | 138 | 03:00 | 128 | 12:00 | ShahCement | 135 | 02:00 | 127 | 12:00
Hathazari | 138 | 07:00 | 134 | 12:00 | Shahjadpur | 140 | 03:00 | 136 | 00:00
Ishurdi | 141 | 03:00 | 135 | 18:00 | Shahjibazar | 138 | 08:00 | 134 | 12:00
Jaldhaka | 133 | 03:00 | 121 | 18:00 | Shahmirpur | 137 | 07:00 | 133 | 12:00
Jamalpur | 135 | 09:00 | 118 | 23:00 | Shariatpur | 140 | 03:00 | 128 | 18:00
Jashore | 155 | 13:00 | 124 | 12:00 | Sherpur | 132 | 09:00 | 116 | 23:00
Jhenaidah | 141 | 04:00 | 122 | 18:00 | Shikalbaha | 128 | 07:00 | 122 | 13:00
Jhenaidah-230 | 142 | 03:00 | 134 | 12:00 | Shikalbaha-230 | 138 | 01:00 | 134 | 11:00
Joydebpur | 137 | 06:00 | 126 | 18:00 | Shitalakhya | 135.8 | 04:00 | 125.5 | 12:00
Joypurhat | 132 | 01:00 | 125 | 12:00 | Sholosohor | 137 | 01:00 | 134 | 12:00
Juldah | 138 | 03:00 | 133 | 12:00 | Shyampur | 138 | 06:00 | 131 | 12:00
Kabirpur | 137 | 01:00 | 128 | 11:00 | Shyampur-230 | 140 | 04:00 | 132 | 12:00
Kachua | 139 | 03:00 | 134 | 12:00 | Siddhirganj | 136 | 02:00 | 128 | 12:00
Kaliakoir | 139 | 02:00 | 132 | 11:00 | Sirajganj | 135 | 02:00 | 125 | 18:30
Kallyanpur | 137 | 05:00 | 131 | 12:00 | Sonargaon | 134 | 05:00 | 127 | 12:00
Kalurghat | 139 | 07:00 | 134 | 12:00 | Sreemongol | 137 | 00:00 | 134 | 12:00
Kamrangirchar | 138 | 06:00 | 129 | 12:00 | Sreepur | 135 | 04:00 | 129 | 18:00
Kaptai | 140 | 6:00 | 136 | 1:00 | Srinagar | 138 | 04:00 | 129 | 12:00
Kasba | 137 | 05:00 | 129 | 12:00 | SSM | 140 | 00:00 | 139 | 06:00
Kazla | 138 | 07:00 | 127 | 13:00 | Sunamganj | 130 | 00:00 | 128 | 12:00
Keranigonj | 138 | 03:00 | 130 | 12:00 | Sylhet | 134 | 01:00 | 131 | 17:00
Khagrachori | 137 | 01:00 | 133 | 12:00 | Sylhet-132 | 133 | 04:00 | 131 | 11:00
Khulna | 138 | 05:00 | 131 | 12:00 | Tangail | 133 | 09:00 | 125 | 18:00
Khulna(S) | 140 | 03:00 | 133 | 12:00 | Taraganj | 132 | 05:00 | 124 | 18:00
Khulshi | 136 | 05:00 | 131 | 12:00 | Tasnim | 134 | 04:00 | 127 | 12:00
Kishoreganj | 137 | 04:00 | 130 | 18:00 | Thakurgaon | 137 | 05:00 | 127 | 18:00
Kodda | 133 | 04:00 | 123 | 11:00 | TK | 138 | 04:00 | 134 | 11:00
KSRM | 138 | 06:00 | 133 | 11:00 | Tongi | 141 | 05:00 | 132 | 19:30
Kulaura | 139 | 04:00 | 136 | 12:00 | Ullahpara | 137 | 05:00 | 130 | 18:00
Kurigram | 133 | 03:00 | 120 | 18:00 | Ullon | 135 | 06:00 | 124 | 12:00
Kushtia | 138 | 04:00 | 128 | 18:00 | Uttara | 139 | 05:00 | 131 | 13:00
Laksam | 139 | 05:00 | 133 | 12:00 | UttaraNew | 139 | 01:00 | 131 | 12:00
Lakshmipur | 134 | 03:00 | 129 | 12:00 | Zigatola | 138 | 05:00 | 129 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division