## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-11-2025 | during | 26-11-2025 | during | 26-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 359 | 338 | 400.75 | 400.75 | 381 | 381 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 29 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 30 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 20 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 28.5 | 21.8 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 0 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 34 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 60 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 49 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 50 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 452 | 452 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 34 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1196.5 | 1486.8 | 5042.6 | 5010.6 | 3159.99 | 3154.99
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 100 | 100 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 23 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | DP High
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 35 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 48 | 40 | 48 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 11 | 5 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.27 | 0 | 3.26 | 0 | 3.26 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 18 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 990 | 1150 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 15 | 0 | 15 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 350 | 354 | 354 | 354 | 355 | 355 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1420.27 | 1710 | 3087.98 | 3093.72 | 2493.76 | 2499.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 207 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 260 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 260 | 225 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 5 | 46.7 | 46.7 | 46.7 | 46.7 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 107 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 42 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 104 | 100 | 160 | 160 | 106 | 106 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 21 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1163 | 1061 | 2489.21 | 2419.21 | 2264.21 | 2194.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-11-2025 | during | 26-11-2025 | during | 26-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 83 | 75 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 57 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.07 | 0 | 43.13 | 0 | 43.13 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 153.07 | 150 | 358.83 | 314 | 299.33 | 254.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 157 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 395 | 361 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1036 | 1006 | 1073 | 1073 | 1011 | 1011
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 888 | 865 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 300 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 812 | 1097 | 0 | 0 | 1148 | 1148 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2027 | 2262 | 2390 | 2312 | 2783.1 | 2705.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 305 | 506 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 640 | 925 | 1085.32 | 1085.32 | 1022 | 1022 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1170.54 | 1656 | 1686.32 | 1686.32 | 1490 | 1490
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 59.67 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 167 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 383 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 4.8 | 0 | 4.8 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 854.95 | 1330 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.02 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1657.64 | 1880 | 3072.67 | 2906.87 | 2977.89 | 2812.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 53 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 179 | 0 | 178 | 0 | 178 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 261.5 | 193 | 510.2 | 297 | 496.2 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 10085.52 | 11404.8 | 19710.81 | 19112.72 | 16975.48 | 16404.39
Forecast Scenario (26-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9350 |  | 0 |  | 9350
|  |  |  | 1:00 | 8740 |  | 0 |  | 8740
|  |  |  | 2:00 | 8290 |  | 0 |  | 8290
|  |  |  | 3:00 | 8030 |  | 0 |  | 8030
|  |  |  | 4:00 | 7820 |  | 0 |  | 7820
|  |  |  | 5:00 | 7700 |  | 0 |  | 7700
|  |  |  | 6:00 | 8040 |  | 0 |  | 8040
|  |  |  | 7:00 | 9010 |  | 0 |  | 9010
|  |  |  | 8:00 | 9590 |  | 0 |  | 9590
|  |  |  | 9:00 | 9380 |  | 0 |  | 9380
|  |  |  | 10:00 | 9280 |  | 0 |  | 9280
|  |  |  | 11:00 | 9460 |  | 0 |  | 9460
|  |  |  | 12:00 | 10080 |  | 0 |  | 10080
|  |  |  | 13:00 | 10360 |  | 0 |  | 10360
|  |  |  | 14:00 | 10080 |  | 0 |  | 10080
|  |  |  | 15:00 | 9730 |  | 0 |  | 9730
|  |  |  | 16:00 | 9580 |  | 0 |  | 9580
|  |  |  | 17:00 | 10080 |  | 0 |  | 10080
|  |  |  | 18:00 | 11400 |  | 0 |  | 11400
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 10940 |  | 0 |  | 10940
|  |  |  | 19:30 | 10840 |  | 0 |  | 10840
|  |  |  | 20:00 | 10650 |  | 0 |  | 10650
|  |  |  | 21:00 | 10530 |  | 0 |  | 10530
|  |  |  | 22:00 | 10170 |  | 0 |  | 10170
|  |  |  | 23:00 | 9670 |  | 0 |  | 9670
Probable Maximum Temperature: |  |  | 27.80°C
Probable Maximum Demand at Day Peak: |  |  | 10080.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.96 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:28 hrs on 26-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-11-2025 | [28 empty] | Date: | 25-11-2025 | [28 empty] | Date: | 25-11-2025 | [28 empty] | Date: | 25-11-2025 | [28 empty] | Date: | 25-11-2025 | [14 empty] | Date: | 25-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 350 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 910 | 0 | 51 | 0 | 0 | 350 | 0 | 58 | 0 | 191 | 30 | 0 | 110 | 0 | 0 | 20 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 362 | 0 | 30 | 70 | 21 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 8 | 8 | 89 | 0 | 0 | 0 | 4684 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 807 | 0 | 835.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 303 | 800 | 0 | 4668.48 | 9352.48 | 99.97
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 350 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 780 | 0 | 51 | 0 | 0 | 355 | 0 | 66 | 0 | 192 | 31 | 0 | 110 | 0 | 0 | 20 | 0 | 76 | 0 | 0 | 0 | 305 | 0 | 366 | 0 | 30 | 29 | 21 | 0 | 11 | 30 | 0 | 15 | 158 | 0 | 8 | 8 | 100 | 0 | 0 | 0 | 4439.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 0 | 832.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 254 | 560 | 0 | 4302.48 | 8741.98 | 99.97
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 350 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 656 | 0 | 0 | 0 | 0 | 300 | 0 | 66 | 0 | 195 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 375 | 0 | 30 | 25 | 16 | 0 | 5 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 4008.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 0 | 829.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 252 | 540 | 0 | 4289.59 | 8298.09 | 99.96
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 31 | 350 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 603 | 0 | 0 | 0 | 0 | 290 | 0 | 77 | 0 | 193 | 5 | 0 | 50 | 0 | 0 | 5 | 0 | 68 | 0 | 0 | 0 | 300 | 0 | 351 | 0 | 30 | 25 | 16 | 0 | 5 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3813 | 887 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 827.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 252 | 540 | 0 | 4217.54 | 8030.54 | 99.96
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 320 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 260 | 0 | 77 | 0 | 200 | 5 | 0 | 50 | 0 | 0 | 5 | 0 | 68 | 0 | 0 | 0 | 275 | 0 | 318 | 0 | 30 | 25 | 16 | 0 | 5 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3644 | 887 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 830.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 252 | 500 | 0 | 4182.44 | 7826.44 | 99.96
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 320 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 260 | 0 | 62 | 0 | 150 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 250 | 0 | 318 | 0 | 30 | 25 | 16 | 0 | 5 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3604 | 887 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 834.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 252 | 500 | 0 | 4102.64 | 7706.64 | 99.95
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 320 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 260 | 0 | 73 | 0 | 202 | 5 | 0 | 50 | 0 | 0 | 14 | 0 | 76 | 0 | 0 | 0 | 280 | 0 | 350 | 0 | 30 | 26 | 16 | 0 | 5 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3782 | 887 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 0 | 832.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 251 | 500 | 0 | 4259.15 | 8041.15 | 99.95
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 350 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 730 | 2 | 5 | 0 | 0 | 393 | 0 | 132 | 0 | 207 | 29 | 0 | 111 | 0 | 0 | 14 | 0 | 64 | 0 | 7 | 0 | 320 | 0 | 385 | 0 | 30 | 18 | 16 | 0 | 72 | 30 | 0 | 15 | 157 | 0 | 7 | 19 | 98 | 0 | 2.16 | 0 | 4458.16 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 821 | 0 | 831.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.04 | 5 | 0 | 0 | 2.87 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.26 | 0 | 58 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 11 | 0.04 | 0 | 0 | 115 | 110 | 0 | 303 | 565 | 0 | 4559.99 | 9018.15 | 99.95
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 12 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1.3 | 46 | 0 | 9 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853 | 9 | 42 | 0 | 0 | 393 | 0 | 132 | 0 | 203 | 32 | 0 | 110 | 0 | 0 | 14 | 0 | 78 | 0 | 28 | 0 | 320 | 0 | 367 | 0 | 30 | 0 | 16 | 0 | 79 | 30 | 0 | 15 | 157 | 0 | 31 | 19 | 85 | 1 | 15.49 | 0 | 4601.79 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 920 | 0 | 830.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.77 | 30 | 0 | 0 | 16.33 | 182 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 2 | 0 | 57 | 35 | 10 | 6 | 0 | 0 | 0 | 1.5 | 63 | 0.16 | 0 | 0 | 115 | 110 | 0 | 307 | 720 | 0 | 4992.43 | 9594.22 | 99.94
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 21 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.26 | 46 | 0 | 7 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 835 | 0 | 43 | 0 | 0 | 350 | 0 | 139 | 0 | 194 | 32 | 0 | 110 | 0 | 0 | 14 | 0 | 82 | 0 | 48 | 0 | 305 | 0 | 325 | 0 | 30 | 0 | 16 | 0 | 32 | 30 | 0 | 15 | 156 | 0 | 35 | 19 | 87 | 1 | 28.77 | 0 | 4379.03 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.58 | 850 | 0 | 834.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.8 | 57 | 0 | 0 | 38.73 | 169 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 3.12 | 0 | 56 | 0 | 18 | 15 | 0 | 0 | 0 | 3.3 | 114 | 0.33 | 0 | 0 | 115 | 110 | 0 | 305 | 750 | 0 | 5002.89 | 9381.92 | 99.94
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 27 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.92 | 46 | 0 | 9 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 18 | 43 | 0 | 0 | 300 | 0 | 184 | 0 | 190 | 32 | 0 | 50 | 0 | 0 | 14 | 0 | 82 | 0 | 60 | 0 | 305 | 0 | 320 | 0 | 30 | 0 | 16 | 0 | 32 | 30 | 0 | 15 | 156 | 0 | 16 | 19 | 85 | 2 | 38.35 | 0 | 4343.27 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.61 | 792 | 0 | 833.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.94 | 83 | 0 | 0 | 54.54 | 162 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 4.6 | 0 | 55 | 0 | 28 | 0 | 0 | 0 | 0 | 4.7 | 154 | 0.47 | 0 | 0 | 100 | 110 | 0 | 305 | 660 | 0 | 4936.35 | 9279.62 | 99.94
11:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 0 | 28.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.27 | 46 | 0 | 9 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 20 | 43 | 0 | 0 | 260 | 0 | 253 | 0 | 209 | 32 | 0 | 50 | 0 | 0 | 14 | 0 | 88 | 0 | 67 | 0 | 310 | 0 | 321 | 0 | 30 | 0 | 16 | 0 | 11 | 20 | 0 | 15 | 157 | 0 | 16 | 8 | 83 | 2 | 43.47 | 0 | 4473.54 | 889 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 804 | 0 | 852.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.1 | 97 | 0 | 0 | 59.15 | 167 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 5.13 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 175 | 0.56 | 0 | 0 | 100 | 110 | 0 | 305 | 610 | 0 | 4990.51 | 9464.05 | 99.93
12:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 30 | 0 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 46 | 0 | 11 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 20 | 43 | 0 | 0 | 260 | 0 | 330 | 0 | 207 | 31 | 0 | 105 | 0 | 0 | 14 | 0 | 104 | 0 | 69 | 0 | 315 | 0 | 395 | 0 | 30 | 0 | 16 | 0 | 78 | 30 | 0 | 15 | 157 | 0 | 16 | 8 | 83 | 2 | 44.07 | 0 | 4968.84 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 812 | 0 | 854.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.67 | 93 | 0 | 0 | 60.02 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 24 | 0 | 0 | 0 | 0 | 5.5 | 179 | 0.54 | 0 | 0 | 115 | 110 | 0 | 305 | 640 | 0 | 5116.68 | 10085.52 | 99.93
13:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 29 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 19 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 18 | 43 | 0 | 0 | 260 | 0 | 330 | 0 | 208 | 29 | 0 | 105 | 0 | 0 | 14 | 0 | 98 | 0 | 62 | 0 | 315 | 0 | 395 | 0 | 30 | 0 | 16 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 16 | 8 | 72 | 2 | 41.33 | 0 | 5011.83 | 881 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 903 | 0 | 856.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.53 | 90 | 0 | 0 | 55.06 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 24 | 0 | 0 | 0 | 0 | 5.2 | 166 | 0.41 | 0 | 0 | 115 | 110 | 0 | 305 | 810 | 0 | 5352.62 | 10364.45 | 99.93
14:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 23 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.39 | 46 | 0 | 15 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 15 | 51 | 0 | 0 | 260 | 0 | 300 | 0 | 196 | 34 | 0 | 105 | 0 | 0 | 14 | 0 | 104 | 0 | 49 | 0 | 320 | 0 | 375 | 0 | 30 | 0 | 16 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 16 | 8 | 72 | 2 | 33.14 | 0 | 4887.53 | 865 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 904 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.09 | 75 | 0 | 0 | 46.88 | 174 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 3.94 | 0 | 53 | 0 | 22 | 0 | 0 | 0 | 0 | 4.3 | 136 | 0.41 | 0 | 0 | 115 | 110 | 0 | 303 | 850 | 0 | 5193.62 | 10081.15 | 99.92
15:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 398 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 15 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.57 | 46 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 11 | 51 | 0 | 0 | 270 | 0 | 280 | 0 | 193 | 34 | 0 | 105 | 0 | 0 | 14 | 0 | 94 | 0 | 34 | 0 | 305 | 0 | 375 | 0 | 30 | 0 | 16 | 0 | 78 | 30 | 0 | 15 | 157 | 0 | 16 | 8 | 73 | 1 | 22.51 | 0 | 4727.08 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 895 | 0 | 839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.47 | 48 | 0 | 0 | 30.63 | 158 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 2.54 | 0 | 53 | 0 | 16 | 0 | 0 | 0 | 0 | 2.5 | 93 | 0.26 | 0 | 0 | 115 | 110 | 0 | 303 | 815 | 0 | 5007.4 | 9734.48 | 99.92
16:00 | 0 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 400 | 3 | 0 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 7 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 46 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 6 | 51 | 0 | 0 | 225 | 0 | 280 | 0 | 184 | 20 | 0 | 105 | 0 | 0 | 14 | 0 | 94 | 0 | 14 | 0 | 300 | 0 | 379 | 0 | 30 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 21 | 8 | 74 | 0 | 7.54 | 0 | 4647.25 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 891 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.55 | 18 | 0 | 0 | 9.78 | 157 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0.89 | 0 | 53 | 0 | 7 | 0 | 0 | 0 | 0 | 1.8 | 34 | 0.1 | 0 | 0 | 115 | 110 | 0 | 305 | 825 | 0 | 4934.12 | 9581.37 | 99.92
17:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 444 | 16 | 0 | 17 | 0 | 15 | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 12 | 280 | 0 | 0 | 1 | 17 | 21.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 12 | 0 | 46 | 1 | 5 | 354 | 0 | 0 | 5 | 0 | 6 | 0 | 0 | 0 | 0 | 1045 | 0 | 51 | 8 | 0 | 225 | 0 | 260 | 0 | 199 | 5 | 1 | 105 | 5 | 0 | 14 | 0 | 96 | 0 | 1 | 0 | 305 | 0 | 346 | 0 | 30 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 156 | 0 | 35 | 18 | 74 | 0 | 0.17 | 0 | 4831.97 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 954 | 0 | 1080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0 | 0 | 0 | 0.5 | 163 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0.05 | 0 | 53 | 35 | 0 | 20 | 0 | 0 | 0 | 0.1 | 1 | 0.06 | 0 | 0 | 115 | 110 | 0 | 386 | 854 | 0 | 5252.42 | 10084.39 | 99.91
18:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 452 | 29 | 0 | 49 | 30 | 60 | 0 | 20 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 34 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 24 | 38 | 0 | 46 | 18 | 5 | 354 | 0 | 0 | 23 | 0 | 35 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 35 | 0 | 225 | 0 | 260 | 0 | 198 | 5 | 21 | 107 | 42 | 0 | 17 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 361 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 57 | 18 | 75 | 0 | 0 | 0 | 5413.8 | 865 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1097 | 0 | 1330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 53 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 506 | 925 | 0 | 5991 | 11404.8 | 99.91
19:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 480 | 22 | 0 | 52 | 0 | 30 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 17 | 21.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 0 | 12 | 353 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 1152 | 0 | 51 | 8 | 0 | 225 | 0 | 260 | 0 | 200 | 5 | 0 | 108 | 34 | 0 | 17 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 387 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 75 | 0 | 0 | 0 | 5160.8 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 55 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 452 | 990 | 0 | 5785 | 10945.8 | 99.9
19:30 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 485 | 16 | 0 | 33 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 21.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 0 | 15 | 354 | 0 | 0 | 19 | 0 | 16 | 0 | 0 | 0 | 0 | 1154 | 0 | 51 | 0 | 0 | 225 | 0 | 260 | 0 | 198 | 5 | 0 | 109 | 15 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 315 | 0 | 392 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 76 | 0 | 0 | 0 | 5110.8 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 416 | 994 | 0 | 5732 | 10842.8
20:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 475 | 16.8 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 19 | 354 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1151 | 0 | 51 | 0 | 0 | 225 | 0 | 260 | 0 | 198 | 5 | 0 | 105 | 17 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 388 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 57 | 19 | 75 | 0 | 0 | 0 | 4956.6 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 403 | 994 | 0 | 5693 | 10649.6 | 99.9
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 472 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22.2 | 22 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 23 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1147 | 0 | 51 | 0 | 0 | 225 | 0 | 260 | 0 | 194 | 5 | 0 | 105 | 0 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 377 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 45 | 19 | 75 | 0 | 0 | 0 | 4858.2 | 865 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 403 | 996 | 0 | 5678 | 10536.2 | 99.9
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 458 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 22.2 | 22 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 27 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 51 | 0 | 0 | 225 | 0 | 260 | 0 | 189 | 5 | 0 | 109 | 0 | 0 | 20 | 0 | 86 | 0 | 0 | 0 | 300 | 0 | 366 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 35 | 19 | 75 | 0 | 0 | 0 | 4745.2 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1047 | 0 | 1110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 353 | 950 | 0 | 5352 | 10097.2 | 99.89
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 24 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 0 | 51 | 0 | 0 | 225 | 0 | 250 | 0 | 191 | 5 | 0 | 109 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 300 | 0 | 366 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 35 | 0 | 75 | 0 | 0 | 0 | 4670 | 865 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 0 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 115 | 0 | 256 | 918 | 0 | 5062 | 9732 | 99.89
Total KWH | 0 | 124800 | 260160 | 0 | 0 | 0 | 0 | 0 | 8391600 | 0 | 10373390 | 90360 | 0 | 227952 | 24000 | 139255 | 0 | 62059 | 93600 | 0 | 0 | 0 | 0 | 0 | 64095 | 6739212 | 0 | 0 | 196256 | 62400 | 484200 | 433440 | 0 | 0 | 0 | 0 | 0 | 100000 | 19680 | 31123 | 0 | 0 | 39360 | 94080 | 20883 | 1105320 | 45200 | 458400 | 8465454.55 | 0 | 0 | 63360 | 0 | 98690 | 455836 | 0 | 0 | 0 | 21779998 | 127845 | 910664 | 68581 | 0 | 6642100 | 0 | 4790000 | 0 | 4775000 | 407304 | 42240 | 2174071 | 108960 | 0 | 372540 | 0 | 2039040 | 0 | 444945 | 0 | 7373000 | 0 | 8880000 | 0 | 718680 | 0 | 457464 | 0 | 1280640 | 650592 | 0 | 382000 | 3694290 | 0 | 606000 | 249600 | 2011200 | 12750 | 276630 | 0 | 110040299.55 | 21690909 | 5452704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 487440 | 21301820 | 0 | 22554982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369000 | 615500 | 0 | 0 | 375760 | 3916273 | 0 | 0 | 0 | 0 | 0 | 8711563 | 0 | 22080 | 0 | 1264581 | 288423 | 173197 | 284419 | 0 | 0 | 0 | 34120.92 | 1126800 | 3340 | 0 | 0 | 2651000 | 2753440 | 0 | 7600000 | 18651636.36 | 0 | 120328988.28 | 230369287.83

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10085.52 | MW | 12:00 Hr. | Energy Generated |  |  | 230.3693 |  | MKWHr.
| Day Peak Demand |  |  | 10085.52 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11404.8 | MW | 18:00 Hr. | Energy Demand |  |  | 230.3693 |  | MKWHr.
| Evening Peak Demand |  |  | 11404.8 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 7706.64 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 734.23 |  | MMCFD
| Maximum Generation of the Day |  |  | 11404.8 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.3426 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.4218 | 0 | 1.1487 | 0 | 0 | 0.19626 | 0 | 0 | 27.7668 | Gas | 96.4406 | Gas | 337957312.57
| Chattogram Zone |  |  | 1.0142 | 30.2455 | 0.37181 | 0 | 1.1053 | 0.14873 | 0 | 0.01968 | 32.9052 | Coal | 79.0635 | Coal | 498829086.2063
| Cumilla Zone |  |  | 20.0717 | 0 | 0.21978 | 0 | 0 | 0.44494 | 2.039 | 0 | 22.7754 | HFO | 3.1687 | HFO | 54550952.55
| Mymensingh Zone |  |  | 2.0112 | 0 | 0.8556 | 0 | 0 | 0.28938 | 0 | 0 | 3.1562 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.4367 | Hydro | 1.1053 | Hydro | 110532
| Khulna Zone |  |  | 5.4527 | 21.3018 | 0 | 0 | 0 | 0.48744 | 21.6909 | 0 | 48.9329 | Solar | 4.2865 | Solar | 68568417.4632
| Barishal Zone |  |  | 5.4044 | 26.2516 | 0 | 0 | 0 | 0.00334 | 0 | 0 | 31.6594 | Import | 46.2849 | Import | 270456252.67
| Rajshahi Zone |  |  | 12.6278 | 0 | 0 | 0 | 0 | 1.3823 | 22.555 | 0 | 36.5652 | Wind | 0.01968 | Wind | 289492.8
| Rangpur Zone |  |  | 0 | 1.2646 | 0.57284 | 0 | 0 | 1.3341 | 0 | 0 | 3.1715
| Total |  |  | 96.4406 | 79.0635 | 3.1687 | 0 | 1.1053 | 4.2865 | 46.2849 | 0.01968 | 230.3693
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 337957312.57 |  | Hydro | 110532
|  |  |  | Coal | 498829086.2063 |  | Solar | 68568417.4632
|  |  |  | HFO | 54550952.55 |  | Import | 270456252.67
|  |  |  | HSD | 0 |  | Wind | 289492.8
[5 empty] | Total: | 123,07,62,046 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6909 | Peak Hr Flow | 865.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47680000.01 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.555 | Peak Hr Flow | 1330.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2484 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.039 | Peak Hr Flow | 100.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2528 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.2849 | Peak Hr Flow | 2295.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4350
|  |  |  | Chattogram |  | 0 |  | 1186
|  |  |  | Cumilla |  | 0 |  | 951
|  |  |  | Mymensingh |  | 0 |  | 876
|  |  |  | Sylhet |  | 0 |  | 417
|  |  |  | Khulna |  | 0 |  | 1257
|  |  |  | Barishal |  | 0 |  | 307
|  |  |  | Rajshahi |  | 0 |  | 998
|  |  |  | Rangpur |  | 0 |  | 762
|  |  |  | Total |  | 0 |  | 11104
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 15:42 | Halishahar-Khulshi 132kV Ckt-2 Scheduled S/D from Halishahar 132/33kV end Due to Annual
maintenance
| 08:03 | 17:24 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-02 Scheduled S/D Due to Annual maintenance
| 08:13 |  | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Annual
maintenance
| 08:19 | 16:54 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to Maintenance
work and from Khulna(S) 230/132kVend.
| 08:20 | 16:36 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Annual Maintenance
| 08:20 | 16:36 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Annual Maintenance
| 08:27 | 16:55 | Bogura(New)-Naogaon 132 kV Ckt-2 Scheduled S/D from Naogaon 132/33kV end Due to Annual
maintenance and from Bogura 230/132kV end Due to Annual Maintenance work
| 08:30 | 16:33 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to
Annual maintenance work
| 08:30 | 16:12 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
Annual maintenance work
| 08:30 | 16:12 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to
Annual maintenance work
| 08:30 | 16:12 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to S/D taken for AM
work on mirpur ss end.
| 08:33 | 16:28 | Rahanpur 400/132kV S/S AT-02 LT Scheduled S/D Due to Annual maintenance
| 08:34 | 16:27 | Rahanpur 400/132kV S/S AT-02 HT Scheduled S/D Due to Annual maintenance
| 08:40 | 14:51 | Bibiana 400/230kV S/S ICT-02 HT Scheduled S/D Due to Annual Maintenance
| 08:40 | 14:52 | Bibiana 400/230kV S/S ICT-02 LT Scheduled S/D Due to Annual Maintenance
| 08:41 |  | Magura 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to 33kV Bus side DS
maintenance(project work of Energypac)
| 08:41 | 17:07 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to Annual
maintenance of KUL-FEN CKT-2 and from Fenchuganj 230/132/33kV end Due to Annual
Maintenance
| 08:50 | 17:51 | Brahmanbaria 132/33kV S/S 401T LT Scheduled S/D
| 08:51 | 17:51 | Brahmanbaria 132/33kV S/S 401T HT Scheduled S/D
| 08:55 |  | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end. and from
Satkhira 132/33kV end Due to Annual maintenance work
| 08:57 | 17:37 | Jashore 132/33kV S/S JH-2(L1) Scheduled S/D Due to Annual Maintenance
| 08:58 | 17:37 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Scheduled S/D Due to annual maintenance
| 09:06 | 16:42 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to Annual Maintenance 2025-26.
| 09:07 | 16:42 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to Annual Maintenance 2025-26.
| 09:09 | 16:52 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
| 09:14 | 17:36 | Bhulta 132/33kV S/S GT2 LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 75.0MW load
interrup.
| 09:17 | 17:25 | Bhulta 132/33kV S/S GT2 HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 75.0MW load
interrup.
| 09:20 | 14:20 | Chandpur 132/33kV S/S 402T (T-01) HT Scheduled S/D Due to SPMD annual Maintenance
| 09:24 |  | Purbasadipur 132/33kV S/S T-4 Transformer HT Project Work S/D
| 09:39 | 17:00 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Dead line
checking
| 09:50 |  | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to A/M
| 09:51 | 15:58 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to A/M
| 09:54 |  | Mahasthangar-Palashbari 132kV Ckt-1 Forced S/D from Palashbari 132/33kV end Due to
Conductor torn
| 10:33 | 15:21 | Bhulta-Rampura 230 kV Ckt-3 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance. and from Bhulta 400/230kV end Due to Annual Maintenance Work by Rampura Grid
SS
| 11:01 | 12:00 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to
Maintenance work at Muradnagar substation
| 11:01 | 12:04 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Maintenance at Aminbazar SS end and from Aminbazar 400/230/132kV end Due to For Rite of
way
| 11:02 | 11:59 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-01 Project Work S/D Due to SCADA
INTEGRATION
| 11:13 | 17:02 | Muradnagar 132/33kV S/S 132KV Busbar-1 Project Work S/D Due to SCADA INTEGRATION
| 11:20 | 16:36 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D
| 11:20 | 16:24 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D
| 11:26 | 17:48 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from Rajshahi 230/132/33kV end Due
to Annual Maintenance.
| 11:26 | 17:48 | Rajshahi-Rajshahi(New) 132kV Ckt-2 Scheduled S/D from Rajshahi 132/33kV end Due to
Annual Maintenance Work -2025
| 12:00 |  | Day Peak Generation is 10082 MW.
| 12:40 |  | Jamalpur 132/33kV S/S T-3 LT Tripped showing Micom relays Due to OTI trip.
| 12:40 |  | Jamalpur 132/33kV S/S T-3 HT Tripped showing Micom relays Due to OTI trip
| 13:07 | 13:57 | Dhamrai-Kaliakoir 132 kV Ckt-2 Forced S/D from Dhamrai 132/33kV end Due to Kailakur ss
annual maintenance and from Kaliakoir 400/230/132kV end Due to Isolating 132 kV Bus-2
from the 400/132 kV Transformer
|  | 13:14 | Sylhet 132/33kV S/S T1 LT is restored.
|  | 13:14 | Sylhet 132/33kV S/S T1 HT is restored.
| 14:31 | 16:57 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Project Work S/D Due to SCADA INTEGRATION
| 14:45 | 16:20 | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to SPMD ANNUAL MAINTENANCE
| 14:45 | 16:20 | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to SPMD ANNUAL MAINTENANCE
| 15:36 |  | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Distance
Z-1 ,1.2 KM. Phase C. Lockout relay relays Due to Distance 1.2 km
| 15:36 | 16:17 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB Initiation relays Due to
Master trip
|  | 15:44 | Rampur 230/132/33 S/S Halishahar-2 is restored.
|  | 17:25 | Dohazari-Sikalbaha 132 kV Ckt-2 is restored.
|  | 17:30 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
|  | 17:33 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) HT is restored.
|  | 17:34 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) LT is restored.
| 18:00 |  | Evening peak generation 11405 MW
|  | 19:56 | Rangpur 132/33kV S/S Rangpur-GTPS is restored.
| 20:55 |  | Raozan unit-2 was synchronized
| 22:12 |  | Amnura 132/33kV S/S T-1 (406T) HT Tripped showing Siemens 7UT61 relays.
| 00:02 |  | Khulna (C) S/S TR-1 425T HT Tripped showing differential relays Due to Incoming cable | [7 empty] | 17.0MW load
|  |  | fault | [7 empty] | interrup.
| 00:02 |  | Khulna (C) S/S TR-1 425T LT Tripped showing No relay relays Due to Incoming cable fault | [7 empty] | 17.0MW load
interrup.
| 00:02 | 01:50 | Khulna (C) S/S Tr-2 415 T HT Tripped showing no relay relays Due to Tr 1 incoming cable | [7 empty] | 8.0MW load
|  |  | fault | [7 empty] | interrup.
| 00:02 | 01:51 | Khulna (C) S/S Tr-2 415 T LT Tripped showing Ins E/F relays Due to Tr 1 incoming cable | [7 empty] | 8.0MW load
|  |  | fault | [7 empty] | interrup.
| 01:17 |  | Bhola Nutan Biddut BD LTD Synchronized with remarks:- GT-12
| 05:00 |  | Minimum Generation: 7592 MW.
| 06:53 |  | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance 2025-26 and from Bhulta 400/230kV end Due to Due to Annual maintenance work
| 07:22 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Due to the burning of the source side | [7 empty] | 8.0MW load
|  |  | A-phase isolator finger of the Korapur 1 No 33 kv feeder maintenance work by PBS. | [7 empty] | interrup.
| 07:22 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Due to the burning of the source side | [7 empty] | 8.0MW load
|  |  | A-phase isolator finger of the Korapur 1 No 33 kv feeder mainte work by PBS team. | [7 empty] | interrup.
| 07:57 |  | Natore-Rajshahi 132kV Ckt-1 Scheduled S/D from Natore 132/33kV end Due to Annual
Maintenance. and from Rajshahi 132/33kV end Due to Annual Maintenance Work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 338 | 8391600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6739212 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 29 | 90360 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 24000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 20 | 62059 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 64095 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.8 | 484200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 433440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 260160 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 60 | 139255 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 49 | 227952 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 124800 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 93600 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 196256 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 452 | 10373390 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 34 | 62400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 1486.8 | 27766779
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 100000 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127845 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 23 | 63360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1105320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 455836 | DP High
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 35 | 98690 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 31123 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 39360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 458400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20883 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 18 | 45200 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 94080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 21779998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 19680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 8465454.55 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1710 | 32905229.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 198 | 4775000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 260 | 4790000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 225 | 6642100 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 5 | 407304 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 910664 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 35 | 68581 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 107 | 2174071 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 42 | 108960 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 100 | 2039040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 372540 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 21 | 42240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 444945 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1061 | 22775445
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 75 | 2011200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 249600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 606000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 276630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 150 | 3156180
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 718680 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 650592 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1280640 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 3694290 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 382000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 457464 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7373000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8880000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1006 | 23436666
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 865 | 21690909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 300 | 5452704 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 487440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1097 | 21301820 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2262 | 48932873
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 506 | 7600000 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2651000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 925 | 18651636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2753440 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3340 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1656 | 31659416.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 369000 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 167 | 3916273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 383 | 8711563 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1330 | 22554982 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 375760 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 615500 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1880 | 36565158
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1264581 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 284419 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34120.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 288423 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173197 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1126800 | -
Rangpur Area Total |  |  |  |  | 950 | 193 | 3171540.92
Eastern Grid Total |  |  |  |  | 17383.855 | 5413.8 | 110040299.55
Western Grid Total |  |  |  |  | 10821.56 | 5991 | 120328988.28
National Grid Total |  |  |  |  | 28205.415 | 11404.8 | 230369287.83
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7779.55 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3324.4 | MW
i) Dhaka area |  |  | 4349.55 |  | MW | i) Khulna area |  |  |  | 1257 | MW
ii) Chattogram area |  |  | 1186 |  | MW | ii) Barishal area |  |  |  | 307.2 | MW
iii) Cumilla area |  |  | 951 |  | MW | iii) Rajshahi area |  |  |  | 998.2 | MW
iv) Mymensingh area |  |  | 876 |  | MW | iv) Rangpur area |  |  |  | 762 | MW
v) Sylhet area |  |  | 417 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11103.95 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 10:00 | 67 | Hathazari | 60 | 18:30 | 133 | Niamatpur | 40 | 18:00
2 | AKSML | 137 | 03:00 | 68 | Ishurdi | 55 | 19:00 | 134 | Noapara | 41 | 18:00
3 | Aftabnagar | 28 | 12:00 | 69 | Jaldhaka | 52 | 18:00 | 135 | PHP | 9 | 11:00
4 | Agargaon | 90 | 13:00 | 70 | Jamalpur | 90 | 18:00 | 136 | Pabna | 69 | 18:00
5 | Agrabad | 64 | 18:00 | 71 | Jashore | 93 | 13:00 | 137 | Palashbari | 85 | 18:00
6 | Amnura | 16 | 13:00 | 72 | Jhenaidah | 94 | 18:00 | 138 | Panchagarh | 45 | 18:00
7 | Ashuganj | 62 | 12:00 | 73 | Joydebpur | 119 | 18:00 | 139 | Patiya | 6 | 18:30
8 | BSRM | 201 | 04:00 | 74 | Joypurhat | 46 | 18:00 | 140 | Patuakhali | 43 | 21:00
9 | Bagerhat | 68 | 18:00 | 75 | Juldah | 16 | 16:00 | 141 | Payra | 22 | 20:00
10 | Bajitpur | 57 | 18:30 | 76 | KSRM | 32 | 08:00 | 142 | Postogola | 53 | 13:00
11 | Bakulia | 65 | 18:00 | 77 | Kabirpur | 178 | 18:30 | 143 | Purbachal | 28 | 13:00
12 | Banani | 34.8 | 13:00 | 78 | Kachua | 54 | 22:00 | 144 | Purbasadipur | 102 | 18:00
13 | Bangabhaban | 16 | 11:00 | 79 | Kallyanpur | 72 | 12:00 | 145 | Rahanpur | 20 | 19:00
14 | Barapukuria | 48 | 18:00 | 80 | Kalurghat | 42 | 17:00 | 146 | Rahim | 30 | 07:00
15 | Barguna | 14 | 18:00 | 81 | Kamrangirchar | 67 | 13:00 | 147 | Rajbari | 57 | 18:00
16 | Barishal | 87 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 111 | 18:00
17 | Barishal-230 | 64 | 18:30 | 83 | Kasba | 22 | 18:00 | 149 | Rajshahi | 66 | 18:00
18 | Baroaulia | 60 | 11:00 | 84 | Kazla | 87 | 12:00 | 150 | Rajshahi-230 | 66 | 13:00
19 | Baroirhat | 50 | 18:00 | 85 | Keranigonj | 63 | 13:00 | 151 | Ramganj | 66 | 18:00
20 | Bashundhara | 131 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 32 | 18:00
21 | BashundharaCement | 13 | 13:00 | 87 | Khulna | 48 | 13:00 | 153 | Rangamati | 12 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 158 | 14:00 | 154 | Rangpur | 109 | 18:00
23 | Benapole | 56 | 18:30 | 89 | Kishoreganj | 85 | 18:00 | 155 | Ruppur | 3.2 | 15:00
24 | Bhaluka | 124 | 18:00 | 90 | Kodda | 264 | 18:00 | 156 | SSM | 2 | 23:00
25 | Bhandaria | 38 | 21:00 | 91 | Kulaura | 30 | 17:00 | 157 | Saidpur | 92 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 48 | 18:00 | 158 | Satkhira | 80 | 18:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | Kushtia | 110 | 18:00 | 159 | Satmasjid | 81 | 14:00
28 | Bhulta | 183 | 20:00 | 94 | Laksam | 20 | 19:30 | 160 | Savar | 172 | 16:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 24 | 18:30 | 161 | SevenRings | 16.67 | 23:00
30 | Bogura | 118 | 18:00 | 96 | Lalbag | 64 | 13:00 | 162 | ShahCement | 26 | 16:00
31 | Borhanuddin | 65 | 21:00 | 97 | Lalmonirhat | 44 | 18:00 | 163 | Shahjadpur | 60 | 18:00
32 | Brahmanbaria | 100 | 18:30 | 98 | MI_Cement | 16.3 | 21:00 | 164 | Shahjibazar | 84 | 18:00
33 | Cantonment | 98 | 13:00 | 99 | Madanganj | 37 | 13:00 | 165 | Shahmirpur | 41 | 18:00
34 | Chandina | 8 | 17:00 | 100 | Madaripur | 67 | 19:00 | 166 | Shariatpur | 56 | 18:00
35 | Chandpur | 58 | 19:30 | 101 | Madartek | 66 | 13:00 | 167 | Sherpur | 104 | 18:00
36 | Chandraghona | 26 | 18:00 | 102 | Madunaghat | 37 | 18:00 | 168 | Shikalbaha | 20 | 12:00
37 | Chapai | 44 | 13:00 | 103 | Magura | 45 | 18:30 | 169 | Shitalakhya | 66 | 12:00
38 | Charsaidpur | 35 | 10:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 36 | 18:00
39 | Chauddagram | 45 | 13:00 | 105 | Maijdee | 22 | 21:00 | 171 | Shyampur | 128 | 09:00
40 | Chhatak | 22 | 19:30 | 106 | Manikganj | 92 | 18:00 | 172 | Siddhirganj | 103 | 12:00
41 | Chowmuhani | 106 | 18:00 | 107 | Maniknagar | 46 | 13:00 | 173 | Sirajganj | 83 | 18:30
42 | Chuadanga | 73 | 18:30 | 108 | Matarbari | 39 | 18:00 | 174 | Sonargaon | 104 | 18:00
43 | Coxsbazar | 98 | 18:00 | 109 | Matuail | 62 | 17:00 | 175 | Sreemongol | 57 | 18:00
44 | Cumilla(N) | 76 | 19:00 | 110 | Metrorail_Motijheel | 26 | 18:30 | 176 | Sreepur | 80 | 16:00
45 | Cumilla(S) | 127 | 14:00 | 111 | Metrorail_Uttara | 9 | 11:00 | 177 | Srinagar | 30.9 | 13:00
46 | Daganbhuiyan | 0 | 01:00 | 112 | Millgate | 92 | 12:00 | 178 | Sunamganj | 39 | 19:30
47 | Daudkandi | 110 | 18:00 | 113 | Mirpur | 117 | 18:00 | 179 | Sylhet | 33 | 18:00
48 | DhakaUniversity | 66 | 13:00 | 114 | Mirsorai | 24 | 09:00 | 180 | Sylhet-132 | 85 | 17:00
49 | Dhamrai | 102 | 18:00 | 115 | Mirzapur | 36 | 18:00 | 181 | TK | 16 | 18:30
50 | Dhanmondi | 74 | 15:00 | 116 | Mithapukur | 46 | 18:00 | 182 | Tangail | 124 | 13:00
51 | Dohazari | 72 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 16 | 18:00
52 | Faridpur | 111 | 18:00 | 118 | Mogbazar | 67.5 | 15:00 | 184 | Tasnim | 30 | 15:00
53 | Fatullah | 105 | 15:00 | 119 | Mongla | 39 | 09:00 | 185 | Thakurgaon | 75 | 18:00
54 | Fenchuganj | 25 | 18:00 | 120 | Motijheel | 30 | 13:00 | 186 | Tongi | 92 | 17:00
55 | Feni | 70 | 18:00 | 121 | Muktagacha | 26 | 07:00 | 187 | Ullahpara | 26 | 18:00
56 | GPH | 11 | 00:00 | 122 | Munshiganj | 82 | 18:30 | 188 | Ullon | 50 | 13:00
57 | Ghatail | 56 | 07:00 | 123 | Muradnagar | 28 | 18:00 | 189 | Uttara | 64 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 132 | 18:00 | 190 | UttaraNew | 28 | 13:00
59 | Ghorashal-230 | 82 | 19:00 | 125 | Naogaon | 77 | 18:00 | 191 | Zigatola | 50 | 12:00
60 | Goalpara | 24 | 13:00 | 126 | Narail | 42 | 18:00
61 | Gollamari | 72 | 12:00 | 127 | Narinda | 54 | 13:00
62 | Gopalganj | 77 | 18:00 | 128 | Narshingdi | 140 | 19:00
63 | Gulshan | 88 | 12:00 | 129 | Natore | 100 | 18:00
64 | Halishahar | 58 | 15:00 | 130 | Nawabganj | 37.2 | 13:00
65 | HaripurSBU | 150 | 15:00 | 131 | Netrakona | 103 | 18:00
66 | Hasnabad | 72 | 20:00 | 132 | New | 63 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9352.48 | 0 |  | 9352.48
1:00 | 8741.98 | 0 |  | 8741.98
2:00 | 8298.09 | 0 |  | 8298.09
3:00 | 8030.54 | 0 |  | 8030.54
4:00 | 7826.44 | 0 |  | 7826.44
5:00 | 7706.64 | 0 |  | 7706.64
6:00 | 8041.15 | 0 |  | 8041.15
7:00 | 9018.15 | 0 |  | 9018.15
8:00 | 9594.22 | 0 |  | 9594.22
9:00 | 9381.92 | 0 |  | 9381.92
10:00 | 9279.62 | 0 |  | 9279.62
11:00 | 9464.05 | 0 |  | 9464.05
12:00 | 10085.52 | 0 |  | 10085.52
13:00 | 10364.45 | 0 |  | 10364.45
14:00 | 10081.15 | 0 |  | 10081.15
15:00 | 9734.48 | 0 |  | 9734.48
16:00 | 9581.37 | 0 |  | 9581.37
17:00 | 10084.39 | 0 |  | 10084.39
18:00 | 11404.8 | 0 |  | 11404.8
19:00 | 10945.8 | 0 |  | 10945.8
19:30 | 10842.8 | 0 |  | 10842.8
20:00 | 10649.6 | 0 |  | 10649.6
21:00 | 10536.2 | 0 |  | 10536.2
22:00 | 10097.2 | 0 |  | 10097.2
23:00 | 9732 | 0 |  | 9732
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4684 | 4668.48 | 9352.48 | DAILY GENERATION CURVE
00:30 | 4561.75 | 4485.48 | 9047.23
01:00 | 4439.5 | 4302.48 | 8741.98 | 25-11-2025
01:30 | 4224 | 4296.035 | 8520.035
02:00 | 4008.5 | 4289.59 | 8298.09
02:30 | 3910.75 | 4253.565 | 8164.315
03:00 | 3813 | 4217.54 | 8030.54
03:30 | 3728.5 | 4199.99 | 7928.49
04:00 | 3644 | 4182.44 | 7826.44
04:30 | 3624 | 4142.54 | 7766.54
05:00 | 3604 | 4102.64 | 7706.64
05:30 | 3693 | 4180.895 | 7873.895
06:00 | 3782 | 4259.15 | 8041.15
06:30 | 4120.08 | 4409.57 | 8529.65
07:00 | 4458.16 | 4559.99 | 9018.15
07:30 | 4529.975 | 4776.21 | 9306.185
08:00 | 4601.79 | 4992.43 | 9594.22
08:30 | 4490.41 | 4997.66 | 9488.07
09:00 | 4379.03 | 5002.89 | 9381.92
09:30 | 4361.15 | 4969.62 | 9330.77
10:00 | 4343.27 | 4936.35 | 9279.62
10:30 | 4408.405 | 4963.43 | 9371.835
11:00 | 4473.54 | 4990.51 | 9464.05
11:30 | 4721.19 | 5053.595 | 9774.785
12:00 | 4968.84 | 5116.68 | 10085.52
12:30 | 4990.335 | 5234.65 | 10224.985
13:00 | 5011.83 | 5352.62 | 10364.45
13:30 | 4949.68 | 5273.12 | 10222.8
14:00 | 4887.53 | 5193.62 | 10081.15
14:30 | 4807.305 | 5100.51 | 9907.815
15:00 | 4727.08 | 5007.4 | 9734.48
15:30 | 4687.165 | 4970.76 | 9657.925
16:00 | 4647.25 | 4934.12 | 9581.37
16:30 | 4739.61 | 5093.27 | 9832.88
17:00 | 4831.97 | 5252.42 | 10084.39
17:30 | 5122.885 | 5621.71 | 10744.595
18:00 | 5413.8 | 5991 | 11404.8
18:30 | 5287.3 | 5888 | 11175.3
19:00 | 5160.8 | 5785 | 10945.8
19:30 | 5110.8 | 5732 | 10842.8
20:00 | 4956.6 | 5693 | 10649.6
20:30 | 4907.4 | 5685.5 | 10592.9 |  | Executive Engineer
21:00 | 4858.2 | 5678 | 10536.2 |  | Network Operation Division
21:30 | 4801.7 | 5515 | 10316.7
22:00 | 4745.2 | 5352 | 10097.2
22:30 | 4707.6 | 5207 | 9914.6
23:00 | 4670 | 5062 | 9732

## En-Curve
QF-LDC-12
Date | 25-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3099 | 1159 | 887 | 0 | 82 | 835.48 | 46 | 3224 | 0 | 0 | 16 | 0 | 0 | 4 | 0 | DAILY ENERGY CURVE
00:30 | 3094.5 | 1103.25 | 887 | 0 | 79 | 833.98 | 46 | 2984 | 0 | 0 | 16 | 0 | 0 | 3.5 | 0 | 25-11-2025
01:00 | 3090 | 1047.5 | 887 | 0 | 76 | 832.48 | 46 | 2744 | 0 | 0 | 16 | 0 | 0 | 3 | 0
01:30 | 3014 | 985 | 887 | 0 | 73 | 831.035 | 46 | 2673.5 | 0 | 0 | 8 | 0 | 0 | 2.5 | 0 | Energy Generated | 230.3693 |  | MKWHr
02:00 | 2938 | 922.5 | 887 | 0 | 70 | 829.59 | 46 | 2603 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2845 | 911.75 | 887 | 0 | 69 | 828.565 | 46 | 2576 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Total Energy Requirement | 230.3693 |  | MKWHr
03:00 | 2752 | 901 | 887 | 0 | 68 | 827.54 | 46 | 2549 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2687 | 894 | 887 | 0 | 68 | 828.99 | 46 | 2517.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2622 | 887 | 887 | 0 | 68 | 830.44 | 46 | 2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2544 | 890 | 887 | 0 | 71 | 832.54 | 46 | 2494.5 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
05:00 | 2466 | 893 | 887 | 0 | 74 | 834.64 | 46 | 2503 | 0 | 0 | 0 | 0 | 0 | 3 | 0
05:30 | 2592 | 925 | 887 | 0 | 75 | 833.395 | 46 | 2513 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0
06:00 | 2718 | 957 | 887 | 0 | 76 | 832.15 | 46 | 2523 | 0 | 0 | 0 | 0 | 0 | 2 | 0
06:30 | 2974 | 1010.5 | 887 | 0 | 70 | 831.815 | 46 | 2675 | 20.835 | 0 | 13 | 0 | 0 | 1.5 | 0
07:00 | 3230 | 1064 | 887 | 0 | 64 | 831.48 | 46 | 2827 | 41.67 | 0 | 26 | 0 | 0 | 1 | 0
07:30 | 3194 | 1064.5 | 887 | 0 | 71 | 831.075 | 46 | 3017 | 135.61 | 0 | 58.5 | 0 | 0 | 1.5 | 0
08:00 | 3158 | 1065 | 887 | 0 | 78 | 830.67 | 46 | 3207 | 229.55 | 0 | 91 | 0 | 0 | 2 | 0
08:30 | 3059 | 999.5 | 887.5 | 0 | 80 | 832.35 | 46 | 3176.5 | 325.72 | 0 | 80 | 0 | 0 | 1.5 | 0
09:00 | 2960 | 934 | 888 | 0 | 82 | 834.03 | 46 | 3146 | 421.89 | 0 | 69 | 0 | 0 | 1 | 0
09:30 | 2889.5 | 952 | 888 | 0 | 82 | 833.76 | 46 | 3074 | 508.01 | 4 | 52 | 0 | 0 | 1.5 | 0
10:00 | 2819 | 970 | 888 | 0 | 82 | 833.49 | 46 | 3002 | 594.13 | 8 | 35 | 0 | 0 | 2 | 0
10:30 | 2871.5 | 981.9 | 888.5 | 0 | 85 | 842.88 | 46 | 2992.5 | 616.055 | 16.5 | 29.5 | 0 | 0 | 1.5 | 0
11:00 | 2924 | 993.8 | 889 | 0 | 88 | 852.27 | 46 | 2983 | 637.98 | 25 | 24 | 0 | 0 | 1 | 0
11:30 | 3080.5 | 1041.65 | 888.5 | 0 | 96 | 853.61 | 46 | 3066.5 | 652.525 | 25 | 24 | 0 | 0 | 0.5 | 0
12:00 | 3237 | 1089.5 | 888 | 0 | 104 | 854.95 | 46 | 3150 | 667.07 | 25 | 24 | 0 | 0 | 0 | 0
12:30 | 3240.5 | 1087.5 | 884.5 | 0 | 101 | 855.685 | 46 | 3316 | 644.8 | 25 | 24 | 0 | 0 | 0 | 0
13:00 | 3244 | 1085.5 | 881 | 0 | 98 | 856.42 | 46 | 3482 | 622.53 | 25 | 24 | 0 | 0 | 0 | 0
13:30 | 3166.5 | 1074.25 | 873 | 0 | 101 | 845.21 | 46 | 3498 | 569.84 | 25 | 24 | 0 | 0 | 0 | 0
14:00 | 3089 | 1063 | 865 | 0 | 104 | 834 | 46 | 3514 | 517.15 | 25 | 24 | 0 | 0 | 0 | 0
14:30 | 3066.5 | 1043 | 865.5 | 0 | 99 | 836.5 | 46 | 3468 | 433.815 | 25 | 24.5 | 0 | 0 | 0 | 0
15:00 | 3044 | 1023 | 866 | 0 | 94 | 839 | 46 | 3422 | 350.48 | 25 | 25 | 0 | 0 | 0 | 0
15:30 | 3015 | 1014.5 | 866 | 0 | 94 | 878 | 46 | 3427.5 | 242.425 | 30 | 44.5 | 0 | 0 | 0 | 0
16:00 | 2986 | 1006 | 866 | 0 | 94 | 917 | 46 | 3433 | 134.37 | 35 | 64 | 0 | 0 | 0 | 0
16:30 | 2976.5 | 1035.4 | 866 | 0 | 95 | 998.5 | 46 | 3539.5 | 70.48 | 55.5 | 150 | 0 | 0 | 0 | 0
17:00 | 2967 | 1064.8 | 866 | 0 | 96 | 1080 | 46 | 3646 | 6.59 | 76 | 236 | 0 | 0 | 0 | 0
17:30 | 3006.5 | 1067.3 | 865.5 | 0 | 98 | 1205 | 46 | 3865.5 | 3.295 | 120.5 | 467 | 0 | 0 | 0 | 0
18:00 | 3046 | 1069.8 | 865 | 0 | 100 | 1330 | 46 | 4085 | 0 | 165 | 698 | 0 | 0 | 0 | 0
18:30 | 3033 | 1090.8 | 865.5 | 0 | 95 | 1279 | 46 | 4093.5 | 0 | 107.5 | 565 | 0 | 0 | 0 | 0
19:00 | 3020 | 1111.8 | 866 | 0 | 90 | 1228 | 46 | 4102 | 0 | 50 | 432 | 0 | 0 | 0 | 0
19:30 | 3032 | 1142.8 | 866 | 0 | 98 | 1220 | 46 | 4073 | 0 | 33 | 332 | 0 | 0 | 0 | 0
20:00 | 3000 | 1126.8 | 866 | 0 | 98 | 1219 | 46 | 4061 | 0 | 8 | 224.8 | 0 | 0 | 0 | 0
20:30 | 2996.5 | 1130 | 865.5 | 0 | 94 | 1220 | 46 | 4049.5 | 0 | 4 | 187.4 | 0 | 0 | 0 | 0
21:00 | 2993 | 1133.2 | 865 | 0 | 90 | 1221 | 46 | 4038 | 0 | 0 | 150 | 0 | 0 | 0 | 0
21:30 | 2980 | 1123.2 | 865.5 | 0 | 88 | 1165.5 | 46 | 3938 | 0 | 0 | 110.5 | 0 | 0 | 0 | 0
22:00 | 2967 | 1113.2 | 866 | 0 | 86 | 1110 | 46 | 3838 | 0 | 0 | 71 | 0 | 0 | 0 | 0
22:30 | 2968 | 1115.6 | 865.5 | 0 | 85 | 1066 | 46 | 3715.5 | 0 | 0 | 53 | 0 | 0 | 0 | 0
23:00 | 2969 | 1118 | 865 | 0 | 84 | 1022 | 46 | 3593 | 0 | 0 | 35 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 398 | 23:00 | 382 | 13:00 | Meghnaghat | 397 | 03:00 | 384 | 13:00
Ashuganj | 403 | 7:00 | 388 | 13:00 | Payra | 416 | 04:00 | 410 | 13:00
Bhulta | 399 | 04:00 | 384 | 13:00 | Rahanpur | 415 | 03:00 | 400 | 18:00
Bibiana | 398 | 01:00 | 391 | 13:00 | Rampal | 412 | 03:00 | 398 | 18:00
BIPTC | 404 | 01:00 | 393 | 18:00
Bogura | 409 | 05:00 | 388 | 18:00
Gopalganj | 408 | 04:00 | 395 | 13:00
Kaliakoir | 395 | 04:00 | 379 | 12:00
Korerhat | 406 | 05:00 | 396 | 11:00
Madunaghat | 404 | 04:00 | 395 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 228 | 13:00 | Kachua | 236 | 01:00 | 233 | 12:00
AKSML | 239 | 04:00 | 230 | 13:00 | Kaliakoir | 240 | 04:00 | 228 | 12:00
Aminbazar | 239 | 23:00 | 229 | 12:00 | Keranigonj | 237 | 03:00 | 225 | 13:00
Ashuganj | 234 | 03:00 | 229 | 12:00 | Khulna(S) | 241 | 03:00 | 230 | 13:00
Ashuganj-400 | 234 | 03:00 | 229 | 12:00 | Korerhat | 239 | 05:00 | 233 | 11:00
Baghabari | 237 | 04:00 | 228 | 18:00 | Madunaghat | 239 | 04:00 | 233 | 12:00
Barapukuria | 225 | 05:00 | 211 | 18:00 | Madunaghat-400 | 240 | 05:00 | 234 | 13:00
Barapukuria-230 | 225 | 05:00 | 211 | 18:00 | Maniknagar | 231 | 03:00 | 222 | 12:00
Barishal | 242 | 02:00 | 236 | 13:00 | Meghnaghat | 238 | 04:00 | 224 | 14:00
Bheramara | 236 | 04:00 | 225 | 18:00 | Meghnaghat-400 | 234 | 03:00 | 225 | 13:00
Bhulta | 233 | 04:00 | 223 | 12:00 | Mirsorai | 236 | 03:00 | 228 | 13:00
Bibiana | 237 | 04:00 | 227 | 12:00 | Rajshahi | 236 | 03:00 | 225 | 18:00
BIPTC | 238 | 02:00 | 225 | 18:00 | Rampal | 238 | 03:00 | 228 | 13:00
Bogura | 237 | 04:00 | 225 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 236 | 04:00 | 225 | 18:00 | Rampura | 232 | 03:00 | 221 | 13:00
Borhanuddin | 244 | 02:00 | 238 | 18:00 | Shikalbaha | 237 | 08:00 | 232 | 12:00
BSRM | 236 | 03:00 | 227 | 13:00 | Shyampur | 235 | 03:00 | 226 | 12:00
Cumilla(N) | 234 | 03:00 | 225 | 13:00 | Siddhirganj | 232 | 00:00 | 223 | 12:00
Faridpur | 242 | 03:00 | 234 | 12:00 | Sirajgonj | 241 | 04:00 | 234 | 18:00
Fenchuganj | 234 | 00:00 | 229 | 11:00 | Sreepur | 231 | 04:00 | 226 | 11:00
Feni | 234 | 03:00 | 225 | 13:00 | Tongi | 234 | 04:00 | 224 | 11:00
Ghorashal | N/A | N/A | N/A | N/A
Ghorashal-230 | 231 | 05:00 | 214 | 18:00
Gopalganj | 242 | 04:00 | 234 | 13:00
GPH | 235 | 10:00 | 215 | 05:00
Haripur | 234 | 05:00 | 225 | 12:00
Hasnabad | 237 | 04:00 | 225 | 13:00
Hathazari | 237 | 03:00 | 229 | 16:00
Ishurdi | 239 | 04:00 | 228 | 18:00
Jhenaidah | 237 | 04:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 128 | 12:00 | Lalbag | 138 | 03:00 | 129 | 13:00
Agargaon | 138 | 02:00 | 131 | 13:00 | Lalmonirhat | 133 | 05:00 | 122 | 18:00
Agrabad | 138 | 08:00 | 133 | 12:00 | Madanganj | 134 | 01:00 | 130 | 18:30
AKS | 135 | 04:00 | 131 | 13:00 | Madaripur | 137 | 11:00 | 135 | 13:00
Aminbazar | 138 | 06:00 | 131 | 12:00 | Madartek | 134 | 05:00 | 126 | 13:00
Amnura | 138 | 02:00 | 130 | 12:00 | Madunaghat | 139 | 02:00 | 135 | 12:00
Ashuganj | 141 | 01:00 | 138 | 12:00 | Magura | 140 | 02:00 | 132 | 13:00
Bagerhat | 136 | 05:00 | 126 | 18:00 | Mahasthangarh | 134 | 02:00 | 127 | 18:00
Bajitpur | 137 | 02:00 | 134 | 12:00 | Maijdee | 135 | 03:00 | 130 | 13:00
Bakulia | 139 | 05:00 | 132 | 13:00 | Manikganj | 138 | 04:00 | 126 | 15:00
Banani | 135 | 03:00 | 126 | 13:00 | Maniknagar | 138 | 03:00 | 130 | 13:00
Bangabhaban | 137 | 01:00 | 131 | 12:00 | Matarbari | 130 | 02:00 | 120 | 13:00
Barapukuria | 137 | 05:00 | 127 | 18:00 | Matuail | 135.6 | 06:00 | 130 | 12:00
Barguna | 136 | 08:00 | 134 | 12:00 | Metrorail_Motijheel | 138 | 03:00 | 130 | 13:00
Barishal | 139 | 03:00 | 135 | 12:00 | Metrorail_Uttara | 140 | 03:00 | 130 | 13:00
Barishal-230 | 139 | 01:00 | 135 | 13:00 | Millgate | 140 | 01:00 | 130 | 13:00
Baroaulia | 138 | 07:00 | 132 | 13:00 | Mirpur | 138 | 04:00 | 130 | 13:00
Baroirhat | 136 | 08:00 | 132 | 13:00 | Mirzapur | 136 | 05:00 | 128 | 12:00
Bashundhara | 135 | 04:00 | 126 | 13:00 | Mithapukur | 134 | 04:00 | 124 | 18:00
BashundharaCement | 134 | 01:00 | 130 | 18:30 | MI_Cement | 136 | 03:00 | 127 | 13:00
Beanibazar | 133 | 04:00 | 130 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 139 | 02:00 | 119 | 13:00 | Mogbazar | 137 | 03:00 | 130 | 11:00
Bhaluka | 133 | 00:00 | 129 | 13:00 | Mongla | 136 | 05:00 | 127 | 18:00
Bhandaria | 138 | 06:00 | 132 | 13:00 | Motijheel | 137 | 01:00 | 131 | 12:00
Bhangura | 137 | 05:00 | 131 | 18:00 | Muktagacha | 136 | 09:00 | 129 | 12:00
Bheramara | 140 | 02:00 | 135 | 18:00 | Munshiganj | 134 | 04:00 | 128 | 12:00
Bheramara(GK) | 140 | 03:00 | 135 | 18:00 | Muradnagar | 137 | 05:00 | 130 | 13:00
Bhulta | 130 | 07:00 | 125 | 00:00 | Mymensingh | 137 | 09:00 | 128 | 12:00
Bog-Sherpur | 136 | 03:00 | 128 | 18:00 | Naogaon | 134 | 04:00 | 125 | 12:00
Bogura | 135 | 03:00 | 129 | 18:00 | Narail | 140 | 04:00 | 130 | 18:00
Bogura-230 | 136 | 04:00 | 128 | 18:00 | Narinda | 138 | 03:00 | 130 | 13:00
Brahmanbaria | 136 | 08:00 | 132 | 11:00 | Narshingdi | 136 | 01:00 | 126 | 13:00
Cantonment | 138 | 01:00 | 131 | 12:00 | Natore | 136 | 01:00 | 130 | 18:00
Chandina | 139 | 05:00 | 133 | 13:00 | Nawabganj | 139 | 04:00 | 130 | 13:00
Chandpur | 138 | 02:00 | 134 | 13:00 | Netrakona | 132 | 22:00 | 127 | 07:00
Chandraghona | 140 | 03:00 | 135 | 12:00 | New | 142 | 04:00 | 131 | 13:00
Chapai | 138 | 01:00 | 133 | 19:00 | Niamatpur | 138 | 00:00 | 134 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 136 | 03:00 | 129 | 12:00 | Noapara | 138 | 01:00 | 130 | 18:00
Chauddagram | 137 | 04:00 | 130 | 06:00 | Pabna | 139 | 02:00 | 132 | 18:00
Chhatak | 132 | 00:00 | 129 | 12:00 | Palashbari | 131 | 04:00 | 121 | 18:00
Chowmuhani | 135 | 03:00 | 130 | 13:00 | Panchagarh | 137 | 04:00 | 126 | 09:00
Chuadanga | 140 | 03:00 | 129 | 18:00 | Patiya | 139 | 05:00 | 134 | 13:00
Coxsbazar | 129 | 04:00 | 122 | 13:00 | Patuakhali | 136 | 01:00 | 134 | 07:00
Cumilla(N) | 139 | 04:00 | 133 | 13:00 | Payra | 137 | 01:00 | 134 | 17:00
Cumilla(S) | 137 | 05:00 | 126 | 12:00 | PHP | 137 | 03:00 | 131 | 13:00
Daganbhuiyan | 137 | 03:00 | 131 | 13:00 | Postogola | 136 | 07:00 | 129 | 13:00
Daudkandi | 135 | 05:00 | 128 | 13:00 | Purbachal | 135 | 02:00 | 127 | 13:00
DhakaUniversity | 135 | 03:00 | 127 | 13:00 | Purbasadipur | 134 | 04:00 | 124 | 12:00
Dhamrai | 136 | 06:00 | 130 | 15:00 | Rahanpur | 139 | 01:00 | 134 | 18:00
Dhanmondi | 137 | 04:00 | 131 | 12:00 | Rahanpur-400 | 140 | 03:00 | 135 | 18:00
Dohazari | 136 | 06:00 | 128 | 13:00 | Rahim | 136 | 05:00 | 130 | 12:00
Faridpur | 140 | 05:00 | 135 | 13:00 | Rajbari | 140 | 03:00 | 134 | 13:00
Fatullah | 140 | 04:00 | 129 | 12:00 | Rajendrapur | 135 | 04:00 | 129 | 12:00
Fenchuganj | 139 | 00:00 | 136 | 11:00 | Rajshahi | 136 | 01:00 | 130 | 13:00
Feni | 135 | 01:00 | 130 | 13:00 | Rajshahi-230 | 136 | 01:00 | 129 | 13:00
Feni-230 | 137 | 03:00 | 131 | 13:00 | Ramganj | 134 | 01:00 | 132 | 11:00
Ghatail | 134 | 10:00 | 126 | 18:00 | Rampur | 139 | 04:00 | 132 | 13:00
Ghorashal | 135 | 00:00 | 131 | 12:00 | Rampura | 135 | 03:00 | 128 | 12:00
Goalpara | 140 | 03:00 | 131 | 13:00 | Rangamati | 139 | 06:00 | 134 | 13:00
Gollamari | 139 | 03:00 | 132 | 18:00 | Rangpur | 134 | 04:00 | 126 | 08:00
Gopalganj | 140 | 04:00 | 134 | 13:00 | Ruppur | 140 | 04:00 | 134 | 18:00
Gopalganj-400 | 140 | 01:00 | 136 | 13:00 | Saidpur | 135 | 05:00 | 123 | 18:00
Gulshan | 134 | 04:00 | 127 | 12:00 | Satkhira | 139 | 04:00 | 129 | 13:00
Halishahar | 139 | 03:00 | 133 | 13:00 | Satmasjid | 139 | 04:00 | 130 | 13:00
Haripur | 136 | 02:00 | 130 | 12:00 | Savar | 139 | 05:00 | 129 | 12:00
HaripurSBU | 137 | 05:00 | 132 | 11:00 | SevenRings | 137 | 05:00 | 130 | 12:00
Hasnabad | 137 | 04:00 | 131 | 11:00 | ShahCement | 136 | 03:00 | 129 | 12:00
Hathazari | 140 | 03:00 | 135 | 15:00 | Shahjadpur | 142 | 03:00 | 134 | 18:00
Ishurdi | 141 | 02:00 | 135 | 18:00 | Shahjibazar | 138 | 08:00 | 134 | 03:00
Jaldhaka | 132 | 04:00 | 120 | 18:00 | Shahmirpur | 138 | 07:00 | 134 | 01:00
Jamalpur | 131 | 09:00 | 122 | 00:00 | Shariatpur | 140 | 03:00 | 134 | 13:00
Jashore | 138 | 03:00 | 121 | 13:00 | Sherpur | 129 | 09:00 | 121 | 00:00
Jhenaidah | 141 | 02:00 | 121 | 18:00 | Shikalbaha | 127 | 05:00 | 123 | 13:00
Jhenaidah-230 | 142 | 03:00 | 132 | 13:00 | Shikalbaha-230 | 140 | 04:00 | 135 | 13:00
Joydebpur | 135 | 22:00 | 126 | 13:00 | Shitalakhya | 136 | 03:00 | 127 | 13:00
Joypurhat | 133 | 04:00 | 124 | 13:00 | Sholosohor | 139 | 02:00 | 135 | 13:00
Juldah | 138 | 00:00 | 133 | 13:00 | Shyampur | 139 | 06:00 | 133 | 10:00
Kabirpur | 136 | 03:00 | 127 | 12:00 | Shyampur-230 | 140 | 03:00 | 134 | 12:00
Kachua | 140 | 04:00 | 135 | 13:00 | Siddhirganj | 136 | 03:00 | 130 | 13:00
Kaliakoir | 139 | 03:00 | 132 | 12:00 | Sirajganj | 134 | 00:00 | 128 | 18:00
Kallyanpur | 139 | 06:00 | 131 | 12:00 | Sonargaon | 135 | 05:00 | 129 | 12:00
Kalurghat | 140 | 03:00 | 135 | 13:00 | Sreemongol | 137 | 02:00 | 133 | 11:00
Kamrangirchar | 137 | 05:00 | 130 | 13:00 | Sreepur | 135 | 03:00 | 128 | 17:00
Kaptai | 137 | 5:00 | 131 | 12:00 | Srinagar | 138 | 03:00 | 130 | 13:00
Kasba | 136 | 04:00 | 130 | 13:00 | SSM | 141 | 23:00 | 140 | 00:00
Kazla | 138 | 04:00 | 130 | 13:00 | Sunamganj | 131 | 05:00 | 128 | 13:00
Keranigonj | 139 | 06:00 | 130 | 13:00 | Sylhet | 134 | 04:00 | 130 | 13:00
Khagrachori | 139 | 04:00 | 133 | 13:00 | Sylhet-132 | 132 | 00:00 | 131 | 11:00
Khulna | 138 | 06:00 | 131 | 13:00 | Tangail | 133 | 03:00 | 126 | 13:00
Khulna(S) | 140 | 03:00 | 133 | 12:00 | Taraganj | 133 | 05:00 | 121 | 18:00
Khulshi | 136 | 04:00 | 122 | 12:00 | Tasnim | 135 | 05:00 | 129 | 12:00
Kishoreganj | 137 | 04:00 | 132 | 13:00 | Thakurgaon | 136 | 04:00 | 125 | 09:00
Kodda | 132 | 01:00 | 124 | 12:00 | TK | 139 | 03:00 | 135 | 16:00
KSRM | 139 | 00:00 | 134 | 12:00 | Tongi | 139 | 04:00 | 134 | 11:00
Kulaura | 138 | 00:00 | 134 | 13:00 | Ullahpara | 137 | 04:00 | 130 | 18:00
Kurigram | 132 | 10:00 | 120 | 18:00 | Ullon | 135 | 03:00 | 127 | 13:00
Kushtia | 137 | 04:00 | 128 | 18:00 | Uttara | 139 | 04:00 | 129 | 14:00
Laksam | 139 | 03:00 | 134 | 13:00 | UttaraNew | 140 | 03:00 | 130 | 12:00
Lakshmipur | 135 | 02:00 | 129 | 13:00 | Zigatola | 139 | 04:00 | 130 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division