## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-11-2025 | during | 27-11-2025 | during | 27-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 336 | 338 | 400.75 | 400.75 | 381 | 381 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 37 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 20 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 27 | 23.5 | 33 | 33 | 33 | 33
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 25 | 52.19 | 52.19 | 52.19 | 52.19
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 60 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 50 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 62 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 430 | 396 | 718 | 718 | 718 | 718 | FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1180 | 1454.5 | 5561.6 | 5530.6 | 4198.18 | 4185.18
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 110 | 180 | 110 | 110 | 110 | 110 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | DP High
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 47 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 48 | 40 | 48 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 11 | 11 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.26 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 5 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 16 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1010 | 1126 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 4 | 0 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 351 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1553.26 | 1865 | 3029.72 | 3027.72 | 2674.5 | 2672.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 196 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 250 | 250 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 230 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 34 | 34 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 15 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 24 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 103 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 45 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 84 | 98 | 160 | 160 | 106 | 106 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 14 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 13 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 15 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 994 | 1039 | 2489.21 | 2419.21 | 2246.51 | 2176.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-11-2025 | during | 27-11-2025 | during | 27-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 66 | 65 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 57 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 33.12 | 0 | 44.07 | 0 | 44.07 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 145.12 | 140 | 359.97 | 314 | 312.47 | 266.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 82 | 82 | 82 | 82
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 158 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 394 | 365 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1036 | 1005 | 1071 | 1071 | 1009 | 1009
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 892 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 41 | 41 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 77 | 0 | 77 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 793 | 1038 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2006 | 2180 | 2388 | 2311 | 2672.1 | 2595.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 303 | 501 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 652 | 920 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1290.5 | 1756 | 1686.32 | 1686.32 | 1553.32 | 1553.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 51.62 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 167 | 176 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.34 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 839.48 | 1175 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.59 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1636.03 | 1765 | 3077.07 | 2910.87 | 2982.29 | 2816.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 54 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 173 | 0 | 178.58 | 0 | 178.58 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 266.7 | 194 | 510.78 | 297 | 496.78 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 10107.61 | 11398.5 | 20173.67 | 19567.72 | 18145.15 | 17557.2
Forecast Scenario (27-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9330 |  | 0 |  | 9330
|  |  |  | 1:00 | 8550 |  | 0 |  | 8550
|  |  |  | 2:00 | 8140 |  | 0 |  | 8140
|  |  |  | 3:00 | 7960 |  | 0 |  | 7960
|  |  |  | 4:00 | 7680 |  | 0 |  | 7680
|  |  |  | 5:00 | 7600 |  | 0 |  | 7600
|  |  |  | 6:00 | 8040 |  | 0 |  | 8040
|  |  |  | 7:00 | 8920 |  | 0 |  | 8920
|  |  |  | 8:00 | 9620 |  | 0 |  | 9620
|  |  |  | 9:00 | 9200 |  | 0 |  | 9200
|  |  |  | 10:00 | 9130 |  | 0 |  | 9130
|  |  |  | 11:00 | 9540 |  | 0 |  | 9540
|  |  |  | 12:00 | 10100 |  | 0 |  | 10100
|  |  |  | 13:00 | 10500 |  | 0 |  | 10500
|  |  |  | 14:00 | 10080 |  | 0 |  | 10080
|  |  |  | 15:00 | 9740 |  | 0 |  | 9740
|  |  |  | 16:00 | 9750 |  | 0 |  | 9750
|  |  |  | 17:00 | 10080 |  | 0 |  | 10080
|  |  |  | 18:00 | 11390 |  | 0 |  | 11390
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 10940 |  | 0 |  | 10940
|  |  |  | 19:30 | 10870 |  | 0 |  | 10870
|  |  |  | 20:00 | 10650 |  | 0 |  | 10650
|  |  |  | 21:00 | 10580 |  | 0 |  | 10580
|  |  |  | 22:00 | 10070 |  | 0 |  | 10070
|  |  |  | 23:00 | 9740 |  | 0 |  | 9740
Probable Maximum Temperature: |  |  | 28.40°C
Probable Maximum Demand at Day Peak: |  |  | 10100.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11390.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11390.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.33 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:55 hrs on 27-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-11-2025 | [28 empty] | Date: | 26-11-2025 | [28 empty] | Date: | 26-11-2025 | [28 empty] | Date: | 26-11-2025 | [28 empty] | Date: | 26-11-2025 | [14 empty] | Date: | 26-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [14 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 25 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 0 | 51 | 0 | 0 | 225 | 0 | 230 | 0 | 209 | 5 | 0 | 109 | 0 | 0 | 20 | 0 | 76 | 0 | 0 | 0 | 305 | 0 | 362 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 35 | 0 | 75 | 0 | 0 | 0 | 4641 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 257 | 850 | 0 | 4689 | 9330 | 99.89
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 5 | 0 | 0 | 225 | 0 | 230 | 0 | 219 | 5 | 0 | 110 | 0 | 0 | 14 | 0 | 74 | 0 | 0 | 0 | 300 | 0 | 367 | 0 | 30 | 0 | 17 | 0 | 5 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 4188 | 866 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 113 | 0 | 257 | 650 | 0 | 4365 | 8553 | 99.89
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 5 | 0 | 0 | 225 | 0 | 230 | 0 | 221 | 5 | 0 | 110 | 0 | 0 | 11 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 302 | 0 | 30 | 0 | 8 | 0 | 5 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 3876 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 129 | 0 | 258 | 540 | 0 | 4268 | 8144 | 99.89
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 0 | 225 | 0 | 230 | 0 | 172 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 68 | 0 | 0 | 0 | 310 | 0 | 304 | 0 | 30 | 0 | 0 | 0 | 2 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 3742 | 884 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 169 | 0 | 259 | 502 | 0 | 4225 | 7967 | 99.89
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 0 | 140 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 304 | 0 | 30 | 0 | 0 | 0 | 2 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 3573 | 732 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 220 | 0 | 258 | 504 | 0 | 4113 | 7686 | 99.89
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 220 | 0 | 230 | 0 | 201 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 304 | 0 | 30 | 0 | 0 | 0 | 2 | 20 | 0 | 15 | 157 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 3536 | 732 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 258 | 500 | 0 | 4071 | 7607 | 99.89
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 18 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 0 | 300 | 0 | 230 | 0 | 208 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 72 | 0 | 0 | 0 | 315 | 0 | 340 | 0 | 30 | 0 | 17 | 0 | 64 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 3957 | 580 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 256 | 502 | 0 | 4091 | 8048 | 99.89
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 2 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 4 | 0 | 0 | 0 | 0 | 0 | 0.48 | 46 | 0 | 27 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 3 | 35 | 0 | 0 | 350 | 0 | 290 | 0 | 211 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 72 | 0 | 7 | 0 | 305 | 0 | 359 | 0 | 30 | 0 | 17 | 0 | 81 | 0 | 0 | 15 | 157 | 0 | 32 | 19 | 85 | 0 | 2.36 | 0 | 4665.84 | 581 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 800 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 5 | 0 | 0 | 2.55 | 165 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0.22 | 0 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 10 | 0.32 | 0 | 0 | 115 | 220 | 0 | 257 | 570 | 0 | 4254.01 | 8919.85 | 99.89
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 10 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 3 | 0 | 0 | 0 | 0 | 0 | 1.24 | 46 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 9 | 43 | 0 | 0 | 305 | 0 | 300 | 0 | 203 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 80 | 0 | 32 | 0 | 310 | 0 | 387 | 0 | 30 | 0 | 8 | 0 | 81 | 0 | 0 | 15 | 157 | 0 | 57 | 19 | 85 | 1 | 14.55 | 0 | 4850.79 | 736 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 833 | 0 | 831.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.39 | 27 | 0 | 0 | 14.74 | 165 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 1.57 | 0 | 55 | 0 | 10 | 6 | 0 | 0 | 0 | 1.6 | 58 | 0.13 | 0 | 0 | 115 | 220 | 0 | 259 | 750 | 0 | 4773.3 | 9624.09 | 99.89
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 18 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 2.21 | 46 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 15 | 43 | 0 | 0 | 220 | 0 | 255 | 0 | 140 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 84 | 0 | 51 | 0 | 300 | 0 | 322 | 0 | 30 | 0 | 17 | 0 | 22 | 30 | 0 | 15 | 158 | 0 | 35 | 19 | 73 | 1 | 29.26 | 1 | 4404.47 | 751 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 780 | 0 | 808.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.37 | 56 | 0 | 0 | 37.86 | 156 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 2.97 | 0 | 56 | 0 | 18 | 0 | 0 | 0 | 0 | 3.3 | 106 | 0.26 | 0 | 0 | 115 | 180 | 0 | 259 | 794 | 0 | 4796.65 | 9201.12 | 99.88
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 25 | 0 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 46 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 18 | 5 | 0 | 0 | 250 | 0 | 220 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 86 | 0 | 64 | 0 | 310 | 0 | 345 | 0 | 30 | 0 | 17 | 0 | 22 | 20 | 0 | 15 | 158 | 0 | 8 | 8 | 70 | 2 | 38.51 | 8 | 4352.87 | 750 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 768 | 0 | 808.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.03 | 81 | 0 | 0 | 50.7 | 156 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 4.3 | 0 | 55 | 0 | 27 | 0 | 0 | 0 | 0 | 4.6 | 144 | 0.4 | 0 | 0 | 115 | 180 | 0 | 251 | 650 | 0 | 4777.99 | 9130.86 | 99.88
11:00 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 28 | 0 | 28 | 5 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 3.22 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 895 | 19 | 5 | 0 | 0 | 250 | 0 | 220 | 0 | 190 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 69 | 0 | 315 | 0 | 396 | 0 | 30 | 0 | 17 | 0 | 55 | 20 | 0 | 15 | 158 | 0 | 8 | 8 | 68 | 2 | 43.45 | 12 | 4600.67 | 883 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 775 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.24 | 96 | 0 | 0 | 59.93 | 163 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 4.95 | 0 | 54 | 0 | 32 | 0 | 0 | 0 | 0 | 5.4 | 164 | 0.51 | 0 | 0 | 115 | 180 | 0 | 278 | 560 | 0 | 4943.03 | 9543.7 | 99.88
12:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 23 | 0 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 3.26 | 46 | 0 | 11 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 19 | 15 | 0 | 0 | 250 | 0 | 250 | 0 | 208 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 84 | 0 | 71 | 0 | 310 | 0 | 394 | 0 | 30 | 0 | 17 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 24 | 8 | 66 | 2 | 33.12 | 12 | 4908.38 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 793 | 0 | 839.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.62 | 100 | 0 | 0 | 58.59 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.34 | 0 | 54 | 0 | 34 | 0 | 0 | 0 | 0 | 5.7 | 173 | 0.5 | 0 | 0 | 115 | 220 | 0 | 303 | 652 | 0 | 5199.23 | 10107.61 | 99.88
13:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 23 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 19 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1135 | 18 | 35 | 0 | 0 | 250 | 0 | 250 | 0 | 200 | 0 | 0 | 100 | 0 | 0 | 14 | 0 | 102 | 0 | 66 | 0 | 315 | 0 | 393 | 0 | 30 | 0 | 17 | 0 | 80 | 30 | 0 | 16 | 158 | 0 | 24 | 8 | 66 | 2 | 42.89 | 10 | 5057.89 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 920 | 0 | 838.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.19 | 91 | 0 | 0 | 52.21 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.56 | 0 | 53 | 0 | 30 | 0 | 0 | 0 | 0 | 5.4 | 162 | 0.53 | 0 | 0 | 115 | 220 | 0 | 303 | 788 | 0 | 5442.17 | 10500.06 | 99.88
14:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 22 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 140 | 2 | 0 | 0 | 0 | 0 | 0 | 2.42 | 46 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 16 | 51 | 0 | 0 | 250 | 0 | 250 | 0 | 196 | 0 | 0 | 100 | 0 | 0 | 14 | 0 | 98 | 0 | 56 | 0 | 305 | 0 | 344 | 0 | 30 | 0 | 17 | 0 | 80 | 30 | 0 | 16 | 158 | 0 | 16 | 8 | 66 | 2 | 37.67 | 0 | 4954.09 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 858 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.72 | 74 | 0 | 0 | 45.22 | 162 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 3.78 | 0 | 55 | 0 | 23 | 0 | 0 | 0 | 0 | 4.5 | 132 | 0.43 | 0 | 0 | 115 | 180 | 0 | 305 | 750 | 0 | 5127.65 | 10081.74 | 99.88
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 14 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 1 | 0 | 0 | 0 | 0 | 0 | 1.62 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1072 | 12 | 51 | 0 | 0 | 250 | 0 | 250 | 0 | 191 | 0 | 0 | 100 | 0 | 0 | 14 | 0 | 88 | 0 | 40 | 0 | 305 | 0 | 325 | 0 | 30 | 0 | 20 | 0 | 77 | 30 | 0 | 15 | 158 | 0 | 8 | 8 | 61 | 1 | 25.9 | 0 | 4796.52 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 828 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.44 | 50 | 0 | 0 | 30.05 | 158 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 2.49 | 0 | 54 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 81 | 0.29 | 0 | 0 | 115 | 180 | 0 | 304 | 736 | 0 | 4944.27 | 9740.79 | 99.88
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 6 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 180 | 1 | 0 | 0 | 0 | 0 | 0 | 0.76 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 0 | 51 | 0 | 0 | 245 | 0 | 250 | 0 | 190 | 0 | 0 | 100 | 0 | 0 | 14 | 0 | 92 | 0 | 19 | 0 | 310 | 0 | 379 | 0 | 30 | 0 | 22 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 28 | 19 | 60 | 0 | 9.69 | 0 | 4839.45 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 812 | 0 | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.43 | 20 | 0 | 0 | 9.47 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.7 | 0 | 54 | 0 | 7 | 0 | 0 | 0 | 0 | 1.3 | 26 | 0.11 | 0 | 0 | 115 | 220 | 0 | 312 | 750 | 0 | 4916.01 | 9755.46 | 99.88
17:00 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 394 | 11.8 | 9 | 26 | 0 | 15 | 0 | 1 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 17 | 25 | 22 | 0 | 0 | 8 | 0 | 0 | 180 | 1 | 0 | 0 | 0 | 8 | 10 | 0 | 46 | 4 | 15 | 354 | 0 | 0 | 7 | 0 | 10 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 13 | 0 | 240 | 0 | 250 | 0 | 184 | 0 | 8 | 102 | 9 | 0 | 14 | 0 | 96 | 0 | 1 | 0 | 305 | 0 | 370 | 0 | 30 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 57 | 19 | 65 | 0 | 0.21 | 0 | 5149.01 | 891 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | 803 | 0 | 878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 1 | 0 | 0 | 0.51 | 175 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0.05 | 0 | 54 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 0 | 115 | 220 | 0 | 311 | 790 | 0 | 4935.11 | 10084.12 | 99.88
18:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 396 | 37 | 17 | 50 | 0 | 60 | 0 | 20 | 62 | 0 | 0 | 0 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 17 | 23.5 | 22 | 0 | 0 | 15 | 5 | 0 | 180 | 0 | 0 | 0 | 0 | 12 | 38 | 0 | 46 | 16 | 11 | 351 | 0 | 0 | 18 | 0 | 47 | 0 | 0 | 0 | 0 | 1126 | 0 | 51 | 24 | 0 | 230 | 0 | 250 | 0 | 196 | 0 | 15 | 103 | 45 | 13 | 14 | 0 | 98 | 0 | 0 | 0 | 305 | 0 | 365 | 0 | 30 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 18 | 65 | 0 | 0 | 0 | 5503.5 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 0 | 1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 920 | 0 | 5895 | 11398.5 | 99.88
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 392 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 24.5 | 22 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 12 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1147 | 0 | 51 | 0 | 0 | 230 | 0 | 250 | 0 | 195 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 86 | 0 | 0 | 0 | 310 | 0 | 340 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 65 | 0 | 0 | 0 | 4957.5 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 55 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 433 | 1060 | 0 | 5989 | 10946.5 | 99.87
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 24.5 | 22 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 17 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 0 | 51 | 0 | 0 | 230 | 0 | 250 | 0 | 190 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 86 | 0 | 0 | 0 | 310 | 0 | 342 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 65 | 0 | 0 | 0 | 4961.5 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 1193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 55 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 406 | 1076 | 0 | 5910 | 10871.5 | 99.87
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 23 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1164 | 0 | 51 | 0 | 0 | 225 | 0 | 250 | 0 | 185 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 343 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 66 | 0 | 0 | 0 | 4949 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 309 | 1078 | 0 | 5710 | 10659 | 99.87
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 27 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1164 | 0 | 51 | 0 | 0 | 225 | 0 | 250 | 0 | 188 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 90 | 0 | 0 | 0 | 300 | 0 | 342 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 24 | 18 | 69 | 0 | 0 | 0 | 4912 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1114.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 309 | 1080 | 0 | 5674.34 | 10586.34 | 99.87
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 29 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 51 | 0 | 0 | 225 | 0 | 250 | 0 | 190 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 330 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 24 | 18 | 66 | 0 | 0 | 0 | 4730 | 891 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 1078.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 309 | 1000 | 0 | 5343.92 | 10073.92 | 99.87
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 0 | 225 | 0 | 250 | 0 | 190 | 0 | 0 | 106 | 0 | 0 | 19 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 341 | 0 | 30 | 0 | 22 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 24 | 18 | 64 | 0 | 0 | 0 | 4643 | 892 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 984 | 0 | 949.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 309 | 950 | 0 | 5185.06 | 9828.06 | 99.87
Total KWH | 0 | 30720 | 110400 | 0 | 0 | 0 | 0 | 0 | 8175600 | 0 | 10005900 | 73440 | 37440 | 165168 | 0 | 83804 | 0 | 50668 | 141120 | 0 | 0 | 0 | 0 | 0 | 42810 | 7406421 | 0 | 0 | 176568 | 38400 | 451200 | 507600 | 0 | 0 | 27600 | 10036 | 0 | 3200000 | 17280 | 0 | 0 | 0 | 18240 | 45120 | 21000 | 999180 | 30900 | 352800 | 8080000 | 0 | 0 | 35040 | 0 | 85309 | 0 | 0 | 0 | 0 | 22319998 | 132435 | 877752 | 51854 | 0 | 5919500 | 0 | 5960000 | 0 | 4647000 | 16344 | 33600 | 2333659 | 76800 | 24360 | 336060 | 0 | 2005440 | 0 | 477982 | 0 | 7460500 | 0 | 8538000 | 0 | 726240 | 161836 | 375168 | 0 | 1381440 | 552768 | 0 | 368000 | 3314260 | 0 | 602400 | 266400 | 1687680 | 12850 | 289630 | 50400 | 111420120 | 20125818 | 6197760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443520 | 20640001 | 0 | 21721179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324748 | 616950 | 0 | 0 | 366000 | 3868182 | 0 | 0 | 0 | 0 | 0 | 8785163 | 0 | 30780 | 0 | 1264581 | 210373 | 201023 | 189273 | 0 | 0 | 0 | 35140.08 | 1054800 | 3214 | 0 | 0 | 2667000 | 4915220 | 0 | 7181064 | 18789818.18 | 0 | 119631607.26 | 231051727.26

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10107.61 | MW | 12:00 Hr. | Energy Generated |  |  | 231.0517 |  | MKWHr.
| Day Peak Demand |  |  | 10107.61 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11398.5 | MW | 18:00 Hr. | Energy Demand |  |  | 231.0517 |  | MKWHr.
| Evening Peak Demand |  |  | 11398.5 | MW | 18:00 Hr. | Maximum Temperature |  |  | 28 |  | °C
| Minimum Generation of the Day |  |  | 7607 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 763.9 |  | MMCFD
| Maximum Generation of the Day |  |  | 11398.5 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.2962 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.5467 | 0 | 0.77397 | 0 | 0 | 0.17657 | 0 | 0 | 27.4973 | Gas | 101.1891 | Gas | 362739574.37
| Chattogram Zone |  |  | 3.5528 | 30.4 | 0.25224 | 0 | 0.99918 | 0.15343 | 0 | 0.01728 | 35.3749 | Coal | 78.2755 | Coal | 492718090.3614
| Cumilla Zone |  |  | 20.0903 | 0 | 0.18661 | 0 | 0 | 0.47798 | 2.0054 | 0 | 22.7604 | HFO | 2.5317 | HFO | 43414956.5
| Mymensingh Zone |  |  | 1.6877 | 0 | 0.9192 | 0 | 0 | 0.30248 | 0 | 0 | 2.9094 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 22.8782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8782 | Hydro | 0.99918 | Hydro | 99918
| Khulna Zone |  |  | 6.1978 | 20.64 | 0 | 0 | 0 | 0.44352 | 20.1258 | 0 | 47.4071 | Solar | 4.1866 | Solar | 66893286.6968
| Barishal Zone |  |  | 7.5822 | 25.9709 | 0 | 0 | 0 | 0.003214 | 0 | 0 | 33.5563 | Import | 43.8524 | Import | 257569913.19
| Rajshahi Zone |  |  | 12.6533 | 0 | 0 | 0 | 0 | 1.3385 | 21.7212 | 0 | 35.713 | Wind | 0.01728 | Wind | 254188.8
| Rangpur Zone |  |  | 0 | 1.2646 | 0.39965 | 0 | 0 | 1.291 | 0 | 0 | 2.9552
| Total |  |  | 101.1891 | 78.2755 | 2.5317 | 0 | 0.99918 | 4.1866 | 43.8524 | 0.01728 | 231.0517
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 362739574.37 |  | Hydro | 99918
|  |  |  | Coal | 492718090.3614 |  | Solar | 66893286.6968
|  |  |  | HFO | 43414956.5 |  | Import | 257569913.19
|  |  |  | HSD | 0 |  | Wind | 254188.8
[5 empty] | Total: | 122,36,89,927 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.1258 | Peak Hr Flow | 892.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47629800.02 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.7212 | Peak Hr Flow | 1175.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2513 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.0054 | Peak Hr Flow | 98.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2772 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.8524 | Peak Hr Flow | 2165.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4262
|  |  |  | Chattogram |  | 0 |  | 1280
|  |  |  | Cumilla |  | 0 |  | 934
|  |  |  | Mymensingh |  | 0 |  | 886
|  |  |  | Sylhet |  | 0 |  | 414
|  |  |  | Khulna |  | 0 |  | 1245
|  |  |  | Barishal |  | 0 |  | 307
|  |  |  | Rajshahi |  | 0 |  | 1004
|  |  |  | Rangpur |  | 0 |  | 756
|  |  |  | Total |  | 0 |  | 11088
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 16:39 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to
Annual maintenance work
| 08:05 | 16:40 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
Annual maintenance work
| 08:05 | 16:58 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to
Annual maintenance work
| 08:13 | 16:48 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Annual Maintenance
| 08:13 | 16:49 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Annual Maintenance
| 08:16 | 16:55 | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
| 08:18 | 16:55 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-02 Scheduled S/D Due to Annual maintenance
| 08:29 | 15:27 | Bogura(New)-Naogaon 132 kV Ckt-2 Scheduled S/D from Naogaon 132/33kV end Due to Annual
maintenance and from Bogura 230/132kVend.
| 08:30 | 16:55 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Annual Maintenance
| 08:33 | 16:12 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) LT Scheduled S/D
| 08:33 | 16:23 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. and from
Khulna (C) end Due to for loop change
| 08:34 | 16:11 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) HT Scheduled S/D
| 08:36 | 16:37 | Bibiana 400/230kV S/S ICT-02 HT Scheduled S/D Due to AM
| 08:36 | 16:37 | Bibiana 400/230kV S/S ICT-02 LT Scheduled S/D Due to AM
| 08:36 | 16:01 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to Kulaura -
Fenchuganj circuit 2 for Annual maintenance and from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 08:40 | 10:36 | Aminbazar-Manikgonj PP 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing REL | [7 empty] | 73.0MW load interrup
|  |  | 316*4 relays Due to General Trip Distance Trip O/L Relay SOTF | [7 empty] | Aminbazar 400/230/132kV end
| 08:40 | 09:10 | Aminbazar-Manikgonj PP 132kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing | [7 empty] | 73.0MW load interrup
|  |  | REL316*4 relays Due to General Trip Distance Trip SOFT | [7 empty] | Aminbazar 400/230/132kV end
| 08:41 | 17:24 | Baghabari 230/132kV S/S T-2 Bank HT Scheduled S/D Due to Annual Maintenance
| 08:43 | 16:30 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to
Annual maintenance and from Gopalganj 400/132kVend.
| 08:45 | 14:56 | Aftabnagar-Rampura 132kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to Annual Maintenance
| 08:51 | 19:53 | Khulshi-MSML 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Annual
Maintenance of 132kV Khulshi-Bakalia ckt-02
| 08:52 | 19:51 | Bakulia-MSML 132 kV Ckt-2 Scheduled S/D from Bakulia 132/33kV end.
| 08:54 | 14:30 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Scheduled S/D Due to Annual Maintenance
| 08:54 | 16:18 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
maintenance on Mirpur - Uttara old ckt bay equipment.
| 08:54 | 14:31 | Jashore 132/33kV S/S JH-2(L1) Scheduled S/D Due to Annual Maintanace
| 09:04 | 15:13 | Bheramara 230/132kV S/S Transformer-1 HT Scheduled S/D Due to AM
| 09:05 | 15:16 | Bheramara 230/132kV S/S Transformer-1 LT Scheduled S/D Due to AM
| 09:08 | 16:33 | Kallyanpur 132/33kV S/S Main bus Scheduled S/D
| 09:15 | 16:24 | Brahmanbaria 132/33kV S/S 401T LT Scheduled S/D
| 09:15 | 16:24 | Brahmanbaria 132/33kV S/S 401T HT Scheduled S/D
| 09:33 | 17:30 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 09:35 | 14:40 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Annual maintenance
| 09:40 | 14:55 | Daudkandi 132/33kV S/S Transformer-1 HT Scheduled S/D Due to SPMD Yearly Maintenance Work.
| 09:40 | 14:57 | Daudkandi 132/33kV S/S Transformer-1 LT Scheduled S/D Due to SPMD Yearly Maintenance Work
| 09:44 | 15:39 | BIPTC S/S 10CF11 Scheduled S/D Due to Shutdown is taken for annual maintenance work
| 09:45 | 13:12 | Bogura 400/230kV S/S ATR-01 HT Scheduled S/D Due to FDS System Aux. contact check (Annual Maintenance)
| 09:45 | 13:13 | Bogura 400/230kV S/S ATR-01 LT Scheduled S/D Due to Annual Maintenance
| 09:48 | 16:24 | Hathazari 230/132/33kV S/S MT-01 LT Scheduled S/D Due to Annual Maintenance
| 09:49 | 16:25 | Hathazari 230/132/33kV S/S MT-01 HT Scheduled S/D Due to Annual Maintenance
| 09:55 |  | Bropukuria - P.Sadipur 230kv Ckt 02-S/D.
| 09:58 |  | Bropukuria - P.Sadipur 230kv Ckt 01-S/D.
| 10:03 | 15:46 | Gopalganj 400/132kV S/S 230kV Barisal CKT-01 Scheduled S/D
| 10:14 | 13:56 | Amnura 132/33kV S/S T-1 (406T) HT Forced S/D Due to Winding Temperature High trip
| 10:14 | 13:59 | Amnura 132/33kV S/S T-1 (406T) LT Forced S/D Due to Winding Temperature High Trip
| 10:15 | 17:01 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to Annual Maintenance
| 10:15 | 17:01 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to Annual Maintenance
| 10:43 | 11:49 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Project Work S/D Due to Semeins Work | [7 empty] | 15.0MW load interrup.
| 10:43 | 11:48 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Project Work S/D Due to Semeins Work | [7 empty] | 15.0MW load interrup.
| 11:03 | 15:45 | Barishal 230/132kV S/S Gopalgonj CKT-1 Scheduled S/D Due to Maintenance
| 11:17 | 11:21 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Tap Change
| 11:28 | 12:50 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Tap Change
| 11:50 | 12:30 | Kaliakoir 400/230/132kV S/S 230kV Bus 2 Scheduled S/D Due to To open 230/132kV HT side
DS which is connected with 230kV Bus 2. DS is mechanically locked
| 12:00 |  | Day Peak Generation: 10104 MW.
| 12:02 | 12:21 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Project Work S/D Due to project work | [7 empty] | 10.0MW load interrup.
| 12:03 | 12:20 | Mirzapur 132/33kV S/S Transformer-02(E07) HT Project Work S/D Due to project work | [7 empty] | 10.0MW load interrup.
| 12:08 |  | Muradnagar 132/33kV S/S 132KV Transformar-02 HT Project Work S/D Due to SCADA INTEGRATION
|  | 12:44 | Jamalpur 132/33kV S/S T-3 HT is restored.
|  | 12:44 | Jamalpur 132/33kV S/S T-3 LT is restored.
| 13:59 | 17:49 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to Annual Maintenance
| 14:00 | 17:48 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to Annual Maintenance
| 15:33 | 17:26 | Daudkandi 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Relay Testing By SPMD , Cumilla
| 15:34 | 17:25 | Daudkandi 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Relay Testing By SPMD , Cumilla
|  | 16:30 | Bhulta-Rampura 230 kV Ckt-4 is restored.
|  | 17:18 | Natore-Rajshahi 132kV Ckt-1 is restored.
|  | 17:27 | Magura 132/33kV S/S T-3 (425T) HT is restored.
| 17:38 | 19:39 | Baghabari 230/132kV S/S T-2 Bank LT Forced S/D Due to T2 X-Former CVT R-Phase এর Top
Cover এ Red Hot দেখা দিলে Emergency S/D নেওয়া হয়।
| 17:38 | 19:39 | Baghabari 230/132kV S/S T-2 Bank HT Forced S/D Due to T2 X-Former CVT R-Phase এর Top
Cover এ Red Hot দেখা দিলে Emergency S/D নেওয়া হয়।
| 18:00 |  | Evening Peak Generation is 11398 MW.
|  | 18:50 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 18:51 | Barishal 230/132kV S/S T-4 LT is restored.
| 19:13 |  | Rupsha 800 MW CCPP (NWPGCL) GT-1 was synchronized at 19:13 hrs for the first time, and
tripped at 19:39 hrs.
| 01:05 |  | Ghorashal 230kV S/S TARFO-2 HT Scheduled S/D Due to Annual maintenace | [7 empty] | 45.0MW load
interrup.
| 04:59 |  | Bheramara 230/132kV S/S Transformer-2 LT Tripped showing differential relays Due to R
phase Connecting insulation kit Fire
| 06:58 |  | Chhatak 132/33kV S/S T-3 LT Scheduled S/D Due to Annual Maintanance
| 06:58 |  | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintanance
| 07:31 |  | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
maintenance(Bay-Equipment)
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 338 | 8175600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | CCPP S/D for minor inspection (schedule outage)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7406421 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 37 | 73440 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 20 | 50668 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 42810 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23.5 | 451200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 507600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 110400 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 60 | 83804 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 50 | 165168 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 30720 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 62 | 141120 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 176568 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 37440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 396 | 10005900 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 38400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 1454.5 | 27497259
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 180 | 3200000 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132435 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 35040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 999180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | DP High
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 47 | 85309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 18240 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 352800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 5 | 10036 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 16 | 30900 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 45120 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 27600 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1126 | 22319998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 17280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 351 | 8080000 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1865 | 35374938
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 196 | 4647000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 250 | 5960000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 5919500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 16344 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 877752 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 24 | 51854 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2333659 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 45 | 76800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 98 | 2005440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 336060 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 13 | 24360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 15 | 33600 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 477982 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1039 | 22760351
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 65 | 1687680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 266400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 602400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 289630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 50400 | Dispatch 0 MW, due to instability of phase voltage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 140 | 2909360
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 726240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 161836 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 552768 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1381440 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3314260 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 368000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 375168 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7460500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8538000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1005 | 22878212
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 20125818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6197760 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 443520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1038 | 20640001 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2180 | 47407099
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 501 | 7181064 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2667000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 920 | 18789818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 4915220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3214 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1756 | 33556316.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 324748 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 176 | 3868182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8785163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30780 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1175 | 21721179 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 366000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 616950 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1765 | 35713002
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1264581 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 189273 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35140.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 210373 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201023 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1054800 | -
Rangpur Area Total |  |  |  |  | 950 | 194 | 2955190.08
Eastern Grid Total |  |  |  |  | 17383.855 | 5503.5 | 111420120
Western Grid Total |  |  |  |  | 10821.56 | 5895 | 119631607.26
National Grid Total |  |  |  |  | 28205.415 | 11398.5 | 231051727.26
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7775.79 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3312.2 | MW
i) Dhaka area |  |  | 4261.99 |  | MW | i) Khulna area |  |  |  | 1245 | MW
ii) Chattogram area |  |  | 1279.8 |  | MW | ii) Barishal area |  |  |  | 307 | MW
iii) Cumilla area |  |  | 934 |  | MW | iii) Rajshahi area |  |  |  | 1004.2 | MW
iv) Mymensingh area |  |  | 886 |  | MW | iv) Rangpur area |  |  |  | 756 | MW
v) Sylhet area |  |  | 414 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11087.99 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 12:00 | 67 | Hathazari | 60 | 18:00 | 133 | Niamatpur | 42 | 18:00
2 | AKSML | 139 | 00:00 | 68 | Ishurdi | 57 | 18:00 | 134 | Noapara | 43 | 18:00
3 | Aftabnagar | 28 | 12:00 | 69 | Jaldhaka | 60 | 18:30 | 135 | PHP | 8 | 02:00
4 | Agargaon | 89 | 14:00 | 70 | Jamalpur | 92 | 18:00 | 136 | Pabna | 63 | 20:00
5 | Agrabad | 64 | 18:00 | 71 | Jashore | 95 | 13:00 | 137 | Palashbari | 82 | 18:00
6 | Amnura | 20 | 19:00 | 72 | Jhenaidah | 94 | 18:00 | 138 | Panchagarh | 41 | 18:00
7 | Ashuganj | 59 | 13:00 | 73 | Joydebpur | 119 | 12:00 | 139 | Patiya | 6.8 | 18:00
8 | BSRM | 202 | 20:00 | 74 | Joypurhat | 47 | 18:00 | 140 | Patuakhali | 42 | 21:00
9 | Bagerhat | 61 | 18:00 | 75 | Juldah | 14 | 08:00 | 141 | Payra | 24 | 18:30
10 | Bajitpur | 56 | 18:30 | 76 | KSRM | 31 | 12:00 | 142 | Postogola | 49 | 12:00
11 | Bakulia | 63 | 18:00 | 77 | Kabirpur | 192 | 18:00 | 143 | Purbachal | 29 | 13:00
12 | Banani | 32.2 | 14:00 | 78 | Kachua | 55 | 20:00 | 144 | Purbasadipur | 102 | 18:00
13 | Bangabhaban | 16 | 15:00 | 79 | Kallyanpur | 75 | 13:00 | 145 | Rahanpur | 16 | 00:00
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 40 | 15:00 | 146 | Rahim | 36 | 16:00
15 | Barguna | 14 | 18:30 | 81 | Kamrangirchar | 65 | 13:00 | 147 | Rajbari | 57 | 18:00
16 | Barishal | 89 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 110 | 18:00
17 | Barishal-230 | 64 | 20:00 | 83 | Kasba | 22 | 18:00 | 149 | Rajshahi | 65 | 18:00
18 | Baroaulia | 56 | 17:00 | 84 | Kazla | 92 | 13:00 | 150 | Rajshahi-230 | 66 | 13:00
19 | Baroirhat | 48 | 18:00 | 85 | Keranigonj | 64 | 13:00 | 151 | Ramganj | 62 | 18:30
20 | Bashundhara | 125 | 13:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 31 | 18:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 52 | 18:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 152 | 14:00 | 154 | Rangpur | 104 | 18:00
23 | Benapole | 40 | 07:00 | 89 | Kishoreganj | 90 | 18:00 | 155 | Ruppur | 3.2 | 16:00
24 | Bhaluka | 124 | 18:00 | 90 | Kodda | 233 | 18:00 | 156 | SSM | 12 | 07:00
25 | Bhandaria | 37 | 21:00 | 91 | Kulaura | 30 | 18:00 | 157 | Saidpur | 96 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 48 | 08:00 | 158 | Satkhira | 86 | 18:30
27 | Bheramara(GK) | 42 | 18:00 | 93 | Kushtia | 110 | 18:00 | 159 | Satmasjid | 75 | 13:00
28 | Bhulta | 180 | 07:00 | 94 | Laksam | 22 | 01:00 | 160 | Savar | 170 | 17:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 24 | 21:00 | 161 | SevenRings | 16.55 | 00:00
30 | Bogura | 122 | 19:00 | 96 | Lalbag | 64 | 13:00 | 162 | ShahCement | 23 | 23:00
31 | Borhanuddin | 63 | 21:00 | 97 | Lalmonirhat | 44 | 18:00 | 163 | Shahjadpur | 59 | 18:00
32 | Brahmanbaria | 86 | 18:00 | 98 | MI_Cement | 15.8 | 00:00 | 164 | Shahjibazar | 77 | 18:00
33 | Cantonment | 100 | 13:00 | 99 | Madanganj | 37 | 21:00 | 165 | Shahmirpur | 41 | 18:30
34 | Chandina | 11 | 18:00 | 100 | Madaripur | 68 | 18:00 | 166 | Shariatpur | 54 | 20:00
35 | Chandpur | 50 | 19:30 | 101 | Madartek | 66 | 18:00 | 167 | Sherpur | 108 | 18:00
36 | Chandraghona | 26 | 18:30 | 102 | Madunaghat | 37 | 17:00 | 168 | Shikalbaha | 24 | 11:00
37 | Chapai | 43 | 12:00 | 103 | Magura | 49 | 18:00 | 169 | Shitalakhya | 64 | 11:00
38 | Charsaidpur | 36 | 00:00 | 104 | Mahasthangarh | 52 | 18:00 | 170 | Sholosohor | 35 | 18:00
39 | Chauddagram | 45 | 19:30 | 105 | Maijdee | 13 | 18:00 | 171 | Shyampur | 136 | 11:00
40 | Chhatak | 23 | 18:30 | 106 | Manikganj | 95 | 18:30 | 172 | Siddhirganj | 94 | 16:00
41 | Chowmuhani | 116 | 18:00 | 107 | Maniknagar | 48 | 13:00 | 173 | Sirajganj | 84 | 18:00
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 35 | 18:00 | 174 | Sonargaon | 128 | 18:30
43 | Coxsbazar | 100 | 18:00 | 109 | Matuail | 59 | 17:00 | 175 | Sreemongol | 61 | 17:00
44 | Cumilla(N) | 85 | 18:30 | 110 | Metrorail_Motijheel | 19 | 17:00 | 176 | Sreepur | 75 | 18:30
45 | Cumilla(S) | 125 | 14:00 | 111 | Metrorail_Uttara | 8 | 10:00 | 177 | Srinagar | 30.5 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 92 | 12:00 | 178 | Sunamganj | 37 | 18:00
47 | Daudkandi | 112 | 21:00 | 113 | Mirpur | 121 | 18:00 | 179 | Sylhet | 36 | 18:00
48 | DhakaUniversity | 66 | 13:00 | 114 | Mirsorai | 19 | 18:00 | 180 | Sylhet-132 | 88 | 18:00
49 | Dhamrai | 106 | 18:00 | 115 | Mirzapur | 35 | 18:00 | 181 | TK | 18 | 22:00
50 | Dhanmondi | 94.5 | 13:00 | 116 | Mithapukur | 45 | 18:00 | 182 | Tangail | 120 | 18:30
51 | Dohazari | 71 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 14 | 08:00
52 | Faridpur | 115 | 18:00 | 118 | Mogbazar | 73.8 | 14:00 | 184 | Tasnim | 18 | 07:00
53 | Fatullah | 100 | 15:00 | 119 | Mongla | 27 | 12:00 | 185 | Thakurgaon | 79 | 18:00
54 | Fenchuganj | 24 | 19:00 | 120 | Motijheel | 29 | 13:00 | 186 | Tongi | 92 | 15:00
55 | Feni | 70 | 18:00 | 121 | Muktagacha | 25 | 08:00 | 187 | Ullahpara | 26 | 18:00
56 | GPH | 90 | 17:00 | 122 | Munshiganj | 72 | 21:00 | 188 | Ullon | 46 | 13:00
57 | Ghatail | 60 | 18:00 | 123 | Muradnagar | 20 | 00:00 | 189 | Uttara | 59 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 139 | 18:00 | 190 | UttaraNew | 28 | 13:00
59 | Ghorashal-230 | 73 | 00:00 | 125 | Naogaon | 83 | 18:00 | 191 | Zigatola | 54 | 13:00
60 | Goalpara | 30 | 13:00 | 126 | Narail | 41 | 18:00
61 | Gollamari | 78 | 13:00 | 127 | Narinda | 52 | 13:00
62 | Gopalganj | 74 | 18:00 | 128 | Narshingdi | 144 | 19:30
63 | Gulshan | 88 | 13:00 | 129 | Natore | 98 | 18:00
64 | Halishahar | 55.5 | 15:00 | 130 | Nawabganj | 29.2 | 21:00
65 | HaripurSBU | 132 | 00:00 | 131 | Netrakona | 100 | 18:00
66 | Hasnabad | 77 | 14:00 | 132 | New | 62 | 17:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9330 | 0 |  | 9330
1:00 | 8553 | 0 |  | 8553
2:00 | 8144 | 0 |  | 8144
3:00 | 7967 | 0 |  | 7967
4:00 | 7686 | 0 |  | 7686
5:00 | 7607 | 0 |  | 7607
6:00 | 8048 | 0 |  | 8048
7:00 | 8919.85 | 0 |  | 8919.85
8:00 | 9624.09 | 0 |  | 9624.09
9:00 | 9201.12 | 0 |  | 9201.12
10:00 | 9130.86 | 0 |  | 9130.86
11:00 | 9543.7 | 0 |  | 9543.7
12:00 | 10107.61 | 0 |  | 10107.61
13:00 | 10500.06 | 0 |  | 10500.06
14:00 | 10081.74 | 0 |  | 10081.74
15:00 | 9740.79 | 0 |  | 9740.79
16:00 | 9755.46 | 0 |  | 9755.46
17:00 | 10084.12 | 0 |  | 10084.12
18:00 | 11398.5 | 0 |  | 11398.5
19:00 | 10946.5 | 0 |  | 10946.5
19:30 | 10871.5 | 0 |  | 10871.5
20:00 | 10659 | 0 |  | 10659
21:00 | 10586.34 | 0 |  | 10586.34
22:00 | 10073.92 | 0 |  | 10073.92
23:00 | 9828.06 | 0 |  | 9828.06
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4641 | 4689 | 9330 | DAILY GENERATION CURVE
00:30 | 4414.5 | 4527 | 8941.5
01:00 | 4188 | 4365 | 8553 | 26-11-2025
01:30 | 4032 | 4316.5 | 8348.5
02:00 | 3876 | 4268 | 8144
02:30 | 3809 | 4246.5 | 8055.5
03:00 | 3742 | 4225 | 7967
03:30 | 3657.5 | 4169 | 7826.5
04:00 | 3573 | 4113 | 7686
04:30 | 3554.5 | 4092 | 7646.5
05:00 | 3536 | 4071 | 7607
05:30 | 3746.5 | 4081 | 7827.5
06:00 | 3957 | 4091 | 8048
06:30 | 4311.42 | 4172.505 | 8483.925
07:00 | 4665.84 | 4254.01 | 8919.85
07:30 | 4758.315 | 4513.655 | 9271.97
08:00 | 4850.79 | 4773.3 | 9624.09
08:30 | 4627.63 | 4784.975 | 9412.605
09:00 | 4404.47 | 4796.65 | 9201.12
09:30 | 4378.67 | 4787.32 | 9165.99
10:00 | 4352.87 | 4777.99 | 9130.86
10:30 | 4476.77 | 4860.51 | 9337.28
11:00 | 4600.67 | 4943.03 | 9543.7
11:30 | 4754.525 | 5071.13 | 9825.655
12:00 | 4908.38 | 5199.23 | 10107.61
12:30 | 4983.135 | 5320.7 | 10303.835
13:00 | 5057.89 | 5442.17 | 10500.06
13:30 | 5005.99 | 5284.91 | 10290.9
14:00 | 4954.09 | 5127.65 | 10081.74
14:30 | 4875.305 | 5035.96 | 9911.265
15:00 | 4796.52 | 4944.27 | 9740.79
15:30 | 4817.985 | 4930.14 | 9748.125
16:00 | 4839.45 | 4916.01 | 9755.46
16:30 | 4994.23 | 4925.56 | 9919.79
17:00 | 5149.01 | 4935.11 | 10084.12
17:30 | 5326.255 | 5415.055 | 10741.31
18:00 | 5503.5 | 5895 | 11398.5
18:30 | 5230.5 | 5942 | 11172.5
19:00 | 4957.5 | 5989 | 10946.5
19:30 | 4961.5 | 5910 | 10871.5
20:00 | 4949 | 5710 | 10659
20:30 | 4930.5 | 5692.17 | 10622.67 |  | Executive Engineer
21:00 | 4912 | 5674.34 | 10586.34 |  | Network Operation Division
21:30 | 4821 | 5509.13 | 10330.13
22:00 | 4730 | 5343.92 | 10073.92
22:30 | 4686.5 | 5264.49 | 9950.99
23:00 | 4643 | 5185.06 | 9828.06

## En-Curve
QF-LDC-12
Date | 26-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2971 | 1107 | 866 | 0 | 76 | 825 | 46 | 3404 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2936 | 1016.5 | 866 | 0 | 75 | 825 | 46 | 3159.5 | 0 | 0 | 17.5 | 0 | 0 | 0 | 0 | 26-11-2025
01:00 | 2901 | 926 | 866 | 0 | 74 | 825 | 46 | 2915 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2853.5 | 923 | 872.5 | 0 | 72 | 824.5 | 46 | 2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 231.0517 |  | MKWHr
02:00 | 2806 | 920 | 879 | 0 | 70 | 824 | 46 | 2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2760.5 | 931.5 | 881.5 | 0 | 69 | 826.5 | 35.5 | 2551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 231.0517 |  | MKWHr
03:00 | 2715 | 943 | 884 | 0 | 68 | 829 | 25 | 2503 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2688 | 977 | 808 | 0 | 68 | 830.5 | 12.5 | 2441.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:00 | 2661 | 1011 | 732 | 0 | 68 | 832 | 0 | 2380 | 0 | 0 | 0 | 0 | 0 | 2 | 0
04:30 | 2670 | 963 | 732 | 0 | 69 | 833.5 | 0 | 2377 | 0 | 0 | 0 | 0 | 0 | 2 | 0
05:00 | 2679 | 915 | 732 | 0 | 70 | 835 | 0 | 2374 | 0 | 0 | 0 | 0 | 0 | 2 | 0
05:30 | 2868 | 997.5 | 656 | 0 | 71 | 831 | 23 | 2378.5 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0
06:00 | 3057 | 1080 | 580 | 0 | 72 | 827 | 46 | 2383 | 0 | 0 | 0 | 0 | 0 | 3 | 0
06:30 | 3179.5 | 1140.5 | 580.5 | 0 | 72 | 829 | 46 | 2586.5 | 20.925 | 0 | 25.5 | 0 | 0 | 3.5 | 0
07:00 | 3302 | 1201 | 581 | 0 | 72 | 831 | 46 | 2790 | 41.85 | 0 | 51 | 0 | 0 | 4 | 0
07:30 | 3306 | 1185 | 658.5 | 0 | 76 | 831.435 | 46 | 2970.5 | 128.535 | 0 | 66.5 | 0 | 0 | 3.5 | 0
08:00 | 3310 | 1169 | 736 | 0 | 80 | 831.87 | 46 | 3151 | 215.22 | 0 | 82 | 0 | 0 | 3 | 0
08:30 | 3150 | 1076.5 | 743.5 | 0 | 82 | 820.38 | 46 | 3108 | 316.225 | 0 | 68.5 | 0 | 0 | 1.5 | 0
09:00 | 2990 | 984 | 751 | 0 | 84 | 808.89 | 46 | 3065 | 417.23 | 0 | 55 | 0 | 0 | 0 | 0
09:30 | 2952.5 | 1001.75 | 750.5 | 0 | 85 | 808.925 | 46 | 2991.5 | 490.315 | 0 | 39.5 | 0 | 0 | 0 | 0
10:00 | 2915 | 1019.5 | 750 | 0 | 86 | 808.96 | 46 | 2918 | 563.4 | 0 | 24 | 0 | 0 | 0 | 0
10:30 | 2983.5 | 1026.25 | 816.5 | 0 | 85 | 818.48 | 46 | 2917 | 604.05 | 6 | 34.5 | 0 | 0 | 0 | 0
11:00 | 3052 | 1033 | 883 | 0 | 84 | 828 | 46 | 2916 | 644.7 | 12 | 45 | 0 | 0 | 0 | 0
11:30 | 3142 | 1084.5 | 887.5 | 0 | 84 | 833.74 | 46 | 3041 | 647.915 | 14.5 | 44.5 | 0 | 0 | 0 | 0
12:00 | 3232 | 1136 | 892 | 0 | 84 | 839.48 | 46 | 3166 | 651.13 | 17 | 44 | 0 | 0 | 0 | 0
12:30 | 3236 | 1142.5 | 892 | 0 | 93 | 838.88 | 46 | 3359.5 | 635.955 | 17 | 43 | 0 | 0 | 0 | 0
13:00 | 3240 | 1149 | 892 | 0 | 102 | 838.28 | 46 | 3553 | 620.78 | 17 | 42 | 0 | 0 | 0 | 0
13:30 | 3176 | 1122 | 892 | 0 | 100 | 836.14 | 46 | 3500 | 567.76 | 17 | 33 | 0 | 0 | 1 | 0
14:00 | 3112 | 1095 | 892 | 0 | 98 | 834 | 46 | 3447 | 514.74 | 17 | 24 | 0 | 0 | 2 | 0
14:30 | 3097.5 | 1092.5 | 892 | 0 | 93 | 835 | 46 | 3397.5 | 427.765 | 8.5 | 20 | 0 | 0 | 1.5 | 0
15:00 | 3083 | 1090 | 892 | 0 | 88 | 836 | 46 | 3348 | 340.79 | 0 | 16 | 0 | 0 | 1 | 0
15:30 | 3174 | 1126 | 892 | 0 | 90 | 839 | 46 | 3315.5 | 233.125 | 0 | 31.5 | 0 | 0 | 1 | 0
16:00 | 3265 | 1162 | 892 | 0 | 92 | 842 | 46 | 3283 | 125.46 | 0 | 47 | 0 | 0 | 1 | 0
16:30 | 3253.5 | 1155 | 891.5 | 0 | 94 | 860 | 46 | 3347.5 | 66.39 | 16.5 | 188.4 | 0 | 0 | 1 | 0
17:00 | 3242 | 1148 | 891 | 0 | 96 | 878 | 46 | 3412 | 7.32 | 33 | 329.8 | 0 | 0 | 1 | 0
17:30 | 3246 | 1146.25 | 891.5 | 0 | 97 | 1026.5 | 46 | 3701 | 3.66 | 46 | 536.9 | 0 | 0 | 0.5 | 0
18:00 | 3250 | 1144.5 | 892 | 0 | 98 | 1175 | 46 | 3990 | 0 | 59 | 744 | 0 | 0 | 0 | 0
18:30 | 3179.5 | 1149 | 892 | 0 | 92 | 1240 | 46 | 4065.5 | 0 | 29.5 | 479 | 0 | 0 | 0 | 0
19:00 | 3109 | 1153.5 | 892 | 0 | 86 | 1305 | 46 | 4141 | 0 | 0 | 214 | 0 | 0 | 0 | 0
19:30 | 3154 | 1180.5 | 892 | 0 | 86 | 1193 | 46 | 4174 | 0 | 0 | 146 | 0 | 0 | 0 | 0
20:00 | 3159 | 1186 | 892 | 0 | 86 | 1102 | 46 | 4077 | 0 | 0 | 111 | 0 | 0 | 0 | 0
20:30 | 3156.5 | 1180 | 892 | 0 | 88 | 1108.17 | 46 | 4075.5 | 0 | 0 | 76.5 | 0 | 0 | 0 | 0
21:00 | 3154 | 1174 | 892 | 0 | 90 | 1114.34 | 46 | 4074 | 0 | 0 | 42 | 0 | 0 | 0 | 0
21:30 | 3041.5 | 1142.5 | 891.5 | 0 | 91 | 1096.63 | 46 | 3979 | 0 | 0 | 42 | 0 | 0 | 0 | 0
22:00 | 2929 | 1111 | 891 | 0 | 92 | 1078.92 | 46 | 3884 | 0 | 0 | 42 | 0 | 0 | 0 | 0
22:30 | 3000.5 | 1125 | 891.5 | 0 | 89 | 1013.99 | 46 | 3743 | 0 | 0 | 42 | 0 | 0 | 0 | 0
23:00 | 3072 | 1139 | 892 | 0 | 86 | 949.06 | 46 | 3602 | 0 | 0 | 42 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 401 | 05:00 | 382 | 12:00 | Meghnaghat | 402 | 04:00 | 384 | 16:00
Ashuganj | 407 | 6:00 | 388 | 12:00 | Payra | 418 | 06:00 | 408 | 18:30
Bhulta | 403 | 06:00 | 383 | 12:00 | Rahanpur | 417 | 04:00 | 400 | 18:30
Bibiana | 400 | 04:00 | 390 | 12:00 | Rampal | 413 | 02:00 | 399 | 18:00
BIPTC | 410 | 04:00 | 393 | 18:00
Bogura | 409 | 04:00 | 390 | 18:30
Gopalganj | 410 | 04:00 | 392 | 18:30
Kaliakoir | 398 | 04:00 | 377 | 12:00
Korerhat | 409 | 03:00 | 395 | 12:00
Madunaghat | 406 | 03:00 | 393 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 242 | 05:00 | 227 | 12:00 | Kachua | 236 | 18:00 | 231 | 16:00
AKSML | 241 | 03:00 | 231 | 12:00 | Kaliakoir | 241 | 04:00 | 227 | 12:00
Aminbazar | 241 | 05:00 | 228 | 12:00 | Keranigonj | 239 | 03:00 | 225 | 12:00
Ashuganj | 238 | 05:00 | 228 | 12:00 | Khulna(S) | 241 | 04:00 | 228 | 18:00
Ashuganj-400 | 238 | 6:00 | 227 | 12:00 | Korerhat | 241 | 03:00 | 232 | 16:00
Baghabari | 238 | 04:00 | 228 | 18:00 | Madunaghat | 240 | 00:00 | 233 | 13:00
Barapukuria | 225 | 03:00 | 213 | 18:00 | Madunaghat-400 | 242 | 04:00 | 233 | 13:00
Barapukuria-230 | 225 | 3:00 | 214 | 19:00 | Maniknagar | 234 | 05:00 | 222 | 12:00
Barishal | 244 | 05:00 | 236 | 12:00 | Meghnaghat | 239 | 08:00 | 230 | 00:00
Bheramara | 237 | 04:00 | 224 | 18:00 | Meghnaghat-400 | 237 | 04:00 | 226 | 12:00
Bhulta | 235 | 03:00 | 223 | 12:00 | Mirsorai | 239 | 06:00 | 227 | 13:00
Bibiana | 234 | 04:00 | 226 | 12:00 | Rajshahi | 237 | 04:00 | 219 | 11:00
BIPTC | 240 | 05:00 | 225 | 18:00 | Rampal | 239 | 03:00 | 227 | 18:00
Bogura | 238 | 04:00 | 226 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 237 | 05:00 | 226 | 18:00 | Rampura | 235 | 05:00 | 221 | 12:00
Borhanuddin | 245 | 03:00 | 240 | 18:00 | Shikalbaha | 240 | 04:00 | 231 | 12:00
BSRM | 238 | 04:00 | 227 | 12:00 | Shyampur | 238 | 04:00 | 225 | 12:00
Cumilla(N) | 236 | 04:00 | 225 | 13:00 | Siddhirganj | 234 | 05:00 | 226 | 13:00
Faridpur | 243 | 04:00 | 233 | 12:00 | Sirajgonj | 243 | 04:00 | 234 | 18:00
Fenchuganj | 236 | 06:00 | 228 | 16:00 | Sreepur | 235 | 04:00 | 223 | 18:30
Feni | 236 | 03:00 | 226 | 12:00 | Tongi | 236 | 04:00 | 223 | 11:00
Ghorashal | 0 | 00:00 | N/A | N/A
Ghorashal-230 | 233 | 05:00 | 217 | 18:30
Gopalganj | 243 | 05:00 | 233 | 13:00
GPH | 240 | 04:00 | 230 | 12:00
Haripur | 236 | 05:00 | 224 | 12:00
Hasnabad | 237 | 06:00 | 225 | 15:00
Hathazari | 239 | 06:00 | 229 | 12:00
Ishurdi | 240 | 04:00 | 227 | 18:00
Jhenaidah | 239 | 04:00 | 225 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 127 | 12:00 | Lalbag | 140 | 05:00 | 129 | 12:00
Agargaon | 139 | 05:00 | 129 | 12:00 | Lalmonirhat | 131 | 05:00 | 120 | 20:00
Agrabad | 139 | 05:00 | 132 | 12:00 | Madanganj | 135 | 05:00 | 130 | 15:00
AKS | 136 | 00:00 | 131 | 12:00 | Madaripur | 140 | 05:00 | 135 | 18:00
Aminbazar | 140 | 03:00 | 129 | 12:00 | Madartek | 135 | 02:00 | 126 | 13:00
Amnura | 138 | 03:00 | 129 | 13:00 | Madunaghat | 139 | 00:00 | 135 | 12:00
Ashuganj | 142 | 06:00 | 137 | 12:00 | Magura | 140 | 01:00 | 131 | 18:00
Bagerhat | 137 | 03:00 | 128 | 18:00 | Mahasthangarh | 135 | 03:00 | 127 | 18:00
Bajitpur | 137 | 00:00 | 129 | 18:30 | Maijdee | 136 | 03:00 | 130 | 12:00
Bakulia | 140 | 06:00 | 132 | 12:00 | Manikganj | 137 | 00:00 | 126 | 16:00
Banani | 136 | 02:00 | 127 | 13:00 | Maniknagar | 140 | 05:00 | 131 | 12:00
Bangabhaban | 140 | 04:00 | 131 | 12:00 | Matarbari | 131 | 03:00 | 123 | 12:00
Barapukuria | 139 | 05:00 | 128 | 18:00 | Matuail | 138 | 04:00 | 130 | 12:00
Barguna | 137 | 04:00 | 133 | 18:30 | Metrorail_Motijheel | 140 | 05:00 | 131 | 12:00
Barishal | 140 | 03:00 | 134 | 18:30 | Metrorail_Uttara | 140 | 02:00 | 129 | 15:00
Barishal-230 | 141 | 05:00 | 135 | 12:00 | Millgate | 141 | 02:00 | 129 | 13:00
Baroaulia | 140 | 06:00 | 133 | 12:00 | Mirpur | 139 | 03:00 | 129 | 12:00
Baroirhat | 138 | 03:00 | 132 | 13:00 | Mirzapur | 136 | 05:00 | 127 | 14:00
Bashundhara | 136 | 03:00 | 127 | 12:00 | Mithapukur | 134 | 04:00 | 123 | 18:00
BashundharaCement | 135 | 05:00 | 130 | 16:00 | MI_Cement | 138 | 05:00 | 127 | 12:00
Beanibazar | 134 | 06:00 | 130 | 11:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 139 | 03:00 | 122 | 12:00 | Mogbazar | 139 | 05:00 | 129 | 12:00
Bhaluka | 134 | 05:00 | 126 | 18:00 | Mongla | 136 | 00:00 | 129 | 18:00
Bhandaria | 138 | 05:00 | 134 | 12:00 | Motijheel | 140 | 04:00 | 131 | 12:00
Bhangura | 137 | 00:00 | 131 | 18:00 | Muktagacha | 133 | 03:00 | 126 | 18:00
Bheramara | 141 | 04:00 | 135 | 18:00 | Munshiganj | 136 | 05:00 | 129 | 12:00
Bheramara(GK) | 140 | 03:00 | 135 | 18:00 | Muradnagar | 138 | 03:00 | 130 | 13:00
Bhulta | 131 | 05:00 | 127 | 12:00 | Mymensingh | 136 | 09:00 | 123 | 18:00
Bog-Sherpur | 136 | 02:00 | 128 | 18:00 | Naogaon | 135 | 05:00 | 125 | 13:00
Bogura | 136 | 02:00 | 129 | 18:00 | Narail | 142 | 05:00 | 130 | 18:00
Bogura-230 | 136 | 03:00 | 129 | 18:00 | Narinda | 140 | 5:00 | 131 | 12:00
Brahmanbaria | 138 | 06:00 | 132 | 12:00 | Narshingdi | 138 | 05:00 | 121 | 08:00
Cantonment | 138 | 00:00 | 129 | 12:00 | Natore | 136 | 01:00 | 130 | 18:00
Chandina | 140 | 03:00 | 133 | 12:00 | Nawabganj | 140 | 03:00 | 131 | 12:00
Chandpur | 139 | 03:00 | 134 | 13:00 | Netrakona | 131 | 10:00 | 122 | 18:00
Chandraghona | 141 | 02:00 | 135 | 12:00 | New | 140 | 00:00 | 130 | 16:00
Chapai | 139 | 03:00 | 134 | 18:00 | Niamatpur | 139 | 05:00 | 134 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 137 | 03:00 | 129 | 16:00 | Noapara | 139 | 05:00 | 131 | 13:00
Chauddagram | 138 | 02:00 | 132 | 12:00 | Pabna | 140 | 04:00 | 131 | 21:00
Chhatak | 132 | 00:00 | 128 | 12:00 | Palashbari | 130 | 03:00 | 122 | 18:00
Chowmuhani | 134 | 02:00 | 129 | 12:00 | Panchagarh | 137 | 03:00 | 119 | 12:00
Chuadanga | 139 | 00:00 | 131 | 12:00 | Patiya | 138 | 07:00 | 133 | 01:00
Coxsbazar | 131 | 02:00 | 121 | 12:00 | Patuakhali | 136 | 05:00 | 133 | 18:00
Cumilla(N) | 139 | 04:00 | 133 | 12:00 | Payra | 137 | 01:00 | 134 | 19:00
Cumilla(S) | 140 | 05:00 | 126 | 11:00 | PHP | 138 | 02:00 | 131 | 13:00
Daganbhuiyan | 138 | 04:00 | 132 | 12:00 | Postogola | 138 | 04:00 | 129 | 12:00
Daudkandi | 134 | 04:00 | 128 | 12:00 | Purbachal | 137 | 03:00 | 127 | 12:00
DhakaUniversity | 136 | 02:00 | 127 | 12:00 | Purbasadipur | 133 | 04:00 | 119 | 08:00
Dhamrai | 136 | 04:00 | 128 | 12:00 | Rahanpur | 140 | 03:00 | 134 | 18:30
Dhanmondi | 138 | 03:00 | 129 | 19:00 | Rahanpur-400 | 140 | 02:00 | 135 | 18:00
Dohazari | 136 | 00:00 | 128 | 12:00 | Rahim | 136 | 05:00 | 129 | 13:00
Faridpur | 140 | 02:00 | 135 | 12:00 | Rajbari | 140 | 01:00 | 134 | 18:00
Fatullah | 141 | 04:00 | 128 | 12:00 | Rajendrapur | 136 | 04:00 | 127 | 18:30
Fenchuganj | 140 | 06:00 | 135 | 12:00 | Rajshahi | 136 | 00:00 | 130 | 12:00
Feni | 136 | 00:00 | 131 | 16:00 | Rajshahi-230 | 137 | 04:00 | 129 | 12:00
Feni-230 | 138 | 01:00 | 132 | 12:00 | Ramganj | 137 | 03:00 | 131 | 16:00
Ghatail | 133 | 09:00 | 125 | 14:00 | Rampur | 139 | 04:00 | 133 | 13:00
Ghorashal | 136 | 02:00 | 130 | 11:00 | Rampura | 136 | 03:00 | 127 | 12:00
Goalpara | 141 | 04:00 | 132 | 20:00 | Rangamati | 140 | 04:00 | 134 | 12:00
Gollamari | 140 | 04:00 | 133 | 12:00 | Rangpur | 133 | 04:00 | 124 | 18:30
Gopalganj | 140 | 04:00 | 133 | 18:00 | Ruppur | 140 | 04:00 | 134 | 18:00
Gopalganj-400 | 141 | 01:00 | 135 | 13:00 | Saidpur | 133 | 02:00 | 119 | 08:00
Gulshan | 136 | 04:00 | 127 | 12:00 | Satkhira | 138 | 05:00 | 129 | 18:30
Halishahar | 139 | 00:00 | 133 | 12:00 | Satmasjid | 138 | 00:00 | 128 | 13:00
Haripur | 137 | 03:00 | 130 | 12:00 | Savar | 138 | 02:00 | 128 | 12:00
HaripurSBU | 138 | 04:00 | 130 | 11:00 | SevenRings | 136 | 03:00 | 128 | 18:30
Hasnabad | 138 | 03:00 | 130 | 12:00 | ShahCement | 137 | 03:00 | 129 | 16:00
Hathazari | 140 | 06:00 | 135 | 11:00 | Shahjadpur | 140 | 00:00 | 135 | 11:00
Ishurdi | 142 | 04:00 | 135 | 18:00 | Shahjibazar | 139 | 07:00 | 134 | 10:00
Jaldhaka | 130 | 04:00 | 120 | 08:00 | Shahmirpur | 138 | 00:00 | 133 | 12:00
Jamalpur | 133 | 09:00 | 119 | 01:00 | Shariatpur | 140 | 02:00 | 134 | 13:00
Jashore | 138 | 00:00 | 123 | 12:00 | Sherpur | 128 | 08:00 | 118 | 18:00
Jhenaidah | 140 | 01:00 | 122 | 18:00 | Shikalbaha | 128 | 00:00 | 122 | 13:00
Jhenaidah-230 | 143 | 04:00 | 133 | 12:00 | Shikalbaha-230 | 141 | 04:00 | 135 | 12:00
Joydebpur | 136 | 01:00 | 125 | 18:00 | Shitalakhya | 138 | 05:00 | 127 | 12:00
Joypurhat | 133 | 04:00 | 124 | 13:00 | Sholosohor | 140 | 01:00 | 134 | 12:00
Juldah | 140 | 03:00 | 134 | 12:00 | Shyampur | 138 | 07:00 | 131 | 12:00
Kabirpur | 138 | 00:00 | 125 | 16:00 | Shyampur-230 | 142 | 05:00 | 133 | 12:00
Kachua | 140 | 01:00 | 135 | 12:00 | Siddhirganj | 137 | 02:00 | 131 | 12:00
Kaliakoir | 139 | 04:00 | 131 | 15:00 | Sirajganj | 135 | 01:00 | 130 | 12:00
Kallyanpur | 140 | 06:00 | 130 | 11:00 | Sonargaon | 135 | 05:00 | 129 | 12:00
Kalurghat | 141 | 04:00 | 135 | 12:00 | Sreemongol | 138 | 06:00 | 133 | 12:00
Kamrangirchar | 140 | 05:00 | 129 | 12:00 | Sreepur | 138 | 04:00 | 129 | 18:30
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 140 | 03:00 | 130 | 13:00
Kasba | 138 | 03:00 | 131 | 12:00 | SSM | 142 | 08:00 | 129 | 13:00
Kazla | 139 | 04:00 | 130 | 13:00 | Sunamganj | 131 | 00:00 | 128 | 18:00
Keranigonj | 140 | 04:00 | 130 | 12:00 | Sylhet | 134 | 01:00 | 130 | 13:00
Khagrachori | 139 | 01:00 | 132 | 15:00 | Sylhet-132 | 132 | 00:00 | 131 | 11:00
Khulna | 139 | 03:00 | 131 | 18:00 | Tangail | 132 | 03:00 | 124 | 14:00
Khulna(S) | 141 | 05:00 | 133 | 18:00 | Taraganj | 133 | 05:00 | 121 | 08:00
Khulshi | 138 | 01:00 | 131 | 12:00 | Tasnim | 140 | 18:00 | 130 | 14:00
Kishoreganj | 136 | 00:00 | 127 | 18:00 | Thakurgaon | 137 | 04:00 | 117 | 12:00
Kodda | 132 | 01:00 | 123 | 12:00 | TK | 139 | 04:00 | 135 | 12:00
KSRM | 140 | 01:00 | 133 | 12:00 | Tongi | 141 | 04:00 | 132 | 17:00
Kulaura | 139 | 03:00 | 134 | 12:00 | Ullahpara | 138 | 05:00 | 130 | 18:00
Kurigram | 130 | 03:00 | 118 | 18:00 | Ullon | 136 | 04:00 | 127 | 12:00
Kushtia | 137 | 01:00 | 128 | 18:00 | Uttara | 142 | 04:00 | 128 | 16:00
Laksam | 139 | 07:00 | 131 | 19:00 | UttaraNew | 140 | 02:00 | 129 | 15:00
Lakshmipur | 137 | 05:00 | 130 | 13:00 | Zigatola | 140 | 05:00 | 130 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division