## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-11-2025 | [28 empty] | Date: | 29-11-2025 | [28 empty] | Date: | 29-11-2025 | [28 empty] | Date: | 29-11-2025 | [28 empty] | Date: | 29-11-2025 | [17 empty] | Date: | 29-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Planat | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723 | 0 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 200 | 0 | 0 | 70 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 362 | 0 | 18 | 0 | 0 | 17 | 0 | 84 | 30 | 0 | 16 | 158 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 4135 | 862 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 835.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 256 | 560 | 0 | 4468.49 | 8603.49 | 99.77
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 9.2 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625 | 0 | 0 | 0 | 170 | 0 | 220 | 5 | 0 | 200 | 0 | 0 | 70 | 0 | 0 | 14 | 0 | 72 | 0 | 0 | 0 | 300 | 0 | 341 | 0 | 18 | 0 | 0 | 17 | 0 | 11 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 3799.2 | 768 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 835.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 257 | 549 | 0 | 4291.11 | 8090.31 | 99.77
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 9.2 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 0 | 0 | 220 | 5 | 0 | 199 | 0 | 0 | 70 | 0 | 0 | 5 | 0 | 62 | 0 | 0 | 0 | 310 | 0 | 321 | 0 | 18 | 0 | 0 | 17 | 0 | 11 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3585.2 | 674 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 824.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 257 | 557 | 0 | 4151.18 | 7736.38 | 99.77
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 9.2 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 0 | 0 | 220 | 5 | 0 | 145 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 62 | 0 | 0 | 0 | 260 | 0 | 318 | 0 | 18 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 3381.2 | 675 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 0 | 0 | 0 | 824.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 257 | 520 | 0 | 3950.55 | 7331.75 | 99.77
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 220 | 5 | 0 | 142 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 60 | 0 | 0 | 0 | 260 | 0 | 357 | 0 | 18 | 0 | 0 | 0 | 0 | 2 | 18 | 0 | 0 | 158 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 3342.5 | 614 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 793 | 0 | 0 | 0 | 842.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 257 | 500 | 0 | 3857.58 | 7200.08 | 99.76
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8.5 | 22 | 0 | 0 | 0 | 0 | 0 | 110 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 0 | 0 | 0 | 0 | 220 | 5 | 0 | 142 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 64 | 0 | 0 | 0 | 260 | 0 | 324 | 0 | 18 | 0 | 0 | 0 | 0 | 2 | 18 | 0 | 0 | 157 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 3331.5 | 583 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 835.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 256 | 500 | 0 | 3790.44 | 7121.94 | 99.76
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 8.5 | 22 | 0 | 0 | 0 | 0 | 0 | 110 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 15 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 220 | 5 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 70 | 0 | 0 | 0 | 290 | 0 | 354 | 0 | 18 | 0 | 0 | 8 | 0 | 23 | 18 | 0 | 0 | 159 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 3636.5 | 583 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 835.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 257 | 528 | 0 | 3854.06 | 7490.56 | 99.76
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 2 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0.27 | 46 | 0 | 27 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 4 | 0 | 0 | 0 | 0 | 320 | 19 | 0 | 201 | 0 | 0 | 111 | 0 | 0 | 10 | 0 | 64 | 0 | 6 | 0 | 310 | 0 | 341 | 0 | 30 | 0 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 159 | 0 | 5 | 5 | 107 | 0 | 2.53 | 0 | 4185.8 | 582 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 828 | 0 | 0 | 0 | 834.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.31 | 5 | 0 | 0 | 2.17 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0.19 | 0 | 54 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 7 | 0.02 | 0 | 0 | 115 | 220 | 0 | 257 | 635 | 0 | 4123.76 | 8309.56 | 99.76
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 11 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 0 | 0 | 0 | 0 | 0 | 1.19 | 46 | 0 | 6 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 0 | 0 | 0 | 0 | 315 | 43 | 0 | 197 | 19 | 0 | 110 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 0 | 315 | 0 | 343 | 0 | 30 | 0 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 159 | 0 | 24 | 19 | 108 | 1 | 13.61 | 0 | 4350.8 | 677 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.46 | 847 | 0 | 0 | 0 | 827.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.92 | 28 | 0 | 0 | 15.14 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.81 | 0 | 54 | 0 | 8 | 0 | 0 | 0 | 0 | 1.6 | 52 | 0.15 | 0 | 0 | 115 | 220 | 0 | 258 | 756 | 0 | 4564.67 | 8915.47 | 99.75
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 19 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 1 | 0 | 0 | 0 | 0 | 0 | 2.15 | 46 | 0 | 6 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710 | 0 | 0 | 6 | 0 | 0 | 295 | 43 | 0 | 193 | 26 | 0 | 109 | 0 | 0 | 0 | 0 | 78 | 0 | 46 | 0 | 300 | 0 | 334 | 0 | 30 | 0 | 0 | 17 | 0 | 76 | 20 | 0 | 0 | 159 | 0 | 8 | 8 | 110 | 1 | 27.66 | 0 | 4101.81 | 771 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.92 | 783 | 0 | 0 | 0 | 829.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.48 | 59 | 0 | 0 | 37.34 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 3.35 | 0 | 56 | 0 | 17 | 0 | 0 | 0 | 0 | 3.4 | 102 | 0.15 | 0 | 0 | 100 | 180 | 0 | 254 | 620 | 0 | 4438.54 | 8540.35 | 99.75
10:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 25 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 0 | 0 | 0 | 0 | 0 | 2.88 | 46 | 0 | 6 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 0 | 8 | 0 | 0 | 220 | 5 | 0 | 192 | 36 | 0 | 50 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | 0 | 300 | 0 | 316 | 0 | 30 | 0 | 0 | 8 | 0 | 41 | 20 | 0 | 0 | 159 | 0 | 8 | 8 | 108 | 2 | 37.37 | 0 | 4023.25 | 771 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 743 | 0 | 0 | 0 | 830.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.47 | 78 | 0 | 0 | 50.93 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 4.33 | 0 | 55 | 0 | 24 | 0 | 0 | 0 | 0 | 4.7 | 134 | 0.11 | 0 | 0 | 100 | 180 | 0 | 253 | 588 | 0 | 4459.77 | 8483.02 | 99.75
11:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 30 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 0 | 0 | 0 | 0 | 0 | 3.26 | 46 | 0 | 2 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 8 | 0 | 0 | 220 | 4 | 0 | 194 | 29 | 0 | 50 | 0 | 0 | 0 | 0 | 80 | 0 | 64 | 0 | 310 | 0 | 340 | 0 | 30 | 0 | 0 | 8 | 0 | 5 | 20 | 0 | 0 | 161 | 0 | 8 | 8 | 107 | 2 | 41.57 | 0 | 4114.83 | 771 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 748 | 0 | 0 | 0 | 840.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.67 | 88 | 0 | 0 | 57.4 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 5 | 0 | 56 | 0 | 28 | 0 | 0 | 0 | 0 | 5.4 | 155 | 0.35 | 0 | 0 | 100 | 180 | 0 | 257 | 564 | 0 | 4552.92 | 8667.75 | 99.75
12:00 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 29 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 0 | 0 | 0 | 0 | 0 | 3.32 | 46 | 0 | 2 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 24 | 0 | 0 | 330 | 10 | 0 | 193 | 36 | 0 | 105 | 0 | 0 | 3 | 0 | 96 | 0 | 60 | 0 | 315 | 0 | 390 | 0 | 30 | 0 | 0 | 12 | 0 | 78 | 30 | 0 | 0 | 160 | 0 | 8 | 8 | 106 | 2 | 42.53 | 0 | 4589.85 | 771 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 770 | 0 | 0 | 0 | 835.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.75 | 93 | 0 | 0 | 56.65 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 5.09 | 0 | 56 | 0 | 32 | 0 | 0 | 0 | 0 | 5.5 | 155 | 0.39 | 0 | 0 | 115 | 220 | 0 | 259 | 566 | 0 | 4729.77 | 9319.62 | 99.74
13:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 364 | 0 | 0 | 1 | 0 | 35 | 0 | 50 | 15 | 0 | 240 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 29 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 0 | 0 | 0 | 0 | 0 | 3.1 | 46 | 0 | 9 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803 | 0 | 0 | 26 | 0 | 0 | 330 | 34 | 2 | 192 | 34 | 0 | 105 | 0 | 0 | 6 | 0 | 96 | 0 | 60 | 0 | 310 | 0 | 359 | 0 | 30 | 0 | 0 | 17 | 0 | 78 | 30 | 0 | 0 | 160 | 0 | 24 | 19 | 99 | 2 | 35.61 | 0 | 4809.71 | 873 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 791 | 0 | 0 | 0 | 926.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.67 | 88 | 0 | 0 | 49.69 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 4.48 | 0 | 55 | 0 | 28 | 0 | 0 | 0 | 0 | 5.2 | 133 | 0.48 | 0 | 0 | 115 | 220 | 0 | 257 | 680 | 0 | 4994.69 | 9804.4 | 99.74
14:00 | 0 | 1 | 34 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 384 | 0 | 0 | 9 | 0 | 45 | 0 | 55 | 48 | 0 | 250 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 22 | 0 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 2.57 | 46 | 0 | 9 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 26 | 0 | 0 | 270 | 43 | 10 | 196 | 37 | 0 | 50 | 0 | 0 | 6 | 0 | 96 | 0 | 47 | 0 | 305 | 0 | 313 | 0 | 30 | 0 | 0 | 17 | 0 | 78 | 20 | 0 | 0 | 160 | 0 | 56 | 19 | 100 | 2 | 34.1 | 0 | 4633.67 | 873 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 781 | 0 | 0 | 0 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.67 | 77 | 0 | 0 | 32.99 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 3.82 | 0 | 55 | 0 | 19 | 0 | 0 | 0 | 0 | 4.2 | 116 | 0.4 | 0 | 0 | 115 | 180 | 0 | 256 | 626 | 0 | 4747.08 | 9380.75 | 99.74
15:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 378 | 0 | 0 | 14 | 0 | 30 | 0 | 55 | 35 | 0 | 250 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 15 | 0 | 22 | 18 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 1.73 | 46 | 0 | 7 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 0 | 26 | 0 | 0 | 270 | 20 | 10 | 194 | 37 | 0 | 50 | 0 | 0 | 6 | 0 | 96 | 0 | 33 | 0 | 300 | 0 | 305 | 0 | 30 | 0 | 0 | 17 | 0 | 41 | 20 | 0 | 0 | 161 | 0 | 58 | 19 | 100 | 1 | 21.5 | 0 | 4509.23 | 878 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 770 | 0 | 0 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.94 | 50 | 0 | 0 | 27.37 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 2.19 | 0 | 55 | 0 | 13 | 0 | 0 | 0 | 0 | 2.8 | 79 | 0.26 | 0 | 0 | 100 | 180 | 0 | 256 | 600 | 0 | 4591.56 | 9100.79 | 99.74
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 430 | 0 | 0 | 23 | 0 | 30 | 0 | 55 | 33 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 6 | 0 | 22 | 18 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0.78 | 46 | 0 | 7 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865 | 5 | 0 | 26 | 0 | 0 | 275 | 20 | 10 | 215 | 38 | 0 | 50 | 0 | 0 | 0 | 0 | 92 | 0 | 13 | 0 | 315 | 0 | 352 | 0 | 30 | 0 | 0 | 17 | 0 | 11 | 20 | 0 | 0 | 161 | 0 | 59 | 19 | 103 | 0 | 7.07 | 0 | 4578.85 | 882 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 822 | 0 | 0 | 0 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.96 | 22 | 0 | 0 | 8.51 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0.63 | 0 | 55 | 0 | 5 | 0 | 0 | 0 | 0 | 1.1 | 27 | 0.11 | 0 | 0 | 100 | 180 | 0 | 257 | 643 | 0 | 4544.31 | 9123.16 | 99.73
17:00 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 397 | 5 | 0 | 24 | 0 | 35 | 0 | 55 | 58 | 0 | 200 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 15 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 0 | 50 | 0 | 0 | 330 | 36 | 10 | 204 | 35 | 0 | 106 | 5 | 0 | 6 | 0 | 88 | 0 | 1 | 0 | 320 | 0 | 330 | 0 | 30 | 0 | 0 | 17 | 0 | 80 | 20 | 0 | 0 | 161 | 0 | 59 | 19 | 106 | 0 | 0.16 | 0 | 4890.16 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | 885 | 0 | 0 | 0 | 1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 1 | 0 | 0 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0.06 | 0 | 55 | 10 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 0 | 100 | 180 | 0 | 253 | 790 | 0 | 4848.05 | 9738.21 | 99.73
18:00 | 0 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 415 | 16.5 | 0 | 48 | 0 | 95 | 0 | 55 | 101 | 0 | 170 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 19 | 355 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 0 | 0 | 1155 | 0 | 0 | 85 | 0 | 0 | 330 | 43 | 12 | 212 | 38 | 0 | 108 | 20 | 0 | 6 | 0 | 98 | 0 | 0 | 0 | 320 | 0 | 405 | 0 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 15 | 159 | 0 | 59 | 19 | 107 | 0 | 0 | 0 | 5574.5 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 400 | 845 | 0 | 5724 | 11298.5 | 99.73
19:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 374 | 0 | 0 | 50 | 0 | 60 | 0 | 35 | 72 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 0 | 20 | 355 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 108 | 0 | 0 | 330 | 43 | 21 | 190 | 37 | 0 | 108 | 48 | 0 | 14 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 367 | 0 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 108 | 0 | 0 | 0 | 5347 | 886 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 0 | 0 | 0 | 1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 356 | 937 | 0 | 5615 | 10962 | 99.73
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 382 | 0 | 0 | 17 | 0 | 60 | 0 | 35 | 69 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 4 | 0 | 0 | 0 | 0 | 3 | 0 | 46 | 0 | 13 | 355 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 137 | 0 | 0 | 330 | 43 | 28 | 192 | 36 | 0 | 108 | 0 | 0 | 14 | 0 | 88 | 0 | 0 | 0 | 305 | 0 | 372 | 0 | 30 | 0 | 0 | 14 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 108 | 0 | 0 | 0 | 5230 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 0 | 0 | 0 | 1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 52 | 0 | 0 | 25 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 326 | 930 | 0 | 5679 | 10909
20:00 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 385 | 0 | 0 | 17 | 0 | 30 | 0 | 35 | 54 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 19 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0 | 148 | 0 | 0 | 330 | 43 | 30 | 198 | 36 | 0 | 108 | 0 | 0 | 14 | 0 | 82 | 0 | 0 | 0 | 300 | 0 | 372 | 0 | 30 | 0 | 0 | 14 | 0 | 80 | 30 | 0 | 16 | 158 | 0 | 59 | 18 | 108 | 0 | 0 | 0 | 5134 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 308 | 896 | 0 | 5549 | 10683 | 99.72
21:00 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 31 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 145 | 0 | 0 | 330 | 43 | 30 | 209 | 40 | 0 | 109 | 0 | 0 | 14 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 408 | 0 | 30 | 0 | 0 | 14 | 0 | 80 | 30 | 0 | 16 | 158 | 0 | 35 | 18 | 109 | 0 | 0 | 0 | 5127 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 0 | 0 | 1174.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 306 | 900 | 0 | 5348.55 | 10475.55 | 99.72
22:00 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 32 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1042 | 0 | 0 | 145 | 0 | 0 | 330 | 43 | 37 | 191 | 38 | 0 | 110 | 0 | 0 | 14 | 0 | 100 | 0 | 0 | 0 | 305 | 0 | 370 | 0 | 30 | 0 | 0 | 14 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 35 | 18 | 110 | 0 | 0 | 0 | 4966 | 884 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 953 | 0 | 0 | 0 | 1110.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 304 | 855 | 0 | 5155.06 | 10121.06 | 99.72
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 31 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 145 | 0 | 0 | 330 | 43 | 41 | 194 | 40 | 0 | 110 | 0 | 0 | 14 | 0 | 108 | 0 | 0 | 0 | 305 | 0 | 366 | 0 | 30 | 0 | 0 | 14 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 8 | 18 | 109 | 0 | 0 | 0 | 4852 | 885 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886 | 0 | 0 | 0 | 919.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 253 | 845 | 0 | 4839.16 | 9691.16 | 99.71
Total KWH | 0 | 155520 | 248160 | 0 | 0 | 0 | 0 | 0 | 7898400 | 0 | 9386730 | 34920 | 0 | 207648 | 0 | 394429 | 0 | 431572 | 406080 | 0 | 4190500 | 0 | 0 | 0 | 32250 | 5821721 | 0 | 0 | 189551 | 0 | 408600 | 519120 | 0 | 0 | 0 | 0 | 0 | 3200000 | 109920 | 0 | 0 | 0 | 0 | 40992 | 21121 | 1097760 | 0 | 363360 | 6538181.82 | 0 | 0 | 31680 | 0 | 86145 | 0 | 0 | 0 | 0 | 19254543 | 9450 | 0 | 1037091 | 180500 | 0 | 6850000 | 722320 | 258240 | 4692000 | 563256 | 0 | 1912362 | 87360 | 0 | 172820 | 0 | 1785600 | 0 | 417555 | 0 | 7346500 | 0 | 8612000 | 0 | 637320 | 0 | 0 | 294244 | 0 | 1243200 | 585312 | 0 | 110000 | 4337730 | 0 | 645600 | 266400 | 2425920 | 12200 | 268340 | 0 | 106542223.82 | 19388363 | 5804928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475920 | 20189091 | 0 | 0 | 0 | 22455272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329920 | 601740 | 0 | 0 | 350248 | 575000 | 0 | 0 | 0 | 0 | 0 | 8997600 | 0 | 31020 | 0 | 1274618 | 100119 | 173945 | 105168 | 0 | 196245 | 0 | 34083.96 | 978480 | 2526 | 0 | 0 | 2631000 | 5176510 | 0 | 6554843 | 17060363.64 | 0 | 113487003.6 | 220029227.42

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-11-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-11-2025 | during | 30-11-2025 | during | 30-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 97.7 | 97.7 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 341 | 354 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 230 | 170 | 450 | 450 | 220 | 220 | U-1 under S/D (Instruction of PDB)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 16.5 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 28 | 22 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 32 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 48 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 30 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 101 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 390 | 415 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1329 | 1610.5 | 5754.9 | 5722.9 | 4288.93 | 4256.93
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance,Unit #2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 8 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 40 | 48 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 19 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.32 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 660 | 1155 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 9 | 0 | 5 | 0 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 355 | 355 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1222.32 | 1771 | 3135.72 | 3149.72 | 2640.5 | 2638.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 193 | 212 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 12 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 24 | 85 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 10 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 108 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 20 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 96 | 98 | 160 | 160 | 96 | 96 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 3 | 6 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 857 | 952 | 2096.21 | 2026.21 | 1969.21 | 1899.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-11-2025 | during | 30-11-2025 | during | 30-11-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 106 | 107 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.53 | 0 | 45.85 | 0 | 45.85 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 166.53 | 185 | 361.95 | 314 | 314.45 | 266.5
| Moulvibazar 10 MW Solar Power Planat | Solar | IPP | 1*10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 80 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 159 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 405 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1015 | 1056 | 1075 | 1075 | 1013 | 1013
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 771 | 887 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 77 | 0 | 77 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 770 | 1120 | 0 | 0 | 1100 | 1100 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1866 | 2257 | 2313 | 2236 | 2694.1 | 2617.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 259 | 400 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 566 | 845 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.39 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1160.39 | 1580 | 1686.32 | 1686.32 | 1553.32 | 1553.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54.75 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 410 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 95 | 95 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.09 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 835.39 | 1319 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.65 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1454.88 | 1733 | 3077.07 | 2911.87 | 3081.69 | 2916.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 55 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 155 | 0 | 178.22 | 0 | 178.22 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 248.5 | 154 | 530.42 | 317 | 496.42 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 9319.62 | 11298.5 | 20030.59 | 19439.02 | 18051.62 | 17444.05
Forecast Scenario (30-11-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9480 |  | 0 |  | 9480
|  |  |  | 1:00 | 8910 |  | 0 |  | 8910
|  |  |  | 2:00 | 8510 |  | 0 |  | 8510
|  |  |  | 3:00 | 8300 |  | 0 |  | 8300
|  |  |  | 4:00 | 8020 |  | 0 |  | 8020
|  |  |  | 5:00 | 7960 |  | 0 |  | 7960
|  |  |  | 6:00 | 8250 |  | 0 |  | 8250
|  |  |  | 7:00 | 9050 |  | 0 |  | 9050
|  |  |  | 8:00 | 9600 |  | 0 |  | 9600
|  |  |  | 9:00 | 9540 |  | 0 |  | 9540
|  |  |  | 10:00 | 9500 |  | 0 |  | 9500
|  |  |  | 11:00 | 9860 |  | 0 |  | 9860
|  |  |  | 12:00 | 10230 |  | 0 |  | 10230
|  |  |  | 13:00 | 10650 |  | 0 |  | 10650
|  |  |  | 14:00 | 10160 |  | 0 |  | 10160
|  |  |  | 15:00 | 10010 |  | 0 |  | 10010
|  |  |  | 16:00 | 9850 |  | 0 |  | 9850
|  |  |  | 17:00 | 10330 |  | 0 |  | 10330
|  |  |  | 18:00 | 11410 |  | 0 |  | 11410
|  |  |  | 18:30 | 11200 |  | 0 |  | 11200
|  |  |  | 19:00 | 11010 |  | 0 |  | 11010
|  |  |  | 19:30 | 10850 |  | 0 |  | 10850
|  |  |  | 20:00 | 10760 |  | 0 |  | 10760
|  |  |  | 21:00 | 10620 |  | 0 |  | 10620
|  |  |  | 22:00 | 10110 |  | 0 |  | 10110
|  |  |  | 23:00 | 9800 |  | 0 |  | 9800
Probable Maximum Temperature: |  |  | 28.40°C
Probable Maximum Demand at Day Peak: |  |  | 10230.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11410.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11410.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 231.92 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:40 hrs on 30-11-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9319.62 | MW | 12:00 Hr. | Energy Generated |  |  | 220.0292 |  | MKWHr.
| Day Peak Demand |  |  | 9319.62 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11298.5 | MW | 18:00 Hr. | Energy Demand |  |  | 220.0292 |  | MKWHr.
| Evening Peak Demand |  |  | 11298.5 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 7121.94 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 747.13 |  | MMCFD
| Maximum Generation of the Day |  |  | 11298.5 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.3632 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.2251 | 0 | 1.9106 | 0 | 0 | 0.18955 | 0 | 0 | 30.3252 | Gas | 96.9543 | Gas | 349558863.51
| Chattogram Zone |  |  | 3.5634 | 25.7927 | 0.15882 | 0 | 1.0978 | 0.030571 | 0 | 0.10992 | 30.7532 | Coal | 70.8716 | Coal | 447939860.2826
| Cumilla Zone |  |  | 16.3886 | 0 | 0.08736 | 0 | 0 | 0.41756 | 1.7856 | 0 | 18.6791 | HFO | 3.274 | HFO | 55766628.83
| Mymensingh Zone |  |  | 2.4259 | 0 | 0.912 | 0 | 0 | 0.28054 | 0 | 0 | 3.6185 | HSD | 0.19625 | HSD | 5375150.55
| Sylhet Zone |  |  | 23.1663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1663 | Hydro | 1.0978 | Hydro | 109776
| Khulna Zone |  |  | 5.8049 | 20.1891 | 0 | 0 | 0 | 0.47592 | 19.3884 | 0 | 45.8583 | Solar | 3.8961 | Solar | 62153155.7916
| Barishal Zone |  |  | 7.8075 | 23.6152 | 0 | 0 | 0 | 0.002526 | 0 | 0 | 31.4252 | Import | 43.6292 | Import | 257535583.43
| Rajshahi Zone |  |  | 9.5726 | 0 | 0 | 0 | 0 | 1.3129 | 22.4553 | 0 | 33.3408 | Wind | 0.10992 | Wind | 1616923.2
| Rangpur Zone |  |  | 0 | 1.2746 | 0.20529 | 0.19625 | 0 | 1.1865 | 0 | 0 | 2.8627
| Total |  |  | 96.9543 | 70.8716 | 3.274 | 0.19625 | 1.0978 | 3.8961 | 43.6292 | 0.10992 | 220.0292
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 349558863.51 |  | Hydro | 109776
|  |  |  | Coal | 447939860.2826 |  | Solar | 62153155.7916
|  |  |  | HFO | 55766628.83 |  | Import | 257535583.43
|  |  |  | HSD | 5375150.55 |  | Wind | 1616923.2
[5 empty] | Total: | 118,00,55,941 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.3884 | Peak Hr Flow | 887.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43442690.92 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.4553 | Peak Hr Flow | 1319.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2218 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7856 | Peak Hr Flow | 98.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2313 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.6292 | Peak Hr Flow | 2304.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4095
|  |  |  | Chattogram |  | 0 |  | 1142
|  |  |  | Cumilla |  | 0 |  | 957
|  |  |  | Mymensingh |  | 0 |  | 886
|  |  |  | Sylhet |  | 0 |  | 429
|  |  |  | Khulna |  | 0 |  | 1258
|  |  |  | Barishal |  | 0 |  | 290
|  |  |  | Rajshahi |  | 0 |  | 1006
|  |  |  | Rangpur |  | 0 |  | 758
|  |  |  | Total |  | 0 |  | 10821
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 15:32 | Nawabganj 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance of 33 kv Busbar | [7 empty] | 11.0MW load
|  |  | for T-1 and T-2, All 33 kv feeders with associated DS, CT, PT, CB, Aux. Tr-1 & 2, All | [7 empty] | interrup.
work performed by Dhaka PBS-2
| 08:15 | 15:30 | Nawabganj 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance of 33 kv Busbar | [7 empty] | 11.0MW load
|  |  | for T-1 and T-2, All 33 kv feeders with associated DS, CT, PT, CB, Aux. Tr-1 & 2, All | [7 empty] | interrup.
work performed by Dhaka PBS-2
| 08:16 | 15:34 | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance of 33 kv Busbar | [7 empty] | 11.0MW load
|  |  | for T-1 and T-2, All 33 kv feeders with associated DS, CT, PT, CB, Aux. Tr-1 & 2, All | [7 empty] | interrup.
work performed by Dhaka PBS-2
| 08:17 | 15:27 | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintenance of 33 kv Busbar | [7 empty] | 11.0MW load
|  |  | for T-1 and T-2, All 33 kv feeders with associated DS, CT, PT, CB, Aux. Tr-1 & 2, All | [7 empty] | interrup.
work performed by Dhaka PBS-2
| 08:20 | 14:31 | Savar 132/33kV S/S T-4 LT Scheduled S/D Due to Annual maintenance
| 08:21 | 17:28 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to
Annual Maintenance
| 08:24 | 14:30 | Savar 132/33kV S/S T-4 HT Scheduled S/D Due to Annual maintenance
| 08:25 | 17:05 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
Annual Maintenance
| 08:25 | 17:04 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to
Annual Maintenance
| 08:25 | 14:34 | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to Annual maintenance
| 08:26 | 16:19 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to Annual Maintenance
| 08:26 | 16:19 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Scheduled S/D Due to Annual Maintenance
| 08:37 | 17:04 | Bogura 230/132kV S/S T-01 LT Scheduled S/D Due to Annual Maintenance Work.
| 08:37 | 17:04 | Bogura 230/132kV S/S T-01 HT Scheduled S/D Due to Annual Maintenance Work.
| 08:40 | 17:06 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D
| 08:41 | 17:40 | Ghorashal 230kV S/S TARFO-2 LT Scheduled S/D Due to A/M | [7 empty] | 45.0MW load
interrup.
| 08:42 | 17:40 | Ghorashal 230kV S/S TARFO-2 HT Scheduled S/D Due to A/M | [7 empty] | 45.0MW load
interrup.
| 08:43 | 15:38 | Khulna (C) S/S North-WestCkt-1 Scheduled S/D Due to For Annual Maintenance
| 08:44 | 15:25 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Scheduled S/D Due to Annual
maintenance
| 08:45 | 16:57 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end.
| 08:46 | 15:47 | Magura 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Annual maintenance of 33kV WZPDCL | [7 empty] | 12.0MW load
|  |  | feeder. | [7 empty] | interrup.
| 08:46 | 14:55 | Savar 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance
| 08:47 | 15:38 | Magura 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Annual maintenance of 33kV WZPDCL | [7 empty] | 12.0MW load
|  |  | feeder. | [7 empty] | interrup.
| 08:49 | 14:31 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV
end Due to For annual deadline checking and maintenance work.
| 08:53 | 12:33 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to PT test
| 09:02 | 15:43 | Jhenaidah 230/132kV S/S Jhenaidah (New)-Jhenaidah (Old) Ckt-1 Scheduled S/D Due to Annual
Maintenance
| 09:03 | 15:43 | Jhenaidah 132/33kV S/S Jhenaidah1-Jhenaidah2, 132kV Circuit-1(L4) Scheduled S/D Due to
Annual maintenance
| 09:07 | 17:05 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Annual Maintenance
| 09:08 | 17:03 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Annual Maintenance
| 09:16 | 15:42 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Deadline Checking and from Ghatail 132/33kV end Due to Annual maintenance work of
Muktagacha Grid SS
| 09:18 | 13:37 | Brahmanbaria 132/33kV S/S 401T HT Scheduled S/D
| 09:18 | 13:37 | Brahmanbaria 132/33kV S/S 401T LT Scheduled S/D
| 09:23 | 11:28 | Gallamari- Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to red
hot
| 09:29 | 14:42 | Fenchuganj 230/132/33kV S/S TR-02B LT Scheduled S/D Due to Annual Maintenance
| 09:30 | 12:26 | Ashuganj-Brahmanbaria 132kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing Distance | [7 empty] | 20.0MW load
|  |  | Relay trip relays. | [7 empty] | interrup.
Brahmanbaria
132/33kV end
| 09:30 | 12:26 | Ashuganj-Brahmanbaria 132kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Distance | [7 empty] | 20.0MW load
|  |  | Relay relays. | [7 empty] | interrup.
Brahmanbaria
132/33kV end
| 09:34 |  | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to maintenance
| 09:34 |  | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to Maintenance
| 09:34 | 14:34 | Fenchuganj 230/132/33kV S/S TR-02B HT Scheduled S/D Due to Annual Maintenance
| 09:47 | 13:20 | Keranigonj 230/132/33kV S/S TR-1 LT Scheduled S/D Due to Annual Maintenance
| 09:48 | 13:20 | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance
| 10:11 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2
| 10:35 | 12:24 | Ashuganj-Shahjibazar 132kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing Distance
Relay relays Due to Ashuganj end trnasformer 12 trip and bus Death
|  | 10:50 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat is restored.
|  | 10:56 | Lalmonirhat-Rangpur 132 kV Ckt-2 is restored.
| 11:02 | 16:04 | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Rangpur 132/33kV end Due to E S Tower
made
| 11:30 | 16:05 | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Lalmonirhat 132/33kV end Due to None
|  | 13:20 | Keranigonj 230/132/33kV S/S TR-1 LT is restored.
|  | 13:20 | Keranigonj 230/132/33kV S/S TR-1 HT is restored.
|  | 13:40 | Sylhet 132/33kV S/S T2 HT is restored.
|  | 13:42 | Sylhet 132/33kV S/S T2 LT is restored.
| 13:44 |  | Brahmanbaria 132/33kV S/S 403T LT Scheduled S/D
| 13:44 | 16:39 | Brahmanbaria 132/33kV S/S 403T HT Scheduled S/D
|  | 14:20 | Chhatak 132/33kV S/S T-3 HT is restored.
| 15:16 |  | Chandina 132/33kV S/S TR-3 HT Tripped showing TR Main relay -2 relays Due to 33kv CB | [7 empty] | 7.0MW load
|  |  | phase B blasted | [7 empty] | interrup.
| 15:16 |  | Chandina 132/33kV S/S TR-3 LT Tripped showing TR Backup relay relays Due to 33 KV CB | [7 empty] | 7.0MW load
|  |  | Phase B Blasted | [7 empty] | interrup.
| 15:31 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- GT-1
|  | 15:32 | Nawabganj 132/33kV S/S TR-1 LT is restored.
| 15:35 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- Running GT-2
|  | 15:42 | Mymensingh RPCL-Tangail 132kV Ckt-1 is restored.
| 15:52 | 17:02 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 LT Scheduled S/D Due to Protection works.
|  | 15:58 | Joypurhat-Naogaon 132kV Ckt-1 is restored.
|  | 15:58 | Joypurhat-Naogaon 132kV Ckt-1 is restored.
| 16:01 | 17:02 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 HT Scheduled S/D Due to Protection works.
| 16:22 |  | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Project Work S/D Due to Tower No. 113
Maintenance work.
| 16:25 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Project Work S/D from Kurigram 132/33kV end Due to
Project work
|  | 16:37 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) HT is restored.
|  | 16:39 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) LT is restored.
|  | 16:43 | Joypurhat 132/33kV S/S Naogaon Ckt.-2 is restored.
|  | 16:52 | Meghnaghat-Shyampur 230kV Ckt-1 is restored.
|  | 16:52 | Meghnaghat-Shyampur 230kV Ckt-1 is restored.
|  | 16:54 | Dohazari-Sikalbaha 132 kV Ckt-2 is restored.
|  | 16:55 | Patiya 132/33kV S/S Sikalbaha-Patiya Ckt-02 is restored.
|  | 16:57 | Natore-Rajshahi 132kV Ckt-2 is restored.
| 18:00 |  | Evening Peak Generation: 11298 MW.
| 01:24 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 04:50 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 05:00 |  | Minimum Generation: 7642 MW.
| 06:38 | 07:04 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Tripped showing Siprotech,siemens | [7 empty] | 40.0MW load
|  |  | relays Due to Birds | [7 empty] | interrup.
| 07:24 |  | Chhatak 132/33kV S/S T-3 LT Scheduled S/D Due to Annual Maintenance
| 07:24 |  | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintenance
| 07:27 |  | Mahasthangarh 132/33kV S/S 406T MTR1 LT Scheduled S/D Due to Annual Maintenance
| 07:28 |  | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to Annual Maintenance
| 07:34 |  | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to Annual
Maintenance and from Meghnaghat 400/230kV end Due to Shyampur 230 kV ckt-2 shutdown
instructed by NLDC.
| 07:43 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to
Annual Maintenance
| 07:51 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to
Annual Maintenacce
| 07:53 |  | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to Yearly
maintenance. and from Rajshahi 132/33kV end Due to Annual maintenance work.
| 07:53 |  | Bogura 132/33kV S/S Transformer-4 HT Scheduled S/D Due to For maintenance work.
| 07:53 |  | Bogura 132/33kV S/S Transformer-4 LT Scheduled S/D Due to For maintenance work.
| 07:53 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) LT Scheduled S/D Due to A/M
| 07:54 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) HT Scheduled S/D Due to A/M
| 07:59 |  | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to
Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 354 | 7898400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 170 | 4190500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5821721 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 16.5 | 34920 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 431572 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 32250 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 408600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 519120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 248160 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 394429 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 48 | 207648 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 30 | 155520 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 101 | 406080 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 189551 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 415 | 9386730 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 1610.5 | 30325201
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3200000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 9450 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 8 | 31680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1097760 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 86145 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 19 | 363360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 40992 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1155 | 19254543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 109920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 355 | 6538181.82 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1771 | 30753152.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 212 | 4692000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 6850000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 180500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 563256 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 12 | 258240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 85 | 1037091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 722320 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 1912362 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 20 | 87360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 98 | 1785600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 6 | 172820 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 417555 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 952 | 18679104
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 107 | 2425920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 266400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 645600 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 268340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 185 | 3618460
| Moulvibazar 10 MW Solar Power Planat |  | IPP | 1*10 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 637320 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 585312 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1243200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 159 | 4337730 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 110000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 294244 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7346500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 405 | 8612000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1056 | 23166306
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 887 | 19388363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 5804928 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 475920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1120 | 20189091 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2257 | 45858302
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 400 | 6554843 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2631000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 845 | 17060363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5176510 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2526 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1580 | 31425242.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 329920 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 575000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8997600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1319 | 22455272 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 350248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 601740 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1733 | 33340800
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 196245 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1274618 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 105168 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34083.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 100119 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173945 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 978480 | -
Rangpur Area Total |  |  |  |  | 950 | 154 | 2862658.96
Eastern Grid Total |  |  |  |  | 17383.855 | 5574.5 | 106542223.82
Western Grid Total |  |  |  |  | 10821.56 | 5724 | 113487003.6
National Grid Total |  |  |  |  | 28205.415 | 11298.5 | 220029227.42
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7508.69 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3312.6 | MW
i) Dhaka area |  |  | 4094.69 |  | MW | i) Khulna area |  |  |  | 1258.5 | MW
ii) Chattogram area |  |  | 1142 |  | MW | ii) Barishal area |  |  |  | 290.5 | MW
iii) Cumilla area |  |  | 957 |  | MW | iii) Rajshahi area |  |  |  | 1005.6 | MW
iv) Mymensingh area |  |  | 886 |  | MW | iv) Rangpur area |  |  |  | 758 | MW
v) Sylhet area |  |  | 429 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10821.29 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 17:00 | 67 | Hathazari | 57 | 18:00 | 133 | Niamatpur | 44 | 18:00
2 | AKSML | 141 | 13:00 | 68 | Ishurdi | 55 | 18:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jaldhaka | 52 | 18:00 | 135 | PHP | 5 | 00:00
4 | Agargaon | 89 | 13:00 | 70 | Jamalpur | 86 | 18:00 | 136 | Pabna | 66 | 18:00
5 | Agrabad | 60 | 18:00 | 71 | Jashore | 99 | 18:00 | 137 | Palashbari | 82 | 18:00
6 | Amnura | 19 | 07:00 | 72 | Jhenaidah | 95 | 18:00 | 138 | Panchagarh | 46 | 18:00
7 | Ashuganj | 56 | 13:00 | 73 | Joydebpur | 118 | 18:00 | 139 | Patiya | 7 | 15:00
8 | BSRM | 205 | 23:00 | 74 | Joypurhat | 49 | 18:00 | 140 | Patuakhali | 43.5 | 21:00
9 | Bagerhat | 62 | 19:30 | 75 | Juldah | 15 | 13:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 63 | 18:00 | 76 | KSRM | 40 | 12:00 | 142 | Postogola | 52 | 13:00
11 | Bakulia | 60 | 18:30 | 77 | Kabirpur | 155 | 16:00 | 143 | Purbachal | 29 | 13:00
12 | Banani | 27.4 | 13:00 | 78 | Kachua | 59 | 18:00 | 144 | Purbasadipur | 101 | 18:00
13 | Bangabhaban | 7 | 11:00 | 79 | Kallyanpur | 78 | 12:00 | 145 | Rahanpur | 21 | 18:00
14 | Barapukuria | 51 | 18:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rahim | 34 | 16:00
15 | Barguna | 14 | 19:30 | 81 | Kamrangirchar | 61 | 13:00 | 147 | Rajbari | 55 | 18:00
16 | Barishal | 69 | 21:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 106 | 18:00
17 | Barishal-230 | 76 | 18:00 | 83 | Kasba | 22 | 20:00 | 149 | Rajshahi | 86 | 13:00
18 | Baroaulia | 64 | 16:00 | 84 | Kazla | 88 | 13:00 | 150 | Rajshahi-230 | 43 | 13:00
19 | Baroirhat | 49 | 21:00 | 85 | Keranigonj | 61 | 18:30 | 151 | Ramganj | 64 | 18:30
20 | Bashundhara | 152 | 13:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 30 | 18:00
21 | BashundharaCement | 7 | 17:00 | 87 | Khulna | 50 | 13:00 | 153 | Rangamati | 12 | 18:30
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 151 | 15:00 | 154 | Rangpur | 109 | 18:00
23 | Benapole | 44 | 18:00 | 89 | Kishoreganj | 83 | 18:00 | 155 | Ruppur | 2 | 14:00
24 | Bhaluka | 125 | 18:00 | 90 | Kodda | 249 | 18:30 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 40 | 19:30 | 91 | Kulaura | 37 | 18:00 | 157 | Saidpur | 90 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 48 | 18:00 | 158 | Satkhira | 80 | 18:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | Kushtia | 113 | 18:00 | 159 | Satmasjid | 76 | 14:00
28 | Bhulta | 181 | 16:00 | 94 | Laksam | 21 | 18:00 | 160 | Savar | 171 | 15:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 23 | 21:00 | 161 | SevenRings | 12.34 | 21:00
30 | Bogura | 121 | 17:00 | 96 | Lalbag | 58 | 12:00 | 162 | ShahCement | 22 | 02:00
31 | Borhanuddin | 63 | 18:00 | 97 | Lalmonirhat | 44 | 18:30 | 163 | Shahjadpur | 53 | 18:00
32 | Brahmanbaria | 90 | 18:00 | 98 | MI_Cement | 12.5 | 20:00 | 164 | Shahjibazar | 83 | 18:00
33 | Cantonment | 92 | 13:00 | 99 | Madanganj | 35 | 13:00 | 165 | Shahmirpur | 37 | 18:00
34 | Chandina | 12 | 02:00 | 100 | Madaripur | 70 | 19:30 | 166 | Shariatpur | 56 | 20:00
35 | Chandpur | 52 | 18:00 | 101 | Madartek | 65 | 13:00 | 167 | Sherpur | 108 | 18:00
36 | Chandraghona | 32 | 18:00 | 102 | Madunaghat | 37 | 18:00 | 168 | Shikalbaha | 20 | 01:00
37 | Chapai | 48 | 18:30 | 103 | Magura | 50 | 18:00 | 169 | Shitalakhya | 61.7 | 11:00
38 | Charsaidpur | 34 | 10:00 | 104 | Mahasthangarh | 50 | 08:00 | 170 | Sholosohor | 35 | 12:00
39 | Chauddagram | 44 | 14:00 | 105 | Maijdee | 21 | 18:00 | 171 | Shyampur | 132 | 11:00
40 | Chhatak | 26 | 18:30 | 106 | Manikganj | 88 | 18:00 | 172 | Siddhirganj | 99 | 12:00
41 | Chowmuhani | 108 | 18:00 | 107 | Maniknagar | 45 | 13:00 | 173 | Sirajganj | 78 | 18:30
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 39 | 18:00 | 174 | Sonargaon | 114 | 17:00
43 | Coxsbazar | 108 | 18:00 | 109 | Matuail | 59 | 12:00 | 175 | Sreemongol | 53 | 18:00
44 | Cumilla(N) | 90 | 18:00 | 110 | Metrorail_Motijheel | 24 | 16:00 | 176 | Sreepur | 77 | 12:00
45 | Cumilla(S) | 122 | 13:00 | 111 | Metrorail_Uttara | 5 | 19:00 | 177 | Srinagar | 31 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 88 | 12:00 | 178 | Sunamganj | 38 | 18:00
47 | Daudkandi | 108 | 20:00 | 113 | Mirpur | 111 | 18:00 | 179 | Sylhet | 44 | 18:00
48 | DhakaUniversity | 52 | 13:00 | 114 | Mirsorai | 10 | 10:00 | 180 | Sylhet-132 | 81 | 18:00
49 | Dhamrai | 98 | 18:00 | 115 | Mirzapur | 40 | 18:30 | 181 | TK | 18 | 21:00
50 | Dhanmondi | 88.6 | 13:00 | 116 | Mithapukur | 46 | 18:00 | 182 | Tangail | 120 | 17:00
51 | Dohazari | 68 | 18:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 13 | 08:00
52 | Faridpur | 111 | 18:00 | 118 | Mogbazar | 64.5 | 14:00 | 184 | Tasnim | 12 | 16:00
53 | Fatullah | 99 | 12:00 | 119 | Mongla | 26 | 18:30 | 185 | Thakurgaon | 78 | 18:00
54 | Fenchuganj | 24 | 18:00 | 120 | Motijheel | 28 | 13:00 | 186 | Tongi | 104 | 11:00
55 | Feni | 67 | 18:00 | 121 | Muktagacha | 24 | 07:00 | 187 | Ullahpara | 25 | 18:00
56 | GPH | 65 | 23:00 | 122 | Munshiganj | 74 | 13:00 | 188 | Ullon | 50 | 13:00
57 | Ghatail | 54 | 08:00 | 123 | Muradnagar | 24 | 19:00 | 189 | Uttara | 61 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 138 | 18:00 | 190 | UttaraNew | 14 | 13:00
59 | Ghorashal-230 | 80 | 19:00 | 125 | Naogaon | 91 | 13:00 | 191 | Zigatola | 54 | 13:00
60 | Goalpara | 30 | 18:00 | 126 | Narail | 41.5 | 18:00
61 | Gollamari | 68 | 18:00 | 127 | Narinda | 55 | 13:00
62 | Gopalganj | 76 | 18:00 | 128 | Narshingdi | 146 | 18:30
63 | Gulshan | 74 | 13:00 | 129 | Natore | 109 | 18:00
64 | Halishahar | 55 | 15:00 | 130 | Nawabganj | 38 | 18:00
65 | HaripurSBU | 121 | 21:00 | 131 | Netrakona | 112 | 18:00
66 | Hasnabad | 85 | 12:00 | 132 | New | 60.6 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8603.49 | 0 |  | 8603.49
1:00 | 8090.31 | 0 |  | 8090.31
2:00 | 7736.38 | 0 |  | 7736.38
3:00 | 7331.75 | 0 |  | 7331.75
4:00 | 7200.08 | 0 |  | 7200.08
5:00 | 7121.94 | 0 |  | 7121.94
6:00 | 7490.56 | 0 |  | 7490.56
7:00 | 8309.56 | 0 |  | 8309.56
8:00 | 8915.47 | 0 |  | 8915.47
9:00 | 8540.35 | 0 |  | 8540.35
10:00 | 8483.02 | 0 |  | 8483.02
11:00 | 8667.75 | 0 |  | 8667.75
12:00 | 9319.62 | 0 |  | 9319.62
13:00 | 9804.4 | 0 |  | 9804.4
14:00 | 9380.75 | 0 |  | 9380.75
15:00 | 9100.79 | 0 |  | 9100.79
16:00 | 9123.16 | 0 |  | 9123.16
17:00 | 9738.21 | 0 |  | 9738.21
18:00 | 11298.5 | 0 |  | 11298.5
19:00 | 10962 | 0 |  | 10962
19:30 | 10909 | 0 |  | 10909
20:00 | 10683 | 0 |  | 10683
21:00 | 10475.55 | 0 |  | 10475.55
22:00 | 10121.06 | 0 |  | 10121.06
23:00 | 9691.16 | 0 |  | 9691.16
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4135 | 4468.49 | 8603.49 | DAILY GENERATION CURVE
00:30 | 3967.1 | 4379.8 | 8346.9
01:00 | 3799.2 | 4291.11 | 8090.31 | 29-11-2025
01:30 | 3692.2 | 4221.145 | 7913.345
02:00 | 3585.2 | 4151.18 | 7736.38
02:30 | 3483.2 | 4050.865 | 7534.065
03:00 | 3381.2 | 3950.55 | 7331.75
03:30 | 3361.85 | 3904.065 | 7265.915
04:00 | 3342.5 | 3857.58 | 7200.08
04:30 | 3337 | 3824.01 | 7161.01
05:00 | 3331.5 | 3790.44 | 7121.94
05:30 | 3484 | 3822.25 | 7306.25
06:00 | 3636.5 | 3854.06 | 7490.56
06:30 | 3911.15 | 3988.91 | 7900.06
07:00 | 4185.8 | 4123.76 | 8309.56
07:30 | 4268.3 | 4344.215 | 8612.515
08:00 | 4350.8 | 4564.67 | 8915.47
08:30 | 4226.305 | 4501.605 | 8727.91
09:00 | 4101.81 | 4438.54 | 8540.35
09:30 | 4062.53 | 4449.155 | 8511.685
10:00 | 4023.25 | 4459.77 | 8483.02
10:30 | 4069.04 | 4506.345 | 8575.385
11:00 | 4114.83 | 4552.92 | 8667.75
11:30 | 4352.34 | 4641.345 | 8993.685
12:00 | 4589.85 | 4729.77 | 9319.62
12:30 | 4699.78 | 4862.23 | 9562.01
13:00 | 4809.71 | 4994.69 | 9804.4
13:30 | 4721.69 | 4870.885 | 9592.575
14:00 | 4633.67 | 4747.08 | 9380.75
14:30 | 4571.45 | 4669.32 | 9240.77
15:00 | 4509.23 | 4591.56 | 9100.79
15:30 | 4544.04 | 4567.935 | 9111.975
16:00 | 4578.85 | 4544.31 | 9123.16
16:30 | 4734.505 | 4696.18 | 9430.685
17:00 | 4890.16 | 4848.05 | 9738.21
17:30 | 5232.33 | 5286.025 | 10518.355
18:00 | 5574.5 | 5724 | 11298.5
18:30 | 5460.75 | 5669.5 | 11130.25
19:00 | 5347 | 5615 | 10962
19:30 | 5230 | 5679 | 10909
20:00 | 5134 | 5549 | 10683
20:30 | 5130.5 | 5448.775 | 10579.275 |  | Executive Engineer
21:00 | 5127 | 5348.55 | 10475.55 |  | Network Operation Division
21:30 | 5046.5 | 5251.805 | 10298.305
22:00 | 4966 | 5155.06 | 10121.06
22:30 | 4909 | 4997.11 | 9906.11
23:00 | 4852 | 4839.16 | 9691.16

## En-Curve
QF-LDC-12
Date | 29-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3005 | 1268 | 862 | 0 | 68 | 835.49 | 46 | 2519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2910.5 | 1211.6 | 815 | 0 | 70 | 835.3 | 46 | 2458 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 29-11-2025
01:00 | 2816 | 1155.2 | 768 | 0 | 72 | 835.11 | 46 | 2397 | 0 | 0 | 0 | 0 | 0 | 1 | 0
01:30 | 2724 | 1130.2 | 721 | 0 | 67 | 829.645 | 46 | 2394 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | Energy Generated | 220.0292 |  | MKWHr
02:00 | 2632 | 1105.2 | 674 | 0 | 62 | 824.18 | 46 | 2391 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2510.5 | 1048.7 | 674.5 | 0 | 62 | 824.365 | 46 | 2364.5 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | Total Energy Requirement | 220.0292 |  | MKWHr
03:00 | 2389 | 992.2 | 675 | 0 | 62 | 824.55 | 46 | 2338 | 0 | 0 | 0 | 0 | 0 | 5 | 0
03:30 | 2360 | 987.35 | 644.5 | 0 | 61 | 833.565 | 46 | 2329.5 | 0 | 0 | 0 | 0 | 0 | 4 | 0
04:00 | 2331 | 982.5 | 614 | 0 | 60 | 842.58 | 46 | 2321 | 0 | 0 | 0 | 0 | 0 | 3 | 0
04:30 | 2322 | 985 | 598.5 | 0 | 62 | 839.01 | 46 | 2304 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0
05:00 | 2313 | 987.5 | 583 | 0 | 64 | 835.44 | 46 | 2287 | 0 | 0 | 0 | 0 | 0 | 6 | 0
05:30 | 2385.5 | 1046 | 583 | 0 | 67 | 835.25 | 46 | 2336.5 | 0 | 0 | 0 | 0 | 0 | 7 | 0
06:00 | 2458 | 1104.5 | 583 | 0 | 70 | 835.06 | 46 | 2386 | 0 | 0 | 0 | 0 | 0 | 8 | 0
06:30 | 2587.5 | 1178.75 | 582.5 | 0 | 67 | 834.965 | 46 | 2572.5 | 18.345 | 0 | 5 | 0 | 0 | 7.5 | 0
07:00 | 2717 | 1253 | 582 | 0 | 64 | 834.87 | 46 | 2759 | 36.69 | 0 | 10 | 0 | 0 | 7 | 0
07:30 | 2770.5 | 1252.5 | 629.5 | 0 | 72 | 831.23 | 46 | 2857 | 118.285 | 0 | 26.5 | 0 | 0 | 9 | 0
08:00 | 2824 | 1252 | 677 | 0 | 80 | 827.59 | 46 | 2955 | 199.88 | 0 | 43 | 0 | 0 | 11 | 0
08:30 | 2721 | 1196.5 | 724 | 0 | 79 | 828.745 | 46 | 2796.5 | 300.665 | 0 | 29.5 | 0 | 0 | 6 | 0
09:00 | 2618 | 1141 | 771 | 0 | 78 | 829.9 | 46 | 2638 | 401.45 | 0 | 16 | 0 | 0 | 1 | 0
09:30 | 2544 | 1124 | 771 | 0 | 77 | 830.065 | 46 | 2623.5 | 467.12 | 1 | 24.5 | 0 | 0 | 3.5 | 0
10:00 | 2470 | 1107 | 771 | 0 | 76 | 830.23 | 46 | 2609 | 532.79 | 2 | 33 | 0 | 0 | 6 | 0
10:30 | 2493 | 1131 | 771 | 0 | 78 | 835.165 | 46 | 2599.5 | 569.22 | 13.5 | 33 | 0 | 0 | 6 | 0
11:00 | 2516 | 1155 | 771 | 0 | 80 | 840.1 | 46 | 2590 | 605.65 | 25 | 33 | 0 | 0 | 6 | 0
11:30 | 2701 | 1244.5 | 771 | 0 | 88 | 837.745 | 46 | 2628 | 609.94 | 28.5 | 33 | 0 | 0 | 6 | 0
12:00 | 2886 | 1334 | 771 | 0 | 96 | 835.39 | 46 | 2666 | 614.23 | 32 | 33 | 0 | 0 | 6 | 0
12:30 | 2859.5 | 1341.5 | 822 | 0 | 96 | 880.78 | 46 | 2803.5 | 585.23 | 33 | 88.5 | 0 | 0 | 6 | 0
13:00 | 2833 | 1349 | 873 | 0 | 96 | 926.17 | 46 | 2941 | 556.23 | 34 | 144 | 0 | 0 | 6 | 0
13:30 | 2695 | 1341.5 | 873 | 0 | 96 | 921.085 | 46 | 2883 | 508.49 | 34.5 | 188 | 0 | 0 | 6 | 0
14:00 | 2557 | 1334 | 873 | 0 | 96 | 916 | 46 | 2825 | 460.75 | 35 | 232 | 0 | 0 | 6 | 0
14:30 | 2542.5 | 1304.5 | 875.5 | 0 | 96 | 920 | 46 | 2798.5 | 386.77 | 43 | 221.5 | 0 | 0 | 6.5 | 0
15:00 | 2528 | 1275 | 878 | 0 | 96 | 924 | 46 | 2772 | 312.79 | 51 | 211 | 0 | 0 | 7 | 0
15:30 | 2594 | 1265.5 | 880 | 0 | 94 | 898 | 46 | 2857 | 217.475 | 38 | 215 | 0 | 0 | 7 | 0
16:00 | 2660 | 1256 | 882 | 0 | 92 | 872 | 46 | 2942 | 122.16 | 25 | 219 | 0 | 0 | 7 | 0
16:30 | 2693 | 1302.5 | 884.5 | 0 | 90 | 972.5 | 46 | 3092.5 | 64.185 | 33 | 244.5 | 0 | 0 | 8 | 0
17:00 | 2726 | 1349 | 887 | 0 | 88 | 1073 | 46 | 3243 | 6.21 | 41 | 270 | 0 | 0 | 9 | 0
17:30 | 2841.5 | 1390 | 887 | 0 | 93 | 1196 | 46 | 3586.5 | 3.105 | 48 | 418.25 | 0 | 0 | 9 | 0
18:00 | 2957 | 1431 | 887 | 0 | 98 | 1319 | 46 | 3930 | 0 | 55 | 566.5 | 0 | 0 | 9 | 0
18:30 | 2902 | 1423.5 | 886.5 | 0 | 95 | 1295.5 | 46 | 3903 | 0 | 44 | 527.75 | 0 | 0 | 7 | 0
19:00 | 2847 | 1416 | 886 | 0 | 92 | 1272 | 46 | 3876 | 0 | 33 | 489 | 0 | 0 | 5 | 0
19:30 | 2856 | 1443 | 887 | 0 | 88 | 1237 | 46 | 3849 | 0 | 25 | 304 | 170 | 0 | 4 | 0
20:00 | 2876 | 1445 | 887 | 0 | 82 | 1232 | 46 | 3708 | 0 | 22 | 213 | 170 | 0 | 2 | 0
20:30 | 2902.5 | 1483 | 887 | 0 | 89 | 1203.275 | 46 | 3733.5 | 0 | 16 | 133 | 85 | 0 | 1 | 0
21:00 | 2929 | 1521 | 887 | 0 | 96 | 1174.55 | 46 | 3759 | 0 | 10 | 53 | 0 | 0 | 0 | 0
21:30 | 2898.5 | 1501 | 885.5 | 0 | 98 | 1142.305 | 46 | 3662 | 0 | 12 | 53 | 0 | 0 | 0 | 0
22:00 | 2868 | 1481 | 884 | 0 | 100 | 1110.06 | 46 | 3565 | 0 | 14 | 53 | 0 | 0 | 0 | 0
22:30 | 2842.5 | 1468.5 | 884.5 | 0 | 104 | 1014.61 | 46 | 3499.5 | 0 | 7 | 39.5 | 0 | 0 | 0 | 0
23:00 | 2817 | 1456 | 885 | 0 | 108 | 919.16 | 46 | 3434 | 0 | 0 | 26 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 03:00 | 387 | 18:00 | Meghnaghat | 405 | 03:00 | 390 | 18:00
Ashuganj | 406 | 1:00 | 386 | 18:00 | Payra | 417 | 01:00 | 410 | 18:00
Bhulta | 403 | 00:00 | 384 | 18:00 | Rahanpur | 416 | 03:00 | 399 | 18:00
Bibiana | 403 | 03:00 | 392 | 18:00 | Rampal | 414 | 01:00 | 400 | 18:00
BIPTC | 407 | 01:00 | 392 | 18:00
Bogura | 409 | 04:00 | 386 | 18:00
Gopalganj | 411 | 03:00 | 396 | 18:00
Kaliakoir | 400 | 03:00 | 380 | 17:00
Korerhat | 411 | 03:00 | 397 | 17:00
Madunaghat | 407 | 01:00 | 396 | 18:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 05:00 | 232 | 12:00 | Kachua | 239 | 01:00 | 229 | 16:00
AKSML | 240 | 00:00 | 232 | 16:00 | Kaliakoir | 240 | 02:00 | 227 | 17:00
Aminbazar | 243 | 05:00 | 232 | 18:00 | Keranigonj | 241 | 03:00 | 229 | 00:00
Ashuganj | 238 | 00:00 | 229 | 18:00 | Khulna(S) | 242 | 03:00 | 230 | 18:00
Ashuganj-400 | 238 | 00:00 | 229 | 18:00 | Korerhat | 242 | 03:00 | 233 | 17:00
Baghabari | 238 | 04:00 | 227 | 18:30 | Madunaghat | 243 | 03:00 | 233 | 18:00
Barapukuria | 225 | 05:00 | 211 | 18:00 | Madunaghat-400 | 244 | 03:00 | 235 | 18:00
Barapukuria-230 | 225 | 05:00 | 211 | 18:00 | Maniknagar | 235 | 00:00 | 225 | 18:00
Barishal | 245 | 02:00 | 237 | 18:00 | Meghnaghat | 243 | 02:00 | 233 | 19:30
Bheramara | 238 | 03:00 | 223 | 18:00 | Meghnaghat-400 | 239 | 03:00 | 229 | 18:00
Bhulta | 237 | 05:00 | 225 | 18:00 | Mirsorai | 241 | 03:00 | 230 | 18:00
Bibiana | 239 | 04:00 | 229 | 18:30 | Rajshahi | 238 | 03:00 | 222 | 18:00
BIPTC | 240 | 03:00 | 223 | 18:00 | Rampal | 239 | 03:00 | 228 | 04:00
Bogura | 238 | 03:00 | 223 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 237 | 04:00 | 223 | 18:00 | Rampura | 236 | 03:00 | 224 | 18:00
Borhanuddin | 245 | 02:00 | 240 | 18:00 | Shikalbaha | 241 | 03:00 | 232 | 18:00
BSRM | 241 | 03:00 | 231 | 16:00 | Shyampur | 240 | 03:00 | 229 | 13:00
Cumilla(N) | 236 | 00:00 | 228 | 17:00 | Siddhirganj | 237 | 03:00 | 227 | 18:00
Faridpur | 244 | 03:00 | 234 | 18:00 | Sirajgonj | 242 | 04:00 | 231 | 18:00
Fenchuganj | 237 | 05:00 | 231 | 12:00 | Sreepur | 234 | 03:00 | 223 | 18:00
Feni | 236 | 00:00 | 229 | 18:00 | Tongi | 234 | 05:00 | 223 | 11:00
Ghorashal | 0 | 00:00 | N/A | N/A
Ghorashal-230 | 240 | 09:00 | 214 | 19:00
Gopalganj | 244 | 03:00 | 234 | 18:00
GPH | 243 | 03:00 | 232 | 18:00
Haripur | 237 | 03:00 | 227 | 18:00
Hasnabad | 239 | 00:00 | 230 | 12:00
Hathazari | 239 | 00:00 | 140 | 02:00
Ishurdi | 241 | 03:00 | 226 | 18:00
Jhenaidah | 240 | 03:00 | 224 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 128 | 12:00 | Lalbag | 140 | 03:00 | 130 | 18:00
Agargaon | 140 | 03:00 | 132 | 13:00 | Lalmonirhat | 132 | 03:00 | 122 | 18:00
Agrabad | 139 | 00:00 | 133 | 18:00 | Madanganj | 137 | 01:00 | 130 | 12:00
AKS | 136 | 05:00 | 132 | 12:00 | Madaripur | 139 | 09:00 | 136 | 16:00
Aminbazar | 141 | 01:00 | 134 | 11:00 | Madartek | 138 | 15:00 | 128 | 18:00
Amnura | 139 | 04:00 | 129 | 18:00 | Madunaghat | 140 | 00:00 | 135 | 18:00
Ashuganj | 142 | 00:00 | 137 | 18:00 | Magura | 140 | 05:00 | 130 | 18:00
Bagerhat | 138 | 05:00 | 128 | 18:00 | Mahasthangarh | 135 | 03:00 | 125 | 18:00
Bajitpur | 136 | 00:00 | 129 | 18:00 | Maijdee | 137 | 03:00 | 129 | 18:00
Bakulia | 141 | 05:00 | 135 | 17:00 | Manikganj | 139 | 03:00 | 122 | 16:00
Banani | 137 | 01:00 | 129 | 18:00 | Maniknagar | 140 | 01:00 | 132 | 13:00
Bangabhaban | 141 | 03:00 | 132 | 13:00 | Matarbari | 132 | 04:00 | 121 | 18:00
Barapukuria | 138 | 05:00 | 128 | 18:00 | Matuail | 139 | 06:00 | 132 | 13:00
Barguna | 136 | 00:00 | 134 | 18:00 | Metrorail_Motijheel | 140 | 01:00 | 132 | 13:00
Barishal | 140 | 03:00 | 135 | 18:30 | Metrorail_Uttara | 141 | 01:00 | 125 | 13:00
Barishal-230 | 141 | 02:00 | 135 | 18:30 | Millgate | 141 | 03:00 | 125 | 17:00
Baroaulia | 138 | 00:00 | 135 | 12:00 | Mirpur | 140 | 03:00 | 132 | 11:00
Baroirhat | 138 | 00:00 | 132 | 18:00 | Mirzapur | 138 | 03:00 | 128 | 18:00
Bashundhara | 137 | 01:00 | 127 | 18:00 | Mithapukur | 135 | 04:00 | 124 | 18:00
BashundharaCement | 137 | 01:00 | 130 | 12:00 | MI_Cement | 138 | 03:00 | 130 | 15:00
Beanibazar | 134 | 00:00 | 131 | 18:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 138 | 02:00 | 126 | 18:00 | Mogbazar | 138 | 06:00 | 131 | 18:00
Bhaluka | 136 | 04:00 | 125 | 18:00 | Mongla | 137 | 00:00 | 129 | 18:00
Bhandaria | 140 | 09:00 | 132 | 19:30 | Motijheel | 141 | 03:00 | 132 | 13:00
Bhangura | 138 | 04:00 | 130 | 18:00 | Muktagacha | 135 | 11:00 | 124 | 18:00
Bheramara | 141 | 02:00 | 135 | 18:00 | Munshiganj | 137 | 04:00 | 130 | 12:00
Bheramara(GK) | 141 | 02:00 | 135 | 18:00 | Muradnagar | 140 | 05:00 | 131 | 18:00
Bhulta | 132 | 00:00 | 127 | 18:30 | Mymensingh | 137 | 10:00 | 122 | 18:00
Bog-Sherpur | 137 | 03:00 | 127 | 18:00 | Naogaon | 135 | 04:00 | 124 | 18:00
Bogura | 136 | 05:00 | 127 | 18:00 | Narail | 141 | 03:00 | 128 | 18:00
Bogura-230 | 136 | 03:00 | 127 | 18:00 | Narinda | 0 | 00:00 | N/A | N/A
Brahmanbaria | 138 | 00:00 | 128 | 11:00 | Narshingdi | 139 | 00:00 | 126 | 18:30
Cantonment | 139 | 02:00 | 132 | 12:00 | Natore | 137 | 01:00 | 129 | 18:00
Chandina | 141 | 03:00 | 134 | 16:00 | Nawabganj | 139 | 05:00 | 131 | 17:00
Chandpur | 140 | 04:00 | 134 | 16:00 | Netrakona | 131 | 03:00 | 121 | 18:00
Chandraghona | 141 | 00:00 | 136 | 17:00 | New | 141 | 05:00 | 125 | 12:00
Chapai | 138 | 00:00 | 132 | 18:00 | Niamatpur | 140 | 02:00 | 132 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 138 | 03:00 | 132 | 12:00 | Noapara | 140 | 03:00 | 131 | 18:00
Chauddagram | 139 | 05:00 | 132 | 16:00 | Pabna | 140 | 02:00 | 132 | 18:00
Chhatak | 133 | 00:00 | 128 | 18:00 | Palashbari | 133 | 04:00 | 120 | 18:00
Chowmuhani | 135 | 01:00 | 130 | 13:00 | Panchagarh | 137 | 03:00 | 123 | 08:00
Chuadanga | 141 | 04:00 | 129 | 18:00 | Patiya | 141 | 03:00 | 134 | 15:00
Coxsbazar | 130 | 02:00 | 120 | 18:00 | Patuakhali | 137 | 03:00 | 134 | 12:00
Cumilla(N) | 140 | 00:00 | 134 | 17:00 | Payra | 137 | 00:00 | 135 | 13:00
Cumilla(S) | 140 | 05:00 | 126 | 12:00 | PHP | 139 | 03:00 | 131 | 18:00
Daganbhuiyan | 139 | 03:00 | 131 | 18:00 | Postogola | 138 | 00:00 | 132 | 11:00
Daudkandi | 137 | 03:00 | 129 | 18:00 | Purbachal | 137 | 02:00 | 129 | 18:00
DhakaUniversity | 137 | 05:00 | 130 | 12:00 | Purbasadipur | 134 | 05:00 | 123 | 17:00
Dhamrai | 141 | 01:00 | 130 | 17:00 | Rahanpur | 140 | 04:00 | 133 | 18:00
Dhanmondi | 139 | 03:00 | 131 | 13:00 | Rahanpur-400 | 140 | 02:00 | 134 | 18:00
Dohazari | 137 | 06:00 | 131 | 17:00 | Rahim | 139 | 05:00 | 132 | 18:00
Faridpur | 141 | 03:00 | 136 | 12:00 | Rajbari | 141 | 02:00 | 134 | 18:00
Fatullah | 142 | 03:00 | 131 | 12:00 | Rajendrapur | 135 | 00:00 | 128 | 18:30
Fenchuganj | 140 | 00:00 | 136 | 18:00 | Rajshahi | 137 | 02:00 | 129 | 18:00
Feni | 137 | 07:00 | 130 | 13:00 | Rajshahi-230 | 137 | 02:00 | 128 | 18:00
Feni-230 | 140 | 04:00 | 131 | 16:00 | Ramganj | 138 | 06:00 | 129 | 13:00
Ghatail | 133 | 03:00 | 122 | 18:00 | Rampur | 139 | 00:00 | 132 | 18:00
Ghorashal | 137 | 01:00 | 130 | 17:00 | Rampura | 137 | 03:00 | 129 | 13:00
Goalpara | 141 | 02:00 | 132 | 18:00 | Rangamati | 140 | 05:00 | 136 | 12:00
Gollamari | 140 | 02:00 | 133 | 18:00 | Rangpur | 134 | 04:00 | 125 | 17:00
Gopalganj | 140 | 03:00 | 133 | 18:00 | Ruppur | 140 | 04:00 | 135 | 19:30
Gopalganj-400 | 142 | 03:00 | 136 | 18:00 | Saidpur | 133 | 05:00 | 128 | 18:00
Gulshan | 136 | 00:00 | 129 | 16:00 | Satkhira | 139 | 02:00 | 128 | 18:00
Halishahar | 141 | 03:00 | 134 | 16:00 | Satmasjid | 139 | 02:00 | 131 | 13:00
Haripur | 139 | 05:00 | 133 | 12:00 | Savar | 139 | 03:00 | 132 | 11:00
HaripurSBU | 138 | 00:00 | 133 | 12:00 | SevenRings | 137 | 03:00 | 129 | 18:00
Hasnabad | 138 | 00:00 | 130 | 12:00 | ShahCement | 138 | 03:00 | 132 | 12:00
Hathazari | 140 | 00:00 | 136 | 12:00 | Shahjadpur | 141 | 01:00 | 134 | 18:00
Ishurdi | 143 | 03:00 | 135 | 18:00 | Shahjibazar | 139 | 00:00 | 131 | 11:00
Jaldhaka | 132 | 06:00 | 120 | 18:00 | Shahmirpur | 140 | 02:00 | 134 | 18:00
Jamalpur | 133 | 10:00 | 119 | 18:00 | Shariatpur | 140 | 03:00 | 134 | 18:00
Jashore | 140 | 04:00 | 127 | 18:00 | Sherpur | 132 | 15:00 | 116 | 18:00
Jhenaidah | 142 | 03:00 | 125 | 07:00 | Shikalbaha | 127 | 00:00 | 124 | 16:00
Jhenaidah-230 | 143 | 03:00 | 132 | 18:00 | Shikalbaha-230 | 141 | 00:00 | 135 | 18:00
Joydebpur | 135 | 00:00 | 126 | 18:00 | Shitalakhya | 138 | 02:00 | 130.7 | 15:00
Joypurhat | 134 | 03:00 | 122 | 18:00 | Sholosohor | 141 | 05:00 | 135 | 18:00
Juldah | 140 | 02:00 | 134 | 18:00 | Shyampur | 140 | 05:00 | 131 | 14:00
Kabirpur | 139 | 04:00 | 124 | 16:00 | Shyampur-230 | 143 | 05:00 | 136 | 12:00
Kachua | 141 | 01:00 | 136 | 19:30 | Siddhirganj | 138 | 00:00 | 133 | 12:00
Kaliakoir | 142 | 00:00 | 132 | 17:00 | Sirajganj | 136 | 02:00 | 128 | 18:00
Kallyanpur | 140 | 00:00 | 134 | 12:00 | Sonargaon | 137 | 00:00 | 132 | 12:00
Kalurghat | 143 | 03:00 | 135 | 17:00 | Sreemongol | 138 | 00:00 | 133 | 11:00
Kamrangirchar | 140 | 03:00 | 130 | 18:00 | Sreepur | 137 | 02:00 | 129 | 18:00
Kaptai | 142 | 3:00 | 138 | 20:00 | Srinagar | 139 | 03:00 | 131 | 17:00
Kasba | 138 | 03:00 | 131 | 18:00 | SSM | 1410 | 05:00 | 140 | 01:00
Kazla | 140 | 04:00 | 132 | 13:00 | Sunamganj | 132 | 04:00 | 128 | 18:00
Keranigonj | 140 | 03:00 | 131 | 13:00 | Sylhet | 135 | 07:00 | 131 | 18:00
Khagrachori | 139 | 00:00 | 134 | 18:00 | Sylhet-132 | 134 | 04:00 | 131 | 18:00
Khulna | 139 | 05:00 | 130 | 18:00 | Tangail | 133 | 04:00 | 125 | 18:00
Khulna(S) | 141 | 03:00 | 132 | 18:00 | Taraganj | 133 | 06:00 | 122 | 18:00
Khulshi | 138 | 00:00 | 132 | 18:00 | Tasnim | 137 | 00:00 | 130 | 08:00
Kishoreganj | 134 | 03:00 | 126 | 18:00 | Thakurgaon | 136 | 03:00 | 121 | 08:00
Kodda | 135 | 00:00 | 128 | 16:00 | TK | 140 | 00:00 | 135 | 18:00
KSRM | 140 | 01:00 | 134 | 16:00 | Tongi | 141 | 05:00 | 129 | 11:00
Kulaura | 139 | 00:00 | 135 | 18:00 | Ullahpara | 138 | 05:00 | 129 | 18:00
Kurigram | 131 | 03:00 | 120 | 07:00 | Ullon | 137 | 03:00 | 129 | 13:00
Kushtia | 136 | 00:00 | 127 | 18:00 | Uttara | 141 | 04:00 | 125 | 16:00
Laksam | 141 | 02:00 | 134 | 18:00 | UttaraNew | 141 | 01:00 | 125 | 13:00
Lakshmipur | 137 | 03:00 | 130 | 18:00 | Zigatola | 140 | 02:00 | 130 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division