## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-11-2025 | [28 empty] | Date: | 30-11-2025 | [28 empty] | Date: | 30-11-2025 | [28 empty] | Date: | 30-11-2025 | [28 empty] | Date: | 30-11-2025 | [17 empty] | Date: | 30-11-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Planat | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 22.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 0 | 145 | 0 | 0 | 330 | 43 | 44 | 206 | 36 | 0 | 110 | 0 | 0 | 14 | 0 | 100 | 0 | 0 | 0 | 300 | 0 | 391 | 0 | 30 | 0 | 0 | 13 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 8 | 0 | 110 | 0 | 0 | 0 | 4725.5 | 885 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 820.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 255 | 710 | 0 | 4548.72 | 9274.22 | 99.71
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 145 | 0 | 0 | 330 | 43 | 44 | 189 | 36 | 0 | 50 | 0 | 0 | 14 | 0 | 90 | 0 | 0 | 0 | 300 | 0 | 357 | 0 | 30 | 0 | 0 | 13 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 8 | 0 | 110 | 0 | 0 | 0 | 4492.5 | 791 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 828.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 256 | 560 | 0 | 4182.32 | 8674.82 | 99.71
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 34 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 0 | 0 | 118 | 0 | 0 | 330 | 5 | 16 | 203 | 36 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 335 | 0 | 30 | 0 | 0 | 13 | 0 | 5 | 20 | 0 | 15 | 159 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4159.5 | 697 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 0 | 0 | 825.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 254 | 500 | 0 | 4074.16 | 8233.66 | 99.71
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 8 | 0 | 0 | 285 | 5 | 5 | 205 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 340 | 0 | 30 | 0 | 0 | 13 | 0 | 5 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3922.5 | 696 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786 | 0 | 0 | 0 | 823.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 255 | 500 | 0 | 4049.96 | 7972.46 | 99.71
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 3 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 8 | 0 | 0 | 240 | 5 | 5 | 202 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 347 | 0 | 30 | 0 | 0 | 12 | 0 | 5 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3854.5 | 603 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 793 | 0 | 0 | 0 | 828.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 256 | 500 | 0 | 3903.97 | 7758.47 | 99.7
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 8 | 0 | 0 | 240 | 5 | 5 | 150 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 300 | 0 | 340 | 0 | 30 | 0 | 0 | 12 | 0 | 5 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3727.5 | 603 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 0 | 0 | 829.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 255 | 500 | 0 | 3915.47 | 7642.97 | 99.7
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 5 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 8 | 0 | 0 | 240 | 5 | 5 | 205 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 352 | 0 | 30 | 0 | 0 | 12 | 0 | 5 | 20 | 0 | 15 | 158 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3808.5 | 696 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 787 | 0 | 0 | 0 | 836.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 255 | 500 | 0 | 4269.41 | 8077.91 | 99.7
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 2 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 3 | 0 | 0 | 0 | 0 | 0 | 0.26 | 46 | 0 | 36 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 3 | 0 | 83 | 0 | 0 | 330 | 22 | 7 | 198 | 36 | 0 | 110 | 0 | 0 | 11 | 0 | 80 | 0 | 6 | 0 | 315 | 0 | 342 | 0 | 30 | 0 | 0 | 12 | 0 | 76 | 30 | 0 | 15 | 158 | 0 | 17 | 12 | 110 | 0 | 1.4 | 0 | 4468.66 | 792 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 813 | 0 | 0 | 0 | 832.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 4 | 0 | 0 | 2.3 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.18 | 0 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 0 | 115 | 220 | 0 | 254 | 530 | 0 | 4477.08 | 8945.74 | 99.7
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 9 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 1.27 | 46 | 0 | 14 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 9 | 0 | 145 | 0 | 0 | 330 | 43 | 23 | 207 | 38 | 0 | 110 | 0 | 0 | 11 | 0 | 94 | 0 | 26 | 0 | 310 | 0 | 342 | 0 | 30 | 0 | 0 | 12 | 0 | 76 | 30 | 0 | 15 | 158 | 0 | 35 | 19 | 110 | 1 | 10.83 | 0 | 4856.1 | 793 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 898 | 0 | 0 | 0 | 839.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.38 | 25 | 0 | 0 | 12.56 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.11 | 0 | 56 | 0 | 7 | 0 | 0 | 0 | 0 | 1.4 | 39 | 0.12 | 0 | 0 | 115 | 220 | 0 | 255 | 710 | 0 | 4850.91 | 9707.01 | 99.69
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 16 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 2.16 | 46 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 825 | 14 | 0 | 145 | 0 | 0 | 330 | 43 | 43 | 192 | 35 | 0 | 108 | 0 | 0 | 11 | 0 | 102 | 0 | 45 | 0 | 305 | 0 | 335 | 0 | 30 | 0 | 0 | 12 | 0 | 76 | 30 | 0 | 17 | 158 | 0 | 16 | 19 | 105 | 1 | 25.26 | 0 | 4684.42 | 794 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 893 | 0 | 0 | 0 | 835.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.49 | 51 | 0 | 0 | 29.92 | 176 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 2.54 | 0 | 56 | 0 | 11 | 34 | 0 | 0 | 0 | 3.6 | 74 | 0.32 | 0 | 0 | 115 | 220 | 0 | 253 | 722 | 0 | 4935.92 | 9620.34 | 99.69
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 21 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 18 | 0 | 81 | 0 | 0 | 330 | 43 | 43 | 202 | 35 | 0 | 107 | 0 | 0 | 11 | 0 | 102 | 0 | 58 | 0 | 300 | 0 | 338 | 0 | 30 | 0 | 0 | 8 | 0 | 79 | 30 | 0 | 17 | 159 | 0 | 16 | 19 | 100 | 2 | 34.81 | 0 | 4693.67 | 794 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.21 | 769 | 0 | 0 | 0 | 830.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.68 | 73 | 0 | 0 | 42.38 | 175 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 3.53 | 0 | 56 | 0 | 19 | 34 | 0 | 0 | 0 | 3.4 | 127 | 0.39 | 0 | 0 | 100 | 180 | 0 | 255 | 632 | 0 | 4800.72 | 9494.39 | 99.69
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 25 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 3.25 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 19 | 0 | 128 | 0 | 0 | 320 | 43 | 41 | 197 | 35 | 0 | 105 | 0 | 0 | 14 | 0 | 102 | 0 | 65 | 0 | 310 | 0 | 354 | 0 | 30 | 0 | 0 | 11 | 0 | 79 | 30 | 0 | 17 | 159 | 0 | 8 | 8 | 94 | 2 | 40.07 | 0 | 4833.32 | 794 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 762 | 0 | 0 | 0 | 832.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.29 | 85 | 0 | 0 | 50.35 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.07 | 0 | 56 | 0 | 20 | 34 | 0 | 0 | 0 | 3.7 | 135 | 0.45 | 0 | 0 | 115 | 220 | 0 | 253 | 656 | 0 | 4979.76 | 9813.08 | 99.69
12:00 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 25 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 3.34 | 46 | 0 | 8 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 19 | 0 | 143 | 0 | 0 | 320 | 43 | 39 | 203 | 37 | 0 | 105 | 0 | 0 | 14 | 0 | 124 | 0 | 67 | 0 | 310 | 0 | 384 | 0 | 30 | 0 | 0 | 11 | 0 | 79 | 30 | 0 | 17 | 159 | 0 | 8 | 8 | 94 | 2 | 40.33 | 0 | 4981.67 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.43 | 822 | 0 | 0 | 0 | 921.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.93 | 85 | 0 | 0 | 49.63 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.33 | 0 | 55 | 0 | 27 | 0 | 0 | 0 | 0 | 4.2 | 147 | 0.43 | 0 | 0 | 115 | 220 | 0 | 255 | 778 | 0 | 5337.85 | 10319.52 | 99.68
13:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 23 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 17 | 0 | 177 | 0 | 0 | 330 | 43 | 40 | 208 | 38 | 0 | 105 | 0 | 0 | 14 | 0 | 122 | 0 | 63 | 0 | 320 | 0 | 384 | 0 | 30 | 0 | 0 | 11 | 0 | 79 | 30 | 0 | 17 | 160 | 0 | 8 | 8 | 73 | 2 | 38.94 | 0 | 5093.07 | 889 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.27 | 907 | 0 | 0 | 0 | 929.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.75 | 80 | 0 | 0 | 48.32 | 202 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.12 | 0 | 55 | 0 | 26 | 0 | 0 | 0 | 0 | 4.7 | 139 | 0.44 | 0 | 0 | 115 | 220 | 0 | 349 | 876 | 0 | 5612.23 | 10705.3 | 99.68
14:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 15 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 46 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 955 | 15 | 0 | 153 | 0 | 0 | 260 | 43 | 42 | 209 | 38 | 0 | 105 | 0 | 0 | 14 | 0 | 118 | 0 | 50 | 0 | 310 | 0 | 409 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 17 | 158 | 0 | 8 | 8 | 74 | 1 | 22.66 | 0 | 4950.17 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 924 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.74 | 54 | 0 | 0 | 37.41 | 180 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 3.42 | 0 | 54 | 0 | 18 | 0 | 0 | 0 | 0 | 4.2 | 112 | 0.34 | 0 | 0 | 115 | 220 | 0 | 264 | 850 | 0 | 5263.11 | 10213.28 | 99.68
15:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 6 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 2 | 0 | 0 | 0 | 0 | 0 | 1.5 | 46 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 945 | 11 | 0 | 107 | 0 | 0 | 300 | 43 | 43 | 198 | 37 | 0 | 104 | 0 | 0 | 14 | 0 | 122 | 0 | 30 | 0 | 310 | 0 | 378 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 16 | 157 | 0 | 8 | 8 | 73 | 1 | 22.66 | 0 | 4839.16 | 889 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.05 | 860 | 0 | 0 | 0 | 937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.58 | 18 | 0 | 0 | 24.06 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.63 | 0 | 53 | 0 | 12 | 0 | 0 | 0 | 0 | 1.6 | 55 | 0.17 | 0 | 0 | 115 | 180 | 0 | 256 | 852 | 0 | 5143.09 | 9982.25 | 99.68
16:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 407 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 4 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 0 | 0 | 0.37 | 46 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 955 | 5 | 0 | 107 | 0 | 0 | 300 | 43 | 44 | 205 | 38 | 0 | 105 | 0 | 0 | 14 | 0 | 116 | 0 | 6 | 0 | 310 | 0 | 394 | 0 | 30 | 0 | 0 | 16 | 0 | 41 | 30 | 0 | 16 | 157 | 0 | 35 | 8 | 73 | 0 | 3.32 | 0 | 4829.69 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 853 | 0 | 0 | 0 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.84 | 17 | 0 | 0 | 6.02 | 179 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0.51 | 0 | 53 | 0 | 4 | 0 | 0 | 0 | 0 | 0.9 | 27 | 0.11 | 0 | 0 | 115 | 180 | 0 | 305 | 860 | 0 | 5067.38 | 9897.07 | 99.67
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 414 | 25 | 0 | 17 | 0 | 15 | 0 | 17 | 15 | 0 | 140 | 0 | 0 | 0 | 5 | 240 | 0 | 0 | 1 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 980 | 0 | 12 | 107 | 0 | 0 | 260 | 43 | 41 | 196 | 38 | 0 | 70 | 15 | 0 | 14 | 0 | 112 | 0 | 1 | 0 | 305 | 0 | 394 | 0 | 30 | 0 | 0 | 16 | 0 | 41 | 30 | 0 | 16 | 158 | 0 | 56 | 19 | 73 | 0 | 0.42 | 0 | 4874.42 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 877 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 1 | 0 | 0 | 0.74 | 165 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.08 | 0 | 53 | 44 | 0 | 18 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 0 | 100 | 180 | 0 | 343 | 850 | 0 | 5094.08 | 9968.5 | 99.67
18:00 | 0 | 34 | 43 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 420 | 47.3 | 0 | 52 | 0 | 45 | 0 | 35 | 48 | 0 | 140 | 0 | 0 | 0 | 30 | 240 | 0 | 0 | 0 | 17 | 21 | 4 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 32 | 0 | 46 | 0 | 4 | 354 | 0 | 0 | 0 | 0 | 29 | 45 | 0 | 0 | 0 | 1120 | 0 | 40 | 107 | 0 | 0 | 330 | 43 | 46 | 190 | 38 | 0 | 108 | 34 | 0 | 14 | 0 | 112 | 0 | 0 | 0 | 310 | 0 | 380 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 56 | 19 | 73 | 0 | 0 | 0 | 5508.3 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1018 | 0 | 0 | 0 | 1287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 54 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 502 | 900 | 0 | 5896 | 11404.3 | 99.67
19:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 411 | 39.1 | 0 | 63 | 0 | 30 | 0 | 17 | 15 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 0 | 0 | 0 | 0 | 60 | 2 | 0 | 0 | 0 | 0 | 33 | 0 | 46 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 17 | 108 | 0 | 0 | 0 | 1110 | 0 | 12 | 10 | 0 | 0 | 330 | 43 | 47 | 190 | 36 | 0 | 106 | 17 | 0 | 14 | 0 | 106 | 0 | 0 | 0 | 300 | 0 | 356 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 70 | 0 | 0 | 0 | 5141.1 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 1292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 54 | 35 | 0 | 34 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 453 | 975 | 0 | 5980 | 11121.1 | 99.67
19:30 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 401 | 15.1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 20 | 0 | 46 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1195 | 0 | 0 | 100 | 0 | 0 | 330 | 43 | 47 | 197 | 36 | 0 | 108 | 0 | 0 | 14 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 380 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 70 | 0 | 0 | 0 | 5153.1 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 405 | 970 | 0 | 5847 | 11000.1
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 400 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 46 | 0 | 16 | 354 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1087 | 0 | 0 | 118 | 0 | 0 | 330 | 43 | 47 | 195 | 39 | 0 | 108 | 0 | 0 | 14 | 0 | 116 | 0 | 0 | 0 | 305 | 0 | 372 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 57 | 19 | 68 | 0 | 0 | 0 | 5014 | 889 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1047 | 0 | 0 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 352 | 980 | 0 | 5775 | 10789 | 99.67
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 388 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 14 | 354 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1050 | 0 | 0 | 108 | 0 | 0 | 330 | 43 | 47 | 198 | 39 | 0 | 108 | 0 | 0 | 14 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 378 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 35 | 19 | 69 | 0 | 0 | 0 | 4904 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 353 | 989 | 0 | 5581 | 10485 | 99.66
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 386 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 14 | 354 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 0 | 26 | 0 | 0 | 330 | 43 | 42 | 210 | 39 | 0 | 108 | 0 | 0 | 14 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 378 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 16 | 158 | 0 | 35 | 19 | 69 | 0 | 0 | 0 | 4775.5 | 881 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 952 | 0 | 0 | 0 | 1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 355 | 960 | 0 | 5343 | 10118.5 | 99.66
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 390 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 15 | 354 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 948 | 0 | 0 | 26 | 0 | 0 | 330 | 43 | 20 | 200 | 40 | 0 | 109 | 0 | 0 | 14 | 0 | 104 | 0 | 0 | 0 | 300 | 0 | 388 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 16 | 158 | 0 | 35 | 19 | 69 | 0 | 0 | 0 | 4694.5 | 881 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 305 | 900 | 0 | 5056 | 9750.5 | 99.66
Total KWH | 0 | 99974 | 182400 | 0 | 0 | 0 | 0 | 0 | 8103600 | 0 | 9606440 | 115560 | 0 | 272304 | 0 | 86564 | 0 | 177711 | 82080 | 0 | 3344500 | 0 | 0 | 0 | 60000 | 5805412 | 0 | 0 | 152070 | 24000 | 447000 | 471960 | 0 | 0 | 6273 | 0 | 0 | 2300000 | 60000 | 0 | 0 | 0 | 0 | 105600 | 21000 | 1107000 | 0 | 285120 | 8298181.82 | 0 | 0 | 0 | 0 | 90327 | 703484 | 0 | 0 | 0 | 21152725 | 131490 | 123781 | 2090909 | 0 | 0 | 7512000 | 864128 | 755520 | 4866000 | 774000 | 0 | 2202491 | 92160 | 0 | 295610 | 0 | 2451840 | 0 | 400827 | 0 | 7488000 | 0 | 8962000 | 0 | 713400 | 0 | 31283 | 353064 | 0 | 1418880 | 665376 | 0 | 386000 | 3324550 | 0 | 546000 | 256800 | 2073600 | 10800 | 242630 | 0 | 112194424.82 | 19696727 | 6332544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421920 | 20785460 | 0 | 0 | 0 | 22505363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270960 | 511220 | 0 | 0 | 305264 | 3470909 | 0 | 0 | 0 | 0 | 0 | 9077890 | 0 | 25200 | 0 | 1284654 | 112888 | 148760 | 218688 | 0 | 358345 | 0 | 27855.6 | 819360 | 2748 | 0 | 0 | 2684000 | 4825310 | 0 | 7154097 | 18704000 | 0 | 119744162.6 | 231938587.42

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-11-2025 | during | 01-12-2025 | during | 01-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 328 | 333 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 140 | 140 | 450 | 450 | 220 | 220 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 47.3 | 53.97 | 53.97 | 17 | 17 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 30 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 4 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 43 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 52 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 5 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 48 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 402 | 420 | 718 | 718 | 718 | 718 | FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1215 | 1509.3 | 5769.1 | 5738.1 | 3366.11 | 3344.11
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 120 | 130 | 120 | 120 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 45 | 0 | 0 | 145 | 145 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 29 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 48 | 40 | 48 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 4 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.34 | 0 | 3.25 | 0 | 3.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 32 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 950 | 1120 | 612 | 612 | 1224 | 1224 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 5 | 0 | 5 | 0 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 353 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1499.34 | 1765 | 2496.97 | 2491.72 | 2788.75 | 2783.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 190 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 320 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 38 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 39 | 46 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 143 | 107 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 40 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 108 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 34 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 112 | 160 | 160 | 108 | 108 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1095 | 1062 | 2432.21 | 2372.21 | 1924.21 | 1864.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-11-2025 | during | 01-12-2025 | during | 01-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 94 | 73 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 56 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.33 | 0 | 44.07 | 0 | 44.07 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 152.33 | 148 | 360.17 | 314 | 312.67 | 266.5
| Moulvibazar 10 MW Solar Power Planat | Solar | IPP | 1*10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 157 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 11 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 384 | 380 | 385 | 385 | 357 | 357 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1020 | 1024 | 1075 | 1075 | 1013 | 1013
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 888 | 888 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71.43 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 822 | 1018 | 0 | 0 | 1100 | 1100 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2031.43 | 2156 | 2352 | 2272 | 2697.1 | 2617.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 255 | 502 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 778 | 900 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 110 | 110 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.43 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1368.43 | 1737 | 1576.32 | 1576.32 | 1553.32 | 1553.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 45.93 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 184 | 179 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 384 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.33 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 921.9 | 1287 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.63 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 85 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1704.79 | 1850 | 3076.97 | 2911.87 | 2981.59 | 2816.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 54 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 147 | 0 | 123.35 | 0 | 123.35 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 233.2 | 153 | 475.55 | 317 | 441.55 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 10319.52 | 11404.3 | 19614.29 | 19068.22 | 17078.3 | 16541.23
Forecast Scenario (01-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9270 |  | 0 |  | 9270
|  |  |  | 1:00 | 8670 |  | 0 |  | 8670
|  |  |  | 2:00 | 8230 |  | 0 |  | 8230
|  |  |  | 3:00 | 7970 |  | 0 |  | 7970
|  |  |  | 4:00 | 7750 |  | 0 |  | 7750
|  |  |  | 5:00 | 7640 |  | 0 |  | 7640
|  |  |  | 6:00 | 8070 |  | 0 |  | 8070
|  |  |  | 7:00 | 8940 |  | 0 |  | 8940
|  |  |  | 8:00 | 9700 |  | 0 |  | 9700
|  |  |  | 9:00 | 9620 |  | 0 |  | 9620
|  |  |  | 10:00 | 9490 |  | 0 |  | 9490
|  |  |  | 11:00 | 9810 |  | 0 |  | 9810
|  |  |  | 12:00 | 10320 |  | 0 |  | 10320
|  |  |  | 13:00 | 10700 |  | 0 |  | 10700
|  |  |  | 14:00 | 10210 |  | 0 |  | 10210
|  |  |  | 15:00 | 9980 |  | 0 |  | 9980
|  |  |  | 16:00 | 9890 |  | 0 |  | 9890
|  |  |  | 17:00 | 9960 |  | 0 |  | 9960
|  |  |  | 18:00 | 11400 |  | 0 |  | 11400
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11120 |  | 0 |  | 11120
|  |  |  | 19:30 | 11000 |  | 0 |  | 11000
|  |  |  | 20:00 | 10780 |  | 0 |  | 10780
|  |  |  | 21:00 | 10480 |  | 0 |  | 10480
|  |  |  | 22:00 | 10110 |  | 0 |  | 10110
|  |  |  | 23:00 | 9700 |  | 0 |  | 9700
Probable Maximum Temperature: |  |  | 29.50°C
Probable Maximum Demand at Day Peak: |  |  | 10320.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 229.81 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:25 hrs on 01-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-11-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10319.52 | MW | 12:00 Hr. | Energy Generated |  |  | 231.9386 |  | MKWHr.
| Day Peak Demand |  |  | 10319.52 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11404.3 | MW | 18:00 Hr. | Energy Demand |  |  | 231.9386 |  | MKWHr.
| Evening Peak Demand |  |  | 11404.3 | MW | 18:00 Hr. | Maximum Temperature |  |  | 29.4 |  | °C
| Minimum Generation of the Day |  |  | 7642.97 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 757.85 |  | MMCFD
| Maximum Generation of the Day |  |  | 11404.3 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.3224 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 27.7789 | 0 | 1.1006 | 0 | 0 | 0.15207 | 0 | 0 | 29.0316 | Gas | 102.2037 | Gas | 369353505.67
| Chattogram Zone |  |  | 3.2886 | 29.4509 | 0.2022 | 0 | 1.107 | 0.15249 | 0 | 0.06 | 34.2612 | Coal | 77.3791 | Coal | 487929273.4454
| Cumilla Zone |  |  | 19.3607 | 0 | 0.21594 | 0 | 0 | 0.40083 | 2.4518 | 0 | 22.4293 | HFO | 2.6531 | HFO | 45360847.33
| Mymensingh Zone |  |  | 2.0736 | 0 | 0.8028 | 0 | 0 | 0.25343 | 0 | 0 | 3.1298 | HSD | 0.35835 | HSD | 9815069.55
| Sylhet Zone |  |  | 23.3113 | 0 | 0 | 0 | 0 | 0.031283 | 0 | 0 | 23.3426 | Hydro | 1.107 | Hydro | 110700
| Khulna Zone |  |  | 6.3325 | 20.7855 | 0 | 0 | 0 | 0.42192 | 19.6967 | 0 | 47.2367 | Solar | 3.5234 | Solar | 55656586.306
| Barishal Zone |  |  | 7.5093 | 25.8581 | 0 | 0 | 0 | 0.002748 | 0 | 0 | 33.3702 | Import | 44.6539 | Import | 265366662.32
| Rajshahi Zone |  |  | 12.5488 | 0 | 0 | 0 | 0 | 1.1126 | 22.5054 | 0 | 36.1668 | Wind | 0.06 | Wind | 882600
| Rangpur Zone |  |  | 0 | 1.2847 | 0.33158 | 0.35835 | 0 | 0.99598 | 0 | 0 | 2.9706
| Total |  |  | 102.2037 | 77.3791 | 2.6531 | 0.35835 | 1.107 | 3.5234 | 44.6539 | 0.06 | 231.9386
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 369353505.67 |  | Hydro | 110700
|  |  |  | Coal | 487929273.4454 |  | Solar | 55656586.306
|  |  |  | HFO | 45360847.33 |  | Import | 265366662.32
|  |  |  | HSD | 9815069.55 |  | Wind | 882600
[5 empty] | Total: | 123,44,75,244 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.6967 | Peak Hr Flow | 888.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46262609.48 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.5054 | Peak Hr Flow | 1287.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2463 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4518 | Peak Hr Flow | 112.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2590 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.6539 | Peak Hr Flow | 2287.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4231
|  |  |  | Chattogram |  | 0 |  | 1235
|  |  |  | Cumilla |  | 0 |  | 907
|  |  |  | Mymensingh |  | 0 |  | 834
|  |  |  | Sylhet |  | 0 |  | 398
|  |  |  | Khulna |  | 0 |  | 1266
|  |  |  | Barishal |  | 0 |  | 314
|  |  |  | Rajshahi |  | 0 |  | 979
|  |  |  | Rangpur |  | 0 |  | 757
|  |  |  | Total |  | 0 |  | 10921
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 |  | Bakulia-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Bakulia 132/33kV end Due to Annual
maintenance and from Shikalbaha 230/132kVend.
| 08:06 | 23:08 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Yearly
maintenance. and from Bhandaria 132/33kV end Due to Annual Maintenance
| 08:16 | 17:35 | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
| 08:18 | 17:34 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-02 Scheduled S/D Due to Annual maintenance
| 08:29 | 09:08 | Chapai 132/33kV S/S T-2 (415T) LT Tripped showing P142 relays Due to Feeder CB fault | [7 empty] | 15.0MW load
interrup.
| 08:29 | 09:09 | Chapai 132/33kV S/S T-3 (425T) LT Tripped showing P142 relays. | [7 empty] | 15.0MW load
interrup.
| 08:39 | 12:20 | Bogura 230/132kV S/S T-01 LT Scheduled S/D Due to Annual Maintenance
| 08:39 | 12:20 | Bogura 230/132kV S/S T-01 HT Scheduled S/D Due to Annual Maintenance
| 08:45 | 17:14 | Haripur 230/132kV S/S Bus-1 Scheduled S/D Due to Annual Maintenance.
| 08:52 | 16:52 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to 132 KV bay
equipment maintenance ( Porthead tower no 47&48 LA measurement) work.
| 08:53 | 15:24 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Scheduled S/D Due to Annual
Maintenance
| 08:55 | 16:52 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV
end Due to Annual maintenance work
| 08:57 | 15:45 | Khulna (C) S/S North- West Ckt-2 Scheduled S/D Due to For Annual Maintenance.
| 09:00 | 16:06 | Barapukuria S/S-P/S 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual Maintenance work
|  | 09:02 | Brahmanbaria 132/33kV S/S 403T LT is restored.
| 09:04 | 17:09 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Ghatail 132/33kV end Due to
Annual Maintenance. and from Muktagacha 132/33kV end Due to Annual maintenances
| 09:06 | 13:50 | Fenchuganj 230/132/33kV S/S TR-02 LT Scheduled S/D Due to Annual Maintenance
| 09:11 | 13:42 | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to Annual Maintenance
| 09:14 | 09:45 | Uttara 132/33kV S/S GT-01 LT Scheduled S/D Due to Due to annual maintenance.
| 09:15 | 09:45 | Uttara 132/33kV S/S GT-01 LT Scheduled S/D Due to Due to maintenance.
| 09:15 | 09:45 | Uttara 132/33kV S/S GT-01 LT Scheduled S/D Due to Due to annual maintenance.
| 09:15 | 18:17 | Uttara 132/33kV S/S GT-01 HT Scheduled S/D Due to Due to annual maintenance.
| 09:22 | 16:18 | Savar 132/33kV S/S Main Bus-I Scheduled S/D Due to Annual maintenance
| 09:24 | 16:53 | Naogaon 132/33kV S/S Nao-SPPP Ckt-1 Scheduled S/D Due to Annual Maintenance.
| 09:27 | 16:22 | Savar 132/33kV S/S T-4 LT Scheduled S/D Due to Annual maintenance
| 09:28 | 16:22 | Savar 132/33kV S/S T-4 HT Scheduled S/D Due to Annual maintenance
| 09:32 |  | BIPTC S/S 10CF21 Scheduled S/D Due to annual maintenance
| 09:35 | 15:28 | Brahmanbaria 132/33kV S/S 402T LT Scheduled S/D
| 09:35 | 15:28 | Brahmanbaria 132/33kV S/S 402T HT Scheduled S/D
|  | 09:51 | Uttara 132/33kV S/S GT-02 HT is restored.
| 09:56 | 17:17 | Tongi 230/132/33kV S/S Tongi-Dhaka Metro Rail Ckt Scheduled S/D Due to Annual maintenance
work
| 10:28 | 13:50 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D Due to Annual maintenance
| 10:30 | 13:50 | Bajitpur 132/33kV S/S Tr-1(404T) HT Scheduled S/D Due to Annual maintenance
| 11:29 | 12:10 | Chowmuhani 132/33kV S/S TR2 Tripped showing Directional E/F relays Due to 33kv | [7 empty] | 28.0MW load
|  |  | Lakshmipur-01 fault . | [7 empty] | interrup.
| 11:29 | 11:42 | Chowmuhani 132/33kV S/S TR3-435T LT Tripped showing O/C, E/F relays Due to 33kv | [7 empty] | 28.0MW load
|  |  | Lakshmipur PBS-01 | [7 empty] | interrup.
|  | 12:20 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 is restored.
|  | 12:20 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 is restored.
|  | 13:50 | Bogura 132/33kV S/S Transformer-4 HT is restored.
|  | 13:51 | Bogura 132/33kV S/S Transformer-4 LT is restored.
| 14:38 | 16:16 | Chowmuhani 132/33kV S/S TR3-435T LT Forced S/D Due to 33kV LPBS-1 feeder bus loop | [7 empty] | 35.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 14:38 | 16:15 | Chowmuhani 132/33kV S/S TR3-435T HT Forced S/D Due to 33kV LPBS-1 feeder bus loop | [7 empty] | 35.0MW load
|  |  | maintenance. | [7 empty] | interrup.
|  | 15:24 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 is restored.
|  | 15:33 | Chhatak 132/33kV S/S T-3 HT is restored.
|  | 15:35 | Chhatak 132/33kV S/S T-3 LT is restored.
|  | 15:36 | Natore-Rajshahi 132kV Ckt-2 is restored.
| 16:07 | 17:00 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing Lockout SPS relays Due to None | [7 empty] | 52.0MW load
interrup.
| 16:07 | 16:59 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing lockout SPS relays. | [7 empty] | 62.0MW load
interrup.
|  | 16:22 | Savar 132/33kV S/S T-4 HT is restored.
|  | 16:30 | Mahasthangarh 132/33kV S/S 406T MTR1 LT is restored.
|  | 16:30 | Mahasthangarh 132/33kV S/S 406T MTR1 HT is restored.
|  | 16:30 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
| 17:05 |  | Amtoli 400KV Main Bus-1 S/D Withdraw.
|  | 17:09 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) HT is restored.
|  | 17:10 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) LT is restored.
|  | 17:17 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT is restored.
|  | 17:17 | Kabirpur - Manikganj 132kV Ckt-2 is restored.
| 17:35 |  | Shikalbaha 225 MW CCPP GT was synchronized
| 18:00 |  | Evening peak generation 11404 MW
| 18:00 |  | Evening peak generation is 11404 MW.
|  | 18:32 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 19:04 |  | Barapukuria- Purbasadipur 230 KV ckt-1 syn.
| 19:16 |  | 230/132 KV T1 syn Purbadadipur 230/132/33 KV S/S.
| 19:16 |  | Raozan unit-2 was shut down
| 19:19 |  | Barapukuria- Purbasadipur 230 KV ckt-2 charge from Purbasadipur.
| 19:31 |  | 230/132 KV T2 syn Purbadadipur 230/132/33 KV S/S.
| 19:34 |  | 132 KV Bus C syn Purbadadipur 230/132/33 KV S/S.
|  | 20:44 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
|  | 20:44 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
| 23:10 | 23:12 | Tongi 230/132/33kV S/S Tongi-Dhaka Metro Rail Ckt Scheduled S/D Due to Only breaker open,
instructed by NLDC sde
| 05:00 |  | Minimum Generation: 7737 MW.
| 06:42 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Annual maintenance
| 06:42 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Annual maintenance
| 07:43 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to Annual Maintenance
| 07:44 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to Annual Maintenance
| 07:45 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT Scheduled S/D Due to A/M
| 07:46 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT Scheduled S/D Due to A/M
| 07:56 |  | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D Due to 33 kv bus -1 auxiliary | [7 empty] | 25.0MW load
|  |  | transformer loop repair | [7 empty] | interrup.
| 07:58 |  | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D Due to 33kv bus-1 auxiliary | [7 empty] | 25.0MW load
|  |  | transformer loop repair | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-11-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 333 | 8103600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 140 | 3344500 | U-1 under S/D (Instruction of PDB)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5805412 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.3 | 115560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 177711 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 30 | 60000 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 447000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 4 | 471960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 43 | 182400 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 86564 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 52 | 272304 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 99974 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 48 | 82080 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 152070 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 420 | 9606440 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 24000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 1509.3 | 29031575
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 130 | 2300000 | Unit #1 Under Maintenance,Unit #2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 131490 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1107000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 45 | 703484 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 29 | 90327 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 4 | 285120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 32 | 105600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 6273 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1120 | 21152725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 60000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 8298181.82 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1765 | 34261200.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4866000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7512000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 38 | 774000 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 755520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 107 | 2090909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 864128 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 123781 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2202491 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 92160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 112 | 2451840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 295610 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 400827 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1062 | 22429266
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 73 | 2073600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 256800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 546000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 242630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 148 | 3129830
| Moulvibazar 10 MW Solar Power Planat |  | IPP | 1*10 | 0 | 0 | 31283 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 713400 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 665376 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1418880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 3324550 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 386000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 353064 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7488000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 8962000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1024 | 23342553
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 888 | 19696727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6332544 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 421920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1018 | 20785460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2156 | 47236651
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 502 | 7154097 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2684000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 900 | 18704000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 4825310 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2748 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1737 | 33370155
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 270960 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 179 | 3470909 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 384 | 9077890 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1287 | 22505363 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 305264 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 511220 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1850 | 36166806
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 358345 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1284654 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 218688 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27855.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 112888 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 148760 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 819360 | -
Rangpur Area Total |  |  |  |  | 950 | 153 | 2970550.6
Eastern Grid Total |  |  |  |  | 17383.855 | 5508.3 | 112194424.82
Western Grid Total |  |  |  |  | 10821.56 | 5896 | 119744162.6
National Grid Total |  |  |  |  | 28205.415 | 11404.3 | 231938587.42
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-11-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7604.76 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3315.8 | MW
i) Dhaka area |  |  | 4230.56 |  | MW | i) Khulna area |  |  |  | 1265.6 | MW
ii) Chattogram area |  |  | 1235.2 |  | MW | ii) Barishal area |  |  |  | 314 | MW
iii) Cumilla area |  |  | 907 |  | MW | iii) Rajshahi area |  |  |  | 979.2 | MW
iv) Mymensingh area |  |  | 834 |  | MW | iv) Rangpur area |  |  |  | 757 | MW
v) Sylhet area |  |  | 398 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10920.56 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 16:00 | 67 | Hathazari | 56 | 19:00 | 133 | Niamatpur | 41 | 18:00
2 | AKSML | 107 | 23:00 | 68 | Ishurdi | 58 | 18:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 52 | 18:00 | 135 | PHP | 9 | 15:00
4 | Agargaon | 93 | 13:00 | 70 | Jamalpur | 93 | 18:00 | 136 | Pabna | 68 | 18:30
5 | Agrabad | 60 | 18:00 | 71 | Jashore | 102 | 13:00 | 137 | Palashbari | 84 | 18:00
6 | Amnura | 17 | 19:30 | 72 | Jhenaidah | 96 | 18:00 | 138 | Panchagarh | 46 | 18:00
7 | Ashuganj | 58 | 13:00 | 73 | Joydebpur | 115 | 12:00 | 139 | Patiya | 5.2 | 18:00
8 | BSRM | 204 | 03:00 | 74 | Joypurhat | 46 | 18:00 | 140 | Patuakhali | 47 | 20:00
9 | Bagerhat | 64 | 18:00 | 75 | Juldah | 12 | 11:00 | 141 | Payra | 24 | 18:30
10 | Bajitpur | 57 | 19:00 | 76 | KSRM | 28 | 07:00 | 142 | Postogola | 51 | 13:00
11 | Bakulia | 60 | 18:00 | 77 | Kabirpur | 182 | 18:00 | 143 | Purbachal | 28 | 12:00
12 | Banani | 48 | 13:00 | 78 | Kachua | 55 | 20:00 | 144 | Purbasadipur | 101 | 18:00
13 | Bangabhaban | 16 | 12:00 | 79 | Kallyanpur | 69 | 12:00 | 145 | Rahanpur | 21 | 18:30
14 | Barapukuria | 53 | 18:00 | 80 | Kalurghat | 38 | 10:00 | 146 | Rahim | 33 | 15:00
15 | Barguna | 12 | 00:00 | 81 | Kamrangirchar | 64 | 13:00 | 147 | Rajbari | 55 | 18:00
16 | Barishal | 87 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 107 | 18:00
17 | Barishal-230 | 66 | 20:00 | 83 | Kasba | 22 | 21:00 | 149 | Rajshahi | 81 | 13:00
18 | Baroaulia | 53 | 09:00 | 84 | Kazla | 78 | 02:00 | 150 | Rajshahi-230 | 42 | 13:00
19 | Baroirhat | 48 | 18:00 | 85 | Keranigonj | 65 | 13:00 | 151 | Ramganj | 64 | 19:30
20 | Bashundhara | 147 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 29 | 17:00
21 | BashundharaCement | 12 | 11:00 | 87 | Khulna | 53 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 164 | 15:00 | 154 | Rangpur | 104 | 18:00
23 | Benapole | 44 | 08:00 | 89 | Kishoreganj | 82 | 18:00 | 155 | Ruppur | 3.4 | 10:00
24 | Bhaluka | 115 | 18:30 | 90 | Kodda | 257 | 18:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 37 | 20:00 | 91 | Kulaura | 29 | 18:00 | 157 | Saidpur | 93 | 18:00
26 | Bhangura | 23 | 18:00 | 92 | Kurigram | 46 | 18:30 | 158 | Satkhira | 80 | 18:00
27 | Bheramara(GK) | 43 | 18:00 | 93 | Kushtia | 113 | 18:00 | 159 | Satmasjid | 77 | 18:00
28 | Bhulta | 184 | 18:30 | 94 | Laksam | 22 | 19:30 | 160 | Savar | 234 | 16:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 23 | 21:00 | 161 | SevenRings | 12.99 | 01:00
30 | Bogura | 112 | 18:30 | 96 | Lalbag | 57 | 17:00 | 162 | ShahCement | 21 | 00:00
31 | Borhanuddin | 63 | 21:00 | 97 | Lalmonirhat | 48 | 18:00 | 163 | Shahjadpur | 58 | 18:00
32 | Brahmanbaria | 84 | 18:00 | 98 | MI_Cement | 17.5 | 23:00 | 164 | Shahjibazar | 78 | 18:00
33 | Cantonment | 76 | 13:00 | 99 | Madanganj | 34 | 15:00 | 165 | Shahmirpur | 37 | 18:00
34 | Chandina | 0 | 00:00 | 100 | Madaripur | 67 | 21:00 | 166 | Shariatpur | 54 | 20:00
35 | Chandpur | 48 | 18:00 | 101 | Madartek | 60 | 13:00 | 167 | Sherpur | 96 | 07:00
36 | Chandraghona | 26 | 18:00 | 102 | Madunaghat | 37 | 18:00 | 168 | Shikalbaha | 22 | 12:00
37 | Chapai | 48 | 18:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 63.1 | 12:00
38 | Charsaidpur | 36 | 12:00 | 104 | Mahasthangarh | 48 | 18:00 | 170 | Sholosohor | 33 | 11:00
39 | Chauddagram | 47 | 21:00 | 105 | Maijdee | 22 | 21:00 | 171 | Shyampur | 134 | 13:00
40 | Chhatak | 23 | 18:30 | 106 | Manikganj | 88 | 18:00 | 172 | Siddhirganj | 99 | 12:00
41 | Chowmuhani | 105 | 18:00 | 107 | Maniknagar | 48 | 13:00 | 173 | Sirajganj | 81 | 19:00
42 | Chuadanga | 72 | 18:00 | 108 | Matarbari | 37 | 18:00 | 174 | Sonargaon | 114 | 16:00
43 | Coxsbazar | 97 | 18:00 | 109 | Matuail | 55.4 | 10:00 | 175 | Sreemongol | 48 | 18:00
44 | Cumilla(N) | 88 | 18:00 | 110 | Metrorail_Motijheel | 35 | 10:00 | 176 | Sreepur | 75 | 19:00
45 | Cumilla(S) | 124 | 12:00 | 111 | Metrorail_Uttara | 7 | 13:00 | 177 | Srinagar | 30.9 | 14:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 86 | 12:00 | 178 | Sunamganj | 37 | 18:00
47 | Daudkandi | 106 | 18:00 | 113 | Mirpur | 115 | 12:00 | 179 | Sylhet | 33 | 18:00
48 | DhakaUniversity | 66 | 13:00 | 114 | Mirsorai | 37 | 14:00 | 180 | Sylhet-132 | 90 | 13:00
49 | Dhamrai | 100 | 16:00 | 115 | Mirzapur | 37 | 07:00 | 181 | TK | 15 | 00:00
50 | Dhanmondi | 86.7 | 13:00 | 116 | Mithapukur | 44 | 08:00 | 182 | Tangail | 114 | 19:00
51 | Dohazari | 67 | 18:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 15 | 18:00
52 | Faridpur | 111 | 18:00 | 118 | Mogbazar | 67.1 | 15:00 | 184 | Tasnim | 16 | 12:00
53 | Fatullah | 96 | 11:00 | 119 | Mongla | 46 | 18:00 | 185 | Thakurgaon | 79 | 18:00
54 | Fenchuganj | 25 | 13:00 | 120 | Motijheel | 29 | 13:00 | 186 | Tongi | 96 | 11:00
55 | Feni | 65 | 13:00 | 121 | Muktagacha | 26 | 18:00 | 187 | Ullahpara | 25 | 18:00
56 | GPH | 73 | 03:00 | 122 | Munshiganj | 85 | 19:00 | 188 | Ullon | 52 | 13:00
57 | Ghatail | 60 | 07:00 | 123 | Muradnagar | 24 | 18:00 | 189 | Uttara | 62 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 132 | 17:00 | 190 | UttaraNew | 13 | 13:00
59 | Ghorashal-230 | 78 | 19:30 | 125 | Naogaon | 82 | 13:00 | 191 | Zigatola | 58 | 13:00
60 | Goalpara | 27 | 07:00 | 126 | Narail | 38 | 18:00
61 | Gollamari | 68 | 13:00 | 127 | Narinda | 54 | 12:00
62 | Gopalganj | 76.6 | 18:00 | 128 | Narshingdi | 138 | 20:00
63 | Gulshan | 84 | 13:00 | 129 | Natore | 101 | 18:00
64 | Halishahar | 67 | 15:00 | 130 | Nawabganj | 28.8 | 20:00
65 | HaripurSBU | 130 | 09:00 | 131 | Netrakona | 104 | 18:00
66 | Hasnabad | 73 | 12:00 | 132 | New | 58.8 | 11:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-11-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9274.22 | 0 |  | 9274.22
1:00 | 8674.82 | 0 |  | 8674.82
2:00 | 8233.66 | 0 |  | 8233.66
3:00 | 7972.46 | 0 |  | 7972.46
4:00 | 7758.47 | 0 |  | 7758.47
5:00 | 7642.97 | 0 |  | 7642.97
6:00 | 8077.91 | 0 |  | 8077.91
7:00 | 8945.74 | 0 |  | 8945.74
8:00 | 9707.01 | 0 |  | 9707.01
9:00 | 9620.34 | 0 |  | 9620.34
10:00 | 9494.39 | 0 |  | 9494.39
11:00 | 9813.08 | 0 |  | 9813.08
12:00 | 10319.52 | 0 |  | 10319.52
13:00 | 10705.3 | 0 |  | 10705.3
14:00 | 10213.28 | 0 |  | 10213.28
15:00 | 9982.25 | 0 |  | 9982.25
16:00 | 9897.07 | 0 |  | 9897.07
17:00 | 9968.5 | 0 |  | 9968.5
18:00 | 11404.3 | 0 |  | 11404.3
19:00 | 11121.1 | 0 |  | 11121.1
19:30 | 11000.1 | 0 |  | 11000.1
20:00 | 10789 | 0 |  | 10789
21:00 | 10485 | 0 |  | 10485
22:00 | 10118.5 | 0 |  | 10118.5
23:00 | 9750.5 | 0 |  | 9750.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-11-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4725.5 | 4548.72 | 9274.22 | DAILY GENERATION CURVE
00:30 | 4609 | 4365.52 | 8974.52
01:00 | 4492.5 | 4182.32 | 8674.82 | 30-11-2025
01:30 | 4326 | 4128.24 | 8454.24
02:00 | 4159.5 | 4074.16 | 8233.66
02:30 | 4041 | 4062.06 | 8103.06
03:00 | 3922.5 | 4049.96 | 7972.46
03:30 | 3888.5 | 3976.965 | 7865.465
04:00 | 3854.5 | 3903.97 | 7758.47
04:30 | 3791 | 3909.72 | 7700.72
05:00 | 3727.5 | 3915.47 | 7642.97
05:30 | 3768 | 4092.44 | 7860.44
06:00 | 3808.5 | 4269.41 | 8077.91
06:30 | 4138.58 | 4373.245 | 8511.825
07:00 | 4468.66 | 4477.08 | 8945.74
07:30 | 4662.38 | 4663.995 | 9326.375
08:00 | 4856.1 | 4850.91 | 9707.01
08:30 | 4770.26 | 4893.415 | 9663.675
09:00 | 4684.42 | 4935.92 | 9620.34
09:30 | 4689.045 | 4868.32 | 9557.365
10:00 | 4693.67 | 4800.72 | 9494.39
10:30 | 4763.495 | 4890.24 | 9653.735
11:00 | 4833.32 | 4979.76 | 9813.08
11:30 | 4907.495 | 5158.805 | 10066.3
12:00 | 4981.67 | 5337.85 | 10319.52
12:30 | 5037.37 | 5475.04 | 10512.41
13:00 | 5093.07 | 5612.23 | 10705.3
13:30 | 5021.62 | 5437.67 | 10459.29
14:00 | 4950.17 | 5263.11 | 10213.28
14:30 | 4894.665 | 5203.1 | 10097.765
15:00 | 4839.16 | 5143.09 | 9982.25
15:30 | 4834.425 | 5105.235 | 9939.66
16:00 | 4829.69 | 5067.38 | 9897.07
16:30 | 4852.055 | 5080.73 | 9932.785
17:00 | 4874.42 | 5094.08 | 9968.5
17:30 | 5191.36 | 5495.04 | 10686.4
18:00 | 5508.3 | 5896 | 11404.3
18:30 | 5324.7 | 5938 | 11262.7
19:00 | 5141.1 | 5980 | 11121.1
19:30 | 5153.1 | 5847 | 11000.1
20:00 | 5014 | 5775 | 10789
20:30 | 4959 | 5678 | 10637 |  | Executive Engineer
21:00 | 4904 | 5581 | 10485 |  | Network Operation Division
21:30 | 4839.75 | 5462 | 10301.75
22:00 | 4775.5 | 5343 | 10118.5
22:30 | 4735 | 5199.5 | 9934.5
23:00 | 4694.5 | 5056 | 9750.5

## En-Curve
QF-LDC-12
Date | 30-11-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2871 | 1495.5 | 885 | 0 | 100 | 820.72 | 46 | 3048 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2773 | 1474.5 | 838 | 0 | 95 | 824.52 | 46 | 2915.5 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 30-11-2025
01:00 | 2675 | 1453.5 | 791 | 0 | 90 | 828.32 | 46 | 2783 | 0 | 0 | 8 | 0 | 0 | 0 | 0
01:30 | 2690 | 1383 | 744 | 0 | 86 | 826.74 | 46 | 2674.5 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | Energy Generated | 231.9386 |  | MKWHr
02:00 | 2705 | 1312.5 | 697 | 0 | 82 | 825.16 | 46 | 2566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2677 | 1220 | 696.5 | 0 | 80 | 824.56 | 46 | 2558 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Total Energy Requirement | 231.9386 |  | MKWHr
03:00 | 2649 | 1127.5 | 696 | 0 | 78 | 823.96 | 46 | 2550 | 0 | 0 | 0 | 0 | 0 | 2 | 0
03:30 | 2594 | 1127.5 | 649.5 | 0 | 80 | 826.465 | 46 | 2537 | 0 | 0 | 0 | 0 | 0 | 5 | 0
04:00 | 2539 | 1127.5 | 603 | 0 | 82 | 828.97 | 46 | 2524 | 0 | 0 | 0 | 0 | 0 | 8 | 0
04:30 | 2516.5 | 1121.5 | 603 | 0 | 83 | 829.22 | 46 | 2493 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0
05:00 | 2494 | 1115.5 | 603 | 0 | 84 | 829.47 | 46 | 2462 | 0 | 0 | 0 | 0 | 0 | 9 | 0
05:30 | 2640 | 1142 | 649.5 | 0 | 82 | 832.94 | 46 | 2460 | 0 | 0 | 0 | 0 | 0 | 8 | 0
06:00 | 2786 | 1168.5 | 696 | 0 | 80 | 836.41 | 46 | 2458 | 0 | 0 | 0 | 0 | 0 | 7 | 0
06:30 | 2903 | 1260.75 | 744 | 0 | 80 | 834.655 | 46 | 2607.5 | 16.42 | 0 | 14.5 | 0 | 0 | 5 | 0
07:00 | 3020 | 1353 | 792 | 0 | 80 | 832.9 | 46 | 2757 | 32.84 | 0 | 29 | 0 | 0 | 3 | 0
07:30 | 3022.5 | 1403.5 | 792.5 | 0 | 87 | 836.12 | 46 | 2990 | 105.255 | 0 | 41.5 | 0 | 0 | 2 | 0
08:00 | 3025 | 1454 | 793 | 0 | 94 | 839.34 | 46 | 3223 | 177.67 | 0 | 54 | 0 | 0 | 1 | 0
08:30 | 2968.5 | 1432.5 | 793.5 | 0 | 98 | 837.195 | 46 | 3163 | 262.48 | 0 | 61.5 | 0 | 0 | 1 | 0
09:00 | 2912 | 1411 | 794 | 0 | 102 | 835.05 | 46 | 3103 | 347.29 | 0 | 69 | 0 | 0 | 1 | 0
09:30 | 2915 | 1368.5 | 794 | 0 | 102 | 832.59 | 46 | 3004.5 | 425.275 | 0 | 69 | 0 | 0 | 0.5 | 0
10:00 | 2918 | 1326 | 794 | 0 | 102 | 830.13 | 46 | 2906 | 503.26 | 0 | 69 | 0 | 0 | 0 | 0
10:30 | 2957 | 1377 | 794 | 0 | 102 | 831.515 | 46 | 2943.5 | 534.72 | 0 | 68 | 0 | 0 | 0 | 0
11:00 | 2996 | 1428 | 794 | 0 | 102 | 832.9 | 46 | 2981 | 566.18 | 0 | 67 | 0 | 0 | 0 | 0
11:30 | 3013 | 1439.5 | 841 | 0 | 113 | 877.4 | 46 | 3097 | 578.9 | 10.5 | 50 | 0 | 0 | 0 | 0
12:00 | 3030 | 1451 | 888 | 0 | 124 | 921.9 | 46 | 3213 | 591.62 | 21 | 33 | 0 | 0 | 0 | 0
12:30 | 3063.5 | 1477 | 888.5 | 0 | 123 | 925.765 | 46 | 3352 | 572.145 | 31.5 | 33 | 0 | 0 | 0 | 0
13:00 | 3097 | 1503 | 889 | 0 | 122 | 929.63 | 46 | 3491 | 552.67 | 42 | 33 | 0 | 0 | 0 | 0
13:30 | 3036 | 1493.5 | 888.5 | 0 | 120 | 880.815 | 46 | 3446 | 481.975 | 33.5 | 33 | 0 | 0 | 0 | 0
14:00 | 2975 | 1484 | 888 | 0 | 118 | 832 | 46 | 3401 | 411.28 | 25 | 33 | 0 | 0 | 0 | 0
14:30 | 3003 | 1428 | 888.5 | 0 | 120 | 884.5 | 46 | 3360.5 | 312.765 | 20.5 | 33 | 0 | 0 | 1 | 0
15:00 | 3031 | 1372 | 889 | 0 | 122 | 937 | 46 | 3320 | 214.25 | 16 | 33 | 0 | 0 | 2 | 0
15:30 | 3013 | 1358.5 | 888.5 | 0 | 119 | 933.5 | 46 | 3348.5 | 155.66 | 16 | 55 | 0 | 0 | 6 | 0
16:00 | 2995 | 1345 | 888 | 0 | 116 | 930 | 46 | 3377 | 97.07 | 16 | 77 | 0 | 0 | 10 | 0
16:30 | 2897 | 1333.5 | 888 | 0 | 114 | 975 | 46 | 3417 | 52.785 | 24.5 | 178.5 | 0 | 0 | 6.5 | 0
17:00 | 2799 | 1322 | 888 | 0 | 112 | 1020 | 46 | 3457 | 8.5 | 33 | 280 | 0 | 0 | 3 | 0
17:30 | 2913 | 1376.5 | 888 | 0 | 112 | 1153.5 | 46 | 3702.5 | 4.25 | 63.5 | 423.15 | 0 | 0 | 4 | 0
18:00 | 3027 | 1431 | 888 | 0 | 112 | 1287 | 46 | 3948 | 0 | 94 | 566.3 | 0 | 0 | 5 | 0
18:30 | 2968.5 | 1383 | 888 | 0 | 109 | 1289.5 | 46 | 3986 | 0 | 63.5 | 485.7 | 40 | 0 | 3.5 | 0
19:00 | 2910 | 1335 | 888 | 0 | 106 | 1292 | 46 | 4024 | 0 | 33 | 405.1 | 80 | 0 | 2 | 0
19:30 | 2944 | 1384 | 888 | 0 | 112 | 1242 | 46 | 4034 | 0 | 16 | 163.1 | 170 | 0 | 1 | 0
20:00 | 2933 | 1405 | 889 | 0 | 116 | 1221 | 46 | 3875 | 0 | 0 | 134 | 170 | 0 | 0 | 0
20:30 | 2944 | 1390.5 | 888.5 | 0 | 111 | 1166 | 46 | 3848 | 0 | 0 | 108 | 135 | 0 | 0 | 0
21:00 | 2955 | 1376 | 888 | 0 | 106 | 1111 | 46 | 3821 | 0 | 0 | 82 | 100 | 0 | 0 | 0
21:30 | 2967.5 | 1332.25 | 884.5 | 0 | 105 | 1091.5 | 46 | 3748.5 | 0 | 0 | 76.5 | 50 | 0 | 0 | 0
22:00 | 2980 | 1288.5 | 881 | 0 | 104 | 1072 | 46 | 3676 | 0 | 0 | 71 | 0 | 0 | 0 | 0
22:30 | 2971.5 | 1277.5 | 881 | 0 | 104 | 1011 | 46 | 3569.5 | 0 | 0 | 71 | 0 | 0 | 3 | 0
23:00 | 2963 | 1266.5 | 881 | 0 | 104 | 950 | 46 | 3463 | 0 | 0 | 71 | 0 | 0 | 6 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-11-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 403 | 04:00 | 384 | 16:00 | Meghnaghat | 405 | 05:00 | 387 | 12:00
Ashuganj | 403 | 1:00 | 385 | 13:00 | Payra | 417 | 01:00 | 410 | 13:00
Bhulta | 400 | 01:00 | 381 | 12:00 | Rahanpur | 416 | 05:00 | 405 | 18:00
Bibiana | 403 | 05:00 | 392 | 11:00 | Rampal | 415 | 05:00 | 399 | 13:00
BIPTC | 408 | 05:00 | 396 | 00:00
Bogura | 409 | 05:00 | 393 | 18:00
Gopalganj | 411 | 05:00 | 396 | 13:00
Kaliakoir | 400 | 04:00 | 381 | 14:00
Korerhat | 410 | 05:00 | 395 | 13:00
Madunaghat | 405 | 04:00 | 393 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 242 | 03:00 | 229 | 13:00 | Kachua | 237 | 04:00 | 229 | 13:00
AKSML | 240 | 01:00 | 231 | 12:00 | Kaliakoir | 240 | 04:00 | 226 | 12:00
Aminbazar | 242 | 05:00 | 230 | 14:00 | Keranigonj | 240 | 04:00 | 226 | 13:00
Ashuganj | 241 | 01:00 | 231 | 12:00 | Khulna(S) | 242 | 05:00 | 230 | 13:00
Ashuganj-400 | 241 | 01:00 | 231 | 12:00 | Korerhat | 240 | 05:00 | 232 | 13:00
Baghabari | 238 | 01:00 | 229 | 18:00 | Madunaghat | 240 | 01:00 | 233 | 12:00
Barapukuria | 225 | 05:00 | 216 | 08:00 | Madunaghat-400 | 242 | 05:00 | 233 | 13:00
Barapukuria-230 | 225 | 05:00 | 216 | 08:00 | Maniknagar | 235 | 02:00 | 223 | 16:00
Barishal | 243 | 01:00 | 236 | 18:00 | Meghnaghat | 242 | 06:00 | 233 | 12:00
Bheramara | 236 | 01:00 | 225 | 13:00 | Meghnaghat-400 | 238 | 04:00 | 227 | 12:00
Bhulta | 235 | 03:00 | 223 | 12:00 | Mirsorai | 239 | 04:00 | 230 | 14:00
Bibiana | 238 | 03:00 | 229 | 12:00 | Rajshahi | 236 | 01:00 | 225 | 12:00
BIPTC | 239 | 01:00 | 226 | 13:00 | Rampal | 238 | 01:00 | 228 | 13:00
Bogura | 237 | 03:00 | 228 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 237 | 05:00 | 227 | 18:00 | Rampura | 234 | 04:00 | 222 | 12:00
Borhanuddin | 245 | 03:00 | 241 | 13:00 | Shikalbaha | 240 | 04:00 | 230 | 12:00
BSRM | 239 | 05:00 | 229 | 13:00 | Shyampur | 239 | 05:00 | 225 | 13:00
Cumilla(N) | 236 | 05:00 | 228 | 15:00 | Siddhirganj | 234 | 00:00 | 228 | 17:00
Faridpur | 243 | 04:00 | 234 | 13:00 | Sirajgonj | 242 | 01:00 | 236 | 18:00
Fenchuganj | 236 | 04:00 | 227 | 17:00 | Sreepur | 234 | 01:00 | 226 | 19:00
Feni | 238 | 04:00 | 229 | 13:00 | Tongi | 236 | 04:00 | 222 | 11:00
Ghorashal | 0 | 0 | 0 | 0
Ghorashal-230 | 232 | 05:00 | 217 | 12:00
Gopalganj | 243 | 04:00 | 234 | 18:00
GPH | 240 | 04:00 | 232 | 13:00
Haripur | 236 | 04:00 | 224 | 13:00
Hasnabad | 239 | 02:00 | 226 | 16:00
Hathazari | 238 | 05:00 | 231 | 12:00
Ishurdi | 240 | 01:00 | 228 | 18:00
Jhenaidah | 238 | 01:00 | 225 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 128 | 12:00 | Lalbag | 139 | 05:00 | 129 | 14:00
Agargaon | 139 | 05:00 | 131 | 12:00 | Lalmonirhat | 131 | 10:00 | 124 | 08:00
Agrabad | 138 | 01:00 | 132 | 12:00 | Madanganj | 135 | 01:00 | 130 | 13:00
AKS | 136 | 02:00 | 131 | 13:00 | Madaripur | 138 | 07:00 | 136 | 12:00
Aminbazar | 141 | 04:00 | 133 | 12:00 | Madartek | 136 | 04:00 | 128 | 12:00
Amnura | 138 | 05:00 | 129 | 17:00 | Madunaghat | 140 | 02:00 | 135 | 13:00
Ashuganj | 142 | 01:00 | 138 | 15:00 | Magura | 141 | 01:00 | 131 | 13:00
Bagerhat | 137 | 02:00 | 127 | 18:00 | Mahasthangarh | 135 | 03:00 | 128 | 18:00
Bajitpur | 137 | 01:00 | 133 | 12:00 | Maijdee | 135 | 04:00 | 130 | 13:00
Bakulia | 139 | 06:00 | 133 | 18:00 | Manikganj | 135 | 04:00 | 120 | 15:00
Banani | 137 | 03:00 | 127 | 12:00 | Maniknagar | 139 | 05:00 | 131 | 13:00
Bangabhaban | 140 | 05:00 | 132 | 12:00 | Matarbari | 130 | 01:00 | 122 | 17:00
Barapukuria | 138 | 03:00 | 131 | 08:00 | Matuail | 137 | 01:00 | 130 | 13:00
Barguna | 137 | 05:00 | 134 | 13:00 | Metrorail_Motijheel | 139 | 05:00 | 131 | 13:00
Barishal | 140 | 01:00 | 135 | 13:00 | Metrorail_Uttara | 136 | 01:00 | 123 | 16:00
Barishal-230 | 140 | 01:00 | 135 | 13:00 | Millgate | 137 | 03:00 | 123 | 16:00
Baroaulia | 140 | 07:00 | 133 | 16:00 | Mirpur | 140 | 02:00 | 132 | 12:00
Baroirhat | 137 | 01:00 | 131 | 12:00 | Mirzapur | 137 | 03:00 | 129 | 12:00
Bashundhara | 137 | 04:00 | 127 | 13:00 | Mithapukur | 134 | 02:00 | 127 | 07:00
BashundharaCement | 135 | 01:00 | 130 | 13:00 | MI_Cement | 137 | 04:00 | 128 | 13:00
Beanibazar | 135 | 05:00 | 131 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 138 | 04:00 | 125 | 13:00 | Mogbazar | 138 | 06:00 | 129 | 16:00
Bhaluka | 134 | 00:00 | 129 | 12:00 | Mongla | 136 | 05:00 | 127 | 18:00
Bhandaria | 138 | 06:00 | 132 | 13:00 | Motijheel | 140 | 05:00 | 132 | 12:00
Bhangura | 138 | 10:00 | 132 | 12:00 | Muktagacha | 134 | 01:00 | 127 | 18:00
Bheramara | 141 | 01:00 | 136 | 13:00 | Munshiganj | 136 | 04:00 | 129 | 12:00
Bheramara(GK) | 141 | 01:00 | 136 | 12:00 | Muradnagar | 138 | 01:00 | 131 | 13:00
Bhulta | 134 | 06:00 | 127 | 12:00 | Mymensingh | 133 | 06:00 | 125 | 18:00
Bog-Sherpur | 136 | 02:00 | 130 | 18:00 | Naogaon | 135 | 05:00 | 128 | 18:00
Bogura | 136 | 04:00 | 130 | 18:00 | Narail | 141 | 01:00 | 130 | 13:00
Bogura-230 | 136 | 03:00 | 130 | 18:00 | Narinda | 139 | 05:00 | 131 | 13:00
Brahmanbaria | 138 | 07:00 | 133 | 16:00 | Narshingdi | 139 | 02:00 | 125 | 16:00
Cantonment | 139 | 04:00 | 131 | 12:00 | Natore | 137 | 01:00 | 131 | 18:00
Chandina | 140 | 02:00 | 134 | 13:00 | Nawabganj | 139 | 04:00 | 129 | 13:00
Chandpur | 138 | 03:00 | 134 | 13:00 | Netrakona | 132 | 02:00 | 125 | 08:00
Chandraghona | 140 | 02:00 | 135 | 13:00 | New | 137 | 04:00 | 124 | 16:00
Chapai | 138 | 04:00 | 134 | 19:30 | Niamatpur | 139 | 03:00 | 135 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 137 | 02:00 | 130 | 12:00 | Noapara | 139 | 01:00 | 131 | 12:00
Chauddagram | 138 | 05:00 | 132 | 12:00 | Pabna | 140 | 00:00 | 134 | 12:00
Chhatak | 133 | 01:00 | 130 | 10:00 | Palashbari | 133 | 04:00 | 124 | 07:00
Chowmuhani | 135 | 05:00 | 129 | 12:00 | Panchagarh | 139 | 17:00 | 126 | 07:00
Chuadanga | 141 | 05:00 | 131 | 13:00 | Patiya | 137 | 09:00 | 134 | 00:00
Coxsbazar | 128 | 04:00 | 120 | 17:00 | Patuakhali | 136 | 00:00 | 134 | 13:00
Cumilla(N) | 140 | 06:00 | 134 | 12:00 | Payra | 137 | 01:00 | 135 | 12:00
Cumilla(S) | 139 | 06:00 | 125 | 12:00 | PHP | 136 | 02:00 | 130 | 13:00
Daganbhuiyan | 136 | 04:00 | 130 | 13:00 | Postogola | 138 | 05:00 | 130 | 12:00
Daudkandi | 135 | 04:00 | 128 | 12:00 | Purbachal | 137 | 03:00 | 127 | 12:00
DhakaUniversity | 136 | 01:00 | 128 | 12:00 | Purbasadipur | 133 | 05:00 | 125 | 08:00
Dhamrai | 138 | 06:00 | 130 | 12:00 | Rahanpur | 140 | 02:00 | 136 | 18:00
Dhanmondi | 138 | 05:00 | 132 | 12:00 | Rahanpur-400 | 140 | 01:00 | 136 | 18:00
Dohazari | 136 | 05:00 | 129 | 12:00 | Rahim | 137 | 02:00 | 131 | 12:00
Faridpur | 140 | 03:00 | 135 | 12:00 | Rajbari | 141 | 05:00 | 134 | 13:00
Fatullah | 142 | 04:00 | 129 | 13:00 | Rajendrapur | 137 | 02:00 | 130 | 12:00
Fenchuganj | 140 | 06:00 | 137 | 11:00 | Rajshahi | 136 | 04:00 | 130 | 13:00
Feni | 137 | 06:00 | 128 | 13:00 | Rajshahi-230 | 136 | 01:00 | 130 | 12:00
Feni-230 | 136 | 01:00 | 129 | 13:00 | Ramganj | 135 | 01:00 | 130 | 19:30
Ghatail | 132 | 06:00 | 124 | 13:00 | Rampur | 139 | 05:00 | 132 | 12:00
Ghorashal | 136 | 00:00 | 132 | 10:00 | Rampura | 136 | 02:00 | 127 | 13:00
Goalpara | 140 | 01:00 | 131 | 18:00 | Rangamati | 140 | 03:00 | 134 | 13:00
Gollamari | 139 | 01:00 | 132 | 18:00 | Rangpur | 134 | 11:00 | 126 | 18:00
Gopalganj | 140 | 02:00 | 133 | 13:00 | Ruppur | 141 | 02:00 | 135 | 18:00
Gopalganj-400 | 142 | 04:00 | 136 | 12:00 | Saidpur | 134 | 05:00 | 126 | 08:00
Gulshan | 136 | 04:00 | 127 | 13:00 | Satkhira | 138 | 03:00 | 129 | 18:00
Halishahar | 140 | 05:00 | 133 | 13:00 | Satmasjid | 139 | 04:00 | 129 | 13:00
Haripur | 138 | 03:00 | 131 | 13:00 | Savar | 138 | 03:00 | 131 | 12:00
HaripurSBU | 138 | 03:00 | 131 | 13:00 | SevenRings | 138 | 01:00 | 131 | 12:00
Hasnabad | 137 | 01:00 | 129 | 12:00 | ShahCement | 137 | 02:00 | 130 | 12:00
Hathazari | 140 | 05:00 | 135 | 16:00 | Shahjadpur | 140 | 00:00 | 135 | 12:00
Ishurdi | 142 | 01:00 | 136 | 13:00 | Shahjibazar | 139 | 00:00 | 134 | 16:00
Jaldhaka | 133 | 05:00 | 124 | 08:00 | Shahmirpur | 140 | 01:00 | 134 | 18:00
Jamalpur | 131 | 17:00 | 121 | 13:00 | Shariatpur | 140 | 04:00 | 134 | 13:00
Jashore | 139 | 05:00 | 127 | 13:00 | Sherpur | 128 | 17:00 | 118 | 00:00
Jhenaidah | 141 | 04:00 | 122 | 18:00 | Shikalbaha | 126 | 00:00 | 123 | 15:00
Jhenaidah-230 | 142 | 01:00 | 132 | 13:00 | Shikalbaha-230 | 141 | 03:00 | 134 | 12:00
Joydebpur | 135 | 20:00 | 127 | 12:00 | Shitalakhya | 137 | 04:00 | 128 | 13:00
Joypurhat | 132 | 01:00 | 125 | 18:00 | Sholosohor | 140 | 02:00 | 135 | 12:00
Juldah | 139 | 01:00 | 134 | 17:00 | Shyampur | 139 | 03:00 | 132 | 14:00
Kabirpur | 136 | 05:00 | 123 | 13:00 | Shyampur-230 | 142 | 04:00 | 133 | 13:00
Kachua | 140 | 03:00 | 135 | 13:00 | Siddhirganj | 138 | 03:00 | 131 | 12:00
Kaliakoir | 141 | 04:00 | 132 | 14:00 | Sirajganj | 136 | 02:00 | 129 | 18:00
Kallyanpur | 140 | 04:00 | 133 | 12:00 | Sonargaon | 137 | 04:00 | 133 | 10:00
Kalurghat | 140 | 05:00 | 135 | 15:00 | Sreemongol | 139 | 01:00 | 135 | 12:00
Kamrangirchar | 137 | 01:00 | 129 | 12:00 | Sreepur | 137 | 01:00 | 132 | 12:00
Kaptai | 141 | 2:00 | 137 | 12:00 | Srinagar | 139 | 03:00 | 129 | 12:00
Kasba | 138 | 04:00 | 131 | 12:00 | SSM | 140 | 00:00 | 138 | 13:00
Kazla | 138 | 08:00 | 131 | 13:00 | Sunamganj | 132 | 03:00 | 129 | 12:00
Keranigonj | 139 | 05:00 | 129 | 13:00 | Sylhet | 135 | 04:00 | 132 | 12:00
Khagrachori | 139 | 01:00 | 133 | 13:00 | Sylhet-132 | 134 | 01:00 | 131 | 13:00
Khulna | 139 | 04:00 | 131 | 13:00 | Tangail | 133 | 03:00 | 124 | 13:00
Khulna(S) | 140 | 03:00 | 132 | 13:00 | Taraganj | 133 | 05:00 | 126 | 18:00
Khulshi | 137 | 01:00 | 124 | 11:00 | Tasnim | 137 | 01:00 | 133 | 10:00
Kishoreganj | 135 | 03:00 | 130 | 12:00 | Thakurgaon | 138 | 17:00 | 127 | 08:00
Kodda | 135 | 02:00 | 125 | 11:00 | TK | 140 | 06:00 | 135 | 16:00
KSRM | 139 | 05:00 | 133 | 13:00 | Tongi | 139 | 04:00 | 126 | 18:30
Kulaura | 139 | 00:00 | 136 | 12:00 | Ullahpara | 138 | 05:00 | 131 | 18:00
Kurigram | 134 | 03:00 | 122 | 18:00 | Ullon | 136 | 03:00 | 127 | 13:00
Kushtia | 137 | 03:00 | 129 | 18:00 | Uttara | 137 | 03:00 | 124 | 15:00
Laksam | 140 | 04:00 | 134 | 12:00 | UttaraNew | 136 | 01:00 | 123 | 16:00
Lakshmipur | 136 | 04:00 | 130 | 13:00 | Zigatola | 139 | 05:00 | 128 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division