## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-12-2025 | [28 empty] | Date: | 01-12-2025 | [28 empty] | Date: | 01-12-2025 | [28 empty] | Date: | 01-12-2025 | [28 empty] | Date: | 01-12-2025 | [17 empty] | Date: | 01-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 14 | 354 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 846 | 0 | 0 | 26 | 0 | 0 | 330 | 51 | 20 | 197 | 40 | 0 | 110 | 0 | 0 | 14 | 0 | 100 | 0 | 0 | 0 | 305 | 0 | 380 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 15 | 158 | 0 | 8 | 8 | 69 | 0 | 0 | 0 | 4541.5 | 882 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 257 | 820 | 0 | 4708 | 9249.5 | 99.66
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 24 | 311 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 819 | 0 | 0 | 26 | 0 | 0 | 325 | 51 | 20 | 197 | 40 | 0 | 110 | 0 | 0 | 14 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 372 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 15 | 158 | 0 | 8 | 0 | 69 | 0 | 0 | 0 | 4450.5 | 787 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 257 | 600 | 0 | 4282 | 8732.5 | 99.65
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 2 | 314 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 722 | 0 | 0 | 26 | 0 | 0 | 280 | 5 | 13 | 210 | 37 | 0 | 110 | 0 | 0 | 14 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 352 | 0 | 30 | 0 | 0 | 5 | 0 | 41 | 20 | 0 | 15 | 159 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 4184.5 | 738 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 257 | 500 | 0 | 4138 | 8322.5 | 99.65
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 2 | 299 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 633 | 0 | 0 | 26 | 0 | 0 | 280 | 5 | 5 | 205 | 5 | 0 | 109 | 0 | 0 | 14 | 0 | 92 | 0 | 0 | 0 | 300 | 0 | 346 | 0 | 30 | 0 | 0 | 5 | 0 | 5 | 20 | 0 | 15 | 159 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 3959.5 | 684 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 256 | 500 | 0 | 4065 | 8024.5 | 99.65
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 2 | 300 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 603 | 0 | 0 | 8 | 0 | 0 | 255 | 5 | 5 | 201 | 5 | 0 | 70 | 0 | 0 | 14 | 0 | 88 | 0 | 0 | 0 | 290 | 0 | 346 | 0 | 30 | 0 | 0 | 5 | 0 | 5 | 20 | 0 | 15 | 159 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 3833.5 | 684 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 259 | 500 | 0 | 3994 | 7827.5 | 99.65
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 2 | 300 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 480 | 0 | 0 | 8 | 0 | 0 | 240 | 5 | 5 | 208 | 5 | 0 | 50 | 0 | 0 | 14 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 360 | 0 | 30 | 0 | 0 | 5 | 0 | 5 | 20 | 0 | 15 | 159 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 3643.5 | 637 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 258 | 500 | 0 | 4094 | 7737.5 | 99.64
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 300 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 600 | 0 | 0 | 8 | 0 | 0 | 330 | 9 | 5 | 205 | 28 | 0 | 50 | 0 | 0 | 14 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 340 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 3925 | 636 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 306 | 544 | 0 | 4290 | 8215 | 99.64
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 46 | 0 | 35 | 350 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 580 | 3 | 0 | 25 | 0 | 0 | 330 | 46 | 12 | 208 | 34 | 0 | 112 | 0 | 0 | 14 | 0 | 90 | 0 | 10 | 0 | 305 | 0 | 351 | 0 | 30 | 0 | 0.36 | 16 | 0 | 82 | 30 | 0 | 15 | 159 | 0 | 8 | 19 | 64 | 0 | 2.25 | 0 | 4128.94 | 737 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 862 | 0 | 0 | 0 | 1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 8 | 0 | 0 | 4.75 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.42 | 0 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0.1 | 4 | 0.04 | 0 | 0 | 115 | 110 | 0 | 306 | 610 | 0 | 4761.78 | 8890.72 | 99.64
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 4 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 46 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 10 | 0 | 86 | 0 | 0 | 330 | 51 | 26 | 200 | 40 | 0 | 110 | 0 | 0 | 5 | 0 | 102 | 0 | 39 | 0 | 305 | 0 | 343 | 0 | 30 | 0 | 1.87 | 17 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 35 | 19 | 64 | 0 | 13.67 | 0 | 4212.8 | 730 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1055 | 0 | 0 | 0 | 1281.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.74 | 16 | 0 | 0 | 16.79 | 189 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 1.47 | 0 | 56 | 0 | 6 | 0 | 0 | 0 | 0 | 1.4 | 39 | 0.15 | 0 | 0 | 115 | 110 | 0 | 363 | 750 | 0 | 5363.16 | 9575.96 | 99.63
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 17 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.24 | 46 | 0 | 6 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 15 | 0 | 90 | 0 | 0 | 330 | 51 | 45 | 183 | 39 | 0 | 109 | 0 | 0 | 5 | 0 | 80 | 0 | 52 | 0 | 300 | 0 | 319 | 0 | 30 | 0 | 6 | 17 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 57 | 19 | 64 | 1 | 24.31 | 0 | 4183.05 | 730 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1056 | 0 | 0 | 0 | 1187.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.13 | 34 | 0 | 0 | 32.45 | 172 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 2.6 | 0 | 56 | 0 | 13 | 0 | 0 | 0 | 0 | 3.2 | 93 | 0.28 | 0 | 0 | 115 | 110 | 0 | 291 | 814 | 0 | 5363.88 | 9546.93 | 99.63
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 21 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.97 | 46 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 510 | 18 | 0 | 56 | 0 | 0 | 330 | 51 | 48 | 208 | 39 | 0 | 108 | 0 | 0 | 5 | 0 | 88 | 0 | 61 | 0 | 305 | 0 | 340 | 0 | 30 | 0 | 8 | 17 | 0 | 79 | 30 | 0 | 15 | 160 | 0 | 16 | 8 | 32 | 2 | 35.28 | 0 | 4251.75 | 780 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 850 | 0 | 0 | 0 | 914.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.28 | 26 | 0 | 0 | 38.03 | 170 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 4.27 | 0 | 56 | 0 | 21 | 0 | 0 | 0 | 0 | 4.4 | 78 | 0.24 | 0 | 0 | 115 | 110 | 0 | 257 | 860 | 0 | 5012.26 | 9264.01 | 99.63
11:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 33 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 46 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 575 | 19 | 0 | 130 | 0 | 0 | 330 | 51 | 46 | 206 | 39 | 0 | 105 | 0 | 0 | 5 | 0 | 96 | 0 | 68 | 0 | 315 | 0 | 340 | 0 | 30 | 0 | 9.7 | 17 | 0 | 79 | 30 | 0 | 15 | 160 | 0 | 16 | 8 | 33 | 2 | 47.52 | 0 | 4439.02 | 779 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 770 | 0 | 0 | 0 | 918.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.62 | 30 | 0 | 0 | 55.9 | 174 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 4.56 | 0 | 55 | 0 | 21 | 0 | 0 | 124 | 0 | 5.2 | 134 | 0.45 | 0 | 0 | 115 | 110 | 0 | 258 | 844 | 0 | 5133.1 | 9572.12 | 99.63
12:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 60 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 31 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 46 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 590 | 19 | 0 | 153 | 0 | 0 | 330 | 51 | 48 | 170 | 39 | 0 | 104 | 0 | 0 | 5 | 0 | 104 | 0 | 53 | 0 | 310 | 0 | 406 | 0 | 30 | 0 | 9 | 17 | 0 | 79 | 30 | 0 | 15 | 160 | 0 | 16 | 8 | 33 | 1 | 43.3 | 0 | 4588.17 | 873 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 805 | 0 | 0 | 0 | 1111.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.36 | 108 | 0 | 0 | 50.85 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.84 | 0 | 55 | 0 | 28 | 0 | 0 | 170 | 0 | 5.5 | 108 | 0.42 | 0 | 0 | 115 | 110 | 0 | 306 | 906 | 0 | 5738.54 | 10326.71 | 99.63
13:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 407 | 35 | 0 | 0 | 0 | 0 | 0 | 55 | 152 | 0 | 140 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 16 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.27 | 46 | 0 | 12 | 354 | 0 | 0 | 0 | 0 | 1 | 31 | 0 | 0 | 0 | 612 | 18 | 0 | 8 | 0 | 0 | 330 | 51 | 47 | 188 | 36 | 0 | 104 | 8 | 0 | 5 | 0 | 98 | 0 | 59 | 0 | 315 | 0 | 396 | 0 | 30 | 0 | 9 | 17 | 0 | 79 | 30 | 0 | 15 | 160 | 0 | 57 | 18 | 33 | 0 | 40.51 | 2 | 4730.28 | 872 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 848 | 0 | 0 | 0 | 1269.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.25 | 70 | 0 | 0 | 61.13 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.7 | 0 | 54 | 0 | 26 | 0 | 0 | 83 | 0 | 4.3 | 40 | 0.39 | 0 | 0 | 115 | 110 | 0 | 305 | 980 | 0 | 5800.59 | 10530.87 | 99.62
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 413 | 54 | 0 | 0 | 0 | 0 | 0 | 55 | 126 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 8 | 0 | 21 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.51 | 46 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 612 | 15 | 0 | 0 | 0 | 0 | 330 | 51 | 0 | 201 | 0 | 0 | 104 | 0 | 0 | 5 | 0 | 98 | 0 | 50 | 0 | 310 | 0 | 368 | 0 | 30 | 0 | 8 | 17 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 57 | 19 | 33 | 0 | 40.84 | 6 | 4492.35 | 872 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 849 | 0 | 0 | 0 | 1278.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.75 | 23 | 0 | 0 | 14.19 | 165 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 1.33 | 0 | 55 | 0 | 16 | 0 | 0 | 0 | 0 | 1.9 | 38 | 0.16 | 0 | 0 | 115 | 110 | 0 | 305 | 980 | 0 | 5529.53 | 10021.88 | 99.62
15:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 392 | 35 | 0 | 0 | 0 | 0 | 0 | 55 | 126 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 9 | 0 | 20.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 46 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 612 | 11 | 0 | 0 | 0 | 0 | 330 | 51 | 0 | 197 | 0 | 0 | 104 | 0 | 0 | 5 | 0 | 122 | 0 | 23 | 0 | 310 | 0 | 345 | 0 | 30 | 0 | 4 | 17 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 56 | 19 | 33 | 0 | 6.72 | 6 | 4404.82 | 872 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 855 | 0 | 0 | 0 | 1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.13 | 19 | 0 | 0 | 6.11 | 175 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.55 | 0 | 53 | 0 | 6 | 0 | 0 | 0 | 0 | 1.3 | 114 | 0.22 | 0 | 0 | 115 | 110 | 0 | 305 | 970 | 0 | 5386.31 | 9791.13 | 99.62
16:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 430 | 35 | 0 | 0 | 0 | 0 | 0 | 55 | 126 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 3 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 46 | 0 | 5 | 354 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 612 | 5 | 0 | 0 | 3 | 0 | 330 | 51 | 0 | 211 | 0 | 0 | 105 | 0 | 0 | 5 | 0 | 108 | 0 | 10 | 0 | 310 | 0 | 380 | 0 | 30 | 0 | 1 | 17 | 0 | 79 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 33 | 0 | 2.26 | 0 | 4489.52 | 873 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 850 | 0 | 0 | 0 | 1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.05 | 5 | 0 | 0 | 4.75 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.41 | 0 | 53 | 0 | 6 | 0 | 0 | 0 | 0 | 0.8 | 37 | 0.11 | 0 | 0 | 115 | 110 | 0 | 305 | 968 | 0 | 5277.12 | 9766.64 | 99.62
17:00 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 430 | 35 | 0 | 17 | 22 | 45 | 0 | 55 | 125 | 0 | 140 | 0 | 0 | 0 | 20 | 240 | 0 | 0 | 1 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 54 | 0.01 | 46 | 0 | 8 | 354 | 0 | 0 | 2 | 0 | 13 | 176 | 0 | 0 | 0 | 612 | 0 | 25 | 0 | 5 | 0 | 330 | 51 | 0 | 210 | 0 | 0 | 104 | 24 | 0 | 7 | 0 | 116 | 0 | 1 | 0 | 305 | 0 | 397 | 0 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 33 | 0 | 0 | 0 | 4858.01 | 873 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 892 | 0 | 0 | 0 | 1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 1 | 0.01 | 0 | 0 | 115 | 110 | 0 | 353 | 1002 | 0 | 5415.03 | 10273.04 | 99.61
18:00 | 0 | 25 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 428 | 35 | 0 | 62 | 48 | 115 | 0 | 55 | 126 | 0 | 140 | 0 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 17 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 12 | 90 | 0 | 46 | 8 | 10 | 352 | 0 | 0 | 29 | 0 | 70 | 221 | 0 | 0 | 0 | 612 | 0 | 100 | 0 | 15 | 0 | 330 | 51 | 0 | 200 | 0 | 16 | 105 | 99 | 3 | 14 | 0 | 116 | 0 | 0 | 0 | 305 | 0 | 395 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 33 | 0 | 0 | 11 | 5391.5 | 872 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1048 | 0 | 0 | 0 | 1270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 455 | 1075 | 0 | 5945 | 11336.5 | 99.61
19:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 393 | 17 | 0 | 77 | 32 | 45 | 0 | 35 | 0 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 20.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 90 | 0 | 46 | 0 | 8 | 352 | 0 | 0 | 0 | 0 | 51 | 225 | 0 | 0 | 0 | 617 | 0 | 10 | 0 | 40 | 0 | 330 | 51 | 0 | 196 | 0 | 0 | 105 | 85 | 0 | 14 | 0 | 106 | 0 | 0 | 0 | 300 | 0 | 371 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 49 | 19 | 33 | 0 | 0 | 12 | 4865.2 | 873 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1097 | 0 | 0 | 0 | 1330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 54 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 453 | 1065 | 0 | 6022 | 10887.2 | 99.61
19:30 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 405 | 0 | 0 | 78 | 16 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 78 | 0 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 28 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 90 | 0 | 330 | 51 | 0 | 199 | 0 | 0 | 105 | 49 | 0 | 14 | 0 | 106 | 0 | 0 | 0 | 310 | 0 | 390 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 33 | 0 | 0 | 12 | 4803 | 872 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 53 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 453 | 1070 | 0 | 6012 | 10815
20:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 391 | 0 | 0 | 78 | 16 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 17 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 105 | 0 | 330 | 51 | 0 | 193 | 0 | 0 | 106 | 51 | 0 | 14 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 370 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 58 | 19 | 33 | 0 | 0 | 12 | 4720 | 872 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 53 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 417 | 1070 | 0 | 5968 | 10688 | 99.61
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 396 | 0 | 0 | 78 | 0 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 10 | 354 | 0 | 0 | 0 | 0 | 16 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 135 | 0 | 330 | 51 | 0 | 192 | 0 | 0 | 106 | 48 | 0 | 14 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 372 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 33 | 0 | 0 | 12 | 4682 | 873 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041 | 0 | 0 | 0 | 1326.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 354 | 1073 | 0 | 5849.03 | 10531.03 | 99.6
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 395 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 13 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 170 | 0 | 310 | 51 | 0 | 194 | 0 | 0 | 106 | 0 | 0 | 14 | 0 | 104 | 0 | 0 | 0 | 295 | 0 | 372 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 59 | 19 | 33 | 0 | 0 | 0 | 4500 | 873 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994 | 0 | 0 | 0 | 1328.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 305 | 1005 | 0 | 5588.91 | 10088.91 | 99.6
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 16 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 555 | 0 | 0 | 0 | 230 | 0 | 280 | 51 | 0 | 197 | 0 | 0 | 109 | 0 | 0 | 14 | 0 | 96 | 0 | 0 | 0 | 295 | 0 | 368 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 35 | 19 | 36 | 0 | 0 | 0 | 4410.5 | 873 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 1207.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 305 | 900 | 0 | 5238.49 | 9648.99 | 99.6
Total KWH | 0 | 168826 | 131942 | 0 | 0 | 0 | 0 | 0 | 8204400 | 0 | 9610390 | 227628 | 0 | 405360 | 103680 | 208004 | 0 | 468158 | 836640 | 0 | 3390000 | 0 | 0 | 0 | 73140 | 5889257 | 0 | 0 | 126286 | 21600 | 402600 | 520920 | 0 | 0 | 0 | 0 | 0 | 0 | 12960 | 0 | 34000 | 0 | 16320 | 331200 | 21242 | 1107000 | 24254 | 257760 | 8261818.18 | 0 | 0 | 53760 | 0 | 247563 | 2808105 | 0 | 0 | 0 | 14432726 | 133650 | 267636 | 669091 | 869500 | 0 | 7640000 | 1047880 | 332160 | 4881000 | 404136 | 34560 | 2409608 | 390240 | 10920 | 238400 | 0 | 2338560 | 0 | 423409 | 0 | 7371000 | 0 | 8992000 | 0 | 722760 | 0 | 57659 | 399768 | 0 | 1657920 | 682560 | 0 | 366000 | 4323360 | 0 | 788400 | 278400 | 1101120 | 8500 | 213440 | 80880 | 107532056.18 | 19327272 | 6242688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391680 | 21330910 | 0 | 0 | 0 | 26301818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260312 | 427280 | 0 | 0 | 261744 | 4183909 | 0 | 0 | 0 | 0 | 0 | 9213381 | 0 | 22020 | 0 | 1304727 | 251368 | 140284 | 212524 | 0 | 343891 | 0 | 29109.48 | 762480 | 2554 | 0 | 0 | 2737000 | 2391130 | 0 | 7596435 | 20654545.45 | 0 | 124389061.93 | 231921118.11

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-12-2025 | during | 02-12-2025 | during | 02-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 350 | 336 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 140 | 140 | 450 | 450 | 220 | 220 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 27 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.5 | 18.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 8 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 115 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 62 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 25 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 60 | 126 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | ST under maint.
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Under maint.
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 430 | 428 | 718 | 718 | 718 | 718 | FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1332.5 | 1710.5 | 5766.1 | 5738.1 | 3420.08 | 3401.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage & #01 under maint.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 29 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 27 | 221 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 70 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 40 | 64 | 40 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 10 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.37 | 0 | 3.34 | 0 | 3.34 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 8 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 90 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 590 | 612 | 612 | 612 | 612 | 612 | #01 under maint.
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 3 | 0 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 352 | 354 | 354 | 354 | 354 | #01 under maint.
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1041.37 | 1474 | 2592.06 | 2600.72 | 2096.84 | 2105.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 170 | 200 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage.
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 15 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 153 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 104 | 105 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 99 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 104 | 116 | 160 | 160 | 124 | 124 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 14 | 17.75 | 17.75 | 17.75 | 17.75 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 3 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 53 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1057 | 1049 | 2435.46 | 2365.46 | 2336.46 | 2266.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-12-2025 | during | 02-12-2025 | during | 02-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 33 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.3 | 0 | 45.85 | 0 | 45.85 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 11 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 101.3 | 122 | 361.95 | 314 | 314.45 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 82 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 157 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 0 | 0 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 406 | 395 | 385 | 385 | 190 | 190 | GBC problem.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1056 | 1036 | 1020 | 1020 | 846 | 846
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 873 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 805 | 1048 | 0 | 0 | 1100 | 1100 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2001 | 2170 | 2344 | 2272 | 2689.1 | 2617.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 306 | 455 | 0 | 0 | 0 | 0 | Coal shortage.
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 906 | 1075 | 1085.32 | 1085.32 | 1025 | 1025 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.42 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1437.42 | 1755 | 1576.32 | 1576.32 | 1493 | 1493
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 55.36 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 184 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.84 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1111.57 | 1270 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.85 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1933.62 | 1868 | 3077.02 | 2911.87 | 2981.64 | 2816.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 53 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 108 | 0 | 125.3 | 0 | 125.3 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 366.5 | 152 | 463.5 | 303 | 443.5 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 10326.71 | 11336.5 | 19636.41 | 19101.47 | 16621.07 | 16095.13
Forecast Scenario (02-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9250 |  | 0 |  | 9250
|  |  |  | 1:00 | 8730 |  | 0 |  | 8730
|  |  |  | 2:00 | 8320 |  | 0 |  | 8320
|  |  |  | 3:00 | 8020 |  | 0 |  | 8020
|  |  |  | 4:00 | 7820 |  | 0 |  | 7820
|  |  |  | 5:00 | 7730 |  | 0 |  | 7730
|  |  |  | 6:00 | 8210 |  | 0 |  | 8210
|  |  |  | 7:00 | 8890 |  | 0 |  | 8890
|  |  |  | 8:00 | 9570 |  | 0 |  | 9570
|  |  |  | 9:00 | 9540 |  | 0 |  | 9540
|  |  |  | 10:00 | 9260 |  | 0 |  | 9260
|  |  |  | 11:00 | 9570 |  | 0 |  | 9570
|  |  |  | 12:00 | 10320 |  | 0 |  | 10320
|  |  |  | 13:00 | 10530 |  | 0 |  | 10530
|  |  |  | 14:00 | 10020 |  | 0 |  | 10020
|  |  |  | 15:00 | 9790 |  | 0 |  | 9790
|  |  |  | 16:00 | 9760 |  | 0 |  | 9760
|  |  |  | 17:00 | 10270 |  | 0 |  | 10270
|  |  |  | 18:00 | 11330 |  | 0 |  | 11330
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 10880 |  | 0 |  | 10880
|  |  |  | 19:30 | 10810 |  | 0 |  | 10810
|  |  |  | 20:00 | 10680 |  | 0 |  | 10680
|  |  |  | 21:00 | 10530 |  | 0 |  | 10530
|  |  |  | 22:00 | 10100 |  | 0 |  | 10100
|  |  |  | 23:00 | 9750 |  | 0 |  | 9750
Probable Maximum Temperature: |  |  | 29.40°C
Probable Maximum Demand at Day Peak: |  |  | 10320.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11330.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11330.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 228.87 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:22 hrs on 02-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10326.71 | MW | 12:00 Hr. | Energy Generated |  |  | 231.9211 |  | MKWHr.
| Day Peak Demand |  |  | 10326.71 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11336.5 | MW | 18:00 Hr. | Energy Demand |  |  | 231.9211 |  | MKWHr.
| Evening Peak Demand |  |  | 11336.5 | MW | 18:00 Hr. | Maximum Temperature |  |  | 28.4 |  | °C
| Minimum Generation of the Day |  |  | 7737.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 749.52 |  | MMCFD
| Maximum Generation of the Day |  |  | 11336.5 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.4724 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.0176 | 0 | 2.645 | 0 | 0 | 0.12629 | 0 | 0 | 30.7888 | Gas | 99.9598 | Gas | 353566292.03
| Chattogram Zone |  |  | 3.0659 | 22.6945 | 0.7071 | 0 | 1.107 | 0.15489 | 0 | 0.01296 | 27.7424 | Coal | 73.5812 | Coal | 469798789.8781
| Cumilla Zone |  |  | 18.4918 | 0 | 0.70336 | 0 | 0 | 0.42341 | 2.3386 | 0 | 21.9571 | HFO | 5.667 | HFO | 95495449.75
| Mymensingh Zone |  |  | 1.1011 | 0 | 1.1477 | 0 | 0 | 0.22194 | 0 | 0 | 2.4707 | HSD | 0.34389 | HSD | 9419174.49
| Sylhet Zone |  |  | 24.5154 | 0 | 0 | 0 | 0 | 0.057659 | 0 | 0 | 24.573 | Hydro | 1.107 | Hydro | 110700
| Khulna Zone |  |  | 6.2427 | 21.3309 | 0 | 0 | 0 | 0.39168 | 19.3273 | 0 | 47.2925 | Solar | 3.2816 | Solar | 51158047.7708
| Barishal Zone |  |  | 5.1281 | 28.251 | 0 | 0 | 0 | 0.002554 | 0 | 0 | 33.3817 | Import | 47.9676 | Import | 289424071.82
| Rajshahi Zone |  |  | 13.3973 | 0 | 0 | 0 | 0 | 0.97136 | 26.3018 | 0 | 40.6705 | Wind | 0.01296 | Wind | 190641.6
| Rangpur Zone |  |  | 0 | 1.3047 | 0.46389 | 0.34389 | 0 | 0.93187 | 0 | 0 | 3.0444
| Total |  |  | 99.9598 | 73.5812 | 5.667 | 0.34389 | 1.107 | 3.2816 | 47.9676 | 0.01296 | 231.9211
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 353566292.03 |  | Hydro | 110700
|  |  |  | Coal | 469798789.8781 |  | Solar | 51158047.7708
|  |  |  | HFO | 95495449.75 |  | Import | 289424071.82
|  |  |  | HSD | 9419174.49 |  | Wind | 190641.6
[5 empty] | Total: | 126,91,63,167 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.3273 | Peak Hr Flow | 872.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50465699.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.3018 | Peak Hr Flow | 1270.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2461 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3386 | Peak Hr Flow | 116.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2869 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.9676 | Peak Hr Flow | 2258.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4280
|  |  |  | Chattogram |  | 0 |  | 1198
|  |  |  | Cumilla |  | 0 |  | 936
|  |  |  | Mymensingh |  | 0 |  | 850
|  |  |  | Sylhet |  | 0 |  | 407
|  |  |  | Khulna |  | 0 |  | 1263
|  |  |  | Barishal |  | 0 |  | 304
|  |  |  | Rajshahi |  | 0 |  | 972
|  |  |  | Rangpur |  | 0 |  | 758
|  |  |  | Total |  | 0 |  | 10968
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:22 | 15:12 | Bheramara(GK) 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual Maintenance
| 08:23 | 17:24 | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D Due to Annual maintenance work
| 08:23 | 17:23 | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D Due to Annual maintenance work
| 08:23 | 16:46 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to For
yearly maintenance work. and from Bhandaria 132/33kVend.
| 08:23 | 15:10 | Bheramara(GK) 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance
| 08:24 | 17:15 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to
Annual Maintenance work.
| 08:24 | 13:54 | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Redhot Maintenance for Betagi
33kv Feeder.
| 08:25 | 13:53 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Redhot Maintenance for Betagi
33kv Feeder.
| 08:29 | 17:20 | Gopalganj (O) - Gopalgan (N) Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to
Annual maintenance work and from Gopalganj 400/132kVend.
| 08:30 | 13:52 | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to Annual maintenance
| 08:31 | 16:35 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance. and from Coxsbazar 132/33kV end Due to Annual maintanance of Doh-cox CKT-02
Bay
| 08:32 | 16:24 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to
Annual Maintenance work.
| 08:33 | 14:07 | Savar 132/33kV S/S T-4 LT Scheduled S/D Due to Annual maintenance
| 08:33 | 14:05 | Savar 132/33kV S/S T-4 HT Scheduled S/D Due to Annual maintenance
| 08:35 |  | Sherpur 132/33kV S/S Bus B Scheduled S/D Due to Annual maintenance
| 08:35 | 13:59 | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
| 08:39 | 14:07 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Annual maintenance
| 08:39 | 14:06 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Annual maintenance
| 08:39 | 20:20 | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end.
| 08:40 | 16:54 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Ghatail 132/33kV end Due to
Annual Maintenance and from Muktagacha 132/33kVend.
| 08:41 | 16:23 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to Annual maitanance
| 08:41 | 15:26 | Halishahar-Khulshi 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end Due to due to
annual maintenance work.
| 08:41 | 16:30 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV end Due to
Annual maintenance and from Palashbari 132/33kV end Due to Annual maintenance
| 08:42 | 12:29 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Annuel Maintanince
| 08:43 | 12:28 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Annuel Maintenence
| 08:43 | 15:29 | Rampur 230/132/33 S/S Halishahar-1 Scheduled S/D Due to Annual Line maintenance of
Halishahar ckt-01
| 08:45 | 14:48 | Jhenaidah 132/33kV S/S Jhenaidah1-Jhenaidah2,132kV Circuit-2(L3) Scheduled S/D Due to
Annual maintenance
| 08:46 | 14:47 | Jhenaidah 230/132kV S/S Jhenaidah (New)-Jhenaidah (Old) Ckt-2 Scheduled S/D Due to Annual
Maintenance.
| 08:46 | 17:22 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
maintenance work.
| 08:49 | 16:11 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 LT Scheduled S/D Due to Annual Maintenance works
| 08:49 | 16:10 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 HT Scheduled S/D Due to Annual Maintenance works
| 08:52 | 20:45 | Cumilla(S) 132/33kV S/S 53.2MW Lakthanavi Scheduled S/D Due to PT Oil Leakage
Rectification from lakdhanavi End.
| 08:58 | 13:05 | Bhaluka 132/33kV S/S 03. Transformer-03 HT Scheduled S/D Due to Annual maitanance
| 08:58 | 13:06 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Scheduled S/D Due to Annual maitanance
| 09:02 | 17:15 | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end. and from Rajshahi
132/33kV end Due to Annual maintenance work-2025.
| 09:03 | 20:21 | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
| 09:15 | 16:47 | BIPTC S/S 10CF22 Scheduled S/D Due to Annual maintenance
| 09:16 |  | Sikalbaha 225 MW GT was synchronized.
| 09:52 |  | At Amtoli 400 KV SS, 400KV Main Bus-1 is S/D.
| 09:54 | 15:24 | Naogaon 132/33kV S/S Nao-SPPP Ckt-1 Scheduled S/D Due to Annual Maintenance.
| 10:20 |  | Saidpur 150 MW was sync.
| 10:42 | 15:17 | Spare 132kV Line Bay Scheduled S/D from Shitalakhya 132/33kV end Due to Due to Annual
maintenance Digital power plant side
| 12:00 |  | Day Peak Generation:10322 MW.
| 12:53 |  | At Amtoli 400 KV SS, 400KV Main Bus-1 S/D is withdrawn.
|  | 13:00 | Ishurdi 132/33kV S/S 132/33 kV T-3 HT is restored.
|  | 13:01 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT is restored.
| 13:01 |  | Purbasadipur-Saidpur 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end. and from
Saidpur 132/33kV end Due to 132 KV Saidpur- Purbosadipur CKT -01 S/D for Maintenance
work.
| 13:07 | 16:14 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Annual Maintenance
| 13:07 |  | Saidpur 150 MW was shut down.
| 13:08 | 16:13 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Annual Maintenance
| 13:09 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to Red hot
maintenance.
| 13:29 |  | Sikalbaha 225 MW ST was synchronized.
| 14:08 | 16:14 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual Maintenance
| 14:08 | 16:15 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual Maintenance
| 15:06 |  | Ashuganj 420 MW CCPP (East) GT was sync.
|  | 15:57 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT is restored.
|  | 15:57 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT is restored.
| 16:30 | 16:52 | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to CB pole
maintenance.
|  | 16:51 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT is restored.
|  | 16:53 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT is restored.
| 17:15 |  | Korerhat-Chowmuhani 230kV ckt-2 was switched on for the first time at 17:15 hrs from both
end. Now, this circuit is sharing the load in parallelly with Korerhat-Chowmuhani
230kV circuit-4.
| 17:27 |  | 250/350MVA 230/132kV Transformer-3 was switched on for the first time at 17:27 hrs at
Chowmuhani 230/132kV grid substation. Now, this transformer is sharing the load in
parallelly with Tr-1.
|  | 17:58 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT is restored.
| 18:00 |  | Evening Peak Generation:11336 MW.
| 18:52 |  | Ashuganj 420 MW CCPP (East) ST was sync.
| 00:12 |  | Bibiyana-3 400 MW CCPP GT and ST both tripped due to GBC-1 trip.
| 00:12 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
| 00:13 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- ST
| 02:21 |  | Bibiyana-3 400 MW CCPP GT was synchronized.
| 02:21 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 05:00 |  | Minimum generation 7704 MW
| 05:06 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- ST
| 07:11 |  | Hasnabad-Shyampur 230kV Ckt-1 Scheduled S/D from Hasnabad 230/132kV end Due to Annual
maintenance. and from Shyampur 230/132kV end Due to Annual maintenance work.
| 07:17 |  | Goalpara- Khulna (C) 132kV Ckt-1 Project Work S/D from Khulna (C) end Due to Project
work and from Goalpara 132/33kV end Due to Maintenence works.
| 07:37 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT Scheduled S/D Due to Annual
Maintenance.
| 07:38 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT Scheduled S/D Due to Annual
Maintenance
| 07:41 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to Annual Maintenance
| 07:41 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to Annual Maintenance
| 07:51 |  | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
maintenance (Dohazari side)
| 07:55 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-1
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 336 | 8204400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 140 | 3390000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5889257 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 227628 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 103680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 468158 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 73140 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18.5 | 402600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 520920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 131942 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 115 | 208004 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 62 | 405360 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 25 | 168826 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 836640 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 126286 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 428 | 9610390 | FGMO
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 21600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 1710.5 | 30788831
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133650 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 29 | 53760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1107000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 2808105 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 70 | 247563 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 34000 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 16320 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 257760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 8 | 24254 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 331200 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14432726 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 12960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 352 | 8261818.18 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1474 | 27742358.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 4881000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 7640000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 15 | 869500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 404136 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 332160 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 669091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1047880 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 267636 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2409608 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 99 | 390240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 116 | 2338560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 238400 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 3 | 10920 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 34560 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 423409 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1049 | 21957100
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 1101120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 278400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 788400 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 213440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 80880 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 122 | 2470740
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 57659 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 722760 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 682560 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1657920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 4323360 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 366000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 399768 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7371000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 395 | 8992000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1036 | 24573027
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 19327272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6242688 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 391680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1048 | 21330910 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2170 | 47292550
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 455 | 7596435 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2737000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1075 | 20654545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2391130 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2554 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1755 | 33381664.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 260312 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 184 | 4183909 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9213381 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1270 | 26301818 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 261744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 427280 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1868 | 40670464
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 343891 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1304727 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 212524 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29109.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 251368 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 140284 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 762480 | -
Rangpur Area Total |  |  |  |  | 950 | 152 | 3044383.48
Eastern Grid Total |  |  |  |  | 17383.855 | 5391.5 | 107532056.18
Western Grid Total |  |  |  |  | 10821.56 | 5945 | 124389061.93
National Grid Total |  |  |  |  | 28205.415 | 11336.5 | 231921118.11
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7671.37 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3297.6 | MW
i) Dhaka area |  |  | 4280.37 |  | MW | i) Khulna area |  |  |  | 1263.4 | MW
ii) Chattogram area |  |  | 1198 |  | MW | ii) Barishal area |  |  |  | 304 | MW
iii) Cumilla area |  |  | 936 |  | MW | iii) Rajshahi area |  |  |  | 972.2 | MW
iv) Mymensingh area |  |  | 850 |  | MW | iv) Rangpur area |  |  |  | 758 | MW
v) Sylhet area |  |  | 407 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10968.97 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 00:00 | 67 | Hathazari | 56 | 19:00 | 133 | Niamatpur | 41 | 18:00
2 | AKSML | 112 | 06:00 | 68 | Ishurdi | 45 | 18:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 28 | 12:00 | 69 | Jaldhaka | 53 | 18:00 | 135 | PHP | 9 | 11:00
4 | Agargaon | 93 | 13:00 | 70 | Jamalpur | 86 | 18:00 | 136 | Pabna | 75 | 18:00
5 | Agrabad | 60 | 18:00 | 71 | Jashore | 98 | 13:00 | 137 | Palashbari | 86 | 18:00
6 | Amnura | 18 | 08:00 | 72 | Jhenaidah | 95 | 18:00 | 138 | Panchagarh | 45 | 18:00
7 | Ashuganj | 69 | 14:00 | 73 | Joydebpur | 122 | 18:00 | 139 | Patiya | 6 | 18:00
8 | BSRM | 160 | 02:00 | 74 | Joypurhat | 44 | 18:00 | 140 | Patuakhali | 42 | 21:00
9 | Bagerhat | 61 | 18:00 | 75 | Juldah | 14 | 11:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 57 | 18:00 | 76 | KSRM | 36 | 06:00 | 142 | Postogola | 49 | 13:00
11 | Bakulia | 62 | 18:00 | 77 | Kabirpur | 190 | 18:00 | 143 | Purbachal | 29 | 13:00
12 | Banani | 49.6 | 13:00 | 78 | Kachua | 55 | 20:00 | 144 | Purbasadipur | 103 | 18:00
13 | Bangabhaban | 15 | 10:00 | 79 | Kallyanpur | 66 | 12:00 | 145 | Rahanpur | 21 | 18:00
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rahim | 42 | 16:00
15 | Barguna | 14 | 18:00 | 81 | Kamrangirchar | 66 | 13:00 | 147 | Rajbari | 57 | 18:00
16 | Barishal | 86 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 94 | 18:00
17 | Barishal-230 | 62 | 19:00 | 83 | Kasba | 21 | 18:00 | 149 | Rajshahi | 91 | 13:00
18 | Baroaulia | 56 | 13:00 | 84 | Kazla | 90 | 13:00 | 150 | Rajshahi-230 | 32 | 00:00
19 | Baroirhat | 50 | 18:00 | 85 | Keranigonj | 65 | 13:00 | 151 | Ramganj | 64 | 18:00
20 | Bashundhara | 147 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 30 | 18:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 46 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 48 | 18:00 | 88 | Khulshi | 165 | 17:00 | 154 | Rangpur | 103 | 18:00
23 | Benapole | 42 | 18:00 | 89 | Kishoreganj | 82 | 18:30 | 155 | Ruppur | 3 | 12:00
24 | Bhaluka | 121 | 18:00 | 90 | Kodda | 258 | 18:00 | 156 | SSM | 3 | 06:00
25 | Bhandaria | 36 | 19:30 | 91 | Kulaura | 29 | 18:00 | 157 | Saidpur | 92 | 18:00
26 | Bhangura | 23 | 18:00 | 92 | Kurigram | 48 | 18:00 | 158 | Satkhira | 84 | 07:00
27 | Bheramara(GK) | 42 | 18:00 | 93 | Kushtia | 112 | 18:00 | 159 | Satmasjid | 78 | 13:00
28 | Bhulta | 180 | 18:30 | 94 | Laksam | 20 | 17:00 | 160 | Savar | 183 | 12:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 23 | 18:00 | 161 | SevenRings | 5.71 | 02:00
30 | Bogura | 113 | 18:00 | 96 | Lalbag | 60 | 13:00 | 162 | ShahCement | 23 | 22:00
31 | Borhanuddin | 63 | 21:00 | 97 | Lalmonirhat | 43 | 18:00 | 163 | Shahjadpur | 56 | 12:00
32 | Brahmanbaria | 84 | 18:00 | 98 | MI_Cement | 17.7 | 00:00 | 164 | Shahjibazar | 74 | 18:00
33 | Cantonment | 78 | 13:00 | 99 | Madanganj | 30 | 00:00 | 165 | Shahmirpur | 38 | 18:00
34 | Chandina | 0 | 00:00 | 100 | Madaripur | 69 | 19:30 | 166 | Shariatpur | 55 | 21:00
35 | Chandpur | 50 | 19:30 | 101 | Madartek | 62 | 13:00 | 167 | Sherpur | 100 | 18:00
36 | Chandraghona | 26 | 18:00 | 102 | Madunaghat | 37 | 18:00 | 168 | Shikalbaha | 23 | 11:00
37 | Chapai | 51 | 12:00 | 103 | Magura | 45 | 18:00 | 169 | Shitalakhya | 64.1 | 12:00
38 | Charsaidpur | 39 | 16:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 34 | 15:00
39 | Chauddagram | 50 | 13:00 | 105 | Maijdee | 21 | 18:00 | 171 | Shyampur | 122 | 02:00
40 | Chhatak | 27 | 17:00 | 106 | Manikganj | 89 | 18:30 | 172 | Siddhirganj | 95 | 15:00
41 | Chowmuhani | 104 | 18:00 | 107 | Maniknagar | 49 | 13:00 | 173 | Sirajganj | 82 | 18:30
42 | Chuadanga | 68 | 18:00 | 108 | Matarbari | 35 | 18:00 | 174 | Sonargaon | 98 | 10:00
43 | Coxsbazar | 103 | 18:00 | 109 | Matuail | 62 | 12:00 | 175 | Sreemongol | 60 | 18:00
44 | Cumilla(N) | 90 | 18:00 | 110 | Metrorail_Motijheel | 32 | 09:00 | 176 | Sreepur | 78 | 18:30
45 | Cumilla(S) | 123 | 15:00 | 111 | Metrorail_Uttara | 7 | 18:00 | 177 | Srinagar | 30 | 20:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 84 | 09:00 | 178 | Sunamganj | 39 | 19:30
47 | Daudkandi | 110 | 20:00 | 113 | Mirpur | 112 | 12:00 | 179 | Sylhet | 32 | 18:00
48 | DhakaUniversity | 64 | 14:00 | 114 | Mirsorai | 38 | 12:00 | 180 | Sylhet-132 | 84 | 17:00
49 | Dhamrai | 108 | 16:00 | 115 | Mirzapur | 33 | 07:00 | 181 | TK | 15 | 18:00
50 | Dhanmondi | 88 | 13:00 | 116 | Mithapukur | 43 | 18:00 | 182 | Tangail | 120 | 17:00
51 | Dohazari | 63 | 18:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 14 | 18:00
52 | Faridpur | 113 | 18:00 | 118 | Mogbazar | 69.6 | 15:00 | 184 | Tasnim | 29 | 16:00
53 | Fatullah | 94 | 15:00 | 119 | Mongla | 44 | 08:00 | 185 | Thakurgaon | 78 | 18:00
54 | Fenchuganj | 23 | 22:00 | 120 | Motijheel | 26 | 13:00 | 186 | Tongi | 95 | 12:00
55 | Feni | 66 | 18:00 | 121 | Muktagacha | 25 | 07:00 | 187 | Ullahpara | 24 | 18:30
56 | GPH | 74 | 18:00 | 122 | Munshiganj | 86 | 14:00 | 188 | Ullon | 54 | 13:00
57 | Ghatail | 62 | 18:00 | 123 | Muradnagar | 24 | 18:00 | 189 | Uttara | 62 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 132 | 18:00 | 190 | UttaraNew | 13 | 13:00
59 | Ghorashal-230 | 83 | 19:30 | 125 | Naogaon | 79 | 13:00 | 191 | Zigatola | 56 | 14:00
60 | Goalpara | 27 | 13:00 | 126 | Narail | 41 | 18:00
61 | Gollamari | 78 | 13:00 | 127 | Narinda | 57 | 13:00
62 | Gopalganj | 75.4 | 18:00 | 128 | Narshingdi | 136 | 20:00
63 | Gulshan | 88 | 13:00 | 129 | Natore | 95 | 18:00
64 | Halishahar | 55 | 11:00 | 130 | Nawabganj | 29.2 | 13:00
65 | HaripurSBU | 141 | 17:00 | 131 | Netrakona | 102 | 18:00
66 | Hasnabad | 71 | 14:00 | 132 | New | 65.4 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9249.5 | 0 |  | 9249.5
1:00 | 8732.5 | 0 |  | 8732.5
2:00 | 8322.5 | 0 |  | 8322.5
3:00 | 8024.5 | 0 |  | 8024.5
4:00 | 7827.5 | 0 |  | 7827.5
5:00 | 7737.5 | 0 |  | 7737.5
6:00 | 8215 | 0 |  | 8215
7:00 | 8890.72 | 0 |  | 8890.72
8:00 | 9575.96 | 0 |  | 9575.96
9:00 | 9546.93 | 0 |  | 9546.93
10:00 | 9264.01 | 0 |  | 9264.01
11:00 | 9572.12 | 0 |  | 9572.12
12:00 | 10326.71 | 0 |  | 10326.71
13:00 | 10530.87 | 0 |  | 10530.87
14:00 | 10021.88 | 0 |  | 10021.88
15:00 | 9791.13 | 0 |  | 9791.13
16:00 | 9766.64 | 0 |  | 9766.64
17:00 | 10273.04 | 0 |  | 10273.04
18:00 | 11336.5 | 0 |  | 11336.5
19:00 | 10887.2 | 0 |  | 10887.2
19:30 | 10815 | 0 |  | 10815
20:00 | 10688 | 0 |  | 10688
21:00 | 10531.03 | 0 |  | 10531.03
22:00 | 10088.91 | 0 |  | 10088.91
23:00 | 9648.99 | 0 |  | 9648.99
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4541.5 | 4708 | 9249.5 | DAILY GENERATION CURVE
00:30 | 4496 | 4495 | 8991
01:00 | 4450.5 | 4282 | 8732.5 | 01-12-2025
01:30 | 4317.5 | 4210 | 8527.5
02:00 | 4184.5 | 4138 | 8322.5
02:30 | 4072 | 4101.5 | 8173.5
03:00 | 3959.5 | 4065 | 8024.5
03:30 | 3896.5 | 4029.5 | 7926
04:00 | 3833.5 | 3994 | 7827.5
04:30 | 3738.5 | 4044 | 7782.5
05:00 | 3643.5 | 4094 | 7737.5
05:30 | 3784.25 | 4192 | 7976.25
06:00 | 3925 | 4290 | 8215
06:30 | 4026.97 | 4525.89 | 8552.86
07:00 | 4128.94 | 4761.78 | 8890.72
07:30 | 4170.87 | 5062.47 | 9233.34
08:00 | 4212.8 | 5363.16 | 9575.96
08:30 | 4197.925 | 5363.52 | 9561.445
09:00 | 4183.05 | 5363.88 | 9546.93
09:30 | 4217.4 | 5188.07 | 9405.47
10:00 | 4251.75 | 5012.26 | 9264.01
10:30 | 4345.385 | 5072.68 | 9418.065
11:00 | 4439.02 | 5133.1 | 9572.12
11:30 | 4513.595 | 5435.82 | 9949.415
12:00 | 4588.17 | 5738.54 | 10326.71
12:30 | 4659.225 | 5769.565 | 10428.79
13:00 | 4730.28 | 5800.59 | 10530.87
13:30 | 4611.315 | 5665.06 | 10276.375
14:00 | 4492.35 | 5529.53 | 10021.88
14:30 | 4448.585 | 5457.92 | 9906.505
15:00 | 4404.82 | 5386.31 | 9791.13
15:30 | 4447.17 | 5331.715 | 9778.885
16:00 | 4489.52 | 5277.12 | 9766.64
16:30 | 4673.765 | 5346.075 | 10019.84
17:00 | 4858.01 | 5415.03 | 10273.04
17:30 | 5124.755 | 5680.015 | 10804.77
18:00 | 5391.5 | 5945 | 11336.5
18:30 | 5128.35 | 5983.5 | 11111.85
19:00 | 4865.2 | 6022 | 10887.2
19:30 | 4803 | 6012 | 10815
20:00 | 4720 | 5968 | 10688
20:30 | 4701 | 5908.515 | 10609.515 |  | Executive Engineer
21:00 | 4682 | 5849.03 | 10531.03 |  | Network Operation Division
21:30 | 4591 | 5718.97 | 10309.97
22:00 | 4500 | 5588.91 | 10088.91
22:30 | 4455.25 | 5413.7 | 9868.95
23:00 | 4410.5 | 5238.49 | 9648.99

## En-Curve
QF-LDC-12
Date | 01-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2961 | 1276.5 | 882 | 0 | 100 | 834 | 46 | 3126 | 0 | 0 | 16 | 0 | 0 | 8 | 0 | DAILY ENERGY CURVE
00:30 | 2951.5 | 1244 | 834.5 | 0 | 100 | 834.5 | 46 | 2963 | 0 | 0 | 12 | 0 | 0 | 5.5 | 0 | 01-12-2025
01:00 | 2942 | 1211.5 | 787 | 0 | 100 | 835 | 46 | 2800 | 0 | 0 | 8 | 0 | 0 | 3 | 0
01:30 | 2913.5 | 1163 | 762.5 | 0 | 95 | 836 | 46 | 2704.5 | 0 | 0 | 4 | 0 | 0 | 3 | 0 | Energy Generated | 231.9211 |  | MKWHr
02:00 | 2885 | 1114.5 | 738 | 0 | 90 | 837 | 46 | 2609 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2853.5 | 1081 | 711 | 0 | 91 | 835 | 46 | 2554 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Total Energy Requirement | 231.9211 |  | MKWHr
03:00 | 2822 | 1047.5 | 684 | 0 | 92 | 833 | 46 | 2499 | 0 | 0 | 0 | 0 | 0 | 1 | 0
03:30 | 2754.5 | 1034.5 | 684 | 0 | 90 | 832 | 46 | 2484.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
04:00 | 2687 | 1021.5 | 684 | 0 | 88 | 831 | 46 | 2470 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2718.5 | 1009 | 660.5 | 0 | 84 | 832.5 | 46 | 2432 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2750 | 996.5 | 637 | 0 | 80 | 834 | 46 | 2394 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2768.5 | 1061.75 | 636.5 | 0 | 82 | 876.5 | 46 | 2505 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2787 | 1127 | 636 | 0 | 84 | 919 | 46 | 2616 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2847.5 | 1156 | 686.5 | 0 | 87 | 1006.5 | 46 | 2689.5 | 20.36 | 0 | 13.5 | 0 | 0 | 0 | 0
07:00 | 2908 | 1185 | 737 | 0 | 90 | 1094 | 46 | 2763 | 40.72 | 0 | 27 | 0 | 0 | 0 | 0
07:30 | 2864.5 | 1207.5 | 733.5 | 0 | 96 | 1187.805 | 46 | 2950.5 | 107.035 | 0 | 40.5 | 0 | 0 | 0 | 0
08:00 | 2821 | 1230 | 730 | 0 | 102 | 1281.61 | 46 | 3138 | 173.35 | 0 | 54 | 0 | 0 | 0 | 0
08:30 | 2766 | 1251.75 | 730 | 0 | 91 | 1234.415 | 46 | 3104.5 | 272.78 | 0 | 65 | 0 | 0 | 0 | 0
09:00 | 2711 | 1273.5 | 730 | 0 | 80 | 1187.22 | 46 | 3071 | 372.21 | 0 | 76 | 0 | 0 | 0 | 0
09:30 | 2755.5 | 1283.5 | 755 | 0 | 84 | 1050.63 | 46 | 2979 | 395.84 | 4 | 52 | 0 | 0 | 0 | 0
10:00 | 2800 | 1293.5 | 780 | 0 | 88 | 914.04 | 46 | 2887 | 419.47 | 8 | 28 | 0 | 0 | 0 | 0
10:30 | 2801.5 | 1320 | 779.5 | 0 | 92 | 916.205 | 46 | 2871.5 | 482.36 | 12.5 | 34.5 | 62 | 0 | 0 | 0
11:00 | 2803 | 1346.5 | 779 | 0 | 96 | 918.37 | 46 | 2856 | 545.25 | 17 | 41 | 124 | 0 | 0 | 0
11:30 | 2852.5 | 1364.5 | 826 | 0 | 100 | 1014.97 | 46 | 2936 | 569.445 | 17 | 76 | 147 | 0 | 0 | 0
12:00 | 2902 | 1382.5 | 873 | 0 | 104 | 1111.57 | 46 | 3016 | 593.64 | 17 | 111 | 170 | 0 | 0 | 0
12:30 | 2934.5 | 1308.5 | 872.5 | 0 | 101 | 1190.695 | 46 | 3084.5 | 522.095 | 17 | 225.5 | 126.5 | 0 | 0 | 0
13:00 | 2967 | 1234.5 | 872 | 0 | 98 | 1269.82 | 46 | 3153 | 450.55 | 17 | 340 | 83 | 0 | 0 | 0
13:30 | 2867 | 1202.75 | 872 | 0 | 98 | 1274.01 | 46 | 3154 | 379.615 | 12.5 | 328.5 | 41.5 | 0 | 0.5 | 0
14:00 | 2767 | 1171 | 872 | 0 | 98 | 1278.2 | 46 | 3155 | 308.68 | 8 | 317 | 0 | 0 | 1 | 0
14:30 | 2764 | 1160.25 | 872 | 0 | 110 | 1214.6 | 46 | 3152 | 272.155 | 8 | 307 | 0 | 0 | 0.5 | 0
15:00 | 2761 | 1149.5 | 872 | 0 | 122 | 1151 | 46 | 3149 | 235.63 | 8 | 297 | 0 | 0 | 0 | 0
15:30 | 2839.5 | 1169.5 | 872.5 | 0 | 115 | 1122.5 | 46 | 3145.5 | 164.885 | 8 | 295.5 | 0 | 0 | 0 | 0
16:00 | 2918 | 1189.5 | 873 | 0 | 108 | 1094 | 46 | 3142 | 94.14 | 8 | 294 | 0 | 0 | 0 | 0
16:30 | 2985 | 1189.75 | 873 | 0 | 112 | 1094 | 46 | 3204 | 50.09 | 34 | 432 | 0 | 0 | 0 | 0
17:00 | 3052 | 1190 | 873 | 0 | 116 | 1094 | 46 | 3266 | 6.04 | 60 | 570 | 0 | 0 | 0 | 0
17:30 | 3061 | 1196.25 | 872.5 | 0 | 116 | 1182 | 46 | 3430.5 | 3.02 | 91 | 806.5 | 0 | 0 | 0 | 0
18:00 | 3070 | 1202.5 | 872 | 0 | 116 | 1270 | 46 | 3595 | 0 | 122 | 1043 | 0 | 0 | 0 | 0
18:30 | 3052 | 1182.35 | 872.5 | 0 | 111 | 1300 | 46 | 3616.5 | 0 | 106 | 824.5 | 0 | 0 | 1 | 0
19:00 | 3034 | 1162.2 | 873 | 0 | 106 | 1330 | 46 | 3638 | 0 | 90 | 606 | 0 | 0 | 2 | 0
19:30 | 3134 | 1182 | 872 | 0 | 106 | 1330 | 46 | 3644 | 0 | 74 | 426 | 0 | 0 | 1 | 0
20:00 | 3103 | 1164 | 872 | 0 | 104 | 1329 | 46 | 3608 | 0 | 74 | 388 | 0 | 0 | 0 | 0
20:30 | 3120.5 | 1167 | 872.5 | 0 | 104 | 1327.515 | 46 | 3548.5 | 0 | 45.5 | 378 | 0 | 0 | 0 | 0
21:00 | 3138 | 1170 | 873 | 0 | 104 | 1326.03 | 46 | 3489 | 0 | 17 | 368 | 0 | 0 | 0 | 0
21:30 | 3110.5 | 1166 | 873 | 0 | 104 | 1327.47 | 46 | 3407 | 0 | 8.5 | 267.5 | 0 | 0 | 0 | 0
22:00 | 3083 | 1162 | 873 | 0 | 104 | 1328.91 | 46 | 3325 | 0 | 0 | 167 | 0 | 0 | 0 | 0
22:30 | 3104.5 | 1164.75 | 873 | 0 | 100 | 1268.2 | 46 | 3202 | 0 | 0 | 110.5 | 0 | 0 | 0 | 0
23:00 | 3126 | 1167.5 | 873 | 0 | 96 | 1207.49 | 46 | 3079 | 0 | 0 | 54 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 401 | 03:00 | 381 | 12:00 | Meghnaghat | 402 | 04:00 | 384 | 12:00
Ashuganj | 401 | 4:00 | 379 | 13:00 | Payra | 416 | 02:00 | 409 | 12:00
Bhulta | 399 | 04:00 | 376 | 12:00 | Rahanpur | 418 | 03:00 | 405 | 13:00
Bibiana | 401 | 04:00 | 390 | 12:00 | Rampal | 413 | 01:00 | 398 | 19:30
BIPTC | 408 | 01:00 | 396 | 08:00
Bogura | 414 | 04:00 | 394 | 13:00
Gopalganj | 410 | 04:00 | 393 | 12:00
Kaliakoir | 400 | 04:00 | 377 | 12:00
Korerhat | 407 | 04:00 | 391 | 12:00
Madunaghat | 402 | 04:00 | 388 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 242 | 04:00 | 228 | 12:00 | Kachua | 239 | 02:00 | 227 | 12:00
AKSML | 239 | 03:00 | 228 | 12:00 | Kaliakoir | 238 | 03:00 | 224 | 12:00
Aminbazar | 241 | 05:00 | 228 | 11:00 | Keranigonj | 239 | 04:00 | 226 | 12:00
Ashuganj | 239 | 01:00 | 227 | 13:00 | Khulna(S) | 241 | 01:00 | 229 | 13:00
Ashuganj-400 | 239 | 01:00 | 227 | 13:00 | Korerhat | 238 | 02:00 | 230 | 12:00
Baghabari | 239 | 01:00 | 229 | 12:00 | Madunaghat | 239 | 04:00 | 229 | 12:00
Barapukuria | 226 | 06:00 | 215 | 18:00 | Madunaghat-400 | 240 | 04:00 | 231 | 13:00
Barapukuria-230 | 226 | 06:00 | 215 | 18:00 | Maniknagar | 234 | 03:00 | 221 | 12:00
Barishal | 243 | 01:00 | 236 | 18:00 | Meghnaghat | 241 | 04:00 | 235 | 00:00
Bheramara | 238 | 05:00 | 225 | 13:00 | Meghnaghat-400 | 237 | 04:00 | 225 | 12:00
Bhulta | 235 | 04:00 | 220 | 12:00 | Mirsorai | 239 | 04:00 | 228 | 13:00
Bibiana | 238 | 04:00 | 228 | 12:00 | Rajshahi | 238 | 06:00 | 225 | 13:00
BIPTC | 241 | 01:00 | 226 | 12:00 | Rampal | 238 | 01:00 | 228 | 12:00
Bogura | 239 | 01:00 | 228 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 239 | 04:00 | 227 | 18:00 | Rampura | 234 | 04:00 | 219 | 13:00
Borhanuddin | 245 | 01:00 | 240 | 13:00 | Shikalbaha | 238 | 04:00 | 229 | 12:00
BSRM | 238 | 04:00 | 227 | 12:00 | Shyampur | 237 | 03:00 | 225 | 12:00
Cumilla(N) | 236 | 01:00 | 225 | 12:00 | Siddhirganj | 234 | 01:00 | 222 | 12:00
Faridpur | 243 | 03:00 | 135 | 18:30 | Sirajgonj | 243 | 01:00 | 235 | 13:00
Fenchuganj | 236 | 02:00 | 229 | 12:00 | Sreepur | 234 | 01:00 | 223 | 13:00
Feni | 237 | 04:00 | 226 | 12:00 | Tongi | 235 | 04:00 | 221 | 11:00
Ghorashal | 0 | 00:00 | N/A | N/A
Ghorashal-230 | 234 | 05:00 | 214 | 19:30
Gopalganj | 243 | 03:00 | 233 | 12:00
GPH | 239 | 03:00 | 229 | 12:00
Haripur | 235 | 03:00 | 222 | 11:00
Hasnabad | 237 | 04:00 | 226 | 13:00
Hathazari | 237 | 04:00 | 228 | 11:00
Ishurdi | 241 | 04:00 | 228 | 13:00
Jhenaidah | 239 | 01:00 | 224 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 126 | 12:00 | Lalbag | 137 | 04:00 | 128 | 12:00
Agargaon | 139 | 04:00 | 130 | 12:00 | Lalmonirhat | 132 | 04:00 | 123 | 18:00
Agrabad | 137 | 01:00 | 130 | 12:00 | Madanganj | 135 | 02:00 | 130 | 18:30
AKS | 135 | 01:00 | 129 | 12:00 | Madaripur | 140 | 04:00 | 135 | 12:00
Aminbazar | 140 | 05:00 | 132 | 11:00 | Madartek | 136 | 06:00 | 125 | 12:00
Amnura | 138 | 00:00 | 131 | 12:00 | Madunaghat | 140 | 04:00 | 133 | 12:00
Ashuganj | 142 | 08:00 | 137 | 13:00 | Magura | 140 | 01:00 | 130 | 13:00
Bagerhat | 137 | 03:00 | 128 | 18:00 | Mahasthangarh | 136 | 05:00 | 128 | 08:00
Bajitpur | 137 | 05:00 | 131 | 12:00 | Maijdee | 135 | 03:00 | 128 | 13:00
Bakulia | 138 | 00:00 | 132 | 12:00 | Manikganj | 132 | 04:00 | 119 | 16:00
Banani | 136 | 03:00 | 125 | 11:00 | Maniknagar | 139 | 03:00 | 129 | 12:00
Bangabhaban | 139 | 06:00 | 130 | 12:00 | Matarbari | 131 | 04:00 | 121 | 10:00
Barapukuria | 138 | 04:00 | 130 | 18:00 | Matuail | 137.3 | 03:00 | 129 | 13:00
Barguna | 137 | 05:00 | 133 | 18:00 | Metrorail_Motijheel | 139 | 03:00 | 129 | 12:00
Barishal | 140 | 01:00 | 134 | 12:00 | Metrorail_Uttara | 134 | 01:00 | 122 | 12:00
Barishal-230 | 140 | 01:00 | 135 | 12:00 | Millgate | 135 | 02:00 | 123 | 12:00
Baroaulia | 138 | 01:00 | 132 | 12:00 | Mirpur | 139 | 05:00 | 130 | 11:00
Baroirhat | 136 | 01:00 | 130 | 12:00 | Mirzapur | 135 | 02:00 | 126 | 12:00
Bashundhara | 136 | 02:00 | 125 | 12:00 | Mithapukur | 135 | 04:00 | 125 | 08:00
BashundharaCement | 135 | 02:00 | 130 | 18:30 | MI_Cement | 137 | 05:00 | 127 | 12:00
Beanibazar | 134 | 00:00 | 130 | 13:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 140 | 03:00 | 126 | 13:00 | Mogbazar | 139 | 05:00 | 127 | 13:00
Bhaluka | 135 | 03:00 | 126 | 13:00 | Mongla | 137 | 02:00 | 128 | 12:00
Bhandaria | 138 | 05:00 | 134 | 12:00 | Motijheel | 139 | 06:00 | 130 | 12:00
Bhangura | 137 | 00:00 | 131 | 13:00 | Muktagacha | 134 | 09:00 | 124 | 18:00
Bheramara | 142 | 01:00 | 136 | 13:00 | Munshiganj | 134 | 00:00 | 128 | 12:00
Bheramara(GK) | 142 | 03:00 | 136 | 13:00 | Muradnagar | 138 | 05:00 | 130 | 12:00
Bhulta | 130 | 00:00 | 126 | 12:00 | Mymensingh | 135 | 09:00 | 121 | 18:00
Bog-Sherpur | 137 | 03:00 | 130 | 08:00 | Naogaon | 135 | 01:00 | 124 | 06:00
Bogura | 138 | 04:00 | 130 | 18:00 | Narail | 140 | 02:00 | 130 | 13:00
Bogura-230 | 137 | 03:00 | 130 | 08:00 | Narinda | 139 | 03:00 | 129 | 12:00
Brahmanbaria | 138 | 05:00 | 132 | 13:00 | Narshingdi | 137 | 00:00 | 124 | 12:00
Cantonment | 138 | 02:00 | 129 | 12:00 | Natore | 138 | 04:00 | 131 | 12:00
Chandina | 140 | 04:00 | 132 | 12:00 | Nawabganj | 138 | 04:00 | 129 | 12:00
Chandpur | 140 | 18:00 | 132 | 12:00 | Netrakona | 131 | 00:00 | 123 | 13:00
Chandraghona | 139 | 02:00 | 133 | 12:00 | New | 136 | 04:00 | 125 | 14:00
Chapai | 137 | 00:00 | 134 | 19:30 | Niamatpur | 139 | 04:00 | 135 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 137 | 03:00 | 128 | 12:00 | Noapara | 139 | 04:00 | 131 | 12:00
Chauddagram | 137 | 01:00 | 130 | 12:00 | Pabna | 140 | 01:00 | 134 | 12:00
Chhatak | 133 | 04:00 | 128 | 14:00 | Palashbari | 134 | 04:00 | 125 | 08:00
Chowmuhani | 133 | 01:00 | 129 | 12:00 | Panchagarh | 139 | 01:00 | 121 | 8:00
Chuadanga | 141 | 05:00 | 130 | 13:00 | Patiya | 139 | 04:00 | 132 | 12:00
Coxsbazar | 130 | 02:00 | 117 | 12:00 | Patuakhali | 136 | 05:00 | 134 | 01:00
Cumilla(N) | 139 | 01:00 | 131 | 12:00 | Payra | 137 | 02:00 | 134 | 13:00
Cumilla(S) | 138 | 04:00 | 125 | 15:00 | PHP | 136 | 05:00 | 128 | 13:00
Daganbhuiyan | 136 | 04:00 | 129 | 12:00 | Postogola | 138 | 04:00 | 129 | 12:00
Daudkandi | 136 | 04:00 | 128 | 12:00 | Purbachal | 136 | 02:00 | 126 | 12:00
DhakaUniversity | 136 | 02:00 | 126 | 13:00 | Purbasadipur | 135 | 04:00 | 125 | 18:00
Dhamrai | 136 | 03:00 | 127 | 12:00 | Rahanpur | 140 | 00:00 | 136 | 08:00
Dhanmondi | 138.5 | 02:00 | 130 | 12:00 | Rahanpur-400 | 141 | 03:00 | 136 | 08:00
Dohazari | 135 | 00:00 | 129 | 13:00 | Rahim | 136 | 05:00 | 129 | 13:00
Faridpur | 140 | 03:00 | 135 | 12:00 | Rajbari | 140 | 02:00 | 134 | 12:00
Fatullah | 141 | 03:00 | 127 | 12:00 | Rajendrapur | 136 | 01:00 | 128 | 13:00
Fenchuganj | 139 | 00:00 | 136 | 12:00 | Rajshahi | 137 | 01:00 | 130 | 12:00
Feni | 135 | 02:00 | 128 | 12:00 | Rajshahi-230 | 137 | 02:00 | 130 | 13:00
Feni-230 | 136 | 04:00 | 129 | 12:00 | Ramganj | 135 | 01:00 | 128 | 12:00
Ghatail | 132 | 04:00 | 122 | 12:00 | Rampur | 138 | 01:00 | 130 | 12:00
Ghorashal | 136 | 00:00 | 130 | 12:00 | Rampura | 136 | 04:00 | 126 | 12:00
Goalpara | 141 | 02:00 | 132 | 12:00 | Rangamati | 139 | 02:00 | 132 | 12:00
Gollamari | 139 | 01:00 | 132 | 12:00 | Rangpur | 134 | 02:00 | 127 | 16:00
Gopalganj | 140 | 02:00 | 132 | 13:00 | Ruppur | 141 | 04:00 | 135 | 13:00
Gopalganj-400 | 141 | 02:00 | 134 | 17:00 | Saidpur | 135 | 11:00 | 122 | 08:00
Gulshan | 136 | 04:00 | 126 | 12:00 | Satkhira | 138 | 03:00 | 129 | 13:00
Halishahar | 138 | 01:00 | 131 | 12:00 | Satmasjid | 138 | 04:00 | 130 | 11:00
Haripur | 138 | 04:00 | 130 | 12:00 | Savar | 138 | 18:00 | 130 | 11:00
HaripurSBU | 138 | 04:00 | 131 | 12:00 | SevenRings | 137 | 01:00 | 129 | 13:00
Hasnabad | 139 | 04:00 | 131 | 15:00 | ShahCement | 137 | 02:00 | 128 | 12:00
Hathazari | 139 | 04:00 | 135 | 11:00 | Shahjadpur | 140 | 00:00 | 135 | 19:00
Ishurdi | 142 | 01:00 | 136 | 13:00 | Shahjibazar | 139 | 01:00 | 134 | 12:00
Jaldhaka | 133 | 04:00 | 121 | 08:00 | Shahmirpur | 138 | 00:00 | 132 | 12:00
Jamalpur | 132 | 09:00 | 121 | 18:00 | Shariatpur | 140 | 02:00 | 134 | 12:00
Jashore | 139 | 04:00 | 127 | 13:00 | Sherpur | 133 | 09:00 | 116 | 18:00
Jhenaidah | 141 | 00:00 | 123 | 18:00 | Shikalbaha | 128 | 01:00 | 121 | 12:00
Jhenaidah-230 | 143 | 03:00 | 132 | 13:00 | Shikalbaha-230 | 140 | 03:00 | 134 | 12:00
Joydebpur | 137 | 05:00 | 126 | 13:00 | Shitalakhya | 137 | 05:00 | 127 | 12:00
Joypurhat | 133 | 01:00 | 125 | 18:00 | Sholosohor | 139 | 01:00 | 133 | 12:00
Juldah | 138 | 18:30 | 132 | 12:00 | Shyampur | 139 | 01:00 | 132 | 12:00
Kabirpur | 136 | 20:00 | 121 | 12:00 | Shyampur-230 | 141 | 03:00 | 133 | 12:00
Kachua | 140 | 02:00 | 133 | 12:00 | Siddhirganj | 137 | 01:00 | 129 | 12:00
Kaliakoir | 140 | 03:00 | 130 | 12:00 | Sirajganj | 137 | 02:00 | 130 | 15:00
Kallyanpur | 139 | 07:00 | 131 | 11:00 | Sonargaon | 136 | 02:00 | 130 | 13:00
Kalurghat | 140 | 04:00 | 133 | 12:00 | Sreemongol | 139 | 01:00 | 134 | 12:00
Kamrangirchar | 138 | 04:00 | 127 | 13:00 | Sreepur | 137 | 01:00 | 130 | 12:00
Kaptai | 141 | 4:00 | 136 | 12:00 | Srinagar | 138 | 03:00 | 128 | 12:00
Kasba | 138 | 04:00 | 129 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kazla | 139 | 04:00 | 129 | 13:00 | Sunamganj | 132 | 03:00 | 128 | 18:30
Keranigonj | 138 | 04:00 | 129 | 12:00 | Sylhet | 135 | 04:00 | 131 | 13:00
Khagrachori | 139 | 04:00 | 131 | 13:00 | Sylhet-132 | 133 | 00:00 | 132 | 10:00
Khulna | 139 | 05:00 | 131 | 12:00 | Tangail | 130 | 00:00 | 122 | 12:00
Khulna(S) | 140 | 01:00 | 132 | 13:00 | Taraganj | 134 | 04:00 | 123 | 08:00
Khulshi | 137 | 01:00 | 130 | 12:00 | Tasnim | 136 | 04:00 | 130 | 15:00
Kishoreganj | 136 | 03:00 | 128 | 13:00 | Thakurgaon | 138 | 19:00 | 119 | 08:00
Kodda | 135 | 20:00 | 122 | 12:00 | TK | 139 | 05:00 | 134 | 13:00
KSRM | 139 | 04:00 | 131 | 12:00 | Tongi | 136 | 04:00 | 125 | 13:00
Kulaura | 140 | 03:00 | 135 | 12:00 | Ullahpara | 138 | 02:00 | 132 | 12:00
Kurigram | 132 | 05:00 | 118 | 07:00 | Ullon | 136 | 04:00 | 126 | 12:00
Kushtia | 138 | 01:00 | 129 | 18:00 | Uttara | 135 | 03:00 | 123 | 16:00
Laksam | 165 | 13:00 | 133 | 12:00 | UttaraNew | 134 | 01:00 | 123 | 13:00
Lakshmipur | 134 | 02:00 | 129 | 12:00 | Zigatola | 138 | 06:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division