## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-12-2025 | during | 03-12-2025 | during | 03-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 359 | 325 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 140 | 140 | 450 | 450 | 220 | 220 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 10 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 16.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 18 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 2 | 73 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 44 | 162 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | ST under maint.
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Under maint.
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 412 | 422 | 718 | 718 | 718 | 718 | FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 10 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1331.5 | 1713.5 | 5753.9 | 5722.9 | 3423.08 | 3401.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage & #01 under maint.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 225 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 22 | 92 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 48 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 11 | 17 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.19 | 0 | 3.37 | 0 | 3.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 14 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 24 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 26 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 578 | 612 | 612 | 612 | 612 | 612 | #01 under maint.
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 6 | 0 | 4 | 0 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1283.19 | 1435 | 2592.09 | 2585.72 | 2096.87 | 2106.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 209 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 240 | 220 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 235 | 220 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 153 | 153 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 11 | 80 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 106 | 108 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 24 | 100 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 102 | 116 | 160 | 160 | 122 | 122 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 14 | 17.75 | 17.75 | 17.75 | 17.75 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 25 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 22 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1001 | 1135 | 2425.46 | 2365.46 | 2282.46 | 2222.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-12-2025 | during | 03-12-2025 | during | 03-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 12 | 157.5 | 157.5 | 76 | 76 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.51 | 0 | 44.07 | 0 | 44.07 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 116.51 | 90 | 360.17 | 314 | 231.17 | 185
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 20 | 30 | 30 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 158 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 192 | 205 | 195 | 195 | 195 | 195 | GBC problem.
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 817 | 868 | 915 | 915 | 851 | 851
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 873 | 848 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 221 | 197 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 53 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 872 | 1109 | 0 | 0 | 1100 | 1100 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2019 | 2154 | 2014 | 1942 | 2689.1 | 2617.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 304 | 506 | 0 | 0 | 306 | 455 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 948 | 900 | 1085.32 | 1085.32 | 1025.32 | 1025.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.34 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1477.34 | 1631 | 1883.32 | 1883.32 | 1799.32 | 1948.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 49.92 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 185 | 181 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.57 | 0 | 5.17 | 0 | 5.17 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 925.38 | 1468 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 46.93 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 82 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1706.8 | 2063 | 3077.04 | 2910.87 | 2542.26 | 2376.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 56 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 22 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.8 | 0 | 4.2 | 0 | 4.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 135 | 0 | 125.3 | 0 | 125.3 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 220.8 | 128 | 476.5 | 317 | 442.5 | 283
System Total |  |  |  |  | 28823.2 | 28205.415 | 9973.14 | 11217.5 | 19497.48 | 18956.27 | 16357.76 | 15990.55
Forecast Scenario (03-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9300 |  | 0 |  | 9300
|  |  |  | 1:00 | 8730 |  | 0 |  | 8730
|  |  |  | 2:00 | 8310 |  | 0 |  | 8310
|  |  |  | 3:00 | 8050 |  | 0 |  | 8050
|  |  |  | 4:00 | 7770 |  | 0 |  | 7770
|  |  |  | 5:00 | 7700 |  | 0 |  | 7700
|  |  |  | 6:00 | 8130 |  | 0 |  | 8130
|  |  |  | 7:00 | 8760 |  | 0 |  | 8760
|  |  |  | 8:00 | 9600 |  | 0 |  | 9600
|  |  |  | 9:00 | 9650 |  | 0 |  | 9650
|  |  |  | 10:00 | 9370 |  | 0 |  | 9370
|  |  |  | 11:00 | 9480 |  | 0 |  | 9480
|  |  |  | 12:00 | 9970 |  | 0 |  | 9970
|  |  |  | 13:00 | 10520 |  | 0 |  | 10520
|  |  |  | 14:00 | 9940 |  | 0 |  | 9940
|  |  |  | 15:00 | 9760 |  | 0 |  | 9760
|  |  |  | 16:00 | 9630 |  | 0 |  | 9630
|  |  |  | 17:00 | 10180 |  | 0 |  | 10180
|  |  |  | 18:00 | 11210 |  | 0 |  | 11210
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 10950 |  | 0 |  | 10950
|  |  |  | 19:30 | 10750 |  | 0 |  | 10750
|  |  |  | 20:00 | 10650 |  | 0 |  | 10650
|  |  |  | 21:00 | 10410 |  | 0 |  | 10410
|  |  |  | 22:00 | 10080 |  | 0 |  | 10080
|  |  |  | 23:00 | 9650 |  | 0 |  | 9650
Probable Maximum Temperature: |  |  | 26.80°C
Probable Maximum Demand at Day Peak: |  |  | 9970.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11210.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11210.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.80 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:17 hrs on 03-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-12-2025 | [28 empty] | Date: | 02-12-2025 | [28 empty] | Date: | 02-12-2025 | [28 empty] | Date: | 02-12-2025 | [28 empty] | Date: | 02-12-2025 | [17 empty] | Date: | 02-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 12 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 495 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 199 | 0 | 0 | 109 | 0 | 0 | 14 | 0 | 90 | 0 | 0 | 0 | 295 | 0 | 389 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 15 | 157 | 0 | 16 | 8 | 35 | 0 | 0 | 0 | 4393 | 845 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 858 | 0 | 0 | 0 | 1080.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 305 | 800 | 0 | 4906.73 | 9299.73 | 99.6
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 6 | 354 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 441 | 0 | 0 | 0 | 320 | 0 | 325 | 51 | 0 | 203 | 0 | 0 | 109 | 0 | 0 | 14 | 0 | 88 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 30 | 0 | 0 | 22 | 0 | 82 | 30 | 0 | 16 | 157 | 0 | 16 | 8 | 36 | 0 | 0 | 0 | 4005 | 752 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 1056.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 256 | 800 | 0 | 4729.16 | 8734.16 | 99.59
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 6 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 250 | 0 | 255 | 51 | 0 | 192 | 0 | 0 | 109 | 0 | 0 | 14 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 30 | 0 | 0 | 17 | 0 | 82 | 30 | 0 | 16 | 159 | 0 | 8 | 0 | 36 | 0 | 0 | 0 | 3845.5 | 704 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 919.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 256 | 800 | 0 | 4470.57 | 8316.07 | 99.59
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 20 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 240 | 0 | 240 | 51 | 0 | 209 | 0 | 0 | 109 | 0 | 0 | 14 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 12 | 0 | 30 | 0 | 0 | 17 | 0 | 41 | 20 | 0 | 16 | 159 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 3806.5 | 670 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 833.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 256 | 700 | 0 | 4248.32 | 8054.82 | 99.59
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 13 | 320 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 240 | 0 | 240 | 5 | 0 | 210 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 86 | 0 | 0 | 0 | 310 | 0 | 97 | 0 | 30 | 0 | 0 | 17 | 0 | 5 | 20 | 0 | 16 | 159 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 3673.5 | 670 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 824.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 256 | 560 | 0 | 4105.09 | 7778.59 | 99.59
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 320 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 240 | 0 | 240 | 5 | 0 | 213 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 103 | 0 | 30 | 0 | 0 | 5 | 0 | 5 | 20 | 0 | 16 | 159 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 3626.5 | 637 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 831.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 258 | 550 | 0 | 4078.17 | 7704.67 | 99.58
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 20 | 320 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 240 | 0 | 240 | 10 | 0 | 216 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 300 | 0 | 197 | 0 | 30 | 0 | 0 | 5 | 0 | 82 | 20 | 0 | 16 | 159 | 0 | 2 | 2 | 52 | 0 | 0 | 0 | 3881.5 | 636 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 0 | 0 | 0 | 837.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 0 | 308 | 615 | 0 | 4249.11 | 8130.61 | 99.58
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 2 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 46 | 0 | 25 | 354 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 550 | 4 | 0 | 0 | 240 | 0 | 240 | 46 | 0 | 214 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 94 | 0 | 5 | 0 | 285 | 0 | 186 | 0 | 30 | 0 | 4 | 17 | 0 | 82 | 30 | 0 | 20 | 159 | 0 | 16 | 8 | 45 | 0 | 1.83 | 0 | 4227.57 | 636 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.64 | 860 | 0 | 0 | 0 | 867.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 5 | 0 | 0 | 1.81 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.21 | 0 | 56 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 5 | 0.02 | 0 | 0 | 115 | 110 | 0 | 312 | 745 | 0 | 4539.57 | 8767.14 | 99.58
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 4 | 0 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 46 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 240 | 0 | 240 | 51 | 0 | 213 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 96 | 0 | 15 | 0 | 285 | 0 | 187 | 0 | 30 | 0 | 1 | 17 | 0 | 82 | 30 | 0 | 18 | 159 | 0 | 30 | 19 | 34 | 0 | 8.89 | 0 | 4305.61 | 730 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 975 | 0 | 0 | 0 | 1087.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.74 | 11 | 0 | 0 | 12.87 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.95 | 0 | 56 | 0 | 6 | 0 | 0 | 0 | 0 | 1.2 | 32 | 0.16 | 0 | 0 | 115 | 110 | 0 | 403 | 896 | 0 | 5303.6 | 9609.21 | 99.58
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 16 | 0 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.26 | 46 | 0 | 5 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 556 | 10 | 0 | 0 | 235 | 0 | 240 | 51 | 0 | 208 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 92 | 0 | 35 | 0 | 275 | 0 | 187 | 0 | 30 | 0 | 3 | 17 | 0 | 82 | 30 | 0 | 18 | 158 | 0 | 57 | 19 | 33 | 1 | 19.19 | 0 | 4287.95 | 777 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 988 | 0 | 0 | 0 | 1019.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.46 | 49 | 0 | 0 | 25.63 | 186 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 2.17 | 0 | 55 | 0 | 13 | 0 | 0 | 0 | 0 | 2.7 | 73 | 0.18 | 0 | 0 | 115 | 110 | 0 | 344 | 932 | 0 | 5362.13 | 9650.08 | 99.58
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 21 | 0 | 19.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.89 | 46 | 0 | 5 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 505 | 17 | 0 | 0 | 235 | 0 | 240 | 43 | 0 | 206 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 92 | 0 | 45 | 0 | 260 | 0 | 187 | 0 | 30 | 0 | 1 | 17 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 16 | 19 | 33 | 1 | 23.28 | 0 | 4264.67 | 777 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 893 | 0 | 0 | 0 | 918.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.35 | 63 | 0 | 0 | 27.46 | 169 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 2.15 | 0 | 54 | 0 | 20 | 0 | 0 | 0 | 0 | 3.9 | 112 | 0.23 | 0 | 0 | 115 | 110 | 0 | 258 | 900 | 0 | 5105.98 | 9370.65 | 99.57
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 21 | 0 | 19.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.51 | 46 | 0 | 5 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 530 | 18 | 0 | 0 | 235 | 0 | 240 | 43 | 0 | 202 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 96 | 0 | 36 | 0 | 260 | 0 | 187 | 0 | 30 | 0 | 6 | 17 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 16 | 19 | 33 | 2 | 41.29 | 0 | 4351.3 | 777 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 815 | 0 | 0 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.01 | 73 | 0 | 0 | 41.97 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.88 | 0 | 55 | 0 | 25 | 0 | 0 | 41 | 0 | 4.7 | 131 | 0.25 | 0 | 0 | 115 | 110 | 0 | 257 | 896 | 0 | 5135.81 | 9487.11 | 99.57
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 412 | 10 | 0 | 2 | 0 | 45 | 0 | 30 | 44 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 16 | 0 | 19.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.19 | 46 | 0 | 11 | 354 | 0 | 0 | 1 | 0 | 22 | 225 | 0 | 0 | 0 | 578 | 19 | 11 | 0 | 235 | 0 | 240 | 51 | 0 | 202 | 0 | 0 | 106 | 24 | 0 | 8 | 0 | 102 | 0 | 22 | 0 | 285 | 0 | 192 | 0 | 30 | 0 | 9 | 17 | 0 | 81 | 30 | 0 | 16 | 157 | 0 | 24 | 19 | 30 | 2 | 41.51 | 0 | 4549.2 | 873 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 872 | 0 | 0 | 0 | 925.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.92 | 82 | 0 | 0 | 46.93 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.57 | 0 | 54 | 0 | 27 | 0 | 0 | 0 | 0 | 4.8 | 135 | 0.34 | 0 | 0 | 115 | 110 | 0 | 304 | 948 | 0 | 5423.94 | 9973.14 | 99.57
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 381 | 40 | 0 | 17 | 0 | 90 | 0 | 49 | 112 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 14 | 0 | 19.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 3.2 | 46 | 0 | 15 | 354 | 0 | 0 | 13 | 0 | 58 | 225 | 0 | 0 | 0 | 612 | 19 | 33 | 0 | 235 | 0 | 240 | 51 | 0 | 202 | 0 | 0 | 105 | 66 | 0 | 14 | 0 | 94 | 0 | 17 | 0 | 315 | 0 | 186 | 20 | 30 | 0 | 9 | 14 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 45 | 19 | 30 | 2 | 39.6 | 0 | 4893.3 | 872 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 927 | 0 | 0 | 0 | 1108.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.76 | 77 | 0 | 0 | 41.18 | 205 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 3.72 | 0 | 53 | 0 | 24 | 0 | 0 | 0 | 0 | 3.9 | 131 | 0.34 | 0 | 0 | 100 | 110 | 0 | 272 | 1016 | 0 | 5626.97 | 10520.27 | 99.56
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 382 | 35 | 0 | 33 | 0 | 60 | 0 | 55 | 72 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 14 | 0 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 42 | 1.37 | 46 | 0 | 8 | 354 | 0 | 0 | 19 | 0 | 68 | 187 | 0 | 0 | 0 | 502 | 15 | 0 | 0 | 230 | 0 | 240 | 51 | 0 | 202 | 0 | 0 | 104 | 100 | 0 | 14 | 0 | 92 | 0 | 20 | 0 | 310 | 0 | 190 | 20 | 30 | 0 | 6 | 22 | 0 | 80 | 20 | 0 | 16 | 158 | 0 | 56 | 19 | 12 | 1 | 28.59 | 0 | 4653.46 | 872 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 877 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.58 | 66 | 0 | 0 | 30.88 | 168 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 2.46 | 0 | 54 | 0 | 18 | 0 | 0 | 0 | 0 | 3.8 | 100 | 0.17 | 0 | 0 | 100 | 110 | 0 | 256 | 900 | 0 | 5293.89 | 9947.35 | 99.56
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 381 | 14.8 | 0 | 34 | 0 | 30 | 0 | 55 | 68 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 14 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 39 | 0.96 | 46 | 0 | 4 | 354 | 0 | 0 | 19 | 0 | 34 | 225 | 0 | 0 | 0 | 563 | 12 | 0 | 0 | 230 | 0 | 240 | 51 | 0 | 202 | 0 | 0 | 105 | 51 | 0 | 14 | 0 | 100 | 0 | 14 | 0 | 305 | 0 | 192 | 20 | 30 | 0 | 4 | 15 | 0 | 81 | 20 | 0 | 16 | 158 | 0 | 56 | 19 | 12 | 1 | 16.64 | 0 | 4595.4 | 873 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 891 | 0 | 0 | 0 | 1122.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7 | 38 | 0 | 0 | 20.97 | 171 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 1.47 | 0 | 56 | 0 | 12 | 0 | 0 | 0 | 0 | 2.3 | 56 | 0.2 | 0 | 0 | 100 | 110 | 0 | 256 | 875 | 0 | 5170.13 | 9765.53 | 99.56
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 382 | 15.9 | 0 | 34 | 0 | 30 | 0 | 55 | 67 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 4 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 20 | 0.36 | 46 | 0 | 4 | 354 | 0 | 0 | 19 | 0 | 34 | 223 | 0 | 0 | 0 | 590 | 5 | 0 | 0 | 230 | 0 | 240 | 51 | 0 | 203 | 0 | 0 | 105 | 17 | 0 | 14 | 0 | 116 | 0 | 7 | 0 | 310 | 0 | 202 | 20 | 30 | 0 | 2 | 14 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 59 | 19 | 12 | 0 | 5.92 | 0 | 4591.18 | 872 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 910 | 0 | 0 | 0 | 1053.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.77 | 15 | 0 | 0 | 7.58 | 175 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0.59 | 0 | 56 | 0 | 5 | 0 | 0 | 0 | 0 | 0.8 | 20 | 0.63 | 0 | 0 | 115 | 110 | 0 | 257 | 840 | 0 | 5040.13 | 9631.31 | 99.56
17:00 | 0 | 30 | 2 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 390 | 16.2 | 13 | 35 | 0 | 145 | 4 | 55 | 162 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 17 | 17.5 | 21 | 0 | 0 | 7 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 12 | 21 | 0 | 46 | 4 | 11 | 354 | 0 | 0 | 19 | 0 | 34 | 224 | 0 | 0 | 0 | 570 | 0 | 26 | 0 | 230 | 0 | 240 | 51 | 0 | 203 | 0 | 8 | 106 | 16 | 5 | 14 | 0 | 108 | 0 | 1 | 0 | 315 | 0 | 206 | 20 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 57 | 19 | 12 | 0 | 0.42 | 2 | 4929.12 | 873 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 997 | 0 | 0 | 0 | 1172.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 0 | 0 | 0.78 | 178 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0.08 | 0 | 56 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 115 | 110 | 0 | 354 | 844 | 0 | 5255.22 | 10184.34 | 99.55
18:00 | 0 | 34 | 18 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 422 | 35 | 0 | 73 | 0 | 145 | 0 | 55 | 162 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 10 | 16.5 | 21 | 0 | 0 | 26 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 14 | 17 | 354 | 0 | 0 | 19 | 0 | 92 | 225 | 0 | 0 | 0 | 612 | 0 | 80 | 0 | 220 | 0 | 220 | 43 | 0 | 209 | 0 | 25 | 108 | 100 | 0 | 14 | 0 | 116 | 0 | 0 | 0 | 305 | 0 | 205 | 20 | 30 | 0 | 0 | 24 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 59 | 19 | 12 | 0 | 0 | 0 | 5241.5 | 848 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 1468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 50 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 506 | 900 | 0 | 5976 | 11217.5 | 99.55
19:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 427 | 39.5 | 0 | 81 | 0 | 80 | 0 | 55 | 108 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 16.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 0 | 23 | 354 | 0 | 0 | 0 | 0 | 51 | 226 | 0 | 0 | 0 | 613 | 0 | 0 | 0 | 220 | 0 | 240 | 43 | 0 | 209 | 0 | 0 | 109 | 99 | 0 | 14 | 0 | 116 | 0 | 0 | 0 | 320 | 0 | 206 | 24 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 16 | 159 | 0 | 59 | 19 | 22 | 0 | 0 | 0 | 5024 | 849 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1461.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 506 | 964 | 0 | 5932.63 | 10956.63 | 99.55
19:30 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 406 | 15.5 | 0 | 97 | 0 | 30 | 0 | 55 | 108 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 16.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 0 | 11 | 354 | 0 | 0 | 0 | 0 | 30 | 227 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 220 | 0 | 240 | 43 | 0 | 207 | 0 | 0 | 109 | 31 | 0 | 14 | 0 | 112 | 0 | 0 | 0 | 315 | 0 | 205 | 24 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 16 | 159 | 0 | 59 | 19 | 23 | 0 | 0 | 0 | 4798 | 849 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 1457.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 507 | 1035 | 0 | 5955.23 | 10753.23 | 99.55
20:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 380 | 15.5 | 0 | 94 | 0 | 0 | 0 | 55 | 108 | 0 | 140 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 0 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 0 | 15 | 354 | 0 | 0 | 0 | 0 | 17 | 228 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 220 | 0 | 240 | 43 | 0 | 206 | 0 | 0 | 109 | 34 | 0 | 14 | 0 | 112 | 0 | 0 | 0 | 310 | 0 | 205 | 24 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 16 | 157 | 0 | 59 | 19 | 33 | 0 | 0 | 0 | 4703 | 849 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 1446.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 507 | 1058 | 0 | 5946.97 | 10649.97 | 99.55
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 370 | 0 | 0 | 90 | 0 | 0 | 0 | 35 | 72 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 18 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 220 | 0 | 240 | 43 | 0 | 209 | 0 | 0 | 109 | 0 | 0 | 14 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 205 | 28 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 16 | 157 | 0 | 59 | 19 | 33 | 0 | 0 | 0 | 4489.5 | 850 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1460.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 403 | 1085 | 0 | 5923.17 | 10412.67 | 99.54
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 370 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 220 | 0 | 240 | 43 | 0 | 210 | 0 | 0 | 110 | 0 | 0 | 14 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 205 | 28 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 16 | 157 | 0 | 59 | 19 | 34 | 0 | 0 | 0 | 4322.5 | 860 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 306 | 1078 | 0 | 5763 | 10085.5 | 99.54
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 24 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 220 | 0 | 240 | 43 | 0 | 210 | 0 | 0 | 109 | 0 | 0 | 14 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 205 | 28 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 16 | 159 | 0 | 59 | 0 | 38 | 0 | 0 | 0 | 4236.5 | 860 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 956 | 0 | 0 | 0 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 308 | 981 | 0 | 5448 | 9684.5 | 99.54
Total KWH | 0 | 101760 | 66720 | 0 | 0 | 0 | 0 | 0 | 8056800 | 0 | 9618610 | 208080 | 29880 | 571680 | 0 | 689749 | 11522 | 507036 | 1039680 | 0 | 3659000 | 0 | 0 | 0 | 72764 | 5820048 | 0 | 0 | 139336 | 19200 | 384600 | 496080 | 0 | 0 | 37636 | 0 | 0 | 0 | 84480 | 0 | 0 | 0 | 34560 | 231360 | 18840 | 1093500 | 33454 | 317280 | 8472727.27 | 0 | 0 | 144000 | 0 | 545309 | 5114472 | 0 | 0 | 0 | 12676362 | 120960 | 192363 | 0 | 5809000 | 0 | 5988000 | 1026864 | 0 | 5019000 | 0 | 39360 | 2420521 | 62160 | 13440 | 302270 | 0 | 2341440 | 0 | 219127 | 0 | 7277000 | 0 | 4041000 | 253000 | 720840 | 0 | 38671 | 441336 | 0 | 1718400 | 649536 | 0 | 375000 | 3317690 | 0 | 883200 | 297600 | 689280 | 9600 | 223220 | 20160 | 104806563.27 | 19036363 | 5329440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318960 | 22007270 | 0 | 0 | 0 | 26567172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231608 | 486830 | 0 | 0 | 249744 | 4252909 | 0 | 0 | 0 | 0 | 0 | 8883854 | 0 | 20340 | 0 | 1284654 | 64426 | 151280 | 60672 | 0 | 34965 | 0 | 28789.32 | 805680 | 1947 | 0 | 0 | 2650000 | 2736201 | 0 | 7826940.7 | 21656727.27 | 0 | 124686772.29 | 229493335.56

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9973.14 | MW | 12:00 Hr. | Energy Generated |  |  | 229.4933 |  | MKWHr.
| Day Peak Demand |  |  | 9973.14 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11217.5 | MW | 18:00 Hr. | Energy Demand |  |  | 229.4933 |  | MKWHr.
| Evening Peak Demand |  |  | 11217.5 | MW | 18:00 Hr. | Maximum Temperature |  |  | 27.4 |  | °C
| Minimum Generation of the Day |  |  | 7704.67 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 728.66 |  | MMCFD
| Maximum Generation of the Day |  |  | 11217.5 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.4924 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.0351 | 0 | 3.3181 | 0 | 0 | 0.13934 | 0 | 0 | 31.4925 | Gas | 97.368 | Gas | 344768325.68
| Chattogram Zone |  |  | 5.4318 | 21.1491 | 1.0263 | 0 | 1.0935 | 0.1398 | 0 | 0.08448 | 28.9249 | Coal | 73.9247 | Coal | 473699215.499
| Cumilla Zone |  |  | 20.5657 | 0 | 0.30732 | 0 | 0 | 0.21913 | 2.3414 | 0 | 23.4335 | HFO | 5.9778 | HFO | 100344727.84
| Mymensingh Zone |  |  | 0.68928 | 0 | 1.201 | 0 | 0 | 0.23282 | 0 | 0 | 2.1231 | HSD | 0.034965 | HSD | 957691.35
| Sylhet Zone |  |  | 18.7938 | 0 | 0 | 0 | 0 | 0.038671 | 0 | 0 | 18.8325 | Hydro | 1.0935 | Hydro | 109350
| Khulna Zone |  |  | 5.3294 | 22.0073 | 0 | 0 | 0 | 0.31896 | 19.0364 | 0 | 46.692 | Solar | 3.0649 | Solar | 49276021.3472
| Barishal Zone |  |  | 5.3862 | 29.4837 | 0 | 0 | 0 | 0.001947 | 0 | 0 | 34.8718 | Import | 47.945 | Import | 290068122.03
| Rajshahi Zone |  |  | 13.1368 | 0 | 0 | 0 | 0 | 0.98852 | 26.5672 | 0 | 40.6925 | Wind | 0.08448 | Wind | 1242700.8
| Rangpur Zone |  |  | 0 | 1.2847 | 0.1251 | 0.034965 | 0 | 0.98575 | 0 | 0 | 2.4305
| Total |  |  | 97.368 | 73.9247 | 5.9778 | 0.034965 | 1.0935 | 3.0649 | 47.945 | 0.08448 | 229.4933
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 344768325.68 |  | Hydro | 109350
|  |  |  | Coal | 473699215.499 |  | Solar | 49276021.3472
|  |  |  | HFO | 100344727.84 |  | Import | 290068122.03
|  |  |  | HSD | 957691.35 |  | Wind | 1242700.8
[5 empty] | Total: | 126,04,66,154 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.0364 | Peak Hr Flow | 848.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50525127.28 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.5672 | Peak Hr Flow | 1468.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2562 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3414 | Peak Hr Flow | 116.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2714 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.945 | Peak Hr Flow | 2432.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4214
|  |  |  | Chattogram |  | 0 |  | 1227
|  |  |  | Cumilla |  | 0 |  | 891
|  |  |  | Mymensingh |  | 0 |  | 807
|  |  |  | Sylhet |  | 0 |  | 408
|  |  |  | Khulna |  | 0 |  | 1212
|  |  |  | Barishal |  | 0 |  | 300
|  |  |  | Rajshahi |  | 0 |  | 964
|  |  |  | Rangpur |  | 0 |  | 776
|  |  |  | Total |  | 0 |  | 10799
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 16:54 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to
Annual Maintenance
| 08:11 | 16:03 | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D
| 08:12 | 16:02 | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D
| 08:17 | 17:26 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual Maintenance
| 08:18 | 17:26 | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintence
| 08:25 | 17:18 | Bhulta 400/230kV S/S ATR-01 HT Scheduled S/D Due to Annual Maintenance Works
| 08:29 | 14:49 | Rampur 230/132/33 S/S Halishahar-1 Scheduled S/D Due to Annual Maintenance
| 08:30 | 12:38 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Annual Maintenance
| 08:30 | 12:36 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Annual Maintenance
| 08:31 | 14:49 | Halishahar-Khulshi 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end.
| 08:32 | 16:39 | Bheramara(GK) 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance
| 08:33 | 16:38 | Bheramara(GK) 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual Maintenance
| 08:33 | 15:47 | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Jashore 132/33kV end Due to Annual
Maintanance
| 08:36 | 16:44 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Annual
Maintenance
| 08:38 | 17:16 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end.
| 08:40 | 19:50 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT Scheduled S/D Due to Annual maintenance
| 08:40 | 19:50 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT Scheduled S/D Due to Annual maintenance
| 08:49 | 13:31 | GPH 230/33kV S/S Transformer-01(D05) HT Forced S/D Due to due to oil centrifuging of oltc
compartment
| 08:52 | 16:41 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
maintenance
| 08:54 | 16:11 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 5.0MW load
interrup.
| 08:54 | 16:09 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 5.0MW load
interrup.
| 08:56 | 11:20 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Scheduled S/D
| 08:56 | 16:30 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV end. and from
Palashbari 132/33kV end Due to Annual Maintenance
| 08:57 | 11:20 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Scheduled S/D
| 08:58 | 17:55 | Gopalganj (O) - Gopalgan (N) Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to
Annual maintenance and from Gopalganj 400/132kVend.
| 09:02 | 15:35 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-1 Project Work S/D Due to NLDC and SCADA
integration work
| 09:03 | 15:34 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-01 Scheduled S/D Due to Project work
| 09:05 | 16:37 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end. and from Ishurdi
132/33kV end Due to A/M
| 09:05 | 12:56 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Annaul Maintenance.
| 09:07 | 17:08 | Haripur 230/132kV S/S Bus-2 Scheduled S/D Due to Annual Maintenance, 2025-26.
| 09:08 | 13:34 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D Due to Annual maintenance
| 09:08 | 13:37 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Scheduled S/D Due to Annual maintenance
| 09:10 | 16:11 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 LT Scheduled S/D Due to Annual Maintenance
| 09:12 | 12:55 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Annaul Maintenance .
| 09:14 | 16:02 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 HT Scheduled S/D Due to Annual Maintenance
| 09:17 | 16:16 | Kallyanpur 132/33kV S/S Reserve bus Scheduled S/D Due to Annual Maintenance.
| 09:18 | 16:29 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Muktagacha 132/33kV end. and from
Ghatail 132/33kV end Due to Annual maintenance
| 09:21 | 16:09 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Annual Maintenance
| 09:31 |  | Kushtia 132/33kV S/S T2 LT Project Work S/D
| 09:32 |  | Kushtia 132/33kV S/S T2 HT Project Work S/D
| 09:37 | 12:45 | BIPTC S/S 20DF13 Scheduled S/D Due to Annual maintenance
| 09:38 | 20:16 | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to By direction
of NLDC
| 09:38 | 17:07 | Rahanpur 132/33kV S/S Rahanpur-1 Scheduled S/D Due to Annual maintenance.
| 09:42 | 20:17 | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to By direction
of NLDC
| 09:48 | 16:23 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to A/M
| 09:48 | 16:21 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to A/M
| 10:03 | 16:45 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual maintenance work and from Bogura 400/230kV end Due to Annual Maintenance
| 10:07 | 11:03 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to Due to low sf6 gas pressure
| 10:18 | 12:08 | AKSML-Baroaulia 132kV Ckt-1 Forced S/D from Baroaulia 132/33kV end Due to Redhot
maintenance at AKSPL S/S
| 10:48 |  | Mirsorai 230/33kV S/S TR-2, 728T HT Forced S/D Due to force Shutdown
| 10:58 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- GT2
| 10:59 | 11:13 | BIPTC S/S 10CF14 Tripped showing 10CF14 relays.
| 11:00 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized
| 11:23 | 12:37 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to Annual maintenance work
at Bus 1.
| 11:24 | 12:38 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to Annual maintenance work
at bus 1
|  | 11:27 | Chandina 132/33kV S/S TR-3 HT is restored.
|  | 11:57 | Chandina 132/33kV S/S TR-3 LT is restored.
| 12:00 |  | Day Peak Generation: 9968 MW.
| 12:44 | 14:33 | Sunamganj 132/33kV S/S Tr-1 HT Forced S/D Due to SAS Maintenance
| 12:50 | 16:28 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Annual Maintenance
| 12:50 | 16:28 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Annual Maintenance
| 13:26 | 16:41 | Kasba 132/33kV S/S 132kv Bus-1 Project Work S/D Due to NLDC and SCADA integration Work
|  | 13:52 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT is restored.
|  | 13:53 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT is restored.
| 15:01 | 16:41 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Scheduled S/D
| 15:14 |  | Purboshadipur 230/132kV ATR-1 transformer was switched ON (with load) at 15:14 hrs. for
the first time. Note that 132kV AIS to GIS bus connection was established using 132kV
Saidpur-1 bay.
| 15:35 | 15:55 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 15:35 | 15:55 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D
| 15:35 | 15:55 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D
| 15:38 | 16:56 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-02 Scheduled S/D Due to Project work
|  | 15:39 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT is restored.
|  | 15:41 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT is restored.
| 15:44 | 16:57 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-2 Project Work S/D Due to NLDC and SCADA
integration work
|  | 16:43 | Cox'sbazar-Dohazari 132 kV Ckt-2 is restored.
|  | 16:54 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT is restored.
|  | 16:54 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT is restored.
| 17:16 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2
|  | 17:32 | Hasnabad-Shyampur 230kV Ckt-1 is restored.
|  | 17:58 | Goalpara- Khulna (C) 132kV Ckt-1 is restored.
| 18:00 |  | Evening Peak Generation: 11217 MW.
| 18:41 |  | Meghnaghat 450 MW CCPP (MPL) Shutdown with remarks:- GT1
| 18:42 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2(False )
| 18:42 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2
| 19:24 |  | Purboshadipur 132kV GIS-AIS bay (132kV Saidpur-1 bay) was forced shutdown at 19:24 hrs.
due to high temperature.
|  | 19:50 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT is restored.
| 04:00 |  | Minimum generation 7537 MW
| 06:22 |  | Goalpara- Khulna (C) 132kV Ckt-1 Project Work S/D from Goalpara 132/33kV end. and from
Khulna (C) end Due to Project work
| 07:08 |  | Hasnabad 230/132kV S/S AUTO TR-2 LT Scheduled S/D Due to annual maintenance
| 07:08 |  | Hasnabad 230/132kV S/S AUTO TR-2 HT Scheduled S/D Due to annual maintenance
| 07:09 |  | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to yearly maintenance
| 07:09 |  | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to yearly maintenance
| 07:11 |  | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance
| 07:11 |  | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance
| 07:14 |  | Barishal 132/33kV S/S 132 kv Summit power Scheduled S/D Due to Annual Maintenance
| 07:15 |  | Bhulta 400/230kV S/S ATR-01 HT Scheduled S/D Due to For Annual Maintenance Works
| 07:18 |  | Chhatak 132/33kV S/S Bus A Scheduled S/D Due to Annual Maintenance
| 07:20 |  | Barishal 132/33kV S/S 132 kv GTPS Scheduled S/D Due to Annual Maintenance
| 07:26 |  | Dhaka University 132/33 kv T-2 was shut down due to A/M
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 325 | 8056800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 140 | 3659000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 11522 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5820048 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 208080 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 507036 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 72764 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16.5 | 384600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 496080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 18 | 66720 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 689749 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 73 | 571680 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 101760 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1039680 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 139336 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 29880 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 422 | 9618610 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 10 | 19200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 1713.5 | 31492545
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 120960 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 144000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1093500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 5114472 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 92 | 545309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 34560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 317280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 14 | 33454 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 231360 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 26 | 37636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12676362 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 84480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 8472727.27 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4895.723 | 1435 | 28924940.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 209 | 5019000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 220 | 5988000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5809000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1026864 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 192363 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2420521 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 62160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 116 | 2341440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 302270 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 13440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 25 | 39360 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 219127 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1135 | 23433545
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 12 | 689280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 297600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 883200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 223220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 20160 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 90 | 2123060
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 38671 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 20 | 253000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 649536 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1718400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3317690 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 375000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 441336 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7277000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 205 | 4041000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 868 | 18832473
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 848 | 19036363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 197 | 5329440 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 318960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1109 | 22007270 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2154 | 46692033
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 506 | 7826940.7 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2650000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 900 | 21656727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2736201 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1947 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1631 | 34871815.97
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 231608 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 181 | 4252909 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8883854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1468 | 26567172 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 249744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 486830 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2063 | 40692457
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 34965 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1284654 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 22 | 60672 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28789.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 64426 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 151280 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 805680 | -
Rangpur Area Total |  |  |  |  | 950 | 128 | 2430466.32
Eastern Grid Total |  |  |  |  | 17383.855 | 5241.5 | 104806563.27
Western Grid Total |  |  |  |  | 10821.56 | 5976 | 124686772.29
National Grid Total |  |  |  |  | 28205.415 | 11217.5 | 229493335.56
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7546.63 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3252.2 | MW
i) Dhaka area |  |  | 4213.63 |  | MW | i) Khulna area |  |  |  | 1212 | MW
ii) Chattogram area |  |  | 1227 |  | MW | ii) Barishal area |  |  |  | 300 | MW
iii) Cumilla area |  |  | 891 |  | MW | iii) Rajshahi area |  |  |  | 964.2 | MW
iv) Mymensingh area |  |  | 807 |  | MW | iv) Rangpur area |  |  |  | 776 | MW
v) Sylhet area |  |  | 408 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10798.83 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 07:00 | 67 | Hathazari | 58 | 13:00 | 133 | Niamatpur | 40 | 18:00
2 | AKSML | 137 | 00:00 | 68 | Ishurdi | 50 | 19:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 54 | 18:00 | 135 | PHP | 7 | 05:00
4 | Agargaon | 93 | 13:00 | 70 | Jamalpur | 84 | 08:00 | 136 | Pabna | 72 | 18:00
5 | Agrabad | 60 | 17:00 | 71 | Jashore | 103 | 13:00 | 137 | Palashbari | 84 | 18:00
6 | Amnura | 15 | 08:00 | 72 | Jhenaidah | 88 | 18:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 66 | 13:00 | 73 | Joydebpur | 119 | 13:00 | 139 | Patiya | 7 | 17:00
8 | BSRM | 203 | 18:00 | 74 | Joypurhat | 45 | 18:00 | 140 | Patuakhali | 43 | 20:00
9 | Bagerhat | 58 | 18:00 | 75 | Juldah | 14 | 15:00 | 141 | Payra | 22 | 01:00
10 | Bajitpur | 64 | 18:00 | 76 | KSRM | 28 | 06:00 | 142 | Postogola | 49 | 13:00
11 | Bakulia | 61 | 12:00 | 77 | Kabirpur | 184 | 18:00 | 143 | Purbachal | 28 | 13:00
12 | Banani | 49.6 | 13:00 | 78 | Kachua | 54 | 18:30 | 144 | Purbasadipur | 108 | 18:00
13 | Bangabhaban | 15 | 10:00 | 79 | Kallyanpur | 75 | 14:00 | 145 | Rahanpur | 21 | 20:00
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rahim | 51 | 11:00
15 | Barguna | 16 | 18:00 | 81 | Kamrangirchar | 59 | 17:00 | 147 | Rajbari | 57 | 18:00
16 | Barishal | 82 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 97 | 18:00
17 | Barishal-230 | 64 | 20:00 | 83 | Kasba | 21 | 18:00 | 149 | Rajshahi | 97 | 13:00
18 | Baroaulia | 60 | 17:00 | 84 | Kazla | 88 | 18:30 | 150 | Rajshahi-230 | 34 | 12:00
19 | Baroirhat | 47 | 17:00 | 85 | Keranigonj | 60 | 12:00 | 151 | Ramganj | 64 | 13:00
20 | Bashundhara | 151 | 13:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 30 | 18:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 46 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 48 | 18:00 | 88 | Khulshi | 160 | 14:00 | 154 | Rangpur | 108 | 18:00
23 | Benapole | 38 | 08:00 | 89 | Kishoreganj | 82 | 18:00 | 155 | Ruppur | 3 | 10:00
24 | Bhaluka | 124 | 19:00 | 90 | Kodda | 250 | 18:00 | 156 | SSM | 12 | 05:00
25 | Bhandaria | 36 | 21:00 | 91 | Kulaura | 30 | 18:00 | 157 | Saidpur | 95 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 49 | 18:00 | 158 | Satkhira | 86 | 08:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | Kushtia | 112 | 18:00 | 159 | Satmasjid | 76 | 13:00
28 | Bhulta | 197 | 18:30 | 94 | Laksam | 21 | 12:00 | 160 | Savar | 188 | 12:00
29 | Bog-Sherpur | 54 | 18:00 | 95 | Lakshmipur | 24 | 20:00 | 161 | SevenRings | 4.19 | 00:00
30 | Bogura | 111 | 18:00 | 96 | Lalbag | 61 | 13:00 | 162 | ShahCement | 24 | 03:00
31 | Borhanuddin | 62 | 20:00 | 97 | Lalmonirhat | 44 | 18:00 | 163 | Shahjadpur | 58 | 18:00
32 | Brahmanbaria | 86 | 19:00 | 98 | MI_Cement | 14.2 | 00:00 | 164 | Shahjibazar | 74 | 18:30
33 | Cantonment | 78 | 13:00 | 99 | Madanganj | 35 | 13:00 | 165 | Shahmirpur | 39.5 | 17:00
34 | Chandina | 10 | 18:00 | 100 | Madaripur | 67 | 19:30 | 166 | Shariatpur | 54 | 20:00
35 | Chandpur | 50 | 19:00 | 101 | Madartek | 62 | 18:00 | 167 | Sherpur | 104 | 08:00
36 | Chandraghona | 26 | 18:00 | 102 | Madunaghat | 36 | 12:00 | 168 | Shikalbaha | 19 | 18:00
37 | Chapai | 46 | 13:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 61.9 | 12:00
38 | Charsaidpur | 34 | 23:00 | 104 | Mahasthangarh | 46 | 20:00 | 170 | Sholosohor | 35 | 12:00
39 | Chauddagram | 47 | 13:00 | 105 | Maijdee | 21 | 18:30 | 171 | Shyampur | 130 | 10:00
40 | Chhatak | 23 | 18:00 | 106 | Manikganj | 85 | 19:00 | 172 | Siddhirganj | 99 | 12:00
41 | Chowmuhani | 104 | 18:00 | 107 | Maniknagar | 50 | 13:00 | 173 | Sirajganj | 82 | 18:30
42 | Chuadanga | 68 | 13:00 | 108 | Matarbari | 36 | 18:00 | 174 | Sonargaon | 99 | 09:00
43 | Coxsbazar | 107 | 18:00 | 109 | Matuail | 60 | 12:00 | 175 | Sreemongol | 57 | 18:00
44 | Cumilla(N) | 92 | 11:00 | 110 | Metrorail_Motijheel | 30 | 18:30 | 176 | Sreepur | 87 | 18:30
45 | Cumilla(S) | 118 | 18:30 | 111 | Metrorail_Uttara | 9 | 15:00 | 177 | Srinagar | 30.61 | 14:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 93 | 12:00 | 178 | Sunamganj | 38 | 18:00
47 | Daudkandi | 90 | 02:00 | 113 | Mirpur | 112 | 13:00 | 179 | Sylhet | 28 | 00:00
48 | DhakaUniversity | 58 | 13:00 | 114 | Mirsorai | 39 | 13:00 | 180 | Sylhet-132 | 86 | 14:00
49 | Dhamrai | 118 | 17:00 | 115 | Mirzapur | 33 | 18:00 | 181 | TK | 18 | 20:00
50 | Dhanmondi | 70 | 14:00 | 116 | Mithapukur | 44 | 18:00 | 182 | Tangail | 120 | 18:00
51 | Dohazari | 65 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 14 | 18:00
52 | Faridpur | 110 | 21:00 | 118 | Mogbazar | 66.8 | 13:00 | 184 | Tasnim | 30 | 05:00
53 | Fatullah | 96 | 12:00 | 119 | Mongla | 31 | 10:00 | 185 | Thakurgaon | 79 | 18:00
54 | Fenchuganj | 26 | 18:00 | 120 | Motijheel | 28 | 13:00 | 186 | Tongi | 95 | 11:00
55 | Feni | 71 | 13:00 | 121 | Muktagacha | 24 | 07:00 | 187 | Ullahpara | 24 | 18:00
56 | GPH | 73 | 03:00 | 122 | Munshiganj | 75 | 13:00 | 188 | Ullon | 53 | 13:00
57 | Ghatail | 58 | 19:00 | 123 | Muradnagar | 25 | 19:00 | 189 | Uttara | 63 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 123 | 08:00 | 190 | UttaraNew | 14 | 13:00
59 | Ghorashal-230 | 80 | 19:00 | 125 | Naogaon | 83 | 18:00 | 191 | Zigatola | 54 | 14:00
60 | Goalpara | 27 | 14:00 | 126 | Narail | 41 | 18:00
61 | Gollamari | 70 | 13:00 | 127 | Narinda | 60 | 13:00
62 | Gopalganj | 73 | 18:00 | 128 | Narshingdi | 137 | 18:30
63 | Gulshan | 82 | 13:00 | 129 | Natore | 96 | 18:00
64 | Halishahar | 64 | 12:00 | 130 | Nawabganj | 28.6 | 20:00
65 | HaripurSBU | 149 | 11:00 | 131 | Netrakona | 96 | 19:00
66 | Hasnabad | 74 | 12:00 | 132 | New | 60.8 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9299.73 | 0 |  | 9299.73
1:00 | 8734.16 | 0 |  | 8734.16
2:00 | 8316.07 | 0 |  | 8316.07
3:00 | 8054.82 | 0 |  | 8054.82
4:00 | 7778.59 | 0 |  | 7778.59
5:00 | 7704.67 | 0 |  | 7704.67
6:00 | 8130.61 | 0 |  | 8130.61
7:00 | 8767.14 | 0 |  | 8767.14
8:00 | 9609.21 | 0 |  | 9609.21
9:00 | 9650.08 | 0 |  | 9650.08
10:00 | 9370.65 | 0 |  | 9370.65
11:00 | 9487.11 | 0 |  | 9487.11
12:00 | 9973.14 | 0 |  | 9973.14
13:00 | 10520.27 | 0 |  | 10520.27
14:00 | 9947.35 | 0 |  | 9947.35
15:00 | 9765.53 | 0 |  | 9765.53
16:00 | 9631.31 | 0 |  | 9631.31
17:00 | 10184.34 | 0 |  | 10184.34
18:00 | 11217.5 | 0 |  | 11217.5
19:00 | 10956.63 | 0 |  | 10956.63
19:30 | 10753.23 | 0 |  | 10753.23
20:00 | 10649.97 | 0 |  | 10649.97
21:00 | 10412.67 | 0 |  | 10412.67
22:00 | 10085.5 | 0 |  | 10085.5
23:00 | 9684.5 | 0 |  | 9684.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4393 | 4906.73 | 9299.73 | DAILY GENERATION CURVE
00:30 | 4199 | 4817.945 | 9016.945
01:00 | 4005 | 4729.16 | 8734.16 | 02-12-2025
01:30 | 3925.25 | 4599.865 | 8525.115
02:00 | 3845.5 | 4470.57 | 8316.07
02:30 | 3826 | 4359.445 | 8185.445
03:00 | 3806.5 | 4248.32 | 8054.82
03:30 | 3740 | 4176.705 | 7916.705
04:00 | 3673.5 | 4105.09 | 7778.59
04:30 | 3650 | 4091.63 | 7741.63
05:00 | 3626.5 | 4078.17 | 7704.67
05:30 | 3754 | 4163.64 | 7917.64
06:00 | 3881.5 | 4249.11 | 8130.61
06:30 | 4054.535 | 4394.34 | 8448.875
07:00 | 4227.57 | 4539.57 | 8767.14
07:30 | 4266.59 | 4921.585 | 9188.175
08:00 | 4305.61 | 5303.6 | 9609.21
08:30 | 4296.78 | 5332.865 | 9629.645
09:00 | 4287.95 | 5362.13 | 9650.08
09:30 | 4276.31 | 5234.055 | 9510.365
10:00 | 4264.67 | 5105.98 | 9370.65
10:30 | 4307.985 | 5120.895 | 9428.88
11:00 | 4351.3 | 5135.81 | 9487.11
11:30 | 4450.25 | 5279.875 | 9730.125
12:00 | 4549.2 | 5423.94 | 9973.14
12:30 | 4721.25 | 5525.455 | 10246.705
13:00 | 4893.3 | 5626.97 | 10520.27
13:30 | 4773.38 | 5460.43 | 10233.81
14:00 | 4653.46 | 5293.89 | 9947.35
14:30 | 4624.43 | 5232.01 | 9856.44
15:00 | 4595.4 | 5170.13 | 9765.53
15:30 | 4593.29 | 5105.13 | 9698.42
16:00 | 4591.18 | 5040.13 | 9631.31
16:30 | 4760.15 | 5147.675 | 9907.825
17:00 | 4929.12 | 5255.22 | 10184.34
17:30 | 5085.31 | 5615.61 | 10700.92
18:00 | 5241.5 | 5976 | 11217.5
18:30 | 5132.75 | 5954.315 | 11087.065
19:00 | 5024 | 5932.63 | 10956.63
19:30 | 4798 | 5955.23 | 10753.23
20:00 | 4703 | 5946.97 | 10649.97
20:30 | 4596.25 | 5935.07 | 10531.32 |  | Executive Engineer
21:00 | 4489.5 | 5923.17 | 10412.67 |  | Network Operation Division
21:30 | 4406 | 5843.085 | 10249.085
22:00 | 4322.5 | 5763 | 10085.5
22:30 | 4279.5 | 5605.5 | 9885
23:00 | 4236.5 | 5448 | 9684.5

## En-Curve
QF-LDC-12
Date | 02-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3183 | 1165 | 845 | 0 | 90 | 1080.73 | 46 | 2866 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3029 | 1161.5 | 798.5 | 0 | 89 | 1068.445 | 46 | 2800.5 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 02-12-2025
01:00 | 2875 | 1158 | 752 | 0 | 88 | 1056.16 | 46 | 2735 | 0 | 0 | 24 | 0 | 0 | 0 | 0
01:30 | 2805 | 1163.25 | 728 | 0 | 86 | 987.865 | 46 | 2693 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | Energy Generated | 229.4933 |  | MKWHr
02:00 | 2735 | 1168.5 | 704 | 0 | 84 | 919.57 | 46 | 2651 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2737 | 1155.5 | 687 | 0 | 83 | 876.445 | 46 | 2596.5 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | Total Energy Requirement | 229.4933 |  | MKWHr
03:00 | 2739 | 1142.5 | 670 | 0 | 82 | 833.32 | 46 | 2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2761.5 | 1106 | 670 | 0 | 84 | 828.705 | 46 | 2420.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2784 | 1069.5 | 670 | 0 | 86 | 824.09 | 46 | 2299 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2774.5 | 1066 | 653.5 | 0 | 89 | 827.63 | 46 | 2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2765 | 1062.5 | 637 | 0 | 92 | 831.17 | 46 | 2271 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2805 | 1094.5 | 636.5 | 0 | 93 | 834.14 | 46 | 2406.5 | 0 | 0 | 2 | 0 | 0 | 0 | 0
06:00 | 2845 | 1126.5 | 636 | 0 | 94 | 837.11 | 46 | 2542 | 0 | 0 | 4 | 0 | 0 | 0 | 0
06:30 | 2921.5 | 1158 | 636 | 0 | 94 | 852.48 | 46 | 2709.5 | 17.395 | 0 | 14 | 0 | 0 | 0 | 0
07:00 | 2998 | 1189.5 | 636 | 0 | 94 | 867.85 | 46 | 2877 | 34.79 | 0 | 24 | 0 | 0 | 0 | 0
07:30 | 3017.5 | 1185 | 683 | 0 | 95 | 977.765 | 46 | 3070.5 | 76.91 | 0 | 36.5 | 0 | 0 | 0 | 0
08:00 | 3037 | 1180.5 | 730 | 0 | 96 | 1087.68 | 46 | 3264 | 119.03 | 0 | 49 | 0 | 0 | 0 | 0
08:30 | 3005 | 1160 | 753.5 | 0 | 94 | 1053.835 | 46 | 3246.5 | 208.31 | 0 | 62.5 | 0 | 0 | 0 | 0
09:00 | 2973 | 1139.5 | 777 | 0 | 92 | 1019.99 | 46 | 3229 | 297.59 | 0 | 76 | 0 | 0 | 0 | 0
09:30 | 2938.5 | 1172 | 777 | 0 | 92 | 969.44 | 46 | 3096.5 | 363.425 | 0 | 55.5 | 0 | 0 | 0 | 0
10:00 | 2904 | 1204.5 | 777 | 0 | 92 | 918.89 | 46 | 2964 | 429.26 | 0 | 35 | 0 | 0 | 0 | 0
10:30 | 2940.5 | 1214.5 | 777 | 0 | 94 | 917.945 | 46 | 2935.5 | 447.935 | 0 | 35 | 20.5 | 0 | 0 | 0
11:00 | 2977 | 1224.5 | 777 | 0 | 96 | 917 | 46 | 2907 | 466.61 | 0 | 35 | 41 | 0 | 0 | 0
11:30 | 2987 | 1186.5 | 825 | 0 | 99 | 921.19 | 46 | 3008.5 | 490.435 | 0 | 146 | 20.5 | 0 | 0 | 0
12:00 | 2997 | 1148.5 | 873 | 0 | 102 | 925.38 | 46 | 3110 | 514.26 | 0 | 257 | 0 | 0 | 0 | 0
12:30 | 2984 | 1151.5 | 872.5 | 0 | 98 | 1016.725 | 46 | 3172 | 491.48 | 0 | 414.5 | 0 | 0 | 0 | 0
13:00 | 2971 | 1154.5 | 872 | 0 | 94 | 1108.07 | 46 | 3234 | 468.7 | 0 | 572 | 0 | 0 | 0 | 0
13:30 | 2879.5 | 1155.5 | 872 | 0 | 93 | 1109.035 | 46 | 3088.5 | 424.275 | 0 | 565.5 | 0 | 0 | 0.5 | 0
14:00 | 2788 | 1156.5 | 872 | 0 | 92 | 1110 | 46 | 2943 | 379.85 | 0 | 559 | 0 | 0 | 1 | 0
14:30 | 2808 | 1148.25 | 872.5 | 0 | 96 | 1116.245 | 46 | 2969 | 309.045 | 0 | 489.4 | 0 | 0 | 2 | 0
15:00 | 2828 | 1140 | 873 | 0 | 100 | 1122.49 | 46 | 2995 | 238.24 | 0 | 419.8 | 0 | 0 | 3 | 0
15:30 | 2875 | 1142.5 | 872.5 | 0 | 108 | 1088.125 | 46 | 3001 | 164.945 | 0 | 394.85 | 0 | 0 | 5.5 | 0
16:00 | 2922 | 1145 | 872 | 0 | 116 | 1053.76 | 46 | 3007 | 91.65 | 0 | 369.9 | 0 | 0 | 8 | 0
16:30 | 2904.5 | 1158.25 | 872.5 | 0 | 112 | 1113.105 | 46 | 3091 | 48.42 | 24.5 | 531.05 | 0 | 0 | 6.5 | 0
17:00 | 2887 | 1171.5 | 873 | 0 | 108 | 1172.45 | 46 | 3175 | 5.19 | 49 | 692.2 | 0 | 0 | 5 | 0
17:30 | 2905.5 | 1182.5 | 860.5 | 0 | 112 | 1320.225 | 46 | 3356 | 2.595 | 55.5 | 854.6 | 0 | 0 | 5.5 | 0
18:00 | 2924 | 1193.5 | 848 | 0 | 116 | 1468 | 46 | 3537 | 0 | 62 | 1017 | 0 | 0 | 6 | 0
18:30 | 2935 | 1207 | 848.5 | 0 | 116 | 1464.815 | 46 | 3575 | 0 | 60.5 | 824.75 | 0 | 0 | 9.5 | 0
19:00 | 2946 | 1220.5 | 849 | 0 | 116 | 1461.63 | 46 | 3613 | 0 | 59 | 632.5 | 0 | 0 | 13 | 0
19:30 | 2896 | 1182.5 | 849 | 0 | 112 | 1457.23 | 46 | 3679 | 0 | 33 | 485.5 | 0 | 0 | 13 | 0
20:00 | 2876 | 1152.5 | 849 | 0 | 112 | 1446.97 | 46 | 3698 | 0 | 16 | 442.5 | 0 | 0 | 11 | 0
20:30 | 2898 | 1151.5 | 849.5 | 0 | 108 | 1453.57 | 46 | 3648 | 0 | 8 | 358.75 | 0 | 0 | 10 | 0
21:00 | 2920 | 1150.5 | 850 | 0 | 104 | 1460.17 | 46 | 3598 | 0 | 0 | 275 | 0 | 0 | 9 | 0
21:30 | 2880.5 | 1149.5 | 855 | 0 | 102 | 1457.085 | 46 | 3531 | 0 | 0 | 219 | 0 | 0 | 9 | 0
22:00 | 2841 | 1148.5 | 860 | 0 | 100 | 1454 | 46 | 3464 | 0 | 0 | 163 | 0 | 0 | 9 | 0
22:30 | 2847 | 1147.5 | 860 | 0 | 105 | 1415 | 46 | 3344.5 | 0 | 0 | 111 | 0 | 0 | 9 | 0
23:00 | 2853 | 1146.5 | 860 | 0 | 110 | 1376 | 46 | 3225 | 0 | 0 | 59 | 0 | 0 | 9 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 05:00 | 383 | 12:00 | Meghnaghat | 400 | 05:00 | 386 | 12:00
Ashuganj | 402 | 6:00 | 393 | 12:00 | Payra | 416 | 05:00 | 408 | 19:30
Bhulta | 399 | 03:00 | 389 | 12:00 | Rahanpur | 419 | 03:00 | 400 | 18:00
Bibiana | 400 | 01:00 | 391 | 12:00 | Rampal | 412 | 05:00 | 399 | 12:00
BIPTC | 407 | 01:00 | 394 | 12:00
Bogura | 413 | 04:00 | 391 | 18:00
Gopalganj | 408 | 04:00 | 394 | 18:00
Kaliakoir | 397 | 04:00 | 379 | 12:00
Korerhat | 403 | 02:00 | 391 | 12:00
Madunaghat | 400 | 04:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 229 | 12:00 | Kachua | 238 | 01:00 | 231 | 11:00
AKSML | 236 | 02:00 | 230 | 11:00 | Kaliakoir | 238 | 05:00 | 226 | 11:00
Aminbazar | 240 | 04:00 | 228 | 11:00 | Keranigonj | 237 | 04:00 | 226 | 12:00
Ashuganj | 238 | 01:00 | 231 | 18:00 | Khulna(S) | 240 | 02:00 | 231 | 12:00
Ashuganj-400 | 238 | 01:00 | 231 | 18:00 | Korerhat | 238 | 03:00 | 231 | 12:00
Baghabari | 239 | 03:00 | 229 | 17:00 | Madunaghat | 237 | 02:00 | 232 | 11:00
Barapukuria | 226 | 05:00 | 212 | 13:00 | Madunaghat-400 | 239 | 04:00 | 233 | 12:00
Barapukuria-230 | 226 | 05:00 | 212 | 13:00 | Maniknagar | 230 | 04:00 | 222 | 12:00
Barishal | 243 | 04:00 | 236 | 20:00 | Meghnaghat | 238 | 01:00 | 231 | 12:00
Bheramara | 238 | 05:00 | 226 | 18:00 | Meghnaghat-400 | 236 | 05:00 | 226 | 12:00
Bhulta | 234 | 04:00 | 222 | 12:00 | Mirsorai | 236 | 02:00 | 229 | 15:00
Bibiana | 235 | 04:00 | 229 | 12:00 | Rajshahi | 239 | 05:00 | 225 | 12:00
BIPTC | 240 | 05:00 | 226 | 18:00 | Rampal | 238 | 04:00 | 228 | 18:00
Bogura | 239 | 03:00 | 226 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 238 | 03:00 | 226 | 18:00 | Rampura | 233 | 04:00 | 221 | 12:00
Borhanuddin | 245 | 03:00 | 240 | 12:00 | Shikalbaha | 236 | 05:00 | 228 | 11:00
BSRM | 236 | 04:00 | 227 | 12:00 | Shyampur | 236 | 04:00 | 225 | 12:00
Cumilla(N) | 235 | 02:00 | 226 | 12:00 | Siddhirganj | 234 | 00:00 | 226 | 15:00
Faridpur | 242 | 03:00 | 233 | 12:00 | Sirajgonj | 243 | 04:00 | 235 | 18:00
Fenchuganj | 235 | 01:00 | 231 | 12:00 | Sreepur | 234 | 03:00 | 225 | 19:00
Feni | 235 | 03:00 | 228 | 11:00 | Tongi | 236 | 04:00 | 223 | 11:00
Ghorashal | 0 | 00:00 | N/A | N/A
Ghorashal-230 | 232 | 05:00 | 215 | 19:00
Gopalganj | 242 | 04:00 | 234 | 12:00
GPH | 237 | 04:00 | 230 | 11:00
Haripur | 234 | 03:00 | 223 | 12:00
Hasnabad | 237 | 03:00 | 226 | 12:00
Hathazari | 236 | 03:00 | 230 | 11:00
Ishurdi | 241 | 05:00 | 229 | 18:00
Jhenaidah | 239 | 04:00 | 226 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 127 | 12:00 | Lalbag | 137 | 04:00 | 129 | 11:00
Agargaon | 137 | 02:00 | 129 | 16:00 | Lalmonirhat | 132 | 01:00 | 120 | 08:00
Agrabad | 137 | 02:00 | 132 | 11:00 | Madanganj | 135 | 05:00 | 130 | 15:00
AKS | 136 | 04:00 | 132 | 13:00 | Madaripur | 140 | 05:00 | 136 | 10:00
Aminbazar | 140 | 18:00 | 131 | 11:00 | Madartek | 135 | 03:00 | 127 | 12:00
Amnura | 139 | 02:00 | 131 | 12:00 | Madunaghat | 138 | 02:00 | 134 | 12:00
Ashuganj | 141 | 02:00 | 138 | 11:00 | Magura | 141 | 06:00 | 133 | 12:00
Bagerhat | 137 | 04:00 | 129 | 18:00 | Mahasthangarh | 136 | 05:00 | 127 | 18:00
Bajitpur | 136 | 01:00 | 126 | 12:00 | Maijdee | 134 | 01:00 | 131 | 11:00
Bakulia | 139 | 04:00 | 133 | 11:00 | Manikganj | 135 | 05:00 | 123 | 12:00
Banani | 136 | 06:00 | 127 | 12:00 | Maniknagar | 139 | 04:00 | 130 | 12:00
Bangabhaban | 139 | 04:00 | 131 | 12:00 | Matarbari | 130 | 04:00 | 120 | 13:00
Barapukuria | 139 | 05:00 | 128 | 13:00 | Matuail | 137.2 | 06:00 | 130 | 12:00
Barguna | 136 | 01:00 | 133 | 13:00 | Metrorail_Motijheel | 139 | 04:00 | 130 | 12:00
Barishal | 139 | 00:00 | 135 | 15:00 | Metrorail_Uttara | 134 | 04:00 | 125 | 12:00
Barishal-230 | 140 | 03:00 | 135 | 12:00 | Millgate | 135 | 02:00 | 124 | 12:00
Baroaulia | 137 | 08:00 | 134 | 11:00 | Mirpur | 139 | 18:00 | 130 | 11:00
Baroirhat | 135 | 03:00 | 131 | 12:00 | Mirzapur | 135 | 03:00 | 127 | 12:00
Bashundhara | 136 | 04:00 | 127 | 12:00 | Mithapukur | 135 | 03:00 | 124 | 08:00
BashundharaCement | 135 | 05:00 | 130 | 15:00 | MI_Cement | 136.7 | 05:00 | 128 | 12:00
Beanibazar | 134 | 05:00 | 131 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 139 | 02:00 | 127 | 13:00 | Mogbazar | 137 | 02:00 | 128 | 13:00
Bhaluka | 135 | 03:00 | 128 | 18:30 | Mongla | 137 | 04:00 | 130 | 18:30
Bhandaria | 139 | 06:00 | 133 | 18:00 | Motijheel | 139 | 04:00 | 131 | 12:00
Bhangura | 138 | 03:00 | 132 | 08:00 | Muktagacha | 131 | 06:00 | 124 | 13:00
Bheramara | 141 | 03:00 | 136 | 18:00 | Munshiganj | 135 | 02:00 | 128 | 11:00
Bheramara(GK) | 141 | 04:00 | 136 | 08:00 | Muradnagar | 137 | 04:00 | 131 | 11:00
Bhulta | 130 | 07:00 | 125 | 11:00 | Mymensingh | 132 | 04:00 | 121 | 13:00
Bog-Sherpur | 138 | 05:00 | 129 | 18:00 | Naogaon | 135 | 04:00 | 125 | 18:00
Bogura | 136 | 05:00 | 130 | 18:30 | Narail | 142 | 03:00 | 131 | 13:00
Bogura-230 | 137 | 03:00 | 129 | 18:00 | Narinda | 139 | 04:00 | 130 | 12:00
Brahmanbaria | 137 | 01:00 | 134 | 16:00 | Narshingdi | 138 | 03:00 | 125 | 12:00
Cantonment | 137 | 02:00 | 130 | 12:00 | Natore | 136 | 00:00 | 131 | 18:00
Chandina | 139 | 04:00 | 133 | 12:00 | Nawabganj | 137 | 04:00 | 129 | 12:00
Chandpur | 139 | 18:00 | 135 | 11:00 | Netrakona | 131 | 22:00 | 123 | 07:00
Chandraghona | 139 | 04:00 | 134 | 11:00 | New | 135 | 05:00 | 126 | 11:00
Chapai | 140 | 03:00 | 130 | 10:00 | Niamatpur | 140 | 06:00 | 134 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 137 | 05:00 | 129 | 12:00 | Noapara | 138 | 03:00 | 132 | 12:00
Chauddagram | 136 | 01:00 | 130 | 12:00 | Pabna | 140 | 03:00 | 134 | 08:00
Chhatak | 133 | 01:00 | 129 | 18:30 | Palashbari | 130 | 03:00 | 122 | 08:00
Chowmuhani | 134 | 01:00 | 130 | 11:00 | Panchagarh | 138 | 04:00 | 118 | 08:00
Chuadanga | 141 | 06:00 | 131 | 13:00 | Patiya | 138 | 01:00 | 133 | 11:00
Coxsbazar | 127 | 05:00 | 117 | 11:00 | Patuakhali | 136 | 01:00 | 134 | 15:00
Cumilla(N) | 138 | 01:00 | 132 | 12:00 | Payra | 137 | 04:00 | 134 | 11:00
Cumilla(S) | 137 | 04:00 | 125 | 16:00 | PHP | 135 | 02:00 | 131 | 11:00
Daganbhuiyan | 135 | 04:00 | 131 | 11:00 | Postogola | 137 | 04:00 | 130 | 12:00
Daudkandi | 136 | 05:00 | 130 | 11:00 | Purbachal | 136 | 03:00 | 127 | 12:00
DhakaUniversity | 136 | 05:00 | 127 | 12:00 | Purbasadipur | 133 | 04:00 | 118 | 08:00
Dhamrai | 137 | 04:00 | 129 | 11:00 | Rahanpur | 141 | 06:00 | 134 | 18:00
Dhanmondi | 138 | 05:00 | 131 | 12:00 | Rahanpur-400 | 141 | 03:00 | 134 | 18:00
Dohazari | 135 | 04:00 | 129 | 11:00 | Rahim | 137 | 05:00 | 130 | 12:00
Faridpur | 140 | 05:00 | 135 | 11:00 | Rajbari | 140 | 03:00 | 135 | 12:00
Fatullah | 140 | 04:00 | 129 | 12:00 | Rajendrapur | 139 | 06:00 | 130 | 18:00
Fenchuganj | 139 | 00:00 | 137 | 11:00 | Rajshahi | 138 | 05:00 | 131 | 12:00
Feni | 134 | 05:00 | 130 | 11:00 | Rajshahi-230 | 138 | 04:00 | 131 | 12:00
Feni-230 | 135 | 03:00 | 125 | 04:00 | Ramganj | 135 | 05:00 | 131 | 10:00
Ghatail | 131 | 03:00 | 123 | 07:00 | Rampur | 137 | 04:00 | 131 | 11:00
Ghorashal | 137 | 00:00 | 131 | 15:00 | Rampura | 135 | 03:00 | 127 | 12:00
Goalpara | 140 | 03:00 | 132 | 18:00 | Rangamati | 138 | 03:00 | 134 | 11:00
Gollamari | 139 | 04:00 | 133 | 12:00 | Rangpur | 135 | 05:00 | 123 | 08:00
Gopalganj | 140 | 05:00 | 133 | 12:00 | Ruppur | 141 | 05:00 | 135 | 18:00
Gopalganj-400 | 141 | 04:00 | 136 | 12:00 | Saidpur | 137 | 04:00 | 123 | 13:00
Gulshan | 134 | 04:00 | 127 | 12:00 | Satkhira | 138 | 04:00 | 129 | 18:00
Halishahar | 137 | 01:00 | 133 | 11:00 | Satmasjid | 137 | 02:00 | 130 | 12:00
Haripur | 137 | 03:00 | 131 | 11:00 | Savar | 140 | 18:00 | 129 | 11:00
HaripurSBU | 137 | 03:00 | 131 | 12:00 | SevenRings | 138 | 23:00 | 131 | 11:00
Hasnabad | 137 | 00:00 | 130 | 12:00 | ShahCement | 137 | 05:00 | 129 | 12:00
Hathazari | 139 | 04:00 | 134 | 15:00 | Shahjadpur | 140 | 00:00 | 135 | 08:00
Ishurdi | 142 | 04:00 | 136 | 18:00 | Shahjibazar | 138 | 00:00 | 135 | 18:00
Jaldhaka | 132 | 05:00 | 120 | 08:00 | Shahmirpur | 136 | 00:00 | 133 | 11:00
Jamalpur | 130 | 09:00 | 120 | 07:00 | Shariatpur | 140 | 03:00 | 135 | 11:00
Jashore | 140 | 05:00 | 128 | 13:00 | Sherpur | 128 | 09:00 | 116 | 07:00
Jhenaidah | 141 | 04:00 | 124 | 13:00 | Shikalbaha | 127 | 03:00 | 122 | 11:00
Jhenaidah-230 | 143 | 05:00 | 133 | 13:00 | Shikalbaha-230 | 138 | 02:00 | 134 | 11:00
Joydebpur | 138 | 23:00 | 127 | 12:00 | Shitalakhya | 136.4 | 04:00 | 128 | 12:00
Joypurhat | 134 | 03:00 | 125 | 18:00 | Sholosohor | 138 | 02:00 | 134 | 11:00
Juldah | 137 | 03:00 | 133 | 10:00 | Shyampur | 139 | 05:00 | 133 | 11:00
Kabirpur | 136 | 19:00 | 124 | 12:00 | Shyampur-230 | 140 | 03:00 | 132 | 11:00
Kachua | 139 | 01:00 | 135 | 11:00 | Siddhirganj | 137 | 05:00 | 130 | 12:00
Kaliakoir | 139 | 03:00 | 131 | 12:00 | Sirajganj | 137 | 04:00 | 130 | 08:00
Kallyanpur | 140 | 18:00 | 133 | 12:00 | Sonargaon | 136 | 04:00 | 130 | 12:00
Kalurghat | 138 | 04:00 | 133 | 11:00 | Sreemongol | 138 | 01:00 | 135 | 12:00
Kamrangirchar | 137 | 02:00 | 129 | 11:00 | Sreepur | 137 | 03:00 | 131 | 18:30
Kaptai | 140 | 4:00 | 136 | 14:00 | Srinagar | 136 | 05:00 | 129 | 12:00
Kasba | 137 | 06:00 | 131 | 11:00 | SSM | 140 | 00:00 | 139 | 13:00
Kazla | 139 | 07:00 | 130 | 12:00 | Sunamganj | 130 | 01:00 | 125 | 18:00
Keranigonj | 137 | 04:00 | 130 | 12:00 | Sylhet | 134 | 00:00 | 132 | 12:00
Khagrachori | 138 | 05:00 | 133 | 11:00 | Sylhet-132 | 133 | 00:00 | 132 | 09:00
Khulna | 138 | 03:00 | 131 | 18:00 | Tangail | 131 | 03:00 | 124 | 07:00
Khulna(S) | 140 | 04:00 | 133 | 18:00 | Taraganj | 133 | 04:00 | 124 | 13:00
Khulshi | 135 | 01:00 | 131 | 11:00 | Tasnim | 136 | 03:00 | 130 | 09:00
Kishoreganj | 135 | 03:00 | 129 | 08:00 | Thakurgaon | 136 | 04:00 | 115 | 08:00
Kodda | 134 | 20:00 | 125 | 11:00 | TK | 137 | 02:00 | 134 | 11:00
KSRM | 138 | 06:00 | 134 | 08:00 | Tongi | 136 | 04:00 | 128 | 11:00
Kulaura | 139 | 06:00 | 136 | 11:00 | Ullahpara | 139 | 03:00 | 131 | 18:00
Kurigram | 133 | 05:00 | 122 | 07:00 | Ullon | 135 | 03:00 | 127 | 12:00
Kushtia | 137 | 02:00 | 129 | 13:00 | Uttara | 134 | 03:00 | 124 | 16:00
Laksam | 139 | 04:00 | 135 | 11:00 | UttaraNew | 134 | 04:00 | 125 | 12:00
Lakshmipur | 134 | 04:00 | 130 | 11:00 | Zigatola | 137 | 04:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division