## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-12-2025 | [28 empty] | Date: | 04-12-2025 | [28 empty] | Date: | 04-12-2025 | [28 empty] | Date: | 04-12-2025 | [28 empty] | Date: | 04-12-2025 | [17 empty] | Date: | 04-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 30 | 354 | 0 | 0 | 0 | 0 | 51 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 176 | 51 | 0 | 188 | 0 | 0 | 110 | 51 | 0 | 14 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 0 | 23 | 0 | 82 | 30 | 0 | 16 | 158 | 0 | 59 | 19 | 37 | 0 | 0 | 0 | 3877 | 872 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037 | 0 | 0 | 0 | 1103.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 254 | 1020 | 0 | 5323.49 | 9200.49 | 99.46
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 195 | 51 | 0 | 186 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 16 | 158 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 3590 | 776 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 965 | 0 | 0 | 0 | 936.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 255 | 950 | 0 | 4917.42 | 8507.42 | 99.45
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 303 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 270 | 51 | 0 | 202 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 315 | 0 | 206 | 0 | 30 | 0 | 0 | 21 | 0 | 11 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 3497 | 728 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 829.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 255 | 900 | 0 | 4599.09 | 8096.09 | 99.44
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 306 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 270 | 5 | 0 | 202 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 0 | 21 | 0 | 11 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 3398 | 682 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 828.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 256 | 820 | 0 | 4407.78 | 7805.78 | 99.44
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 308 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 220 | 0 | 220 | 5 | 0 | 141 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 72 | 0 | 0 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 0 | 21 | 0 | 11 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 3357 | 682 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 826.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 254 | 690 | 0 | 4241.71 | 7598.71 | 99.44
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 305 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 220 | 0 | 220 | 5 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 64 | 0 | 0 | 0 | 300 | 0 | 206 | 0 | 30 | 0 | 0 | 21 | 0 | 11 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 3452 | 635 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766 | 0 | 0 | 0 | 829.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 256 | 585 | 0 | 4104.74 | 7556.74 | 99.43
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 220 | 0 | 220 | 10 | 0 | 200 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 68 | 0 | 0 | 0 | 290 | 0 | 206 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 16 | 158 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 3821 | 635 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 826.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 256 | 558 | 0 | 4135.94 | 7956.94 | 99.43
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0.28 | 40 | 0 | 38 | 355 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 460 | 2 | 0 | 0 | 265 | 0 | 240 | 43 | 0 | 206 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 76 | 0 | 5 | 0 | 275 | 0 | 206 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 35 | 8 | 35 | 0 | 1.65 | 0 | 4065.93 | 634 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 880 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.16 | 3 | 0 | 0 | 2.2 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.16 | 0 | 56 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 5 | 0 | 0 | 0 | 115 | 220 | 0 | 297 | 630 | 0 | 4634.62 | 8700.55 | 99.43
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 8 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.81 | 40 | 0 | 12 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 300 | 0 | 240 | 43 | 0 | 196 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 80 | 0 | 23 | 0 | 265 | 0 | 206 | 0 | 30 | 0 | 1 | 21 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 56 | 19 | 35 | 1 | 10.51 | 0 | 4122.32 | 707 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1102 | 0 | 0 | 0 | 1122.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.97 | 20 | 0 | 0 | 11.89 | 156 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0.99 | 0 | 56 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 39 | 0 | 0 | 0 | 100 | 180 | 0 | 356 | 862 | 0 | 5279.47 | 9401.79 | 99.43
09:00 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 16 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.43 | 40 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 509 | 13 | 0 | 0 | 290 | 0 | 240 | 43 | 0 | 200 | 0 | 0 | 109 | 0 | 0 | 6 | 0 | 84 | 0 | 42 | 0 | 265 | 0 | 206 | 0 | 30 | 0 | 2 | 21 | 0 | 79 | 30 | 0 | 18 | 159 | 0 | 56 | 19 | 20 | 1 | 25.77 | 0 | 4173.2 | 775 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 1110 | 0 | 0 | 0 | 1032.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.25 | 45 | 0 | 0 | 29.19 | 166 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 2.43 | 0 | 56 | 0 | 12 | 0 | 0 | 0 | 0 | 2.4 | 76 | 0 | 0 | 0 | 100 | 180 | 0 | 308 | 905 | 0 | 5401.87 | 9575.07 | 99.42
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 22 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 40 | 0 | 2 | 356 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 475 | 17 | 0 | 0 | 240 | 0 | 240 | 43 | 0 | 200 | 0 | 0 | 106 | 0 | 0 | 6 | 0 | 84 | 0 | 56 | 0 | 270 | 0 | 206 | 0 | 30 | 0 | 4 | 22 | 0 | 41 | 30 | 0 | 18 | 158 | 0 | 56 | 19 | 20 | 2 | 35.31 | 0 | 4094.76 | 775 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1000 | 0 | 0 | 0 | 934.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.93 | 72 | 0 | 0 | 40.21 | 162 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 3.37 | 0 | 56 | 0 | 19 | 0 | 0 | 0 | 0 | 3.7 | 118 | 0 | 0 | 0 | 100 | 180 | 0 | 306 | 870 | 0 | 5276.09 | 9370.85 | 99.42
11:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 27 | 0 | 23.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 40 | 0 | 3 | 354 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 527 | 19 | 0 | 0 | 240 | 0 | 240 | 43 | 0 | 206 | 0 | 0 | 106 | 0 | 0 | 6 | 0 | 98 | 0 | 61 | 0 | 315 | 0 | 206 | 0 | 30 | 0 | 11 | 24 | 0 | 79 | 30 | 0 | 14 | 159 | 0 | 58 | 19 | 20 | 2 | 41.7 | 0 | 4335.87 | 776 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 925 | 0 | 0 | 0 | 953.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.09 | 84 | 0 | 0 | 51.18 | 167 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 4.43 | 0 | 56 | 0 | 25 | 0 | 0 | 0 | 0 | 4.5 | 142 | 0 | 0 | 0 | 100 | 180 | 0 | 304 | 850 | 0 | 5304.27 | 9640.14 | 99.42
12:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 480 | 24 | 0 | 12 | 0 | 60 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 28 | 0 | 23.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 3.29 | 40 | 0 | 7 | 355 | 0 | 0 | 7 | 0 | 25 | 225 | 0 | 0 | 0 | 590 | 19 | 14 | 0 | 240 | 0 | 240 | 43 | 0 | 203 | 0 | 0 | 104 | 0 | 0 | 6 | 0 | 100 | 0 | 65 | 0 | 315 | 0 | 206 | 0 | 30 | 0 | 11 | 24 | 0 | 79 | 30 | 0 | 14 | 157 | 0 | 59 | 19 | 20 | 2 | 38.91 | 0 | 4651 | 844 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 948 | 0 | 0 | 0 | 1041.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.61 | 91 | 0 | 0 | 46.2 | 168 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 5.05 | 0 | 55 | 0 | 26 | 0 | 0 | 0 | 0 | 4.6 | 153 | 0 | 0 | 0 | 100 | 220 | 0 | 305 | 825 | 0 | 5536.39 | 10187.39 | 99.42
13:00 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 420 | 40 | 0 | 18 | 0 | 110 | 0 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 20 | 0 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3.04 | 40 | 0 | 15 | 355 | 0 | 0 | 25 | 0 | 56 | 225 | 0 | 0 | 0 | 580 | 16 | 60 | 0 | 240 | 0 | 240 | 51 | 0 | 214 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 104 | 0 | 59 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 7 | 24 | 0 | 83 | 30 | 0 | 14 | 158 | 0 | 59 | 19 | 18 | 2 | 36.12 | 0 | 4827.66 | 844 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1035 | 0 | 0 | 0 | 1168.24 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 44.5 | 80 | 0 | 0 | 47.32 | 165 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 4.2 | 0 | 54 | 0 | 24 | 0 | 0 | 0 | 0 | 4.4 | 105 | 0 | 0 | 0 | 115 | 180 | 0 | 306 | 882 | 0 | 5690.66 | 10518.32 | 99.42
14:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 399 | 38.6 | 0 | 34 | 0 | 75 | 0 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 12 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.41 | 40 | 0 | 9 | 355 | 0 | 0 | 32 | 0 | 51 | 225 | 0 | 0 | 0 | 560 | 15 | 20 | 0 | 235 | 0 | 240 | 51 | 0 | 197 | 0 | 0 | 104 | 0 | 0 | 11 | 0 | 100 | 0 | 47 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 8 | 24 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 59 | 19 | 18 | 1 | 29.87 | 0 | 4593.38 | 844 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1004 | 0 | 0 | 0 | 1030.2 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 37.44 | 68 | 0 | 0 | 38.64 | 158 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 2.99 | 0 | 53 | 0 | 18 | 0 | 0 | 0 | 0 | 3.4 | 77 | 0 | 0 | 0 | 115 | 180 | 0 | 305 | 898 | 0 | 5527.67 | 10121.05 | 99.41
15:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 395 | 33.9 | 0 | 34 | 0 | 75 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 15 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 25 | 1.65 | 40 | 0 | 4 | 355 | 0 | 0 | 33 | 0 | 51 | 222 | 0 | 0 | 0 | 560 | 11 | 20 | 0 | 240 | 0 | 240 | 51 | 0 | 196 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 96 | 0 | 32 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 4 | 24 | 0 | 81 | 30 | 0 | 14 | 158 | 0 | 59 | 19 | 18 | 1 | 19.86 | 0 | 4555.41 | 844 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 947 | 0 | 0 | 0 | 974 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 22.45 | 46 | 0 | 0 | 24.27 | 161 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 1.39 | 0 | 53 | 0 | 12 | 0 | 0 | 0 | 0 | 2.1 | 74 | 0 | 0 | 0 | 115 | 180 | 0 | 304 | 830 | 0 | 5263.21 | 9818.62 | 99.41
16:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 415 | 33.9 | 0 | 34 | 0 | 75 | 0 | 35 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 23.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0.78 | 40 | 0 | 2 | 354 | 0 | 0 | 33 | 0 | 48 | 223 | 0 | 0 | 0 | 560 | 6 | 20 | 0 | 240 | 0 | 240 | 51 | 0 | 204 | 0 | 0 | 105 | 5 | 0 | 11 | 0 | 94 | 0 | 14 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 1 | 24 | 0 | 82 | 30 | 0 | 14 | 156 | 0 | 59 | 19 | 18 | 0 | 8.43 | 0 | 4571.61 | 844 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 939 | 0 | 0 | 0 | 931 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 13.25 | 14 | 0 | 0 | 8.85 | 162 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0.63 | 0 | 53 | 0 | 5 | 0 | 0 | 0 | 0 | 1.4 | 24 | 0 | 0 | 0 | 115 | 180 | 0 | 306 | 830 | 0 | 5105.13 | 9676.74 | 99.41
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 405 | 34.9 | 0 | 35 | 15 | 138 | 0 | 35 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 12 | 38 | 0.01 | 40 | 2 | 14 | 354 | 0 | 0 | 33 | 0 | 57 | 225 | 0 | 0 | 0 | 560 | 0 | 31 | 0 | 230 | 0 | 240 | 51 | 0 | 192 | 0 | 0 | 109 | 45 | 0 | 11 | 0 | 96 | 0 | 1 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 15 | 156 | 0 | 59 | 19 | 18 | 0 | 0.31 | 0 | 4779.22 | 844 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 980 | 0 | 0 | 0 | 1101 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0.66 | 1 | 0 | 0 | 0.46 | 170 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0.04 | 0 | 53 | 30 | 0 | 7 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 115 | 180 | 0 | 356 | 900 | 0 | 5382.26 | 10161.48 | 99.41
18:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 401 | 34.2 | 0 | 90 | 38 | 175 | 0 | 50 | 87 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 17 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 31 | 0 | 24 | 25 | 0 | 40 | 19 | 13 | 354 | 0 | 0 | 33 | 0 | 89 | 228 | 0 | 0 | 0 | 560 | 0 | 93 | 0 | 230 | 0 | 240 | 51 | 0 | 216 | 0 | 0 | 108 | 99 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 82 | 30 | 0 | 15 | 156 | 0 | 59 | 28 | 18 | 0 | 0 | 0 | 5156.2 | 844 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 1326 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 50 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 500 | 974 | 0 | 6046 | 11202.2 | 99.41
19:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 410 | 30.6 | 0 | 103 | 45 | 95 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 17 | 26 | 354 | 0 | 0 | 19 | 0 | 51 | 227 | 0 | 0 | 0 | 560 | 0 | 50 | 0 | 225 | 0 | 240 | 51 | 0 | 207 | 0 | 0 | 109 | 51 | 0 | 11 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 83 | 30 | 0 | 15 | 156 | 0 | 59 | 19 | 20 | 0 | 0 | 0 | 4783.1 | 844 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 52 | 50 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 990 | 0 | 6050 | 10833.1 | 99.41
19:30 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 425 | 17 | 0 | 75 | 15 | 45 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 18.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 15 | 354 | 0 | 0 | 19 | 0 | 51 | 226 | 0 | 0 | 0 | 566 | 0 | 5 | 0 | 225 | 0 | 240 | 51 | 0 | 207 | 0 | 0 | 109 | 51 | 0 | 17 | 0 | 94 | 0 | 0 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 83 | 30 | 0 | 15 | 156 | 0 | 59 | 19 | 20 | 0 | 0 | 0 | 4593.5 | 844 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 0 | 0 | 1331 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 53 | 50 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 1000 | 0 | 6097 | 10690.5
20:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 420 | 17 | 0 | 74 | 15 | 45 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 32 | 354 | 0 | 0 | 19 | 0 | 48 | 227 | 0 | 0 | 0 | 562 | 0 | 5 | 0 | 225 | 0 | 240 | 51 | 0 | 207 | 0 | 0 | 109 | 49 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 83 | 30 | 0 | 15 | 156 | 0 | 59 | 19 | 22 | 0 | 0 | 0 | 4573 | 844 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1321 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 53 | 50 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 1010 | 0 | 6018 | 10591 | 99.41
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 445 | 0 | 0 | 70 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 19.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 31 | 354 | 0 | 0 | 0 | 0 | 50 | 228 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 220 | 0 | 240 | 51 | 0 | 199 | 0 | 0 | 110 | 50 | 0 | 17 | 0 | 88 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 83 | 30 | 0 | 18 | 156 | 0 | 59 | 19 | 22 | 0 | 0 | 0 | 4462.5 | 844 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 0 | 0 | 1322.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 501 | 1012 | 0 | 5908.72 | 10371.22 | 99.41
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 410 | 0 | 0 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 17.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 17 | 228 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 220 | 0 | 230 | 51 | 0 | 201 | 0 | 0 | 110 | 17 | 0 | 18 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 83 | 30 | 0 | 17 | 156 | 0 | 59 | 19 | 22 | 0 | 0 | 0 | 4296.5 | 844 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 0 | 0 | 0 | 1322.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 409 | 1010 | 0 | 5773.27 | 10069.77 | 99.41
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 436 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 220 | 0 | 230 | 51 | 0 | 200 | 0 | 0 | 111 | 0 | 0 | 18 | 0 | 88 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 0 | 24 | 0 | 83 | 30 | 0 | 17 | 156 | 0 | 59 | 19 | 22 | 0 | 0 | 0 | 4209 | 844 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994 | 0 | 0 | 0 | 1206.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 309 | 950 | 0 | 5393.17 | 9602.17 | 99.41
Total KWH | 0 | 204480 | 186720 | 0 | 0 | 0 | 0 | 0 | 8319600 | 0 | 10115350 | 288000 | 0 | 649440 | 103200 | 893487 | 0 | 351074 | 519840 | 0 | 0 | 0 | 0 | 0 | 53190 | 6509003 | 0 | 0 | 161430 | 3600 | 413400 | 514080 | 0 | 0 | 0 | 0 | 0 | 0 | 201600 | 0 | 68304 | 0 | 45120 | 288000 | 18285 | 964000 | 64399 | 492000 | 8370909.09 | 0 | 0 | 247200 | 0 | 672436 | 5332992 | 0 | 0 | 0 | 10510908 | 125145 | 436581 | 0 | 6007000 | 0 | 5760000 | 1069064 | 0 | 4880000 | 0 | 0 | 2496457 | 399840 | 0 | 300740 | 0 | 2069760 | 0 | 408982 | 0 | 7347500 | 0 | 5038000 | 0 | 715920 | 0 | 49894 | 564240 | 0 | 1550400 | 673828 | 0 | 380000 | 3312360 | 0 | 1026000 | 336000 | 556800 | 10150 | 247470 | 0 | 102324178.09 | 18937454 | 4280832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429840 | 23141820 | 0 | 0 | 0 | 25946892 | 0 | 0 | 0 | 820704 | 0 | 0 | 0 | 0 | 0 | 274084 | 519255 | 0 | 0 | 290256 | 4139618 | 0 | 0 | 0 | 0 | 0 | 9046109 | 0 | 25320 | 0 | 1264581 | 201896 | 145469 | 186172 | 0 | 0 | 0 | 27230.4 | 843840 | 0 | 0 | 0 | 2641000 | 5222651 | 0 | 8027565.7 | 21697454.55 | 0 | 128110043.65 | 230434221.74

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-12-2025 | during | 05-12-2025 | during | 05-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 339 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 24 | 34.2 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 38 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 50 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23.8 | 18 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 175 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 12 | 90 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 50 | 87 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 480 | 401 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1335.8 | 1634.2 | 5765.15 | 5734.15 | 3524.36 | 3502.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 7 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 228 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 25 | 89 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 31 | 40 | 48 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 13 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.29 | 0 | 3.52 | 0 | 3.52 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 19 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 25 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 590 | 560 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 3 | 0 | 10 | 0 | 10 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 355 | 354 | 150 | 150 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1295.29 | 1419 | 2378.24 | 2377.72 | 2087.02 | 2102.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 216 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 240 | 240 | 318.81 | 318.81 | 318.81 | 318.81 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 240 | 230 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 14 | 93 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 104 | 108 | 163 | 163 | 111 | 111 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 99 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 100 | 96 | 160 | 160 | 102 | 102 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 11 | 24.5 | 24.5 | 14 | 14 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1015 | 1144 | 2432.21 | 2372.21 | 2135.71 | 2084.71
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-12-2025 | during | 05-12-2025 | during | 05-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 20 | 18 | 157.5 | 157.5 | 37 | 37 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 28 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 60 | 60 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 38.91 | 0 | 47.85 | 0 | 47.85 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 138.91 | 105 | 363.85 | 314 | 195.85 | 146
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 82 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 157 | 156 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 14 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 206 | 207 | 195 | 195 | 195 | 195 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 866 | 854 | 883 | 883 | 849 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 844 | 844 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 181 | 173 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 948 | 1050 | 590 | 590 | 550 | 550 | Unit1 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2043 | 2067 | 2937 | 2862 | 2142.1 | 2067.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 305 | 500 | 0 | 0 | 304 | 507 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 825 | 974 | 1085.32 | 1085.32 | 1025.32 | 1025.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1450 | 1809 | 1993.32 | 1993.32 | 1797.32 | 2000.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 43.61 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 168 | 172 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 409 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.05 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1041.93 | 1326 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 46.2 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 91 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1804.79 | 2025 | 3172.02 | 3005.87 | 2658.64 | 2492.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 52 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 43 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.6 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 153 | 0 | 178.23 | 0 | 178.23 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 238.6 | 145 | 510.43 | 317 | 496.43 | 283
System Total |  |  |  |  | 28823.2 | 28216.665 | 10187.39 | 11202.2 | 20435.22 | 19859.27 | 15886.43 | 15527.48
Forecast Scenario (05-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9250 |  | 0 |  | 9250
|  |  |  | 1:00 | 8750 |  | 0 |  | 8750
|  |  |  | 2:00 | 8250 |  | 0 |  | 8250
|  |  |  | 3:00 | 7970 |  | 0 |  | 7970
|  |  |  | 4:00 | 7800 |  | 0 |  | 7800
|  |  |  | 5:00 | 7650 |  | 0 |  | 7650
|  |  |  | 6:00 | 7750 |  | 0 |  | 7750
|  |  |  | 7:00 | 7950 |  | 0 |  | 7950
|  |  |  | 8:00 | 8520 |  | 0 |  | 8520
|  |  |  | 9:00 | 8170 |  | 0 |  | 8170
|  |  |  | 10:00 | 8050 |  | 0 |  | 8050
|  |  |  | 11:00 | 8500 |  | 0 |  | 8500
|  |  |  | 12:00 | 9300 |  | 0 |  | 9300
|  |  |  | 13:00 | 10180 |  | 0 |  | 10180
|  |  |  | 14:00 | 8430 |  | 0 |  | 8430
|  |  |  | 15:00 | 7970 |  | 0 |  | 7970
|  |  |  | 16:00 | 7780 |  | 0 |  | 7780
|  |  |  | 17:00 | 8360 |  | 0 |  | 8360
|  |  |  | 18:00 | 9700 |  | 0 |  | 9700
|  |  |  | 18:30 | 9600 |  | 0 |  | 9600
|  |  |  | 19:00 | 9480 |  | 0 |  | 9480
|  |  |  | 19:30 | 9400 |  | 0 |  | 9400
|  |  |  | 20:00 | 9400 |  | 0 |  | 9400
|  |  |  | 21:00 | 9500 |  | 0 |  | 9500
|  |  |  | 22:00 | 9100 |  | 0 |  | 9100
|  |  |  | 23:00 | 8850 |  | 0 |  | 8850
Probable Maximum Temperature: |  |  | 26.60°C
Probable Maximum Demand at Day Peak: |  |  | 9300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 9700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 206.66 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:28 hrs on 05-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10187.39 | MW | 12:00 Hr. | Energy Generated |  |  | 230.4342 |  | MKWHr.
| Day Peak Demand |  |  | 10187.39 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11202.2 | MW | 18:00 Hr. | Energy Demand |  |  | 230.4342 |  | MKWHr.
| Evening Peak Demand |  |  | 11202.2 | MW | 18:00 Hr. | Maximum Temperature |  |  | 26.7 |  | °C
| Minimum Generation of the Day |  |  | 7556.74 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 730.38 |  | MMCFD
| Maximum Generation of the Day |  |  | 11202.2 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.6109 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.8714 | 0 | 3.253 | 0 | 0 | 0.16143 | 0 | 0 | 29.2859 | Gas | 97.6789 | Gas | 343836572.89
| Chattogram Zone |  |  | 5.825 | 18.8818 | 1.3855 | 0 | 0.964 | 0.14343 | 0 | 0.2016 | 27.4013 | Coal | 73.0132 | Coal | 470301481.8088
| Cumilla Zone |  |  | 20.5133 | 0 | 0.83642 | 0 | 0 | 0.40898 | 2.0698 | 0 | 23.8284 | HFO | 8.0457 | HFO | 136695268.98
| Mymensingh Zone |  |  | 0.5568 | 0 | 1.362 | 0 | 0 | 0.25762 | 0 | 0 | 2.1764 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.5822 | 0 | 0 | 0 | 0 | 0.049894 | 0 | 0 | 19.6321 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 4.2808 | 23.1418 | 0 | 0 | 0 | 0.42984 | 18.9375 | 0 | 46.7899 | Solar | 3.5767 | Solar | 56285790.364
| Barishal Zone |  |  | 7.8637 | 29.725 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5887 | Import | 46.9541 | Import | 282772910.82
| Rajshahi Zone |  |  | 13.1857 | 0 | 0.8207 | 0 | 0 | 1.1089 | 25.9469 | 0 | 41.0622 | Wind | 0.2016 | Wind | 2965536
| Rangpur Zone |  |  | 0 | 1.2646 | 0.38807 | 0 | 0 | 1.0165 | 0 | 0 | 2.6692
| Total |  |  | 97.6789 | 73.0132 | 8.0457 | 0 | 0.964 | 3.5767 | 46.9541 | 0.2016 | 230.4342
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 343836572.89 |  | Hydro | 96400
|  |  |  | Coal | 470301481.8088 |  | Solar | 56285790.364
|  |  |  | HFO | 136695268.98 |  | Import | 282772910.82
|  |  |  | HSD | 0 |  | Wind | 2965536
[5 empty] | Total: | 129,29,53,960 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.9375 | Peak Hr Flow | 844.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 53637000.01 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.9469 | Peak Hr Flow | 1326.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2578 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.0698 | Peak Hr Flow | 96.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2864 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.9541 | Peak Hr Flow | 2266.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4207
|  |  |  | Chattogram |  | 0 |  | 1225
|  |  |  | Cumilla |  | 0 |  | 883
|  |  |  | Mymensingh |  | 0 |  | 857
|  |  |  | Sylhet |  | 0 |  | 389
|  |  |  | Khulna |  | 0 |  | 1225
|  |  |  | Barishal |  | 0 |  | 312
|  |  |  | Rajshahi |  | 0 |  | 985
|  |  |  | Rangpur |  | 0 |  | 780
|  |  |  | Total |  | 0 |  | 10863
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:14 | 16:54 | Ishwardi-Natore 132kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to A/M and from
Natore 132/33kV end Due to Yearly maintenance.
| 08:21 | 16:57 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to
Annual Maintenance
| 08:21 | 16:46 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to
Annual Maintenance
| 08:22 | 17:28 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 132/33kV end Due to
Annual Maintenance and from Gopalganj 400/132kV end Due to Annual Maintenance
| 08:26 | 16:55 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
Maintenance of Doh-Cox ckt-2 and from Dohazari 132/33kV end Due to Annual Maintenance
| 08:28 | 18:18 | Bhulta 400/230kV S/S ATR-01 HT Scheduled S/D
| 08:30 | 15:05 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance Work
| 08:31 | 11:09 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Scheduled S/D Due to Annual maintenance
| 08:31 | 11:10 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Scheduled S/D Due to Annual maintenance
| 08:33 | 16:11 | Rajshahi 230/132/33kV S/S 132 kV Main BUS-02 Scheduled S/D Due to Annual Maintenance
| 08:33 | 16:14 | Mithapukur-Palashbari 132kV Ckt-2 Scheduled S/D from Mithapukur 132/33kV end Due to
Annual maintenance. and from Palashbari 132/33kV end Due to Annual maintenance
| 08:34 | 13:42 | Ghatail 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 20.0MW load
interrup.
| 08:35 | 13:33 | Ghatail 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance 33KV Bus 1 | [7 empty] | 20.0MW load
interrup.
| 08:40 |  | Bhaluka 132/33kV S/S Bus B Scheduled S/D Due to Annual maintenance
| 08:43 | 18:04 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Dead line
Checking.
| 08:44 | 16:28 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to
Annual Maintenance
| 08:45 | 14:58 | Bheramara(GK) 132/33kV S/S TR-4 LT Scheduled S/D Due to Annual Maintenance
| 08:46 | 14:54 | Bheramara(GK) 132/33kV S/S TR-4 HT Scheduled S/D Due to Annual Maintenance
| 08:48 | 08:48 | Barapukuria-Bogura 230 kV Ckt-1 Tripped from Bogura 400/230kV end showing BCU, Main-2 (GE
Relay) relays Due to Broken Conductor
| 08:55 | 16:12 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Muktagacha 132/33kV end. and from
Ghatail 132/33kV end Due to Annual Maintenance
| 08:58 | 16:50 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual Maintanance
| 09:00 | 17:16 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 LT Scheduled S/D Due to Ten-Delta test
| 09:01 | 17:09 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 HT Scheduled S/D Due to Ten Delta test
| 09:03 | 16:53 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Scheduled
Maintenance
| 09:06 | 15:44 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 LT Scheduled S/D Due to Annual maintenance
| 09:07 | 15:42 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 HT Scheduled S/D Due to AM
| 09:10 | 19:24 | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end.
| 09:11 | 19:25 | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
| 09:16 | 10:11 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintanance
| 09:16 | 10:11 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Mintanance
| 09:18 | 11:19 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to Annual
Maintenance
| 09:25 | 16:38 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to annual maintenance
| 09:25 | 16:38 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to annual maintanence
| 09:26 | 16:37 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to annual maintanence
| 09:26 | 16:37 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to annual maintenance
| 09:41 | 16:39 | Mymensingh-Netrokona 132kV Ckt-1 Project Work S/D from Netrakona 132/33kV end Due to
Equipment changing by G2G
| 09:50 | 12:38 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to for scada work
| 10:10 | 15:40 | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D Due to Annual Maintenance work
| 10:11 | 15:40 | Rangpur 132/33kV S/S T-1(414T) HT Scheduled S/D Due to Annual Maintenance works
| 10:14 | 10:50 | Chhatak 132/33kV S/S T-3 HT Scheduled S/D
| 10:14 | 10:50 | Chhatak 132/33kV S/S T-3 LT Scheduled S/D
| 10:31 | 16:22 | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D Due to Yearly maintenance.
| 10:32 | 16:17 | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D Due to Yearly maintenance.
| 10:53 | 12:02 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to 132 kv DS
(101S) Cleaning and from Sylhet 132/33kV end Due to Chattak side job purpouse.
| 11:20 | 16:35 | Hathazari 230/132/33kV S/S MT-04 HT Scheduled S/D Due to Annual Maintenance
| 11:20 | 16:35 | Hathazari 230/132/33kV S/S MT-04 LT Scheduled S/D Due to Annual Maintenance
| 11:23 | 12:48 | Bhaluka-Mymensingh 132 kV Ckt-2 Scheduled S/D from Bhaluka 132/33kV end Due to Annual
maintenance work
| 11:32 |  | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to Annual maintenance work
| 11:33 |  | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to Annual maintenance work
| 11:40 |  | Rampur 230/132/33 S/S TR-1 LT Project Work S/D Due to On demand of PDB rampur 33kv S/S
| 12:00 |  | Day peak generation 10183 MW
| 13:47 | 15:25 | Ghatail 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 20.0MW load
interrup.
| 13:48 | 15:24 | Ghatail 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 20.0MW load
interrup.
| 14:30 | 17:14 | Kasba 132/33kV S/S TR-2 HT Scheduled S/D Due to nldc and scada work by ESPNER project
|  | 15:38 | Sylhet 132/33kV S/S T4 LT is restored.
|  | 15:38 | Sylhet 132/33kV S/S T4 HT is restored.
|  | 16:01 | Chhatak 132/33kV S/S Bus A is restored.
|  | 16:04 | Chhatak 132/33kV S/S T-2 HT is restored.
|  | 16:04 | Chhatak 132/33kV S/S T-2 LT is restored.
| 16:10 | 16:44 | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to To fill OLTC with oil
| 16:10 | 16:44 | Haripur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to To fill OLTC with oil
| 16:15 | 19:22 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D Due to CT core connection
| 16:15 | 19:22 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D Due to CT core connection
|  | 16:33 | Sherpur 132/33kV S/S Bus B is restored.
|  | 16:45 | Goalpara- Khulna (C) 132kV Ckt-2 is restored.
| 17:03 |  | TR-1 Transformer close at Bakergonj 132/33 KV S/S.
| 17:03 |  | 25/41MVA Transformer-1 is switched on at Bakerganj Substation for the first time.
| 17:03 | 19:22 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to CT core
connection
|  | 17:03 | Barishal 132/33kV S/S 132 kv GTPS is restored.
|  | 17:03 | Barishal 132/33kV S/S 132 kv GTPS is restored.
| 18:00 |  | Evening Peak Generation is 11202 MW.
| 18:03 | 18:30 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Annual Maintenance
| 18:47 | 18:55 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing O/C, E/F relays Due to 33 kV | [7 empty] | 42.0MW load
|  |  | polashpur feeder fault. | [7 empty] | interrup.
|  | 19:15 | Purbasadipur 132/33kV S/S T-4 Transformer HT is restored.
|  | 19:17 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
|  | 19:19 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
| 19:27 |  | 80/120MVA 132/33kV Transformer-1 (Previously known as T-4 in the same substation) was
switched on from 132kV GIS bus-B for the first time at 19:27 hrs at Purbosadipur
Substation.
|  | 20:12 | Rangpur 132/33kV S/S Rangpur-GTPS is restored.
| 00:46 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 00:46 |  | Meghnaghat CCPP(Summit)-2 GT Synchronized with remarks:- None
| 00:46 |  | Summit Meghnaghat-2 589 MW CCPP GT was sync.
| 02:55 |  | Meghnaghat CCPP(Summit)-2 ST Synchronized with remarks:- None
| 02:55 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 05:00 |  | Minimum Generation: 7464 MW.
| 06:20 |  | Goalpara- Khulna (C) 132kV Ckt-2 Project Work S/D from Goalpara 132/33kV end Due to
instruction by the ALDC, Khulna and from Khulna (C) end Due to For project work shutdown
| 06:26 |  | Goalpara- Khulna (C) 132kV Ckt-2 Project Work S/D from Khulna (C) end Due to For project
work shutdown
| 06:28 |  | Halishahar 132/33kV S/S 415T(TR-2) HT Project Work S/D Due to 33kv cable shifting work.
| 06:39 |  | Halishahar 132/33kV S/S 425T(TR-3) HT Project Work S/D Due to 33 kv cable shifting work.
| 06:44 |  | Natore-Rajshahi 132kV Ckt-2 Project Work S/D from Rajshahi 132/33kV end Due to FOR MAIN
BUS SHUTDOWN
| 06:44 |  | Natore-Rajshahi 132kV Ckt-1 Project Work S/D from Rajshahi 132/33kV end Due to FOR MAIN
BUS SHUTDOWN
| 06:46 |  | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw Project Work S/D Due to FOR MAIN BUS SHUTDOWN
| 06:48 |  | Rajshahi 132/33kV S/S Main Bus Project Work S/D Due to FOR MAIN BUS SHUTDOWN
| 06:48 |  | Rajshahi-Rajshahi(New) 132kV Ckt-2 Project Work S/D from Rajshahi 132/33kV end Due to
FOR MAIN BUS SHUTDOWN
| 06:48 |  | Rajshahi-Rajshahi(New) 132kV Ckt-1 Project Work S/D from Rajshahi 132/33kV end Due to
FOR MAIN BUS SHUTDOWN
| 06:49 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Project Work S/D Due to FOR MAIN BUS | [7 empty] | 12.0MW load
|  |  | SHUTDOWN | [7 empty] | interrup.
| 06:49 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Project Work S/D Due to FOR MAIN BUS S/D
| 06:49 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Project Work S/D Due to For bus shutdown
| 07:22 |  | Barishal 132/33kV S/S 132 kv Summit power Scheduled S/D Due to Annual maintenance.
| 07:28 |  | Hasnabad 230/132kV S/S AUTO TR-2 LT Scheduled S/D Due to annual maintenance
| 07:28 |  | Hasnabad 230/132kV S/S AUTO TR-2 HT Scheduled S/D Due to annual maintenance
| 07:36 |  | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D
| 07:52 |  | JERA Meghnaghat Power Limited 718 MW CCPP was shutdown.
| 07:55 |  | Chauddagram-Feni 132 kV Ckt-2 Project Work S/D from Feni 230/132kV end Due to XLPE Cable | [7 empty] | 18.0MW load
|  |  | Dresing | [7 empty] | interrup. Feni
230/132kV end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8319600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6509003 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 34.2 | 288000 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 38 | 103200 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 50 | 351074 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 53190 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 413400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 514080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 186720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 175 | 893487 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 90 | 649440 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 204480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 87 | 519840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 161430 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | RMS upstream gas valve has been kept shut by TITAS
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 401 | 10115350 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 3600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1634.2 | 29285894
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125145 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 247200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 228 | 5332992 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 89 | 672436 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 68304 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 45120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 492000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18285 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 19 | 64399 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 288000 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 560 | 10510908 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 201600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 8370909.09 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1419 | 27401298.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 216 | 4880000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 240 | 5760000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 6007000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1069064 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 93 | 436581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2496457 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 99 | 399840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 96 | 2069760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 300740 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 408982 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1144 | 23828424
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 556800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 336000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1026000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 247470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 105 | 2176420
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 49894 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 715920 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 673828 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1550400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 156 | 3312360 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 380000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 564240 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7347500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5038000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 854 | 19632142
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 844 | 18937454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 173 | 4280832 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 429840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1050 | 23141820 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2067 | 46789946
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 500 | 8027565.7 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2641000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 974 | 21697454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5222651 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1809 | 37588671.25
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 274084 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 172 | 4139618 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9046109 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 820704 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1326 | 25946892 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 290256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 519255 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2025 | 41062238
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1264581 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 43 | 186172 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27230.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 201896 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 145469 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 843840 | -
Rangpur Area Total |  |  |  |  | 950 | 145 | 2669188.4
Eastern Grid Total |  |  |  |  | 17395.105 | 5156.2 | 102324178.09
Western Grid Total |  |  |  |  | 10821.56 | 6046 | 128110043.65
National Grid Total |  |  |  |  | 28216.665 | 11202.2 | 230434221.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7561.36 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3302.2 | MW
i) Dhaka area |  |  | 4207.06 |  | MW | i) Khulna area |  |  |  | 1225 | MW
ii) Chattogram area |  |  | 1225.3 |  | MW | ii) Barishal area |  |  |  | 312 | MW
iii) Cumilla area |  |  | 883 |  | MW | iii) Rajshahi area |  |  |  | 985.2 | MW
iv) Mymensingh area |  |  | 857 |  | MW | iv) Rangpur area |  |  |  | 780 | MW
v) Sylhet area |  |  | 389 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10863.56 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 57 | 18:00 | 133 | Niamatpur | 42 | 18:00
2 | AKSML | 136.8 | 07:00 | 68 | Ishurdi | 49 | 18:00 | 134 | Noapara | 37 | 18:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 60 | 18:00 | 135 | PHP | 8 | 04:00
4 | Agargaon | 88 | 14:00 | 70 | Jamalpur | 87 | 18:30 | 136 | Pabna | 79 | 08:00
5 | Agrabad | 68 | 18:00 | 71 | Jashore | 98 | 13:00 | 137 | Palashbari | 88 | 18:00
6 | Amnura | 17 | 13:00 | 72 | Jhenaidah | 93 | 18:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 56 | 11:00 | 73 | Joydebpur | 86 | 18:00 | 139 | Patiya | 6 | 18:00
8 | BSRM | 202 | 05:00 | 74 | Joypurhat | 41 | 18:00 | 140 | Patuakhali | 43 | 21:00
9 | Bagerhat | 61 | 18:30 | 75 | Juldah | 14 | 08:00 | 141 | Payra | 20 | 18:00
10 | Bajitpur | 60 | 19:30 | 76 | KSRM | 40 | 05:00 | 142 | Postogola | 45 | 13:00
11 | Bakulia | 60 | 13:00 | 77 | Kabirpur | 199 | 15:00 | 143 | Purbachal | 27 | 12:00
12 | Banani | 46 | 12:00 | 78 | Kachua | 50 | 19:00 | 144 | Purbasadipur | 106 | 18:00
13 | Bangabhaban | 14 | 11:00 | 79 | Kallyanpur | 72 | 12:00 | 145 | Rahanpur | 21 | 18:30
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rahim | 38 | 00:00
15 | Barguna | 14 | 19:30 | 81 | Kamrangirchar | 62 | 13:00 | 147 | Rajbari | 57 | 18:00
16 | Barishal | 82 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 107 | 18:00
17 | Barishal-230 | 72 | 19:00 | 83 | Kasba | 27 | 18:00 | 149 | Rajshahi | 84 | 13:00
18 | Baroaulia | 58 | 11:00 | 84 | Kazla | 91 | 13:00 | 150 | Rajshahi-230 | 46 | 18:00
19 | Baroirhat | 43 | 13:00 | 85 | Keranigonj | 65 | 13:00 | 151 | Ramganj | 72 | 18:00
20 | Bashundhara | 145 | 12:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 26 | 00:00
21 | BashundharaCement | 12 | 13:00 | 87 | Khulna | 46 | 13:00 | 153 | Rangamati | 12 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 187 | 13:00 | 154 | Rangpur | 97 | 18:00
23 | Benapole | 38 | 18:00 | 89 | Kishoreganj | 79 | 18:00 | 155 | Ruppur | 3 | 11:00
24 | Bhaluka | 125 | 18:00 | 90 | Kodda | 277 | 18:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 35 | 20:00 | 91 | Kulaura | 30 | 18:00 | 157 | Saidpur | 86 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 50 | 18:00 | 158 | Satkhira | 85 | 18:00
27 | Bheramara(GK) | 43 | 18:00 | 93 | Kushtia | 112 | 13:00 | 159 | Satmasjid | 78 | 13:00
28 | Bhulta | 182 | 11:00 | 94 | Laksam | 20 | 18:00 | 160 | Savar | 164 | 16:00
29 | Bog-Sherpur | 54 | 18:30 | 95 | Lakshmipur | 28 | 20:00 | 161 | SevenRings | 7.32 | 13:00
30 | Bogura | 115 | 18:30 | 96 | Lalbag | 60 | 13:00 | 162 | ShahCement | 23 | 23:00
31 | Borhanuddin | 64 | 21:00 | 97 | Lalmonirhat | 44 | 18:00 | 163 | Shahjadpur | 53 | 12:00
32 | Brahmanbaria | 80 | 20:00 | 98 | MI_Cement | 8.4 | 01:00 | 164 | Shahjibazar | 74 | 21:00
33 | Cantonment | 77 | 13:00 | 99 | Madanganj | 31 | 00:00 | 165 | Shahmirpur | 32 | 16:00
34 | Chandina | 7 | 13:00 | 100 | Madaripur | 67 | 20:00 | 166 | Shariatpur | 53 | 19:30
35 | Chandpur | 50 | 18:00 | 101 | Madartek | 60 | 13:00 | 167 | Sherpur | 104 | 18:00
36 | Chandraghona | 27 | 18:00 | 102 | Madunaghat | 46 | 18:00 | 168 | Shikalbaha | 26 | 14:00
37 | Chapai | 48 | 12:00 | 103 | Magura | 45 | 18:00 | 169 | Shitalakhya | 62.4 | 12:00
38 | Charsaidpur | 34 | 00:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 35 | 15:00
39 | Chauddagram | 45 | 13:00 | 105 | Maijdee | 22 | 20:00 | 171 | Shyampur | 142 | 11:00
40 | Chhatak | 21 | 20:00 | 106 | Manikganj | 93 | 18:00 | 172 | Siddhirganj | 93 | 12:00
41 | Chowmuhani | 95 | 19:00 | 107 | Maniknagar | 48 | 13:00 | 173 | Sirajganj | 76 | 18:00
42 | Chuadanga | 68 | 19:00 | 108 | Matarbari | 36 | 18:00 | 174 | Sonargaon | 92 | 15:00
43 | Coxsbazar | 107 | 18:00 | 109 | Matuail | 60 | 13:00 | 175 | Sreemongol | 60 | 18:00
44 | Cumilla(N) | 95 | 17:00 | 110 | Metrorail_Motijheel | 26 | 13:00 | 176 | Sreepur | 97 | 18:00
45 | Cumilla(S) | 102 | 14:00 | 111 | Metrorail_Uttara | 5 | 11:00 | 177 | Srinagar | 30.1 | 20:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 87 | 15:00 | 178 | Sunamganj | 39 | 19:30
47 | Daudkandi | 106 | 19:00 | 113 | Mirpur | 108 | 18:00 | 179 | Sylhet | 39 | 18:00
48 | DhakaUniversity | 60 | 13:00 | 114 | Mirsorai | 43 | 12:00 | 180 | Sylhet-132 | 83 | 13:00
49 | Dhamrai | 102 | 18:00 | 115 | Mirzapur | 34 | 18:00 | 181 | TK | 15 | 18:00
50 | Dhanmondi | 82 | 13:00 | 116 | Mithapukur | 46 | 18:00 | 182 | Tangail | 130 | 18:00
51 | Dohazari | 64 | 17:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 27 | 18:00
52 | Faridpur | 112 | 18:00 | 118 | Mogbazar | 66.6 | 14:00 | 184 | Tasnim | 27 | 16:00
53 | Fatullah | 97 | 12:00 | 119 | Mongla | 31 | 18:00 | 185 | Thakurgaon | 79 | 18:00
54 | Fenchuganj | 19 | 18:30 | 120 | Motijheel | 26 | 13:00 | 186 | Tongi | 108 | 17:00
55 | Feni | 68 | 13:00 | 121 | Muktagacha | 28 | 18:30 | 187 | Ullahpara | 24 | 18:00
56 | GPH | 75 | 15:00 | 122 | Munshiganj | 76 | 18:00 | 188 | Ullon | 50 | 14:00
57 | Ghatail | 64 | 18:00 | 123 | Muradnagar | 25 | 20:00 | 189 | Uttara | 62 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 131 | 18:00 | 190 | UttaraNew | 13 | 13:00
59 | Ghorashal-230 | 79 | 18:30 | 125 | Naogaon | 89 | 18:00 | 191 | Zigatola | 53 | 13:00
60 | Goalpara | 27 | 13:00 | 126 | Narail | 39.5 | 18:30
61 | Gollamari | 78 | 13:00 | 127 | Narinda | 58 | 13:00
62 | Gopalganj | 74 | 18:00 | 128 | Narshingdi | 137 | 19:30
63 | Gulshan | 82 | 13:00 | 129 | Natore | 95 | 18:00
64 | Halishahar | 52.5 | 10:00 | 130 | Nawabganj | 28.4 | 21:00
65 | HaripurSBU | 150 | 13:00 | 131 | Netrakona | 99 | 17:00
66 | Hasnabad | 76 | 14:00 | 132 | New | 62 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9200.49 | 0 |  | 9200.49
1:00 | 8507.42 | 0 |  | 8507.42
2:00 | 8096.09 | 0 |  | 8096.09
3:00 | 7805.78 | 0 |  | 7805.78
4:00 | 7598.71 | 0 |  | 7598.71
5:00 | 7556.74 | 0 |  | 7556.74
6:00 | 7956.94 | 0 |  | 7956.94
7:00 | 8700.55 | 0 |  | 8700.55
8:00 | 9401.79 | 0 |  | 9401.79
9:00 | 9575.07 | 0 |  | 9575.07
10:00 | 9370.85 | 0 |  | 9370.85
11:00 | 9640.14 | 0 |  | 9640.14
12:00 | 10187.39 | 0 |  | 10187.39
13:00 | 10518.32 | 0 |  | 10518.32
14:00 | 10121.05 | 0 |  | 10121.05
15:00 | 9818.62 | 0 |  | 9818.62
16:00 | 9676.74 | 0 |  | 9676.74
17:00 | 10161.48 | 0 |  | 10161.48
18:00 | 11202.2 | 0 |  | 11202.2
19:00 | 10833.1 | 0 |  | 10833.1
19:30 | 10690.5 | 0 |  | 10690.5
20:00 | 10591 | 0 |  | 10591
21:00 | 10371.22 | 0 |  | 10371.22
22:00 | 10069.77 | 0 |  | 10069.77
23:00 | 9602.17 | 0 |  | 9602.17
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 3877 | 5323.49 | 9200.49 | DAILY GENERATION CURVE
00:30 | 3733.5 | 5120.455 | 8853.955
01:00 | 3590 | 4917.42 | 8507.42 | 04-12-2025
01:30 | 3543.5 | 4758.255 | 8301.755
02:00 | 3497 | 4599.09 | 8096.09
02:30 | 3447.5 | 4503.435 | 7950.935
03:00 | 3398 | 4407.78 | 7805.78
03:30 | 3377.5 | 4324.745 | 7702.245
04:00 | 3357 | 4241.71 | 7598.71
04:30 | 3404.5 | 4173.225 | 7577.725
05:00 | 3452 | 4104.74 | 7556.74
05:30 | 3636.5 | 4120.34 | 7756.84
06:00 | 3821 | 4135.94 | 7956.94
06:30 | 3943.465 | 4385.28 | 8328.745
07:00 | 4065.93 | 4634.62 | 8700.55
07:30 | 4094.125 | 4957.045 | 9051.17
08:00 | 4122.32 | 5279.47 | 9401.79
08:30 | 4147.76 | 5340.67 | 9488.43
09:00 | 4173.2 | 5401.87 | 9575.07
09:30 | 4133.98 | 5338.98 | 9472.96
10:00 | 4094.76 | 5276.09 | 9370.85
10:30 | 4215.315 | 5290.18 | 9505.495
11:00 | 4335.87 | 5304.27 | 9640.14
11:30 | 4493.435 | 5420.33 | 9913.765
12:00 | 4651 | 5536.39 | 10187.39
12:30 | 4739.33 | 5613.525 | 10352.855
13:00 | 4827.66 | 5690.66 | 10518.32
13:30 | 4710.52 | 5609.165 | 10319.685
14:00 | 4593.38 | 5527.67 | 10121.05
14:30 | 4574.395 | 5395.44 | 9969.835
15:00 | 4555.41 | 5263.21 | 9818.62
15:30 | 4563.51 | 5184.17 | 9747.68
16:00 | 4571.61 | 5105.13 | 9676.74
16:30 | 4675.415 | 5243.695 | 9919.11
17:00 | 4779.22 | 5382.26 | 10161.48
17:30 | 4967.71 | 5714.13 | 10681.84
18:00 | 5156.2 | 6046 | 11202.2
18:30 | 4969.65 | 6048 | 11017.65
19:00 | 4783.1 | 6050 | 10833.1
19:30 | 4593.5 | 6097 | 10690.5
20:00 | 4573 | 6018 | 10591
20:30 | 4517.75 | 5963.36 | 10481.11 |  | Executive Engineer
21:00 | 4462.5 | 5908.72 | 10371.22 |  | Network Operation Division
21:30 | 4379.5 | 5840.995 | 10220.495
22:00 | 4296.5 | 5773.27 | 10069.77
22:30 | 4252.75 | 5583.22 | 9835.97
23:00 | 4209 | 5393.17 | 9602.17

## En-Curve
QF-LDC-12
Date | 04-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2957 | 1148 | 872 | 0 | 86 | 1103.49 | 40 | 2720 | 0 | 0 | 256 | 0 | 0 | 18 | 0 | DAILY ENERGY CURVE
00:30 | 2945.5 | 1145.5 | 824 | 0 | 80 | 1019.955 | 40 | 2649.5 | 0 | 0 | 128 | 0 | 0 | 21.5 | 0 | 04-12-2025
01:00 | 2934 | 1143 | 776 | 0 | 74 | 936.42 | 40 | 2579 | 0 | 0 | 0 | 0 | 0 | 25 | 0
01:30 | 2952 | 1115.5 | 752 | 0 | 74 | 882.755 | 40 | 2459.5 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | Energy Generated | 230.4342 |  | MKWHr
02:00 | 2970 | 1088 | 728 | 0 | 74 | 829.09 | 40 | 2340 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2943.5 | 1064.5 | 705 | 0 | 75 | 828.935 | 40 | 2267.5 | 0 | 0 | 0 | 0 | 0 | 26.5 | 0 | Total Energy Requirement | 230.4342 |  | MKWHr
03:00 | 2917 | 1041 | 682 | 0 | 76 | 828.78 | 40 | 2195 | 0 | 0 | 0 | 0 | 0 | 26 | 0
03:30 | 2794 | 1013.5 | 682 | 0 | 74 | 827.745 | 40 | 2247.5 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0
04:00 | 2671 | 986 | 682 | 0 | 72 | 826.71 | 40 | 2300 | 0 | 0 | 0 | 0 | 0 | 21 | 0
04:30 | 2704.5 | 984 | 658.5 | 0 | 68 | 828.225 | 40 | 2277 | 0 | 0 | 0 | 0 | 0 | 17.5 | 0
05:00 | 2738 | 982 | 635 | 0 | 64 | 829.74 | 40 | 2254 | 0 | 0 | 0 | 0 | 0 | 14 | 0
05:30 | 2822.5 | 1030.5 | 635 | 0 | 66 | 828.34 | 40 | 2320.5 | 0 | 0 | 0 | 0 | 0 | 14 | 0
06:00 | 2907 | 1079 | 635 | 0 | 68 | 826.94 | 40 | 2387 | 0 | 0 | 0 | 0 | 0 | 14 | 0
06:30 | 2963 | 1112.5 | 634.5 | 0 | 72 | 923.47 | 40 | 2532.5 | 13.775 | 0 | 21.5 | 0 | 0 | 15.5 | 0
07:00 | 3019 | 1146 | 634 | 0 | 76 | 1020 | 40 | 2678 | 27.55 | 0 | 43 | 0 | 0 | 17 | 0
07:30 | 2969 | 1097 | 670.5 | 0 | 78 | 1071.31 | 40 | 2964 | 89.86 | 0 | 59 | 0 | 0 | 12.5 | 0
08:00 | 2919 | 1048 | 707 | 0 | 80 | 1122.62 | 40 | 3250 | 152.17 | 0 | 75 | 0 | 0 | 8 | 0
08:30 | 2924 | 1050 | 741 | 0 | 82 | 1077.61 | 40 | 3246 | 243.82 | 4.5 | 75 | 0 | 0 | 4.5 | 0
09:00 | 2929 | 1052 | 775 | 0 | 84 | 1032.6 | 40 | 3242 | 335.47 | 9 | 75 | 0 | 0 | 1 | 0
09:30 | 2898.5 | 1039 | 775 | 0 | 84 | 983.74 | 40 | 3152.5 | 412.22 | 12.5 | 75 | 0 | 0 | 0.5 | 0
10:00 | 2868 | 1026 | 775 | 0 | 84 | 934.88 | 40 | 3063 | 488.97 | 16 | 75 | 0 | 0 | 0 | 0
10:30 | 2890.5 | 1093.4 | 775.5 | 0 | 91 | 943.975 | 40 | 3039.5 | 539.62 | 16 | 76 | 0 | 0 | 0 | 0
11:00 | 2913 | 1160.8 | 776 | 0 | 98 | 953.07 | 40 | 3016 | 590.27 | 16 | 77 | 0 | 0 | 0 | 0
11:30 | 2921.5 | 1190.3 | 810 | 0 | 99 | 997.5 | 40 | 3047 | 598.465 | 16 | 194 | 0 | 0 | 0 | 0
12:00 | 2930 | 1219.8 | 844 | 0 | 100 | 1041.93 | 40 | 3078 | 606.66 | 16 | 311 | 0 | 0 | 0 | 0
12:30 | 2902 | 1176.15 | 844 | 0 | 102 | 1105.085 | 40 | 3145 | 562.62 | 18 | 458 | 0 | 0 | 0 | 0
13:00 | 2874 | 1132.5 | 844 | 0 | 104 | 1168.24 | 40 | 3212 | 518.58 | 20 | 605 | 0 | 0 | 0 | 0
13:30 | 2855.5 | 1115 | 844 | 0 | 102 | 1099.22 | 40 | 3193.5 | 467.665 | 22.5 | 580.3 | 0 | 0 | 0 | 0
14:00 | 2837 | 1097.5 | 844 | 0 | 100 | 1030.2 | 40 | 3175 | 416.75 | 25 | 555.6 | 0 | 0 | 0 | 0
14:30 | 2842 | 1099.75 | 844 | 0 | 98 | 1002.1 | 40 | 3112 | 359.235 | 20.5 | 551.75 | 0 | 0 | 0.5 | 0
15:00 | 2847 | 1102 | 844 | 0 | 96 | 974 | 40 | 3049 | 301.72 | 16 | 547.9 | 0 | 0 | 1 | 0
15:30 | 2879.5 | 1110.25 | 844 | 0 | 95 | 952.5 | 40 | 3045.5 | 210.03 | 16 | 554.4 | 0 | 0 | 0.5 | 0
16:00 | 2912 | 1118.5 | 844 | 0 | 94 | 931 | 40 | 3042 | 118.34 | 16 | 560.9 | 0 | 0 | 0 | 0
16:30 | 2906 | 1123.75 | 844 | 0 | 95 | 1016 | 40 | 3122.5 | 62.46 | 43.5 | 665.9 | 0 | 0 | 0 | 0
17:00 | 2900 | 1129 | 844 | 0 | 96 | 1101 | 40 | 3203 | 6.58 | 71 | 770.9 | 0 | 0 | 0 | 0
17:30 | 2935.5 | 1140.5 | 844 | 0 | 96 | 1213.5 | 40 | 3346.5 | 3.29 | 111.5 | 949.55 | 0 | 0 | 1.5 | 0
18:00 | 2971 | 1152 | 844 | 0 | 96 | 1326 | 40 | 3490 | 0 | 152 | 1128.2 | 0 | 0 | 3 | 0
18:30 | 2922 | 1160.75 | 844 | 0 | 96 | 1329 | 40 | 3523.5 | 0 | 123.5 | 975.4 | 0 | 0 | 3.5 | 0
19:00 | 2873 | 1169.5 | 844 | 0 | 96 | 1332 | 40 | 3557 | 0 | 95 | 822.6 | 0 | 0 | 4 | 0
19:30 | 2921 | 1194.5 | 844 | 0 | 94 | 1331 | 40 | 3580 | 0 | 65 | 617 | 0 | 0 | 4 | 0
20:00 | 2897 | 1202 | 844 | 0 | 86 | 1321 | 40 | 3600 | 0 | 65 | 533 | 0 | 0 | 3 | 0
20:30 | 2906.5 | 1214.25 | 844 | 0 | 87 | 1321.86 | 40 | 3604.5 | 0 | 41 | 419 | 0 | 0 | 3 | 0
21:00 | 2916 | 1226.5 | 844 | 0 | 88 | 1322.72 | 40 | 3609 | 0 | 17 | 305 | 0 | 0 | 3 | 0
21:30 | 2886.5 | 1204.5 | 844 | 0 | 90 | 1322.495 | 40 | 3560.5 | 0 | 8.5 | 258 | 0 | 0 | 6 | 0
22:00 | 2857 | 1182.5 | 844 | 0 | 92 | 1322.27 | 40 | 3512 | 0 | 0 | 211 | 0 | 0 | 9 | 0
22:30 | 2862 | 1192.25 | 844 | 0 | 90 | 1264.22 | 40 | 3368 | 0 | 0 | 167 | 0 | 0 | 8.5 | 0
23:00 | 2867 | 1202 | 844 | 0 | 88 | 1206.17 | 40 | 3224 | 0 | 0 | 123 | 0 | 0 | 8 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 04:00 | 384 | 12:00 | Meghnaghat | 400 | 03:00 | 384 | 12:00
Ashuganj | 409 | 5:00 | 395 | 12:00 | Payra | 416 | 04:00 | 410 | 13:00
Bhulta | 405 | 06:00 | 390 | 12:00 | Rahanpur | 420 | 04:00 | 407 | 18:00
Bibiana | 401 | 04:00 | 391 | 12:00 | Rampal | 413 | 06:00 | 399 | 18:00
BIPTC | 407 | 02:00 | 393 | 12:00
Bogura | 415 | 04:00 | 397 | 18:00
Gopalganj | 409 | 04:00 | 396 | 12:00
Kaliakoir | 398 | 04:00 | 381 | 12:00
Korerhat | 403 | 06:00 | 393 | 11:00
Madunaghat | 398 | 08:00 | 391 | 02:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 04:00 | 230 | 02:00 | Kachua | 239 | 03:00 | 228 | 12:00
AKSML | 238 | 03:00 | 230 | 11:00 | Kaliakoir | 239 | 04:00 | 227 | 11:00
Aminbazar | 240 | 04:00 | 229 | 12:00 | Keranigonj | 239 | 04:00 | 227 | 12:00
Ashuganj | 240 | 06:00 | 234 | 21:00 | Khulna(S) | 241 | 05:00 | 230 | 18:00
Ashuganj-400 | 240 | 06:00 | 234 | 21:00 | Korerhat | 238 | 06:00 | 232 | 11:00
Baghabari | 240 | 03:00 | 231 | 18:00 | Madunaghat | 236 | 05:00 | 136 | 04:00
Barapukuria | 229 | 04:00 | 214 | 09:00 | Madunaghat-400 | 238 | 08:00 | 233 | 11:00
Barapukuria-230 | 229 | 04:00 | 214 | 09:00 | Maniknagar | 235 | 03:00 | 222 | 11:00
Barishal | 243 | 03:00 | 236 | 19:30 | Meghnaghat | 242 | 05:00 | 230 | 12:00
Bheramara | 239 | 05:00 | 228 | 18:00 | Meghnaghat-400 | 237 | 04:00 | 225 | 12:00
Bhulta | 236 | 04:00 | 222 | 12:00 | Mirsorai | 237 | 04:00 | 228 | 11:00
Bibiana | 237 | 05:00 | 229 | 11:00 | Rajshahi | 239 | 06:00 | 223 | 16:00
BIPTC | 241 | 06:00 | 229 | 18:00 | Rampal | 239 | 06:00 | 228 | 18:00
Bogura | 241 | 05:00 | 231 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 240 | 04:00 | 230 | 18:00 | Rampura | 236 | 05:00 | 221 | 12:00
Borhanuddin | 245 | 04:00 | 240 | 13:00 | Shikalbaha | 235 | 05:00 | 230 | 01:00
BSRM | 238 | 04:00 | 227 | 12:00 | Shyampur | 237 | 04:00 | 226 | 12:00
Cumilla(N) | 236 | 04:00 | 227 | 12:00 | Siddhirganj | 234 | 01:00 | 223 | 10:00
Faridpur | 242 | 04:00 | 234 | 12:00 | Sirajgonj | 245 | 05:00 | 238 | 12:00
Fenchuganj | 238 | 06:00 | 232 | 12:00 | Sreepur | 236 | 05:00 | 226 | 12:00
Feni | 237 | 04:00 | 228 | 12:00 | Tongi | 235 | 04:00 | 224 | 12:00
Ghorashal | 0 | 00:00 | N/A | N/A
Ghorashal-230 | 235 | 05:00 | 219 | 18:00
Gopalganj | 243 | 04:00 | 235 | 11:00
GPH | 238 | 04:00 | 230 | 11:00
Haripur | 236 | 04:00 | 223 | 12:00
Hasnabad | 239 | 05:00 | 227 | 11:00
Hathazari | 235 | 17:00 | 228 | 15:00
Ishurdi | 242 | 05:00 | 231 | 18:00
Jhenaidah | 240 | 04:00 | 228 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 127 | 12:00 | Lalbag | 138 | 04:00 | 132 | 10:00
Agargaon | 138 | 02:00 | 131 | 12:00 | Lalmonirhat | 132 | 05:00 | 125 | 09:00
Agrabad | 136 | 00:00 | 133 | 11:00 | Madanganj | 135 | 00:00 | 131 | 13:00
AKS | 135 | 03:00 | 131 | 12:00 | Madaripur | 140 | 04:00 | 136 | 11:00
Aminbazar | 140 | 01:00 | 134 | 11:00 | Madartek | 136 | 04:00 | 126 | 12:00
Amnura | 139 | 03:00 | 132 | 12:00 | Madunaghat | 138 | 04:00 | 135 | 11:00
Ashuganj | 143 | 06:00 | 140 | 11:00 | Magura | 142 | 05:00 | 133 | 12:00
Bagerhat | 138 | 04:00 | 129 | 18:00 | Mahasthangarh | 137 | 06:00 | 130 | 08:00
Bajitpur | 139 | 05:00 | 133 | 12:00 | Maijdee | 134 | 04:00 | 129 | 12:00
Bakulia | 138 | 05:00 | 134 | 10:00 | Manikganj | 134 | 04:00 | 122 | 15:00
Banani | 137 | 04:00 | 126 | 12:00 | Maniknagar | 141 | 06:00 | 131 | 11:00
Bangabhaban | 140 | 04:00 | 130 | 12:00 | Matarbari | 130 | 02:00 | 120 | 11:00
Barapukuria | 140 | 04:00 | 130 | 09:00 | Matuail | 138 | 04:00 | 130.5 | 13:00
Barguna | 136 | 05:00 | 134 | 12:00 | Metrorail_Motijheel | 141 | 06:00 | 131 | 11:00
Barishal | 140 | 03:00 | 135 | 11:00 | Metrorail_Uttara | 135 | 04:00 | 125 | 12:00
Barishal-230 | 141 | 04:00 | 135 | 19:30 | Millgate | 135 | 02:00 | 125 | 12:00
Baroaulia | 138 | 07:00 | 133 | 12:00 | Mirpur | 140 | 02:00 | 133 | 11:00
Baroirhat | 136 | 05:00 | 130 | 12:00 | Mirzapur | 134 | 02:00 | 127 | 08:00
Bashundhara | 137 | 04:00 | 127 | 11:00 | Mithapukur | 135 | 03:00 | 127 | 09:00
BashundharaCement | 135 | 00:00 | 131 | 13:00 | MI_Cement | 138 | 05:00 | 127 | 12:00
Beanibazar | 134 | 00:00 | 132 | 11:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 139 | 05:00 | 128 | 13:00 | Mogbazar | 140 | 05:00 | 129 | 12:00
Bhaluka | 135 | 05:00 | 129 | 18:00 | Mongla | 137 | 06:00 | 130 | 12:00
Bhandaria | 140 | 06:00 | 134 | 12:00 | Motijheel | 140 | 03:00 | 130 | 12:00
Bhangura | 138 | 04:00 | 134 | 11:00 | Muktagacha | 132 | 00:00 | 122 | 18:00
Bheramara | 141 | 03:00 | 136 | 18:00 | Munshiganj | 136 | 06:00 | 128 | 11:00
Bheramara(GK) | 141 | 02:00 | 137 | 08:00 | Muradnagar | 138 | 04:00 | 131 | 11:00
Bhulta | 133 | 03:00 | 125 | 12:00 | Mymensingh | 133 | 06:00 | 120 | 18:00
Bog-Sherpur | 138 | 04:00 | 132 | 08:00 | Naogaon | 135 | 05:00 | 129 | 08:00
Bogura | 138 | 05:00 | 132 | 08:00 | Narail | 142 | 04:00 | 133 | 13:00
Bogura-230 | 138 | 04:00 | 132 | 08:00 | Narinda | 141 | 06:00 | 131 | 11:00
Brahmanbaria | 138 | 05:00 | 134 | 12:00 | Narshingdi | 139 | 05:00 | 126 | 10:00
Cantonment | 138 | 04:00 | 131 | 11:00 | Natore | 136 | 00:00 | 132 | 11:00
Chandina | 139 | 04:00 | 132 | 12:00 | Nawabganj | 138 | 04:00 | 130 | 11:00
Chandpur | 139 | 18:00 | 134 | 12:00 | Netrakona | 132 | 06:00 | 126 | 12:00
Chandraghona | 138 | 02:00 | 135 | 11:00 | New | 136 | 04:00 | 125 | 13:00
Chapai | 139 | 06:00 | 135 | 13:00 | Niamatpur | 140 | 03:00 | 135 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 138 | 05:00 | 130 | 11:00 | Noapara | 138 | 02:00 | 132 | 12:00
Chauddagram | 137 | 03:00 | 131 | 11:00 | Pabna | 141 | 05:00 | 134 | 18:00
Chhatak | 132 | 00:00 | 129 | 11:00 | Palashbari | 135 | 05:00 | 127 | 08:00
Chowmuhani | 135 | 06:00 | 130 | 11:00 | Panchagarh | 139 | 04:00 | 128 | 09:00
Chuadanga | 142 | 04:00 | 132 | 13:00 | Patiya | 138 | 04:00 | 133 | 11:00
Coxsbazar | 130 | 05:00 | 116 | 11:00 | Patuakhali | 136 | 04:00 | 133 | 18:00
Cumilla(N) | 139 | 04:00 | 132 | 12:00 | Payra | 137 | 03:00 | 134 | 18:00
Cumilla(S) | 139 | 04:00 | 126 | 00:00 | PHP | 136 | 04:00 | 130 | 12:00
Daganbhuiyan | 136 | 04:00 | 130 | 12:00 | Postogola | 138 | 05:00 | 129 | 11:00
Daudkandi | 135 | 03:00 | 128 | 12:00 | Purbachal | 138 | 04:00 | 127 | 11:00
DhakaUniversity | 137 | 05:00 | 129 | 11:00 | Purbasadipur | 134 | 04:00 | 124 | 08:00
Dhamrai | 136 | 04:00 | 131 | 11:00 | Rahanpur | 141 | 04:00 | 136 | 18:00
Dhanmondi | 139.5 | 06:00 | 131 | 12:00 | Rahanpur-400 | 141 | 03:00 | 137 | 08:00
Dohazari | 135 | 03:00 | 130 | 11:00 | Rahim | 138 | 06:00 | 130 | 12:00
Faridpur | 140 | 04:00 | 135 | 12:00 | Rajbari | 140 | 04:00 | 135 | 12:00
Fatullah | 142 | 06:00 | 128 | 12:00 | Rajendrapur | 138 | 05:00 | 129 | 12:00
Fenchuganj | 140 | 06:00 | 137 | 09:00 | Rajshahi | 138 | 02:00 | 132 | 12:00
Feni | 134 | 03:00 | 129 | 15:00 | Rajshahi-230 | 138 | 05:00 | 132 | 13:00
Feni-230 | 136 | 04:00 | 130 | 12:00 | Ramganj | 135 | 02:00 | 130 | 13:00
Ghatail | 130 | 00:00 | 119 | 08:00 | Rampur | 137 | 04:00 | 133 | 11:00
Ghorashal | 137 | 00:00 | 129 | 12:00 | Rampura | 137 | 05:00 | 127 | 12:00
Goalpara | 138 | 00:00 | 133 | 12:00 | Rangamati | 137 | 00:00 | 134 | 11:00
Gollamari | 140 | 05:00 | 133 | 12:00 | Rangpur | 134 | 05:00 | 127 | 08:00
Gopalganj | 140 | 04:00 | 133 | 12:00 | Ruppur | 142 | 05:00 | 136 | 18:00
Gopalganj-400 | 141 | 04:00 | 136 | 12:00 | Saidpur | 137 | 06:00 | 126 | 09:00
Gulshan | 137 | 05:00 | 127 | 12:00 | Satkhira | 138 | 04:00 | 129 | 18:00
Halishahar | 138 | 04:00 | 133 | 11:00 | Satmasjid | 138 | 04:00 | 130 | 12:00
Haripur | 138 | 04:00 | 131 | 12:00 | Savar | 139 | 04:00 | 132 | 11:00
HaripurSBU | 138 | 04:00 | 132 | 11:00 | SevenRings | 139 | 04:00 | 130 | 13:00
Hasnabad | 138 | 05:00 | 130 | 11:00 | ShahCement | 138 | 05:00 | 130 | 11:00
Hathazari | 139 | 06:00 | 134 | 13:00 | Shahjadpur | 147 | 11:00 | 136 | 09:00
Ishurdi | 143 | 04:00 | 137 | 18:00 | Shahjibazar | 140 | 06:00 | 135 | 10:00
Jaldhaka | 130 | 19:30 | 123 | 09:00 | Shahmirpur | 138 | 04:00 | 134 | 11:00
Jamalpur | 132 | 00:00 | 120 | 01:00 | Shariatpur | 140 | 05:00 | 135 | 12:00
Jashore | 140 | 04:00 | 130 | 13:00 | Sherpur | 130 | 10:00 | 116 | 01:00
Jhenaidah | 143 | 06:00 | 124 | 13:00 | Shikalbaha | 127 | 00:00 | 123 | 11:00
Jhenaidah-230 | 144 | 05:00 | 135 | 13:00 | Shikalbaha-230 | 139 | 05:00 | 135 | 11:00
Joydebpur | 140 | 23:00 | 133 | 14:00 | Shitalakhya | 138 | 05:00 | 127 | 12:00
Joypurhat | 135 | 04:00 | 127 | 12:00 | Sholosohor | 138 | 04:00 | 134 | 11:00
Juldah | 137 | 18:30 | 134 | 09:00 | Shyampur | 140 | 02:00 | 135 | 11:00
Kabirpur | 137 | 18:30 | 124 | 12:00 | Shyampur-230 | 141 | 04:00 | 133 | 12:00
Kachua | 140 | 03:00 | 135 | 12:00 | Siddhirganj | 138 | 03:00 | 130 | 12:00
Kaliakoir | 139 | 03:00 | 132 | 11:00 | Sirajganj | 137 | 04:00 | 132 | 08:00
Kallyanpur | 139 | 01:00 | 134 | 10:00 | Sonargaon | 137 | 04:00 | 130 | 12:00
Kalurghat | 138 | 02:00 | 134 | 11:00 | Sreemongol | 138 | 04:00 | 135 | 12:00
Kamrangirchar | 138 | 04:00 | 129 | 12:00 | Sreepur | 138 | 05:00 | 132 | 12:00
Kaptai | 140 | 7:00 | 138 | 10:00 | Srinagar | 138 | 05:00 | 130 | 12:00
Kasba | 138 | 04:00 | 130 | 11:00 | SSM | 140 | 00:00 | 140 | 00:00
Kazla | 140 | 05:00 | 130 | 13:00 | Sunamganj | 133 | 05:00 | 129 | 11:00
Keranigonj | 138 | 04:00 | 130 | 12:00 | Sylhet | 135 | 05:00 | 132 | 12:00
Khagrachori | 138 | 05:00 | 133 | 12:00 | Sylhet-132 | 134 | 04:00 | 131 | 12:00
Khulna | 139 | 06:00 | 131 | 18:00 | Tangail | 131 | 00:00 | 122 | 08:00
Khulna(S) | 141 | 05:00 | 133 | 18:00 | Taraganj | 135 | 04:00 | 124 | 12:00
Khulshi | 136 | 04:00 | 132 | 10:00 | Tasnim | 137 | 04:00 | 130 | 12:00
Kishoreganj | 135 | 04:00 | 131 | 12:00 | Thakurgaon | 137 | 04:00 | 124 | 09:00
Kodda | 135 | 18:00 | 125 | 08:00 | TK | 138 | 03:00 | 134 | 11:00
KSRM | 138 | 03:00 | 133 | 13:00 | Tongi | 137 | 04:00 | 128 | 12:00
Kulaura | 139 | 01:00 | 136 | 12:00 | Ullahpara | 139 | 04:00 | 133 | 18:00
Kurigram | 130 | 03:00 | 122 | 08:00 | Ullon | 137 | 05:00 | 127 | 12:00
Kushtia | 138 | 05:00 | 129 | 18:00 | Uttara | 135 | 04:00 | 125 | 12:00
Laksam | 139 | 02:00 | 134 | 12:00 | UttaraNew | 135 | 04:00 | 125 | 12:00
Lakshmipur | 134 | 04:00 | 130 | 11:00 | Zigatola | 138 | 04:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division