## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-12-2025 | during | 07-12-2025 | during | 07-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 363 | 312 | 412 | 412 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 50.7 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 45 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26.5 | 21 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 16 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 42 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 104 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 410 | 408 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1156.5 | 1634.7 | 5765.15 | 5734.15 | 2584.81 | 2562.81
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 227 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 100 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 48 | 40 | 64 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 26 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.36 | 0 | 3.35 | 0 | 3.35 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 38 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 530 | 567 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 16 | 1 | 8 | 1 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 215 | 355 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1024.36 | 1494 | 2583.07 | 2579.72 | 2087.85 | 2100.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 205 | 190 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 280 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 235 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 70 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 106 | 109 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 84 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 98 | 116 | 160 | 160 | 108 | 108 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 18 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1254 | 1153 | 2432.21 | 2372.21 | 1954.21 | 1903.21
2584.81
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-12-2025 | during | 07-12-2025 | during | 07-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 82 | 72 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 19 | 60 | 60 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 59 | 20 | 20 | 60 | 60 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.4 | 0 | 47.8 | 0 | 47.8 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 145.4 | 162 | 363.8 | 314 | 316.3 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | GT#4 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 158 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 15 | 15 | 15 | 15 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 207 | 207 | 195 | 195 | 195 | 195 | GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 865 | 856 | 878 | 878 | 844 | 844
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 704 | 771 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70.39 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 395 | 597 | 0 | 0 | 1234 | 1234 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1419.39 | 1618 | 2354 | 2272 | 2833.1 | 2751.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 255 | 506 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 600 | 1085 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Standby
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1190.54 | 1926 | 1993.32 | 1993.32 | 1553.32 | 1553.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 52.1 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 188 | 182 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 407 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 95 | 95 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 4.9 | 0 | 4.9 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 846.52 | 1452 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.93 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1646.55 | 2041 | 3076.77 | 2910.87 | 2658.39 | 2492.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 48 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 147 | 0 | 174.21 | 0 | 174.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 179.1 | 118 | 451.41 | 262 | 492.41 | 283
System Total |  |  |  |  | 28823.2 | 28216.665 | 8880.84 | 11002.7 | 19897.73 | 19316.27 | 15324.39 | 14756.93
Forecast Scenario (07-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9270 |  | 0 |  | 9270
|  |  |  | 1:00 | 8670 |  | 0 |  | 8670
|  |  |  | 2:00 | 8230 |  | 0 |  | 8230
|  |  |  | 3:00 | 7970 |  | 0 |  | 7970
|  |  |  | 4:00 | 7750 |  | 0 |  | 7750
|  |  |  | 5:00 | 7640 |  | 0 |  | 7640
|  |  |  | 6:00 | 8070 |  | 0 |  | 8070
|  |  |  | 7:00 | 8940 |  | 0 |  | 8940
|  |  |  | 8:00 | 9700 |  | 0 |  | 9700
|  |  |  | 9:00 | 9620 |  | 0 |  | 9620
|  |  |  | 10:00 | 9490 |  | 0 |  | 9490
|  |  |  | 11:00 | 9810 |  | 0 |  | 9810
|  |  |  | 12:00 | 10320 |  | 0 |  | 10320
|  |  |  | 13:00 | 10710 |  | 0 |  | 10710
|  |  |  | 14:00 | 10210 |  | 0 |  | 10210
|  |  |  | 15:00 | 9980 |  | 0 |  | 9980
|  |  |  | 16:00 | 9890 |  | 0 |  | 9890
|  |  |  | 17:00 | 9960 |  | 0 |  | 9960
|  |  |  | 18:00 | 11400 |  | 0 |  | 11400
|  |  |  | 18:30 | 11200 |  | 0 |  | 11200
|  |  |  | 19:00 | 11120 |  | 0 |  | 11120
|  |  |  | 19:30 | 11000 |  | 0 |  | 11000
|  |  |  | 20:00 | 10780 |  | 0 |  | 10780
|  |  |  | 21:00 | 10480 |  | 0 |  | 10480
|  |  |  | 22:00 | 10110 |  | 0 |  | 10110
|  |  |  | 23:00 | 9750 |  | 0 |  | 9750
Probable Maximum Temperature: |  |  | 24.90°C
Probable Maximum Demand at Day Peak: |  |  | 10320.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 229.87 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:46 hrs on 07-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-12-2025 | [28 empty] | Date: | 06-12-2025 | [28 empty] | Date: | 06-12-2025 | [28 empty] | Date: | 06-12-2025 | [28 empty] | Date: | 06-12-2025 | [17 empty] | Date: | 06-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 155 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 280 | 0 | 270 | 51 | 0 | 194 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 25 | 0 | 84 | 30 | 0 | 16 | 158 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 4135 | 752 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 0 | 0 | 0 | 830.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 257 | 700 | 0 | 4267.97 | 8402.97 | 99.39
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 475 | 0 | 0 | 0 | 280 | 0 | 270 | 0 | 0 | 204 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 20 | 0 | 0 | 0 | 0 | 41 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 3743 | 845 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431 | 0 | 0 | 0 | 832.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 257 | 570 | 0 | 4116.72 | 7859.72 | 99.39
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 436 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 0 | 211 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 159 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3536 | 751 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 829.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 257 | 560 | 0 | 3909.71 | 7445.71 | 99.39
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 0 | 201 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 320 | 0 | 207 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 159 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 3465 | 626 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 830.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 257 | 560 | 0 | 3791.99 | 7256.99 | 99.39
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 159 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 3388 | 468 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 834.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 257 | 560 | 0 | 3608.54 | 6996.54 | 99.38
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 230 | 0 | 220 | 0 | 0 | 204 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 159 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 3380 | 468 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 831.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 258 | 560 | 0 | 3592.96 | 6972.96 | 99.38
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 155 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 230 | 0 | 220 | 10 | 0 | 196 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 16 | 159 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 3786 | 469 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 828.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 256 | 563 | 0 | 3682.62 | 7468.62 | 99.38
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 335 | 0 | 0 | 2 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.12 | 40 | 0 | 39 | 155 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 520 | 3 | 0 | 0 | 300 | 0 | 270 | 51 | 0 | 215 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 78 | 0 | 6 | 0 | 315 | 0 | 208 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 16 | 159 | 0 | 2 | 19 | 113 | 0 | 1.67 | 0 | 4126.79 | 468 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 426 | 0 | 0 | 0 | 932.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.18 | 4 | 0 | 0 | 2.19 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.01 | 0 | 0 | 115 | 220 | 0 | 259 | 606 | 0 | 3954.47 | 8081.26 | 99.38
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 335 | 0 | 0 | 9 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0.44 | 40 | 0 | 8 | 155 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 393 | 0 | 330 | 51 | 0 | 203 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 82 | 0 | 28 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 2 | 16 | 0 | 79 | 30 | 0 | 16 | 160 | 0 | 24 | 19 | 113 | 1 | 13.01 | 0 | 4375.95 | 657 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 472 | 0 | 0 | 0 | 936.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.18 | 25 | 0 | 0 | 12.15 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 7 | 0 | 0 | 0 | 0 | 1 | 43 | 0.12 | 0 | 0 | 115 | 220 | 0 | 258 | 750 | 0 | 4449.58 | 8825.53 | 99.38
09:00 | 0 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 280 | 0 | 0 | 16 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1.09 | 40 | 0 | 2 | 170 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 515 | 0 | 0 | 0 | 320 | 0 | 300 | 51 | 0 | 202 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 72 | 0 | 48 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 3.72 | 16 | 0 | 51 | 20 | 0 | 16 | 160 | 0 | 32 | 19 | 94 | 1 | 27.99 | 0 | 4068.3 | 656 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 418 | 0 | 0 | 0 | 827.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.29 | 53 | 0 | 0 | 30.88 | 174 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 53 | 0 | 14 | 0 | 0 | 0 | 0 | 2.9 | 89 | 0.07 | 0 | 0 | 100 | 180 | 0 | 254 | 608 | 0 | 4154.13 | 8222.43 | 99.38
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 240 | 0 | 0 | 23 | 0 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.89 | 40 | 0 | 2 | 170 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 455 | 0 | 0 | 0 | 250 | 0 | 270 | 43 | 0 | 204 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 80 | 0 | 61 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 9 | 16 | 0 | 22 | 20 | 0 | 16 | 160 | 0 | 24 | 8 | 93 | 2 | 37.26 | 0 | 3783.65 | 657 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 388 | 0 | 0 | 0 | 838.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.73 | 74 | 0 | 0 | 41.96 | 169 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 53 | 0 | 20 | 0 | 0 | 0 | 0 | 4.1 | 125 | 0.1 | 0 | 0 | 100 | 180 | 0 | 257 | 571 | 0 | 4150.46 | 7934.11 | 99.38
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 270 | 0 | 0 | 27 | 0 | 26 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.28 | 40 | 0 | 4 | 170 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 458 | 0 | 0 | 0 | 250 | 0 | 330 | 43 | 0 | 211 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 82 | 0 | 59 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 22 | 20 | 0 | 16 | 160 | 0 | 8 | 8 | 81 | 2 | 43.2 | 0 | 3871.48 | 657 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 392 | 0 | 0 | 0 | 830.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.5 | 87 | 0 | 0 | 49.61 | 174 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 50 | 0 | 26 | 0 | 0 | 0 | 0 | 4.8 | 146 | 0.23 | 0 | 0 | 100 | 180 | 0 | 255 | 595 | 0 | 4286.06 | 8157.54 | 99.38
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 300 | 0 | 0 | 26 | 0 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3.36 | 40 | 0 | 6 | 215 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 530 | 0 | 0 | 0 | 393 | 0 | 330 | 43 | 0 | 205 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 98 | 0 | 68 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 8 | 8 | 82 | 2 | 45.4 | 0 | 4445.26 | 704 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.39 | 395 | 0 | 0 | 0 | 846.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.1 | 93 | 0 | 0 | 52.93 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 5.1 | 147 | 0.54 | 0 | 0 | 115 | 220 | 0 | 255 | 600 | 0 | 4435.58 | 8880.84 | 99.38
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 300 | 0 | 0 | 22 | 0 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 40 | 0 | 15 | 250 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 393 | 0 | 330 | 51 | 0 | 200 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 94 | 0 | 63 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 10 | 16 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 24 | 19 | 74 | 2 | 43.13 | 0 | 4517.75 | 750 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.47 | 451 | 0 | 0 | 0 | 924.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.81 | 86 | 0 | 0 | 43.02 | 199 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 4.4 | 137 | 0.44 | 0 | 0 | 115 | 220 | 0 | 254 | 702 | 0 | 4691.27 | 9209.02 | 99.37
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 250 | 0 | 0 | 20 | 0 | 22.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.55 | 40 | 0 | 11 | 250 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 360 | 0 | 330 | 51 | 0 | 212 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 102 | 0 | 55 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 9 | 16 | 0 | 80 | 30 | 0 | 16 | 159 | 0 | 45 | 19 | 73 | 2 | 33.13 | 0 | 4349.18 | 844 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 505 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.78 | 70 | 0 | 0 | 38.3 | 186 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 2.46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 4.1 | 70 | 0.35 | 0 | 0 | 115 | 220 | 0 | 254 | 750 | 0 | 4642.99 | 8992.17 | 99.37
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 13 | 0 | 26 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 40 | 0 | 3 | 250 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 245 | 0 | 330 | 51 | 0 | 212 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 106 | 0 | 35 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 4.84 | 16 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 45 | 19 | 73 | 1 | 21.51 | 0 | 4303.09 | 725 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.04 | 525 | 0 | 0 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.72 | 45 | 0 | 0 | 22.84 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.15 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 2.5 | 74 | 0.25 | 0 | 0 | 115 | 220 | 0 | 254 | 750 | 0 | 4499.5 | 8802.59 | 99.37
16:00 | 0 | 17 | 6 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 26 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0.86 | 40 | 0 | 7 | 355 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 240 | 0 | 330 | 51 | 0 | 206 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 102 | 0 | 13 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 1.89 | 16 | 0 | 81 | 30 | 0 | 16 | 160 | 0 | 59 | 19 | 73 | 0 | 8.62 | 0 | 4438.37 | 631 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 524 | 0 | 0 | 0 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.71 | 20 | 0 | 0 | 7.96 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.58 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.1 | 25 | 0.11 | 0 | 0 | 115 | 220 | 0 | 301 | 782 | 0 | 4430.46 | 8868.83 | 99.37
17:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 3 | 0 | 48 | 48 | 0 | 4 | 40 | 0 | 0 | 0 | 414 | 0 | 13 | 280 | 0 | 0 | 1 | 17 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 25 | 0.02 | 40 | 1 | 9 | 355 | 0 | 0 | 2 | 0 | 51 | 225 | 0 | 0 | 0 | 580 | 0 | 25 | 0 | 235 | 0 | 330 | 51 | 0 | 207 | 0 | 0 | 106 | 1 | 0 | 14 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 0 | 16 | 159 | 0 | 59 | 19 | 73 | 0 | 0.22 | 2 | 4721.24 | 631 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.05 | 529 | 0 | 0 | 0 | 1139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 1 | 0 | 0 | 0.52 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.05 | 0 | 0 | 14 | 0 | 4 | 0 | 0 | 0 | 0.1 | 0 | 0.01 | 0 | 0 | 115 | 220 | 0 | 450 | 931 | 0 | 4887.16 | 9608.4 | 99.37
18:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 42 | 17 | 13 | 100 | 195 | 0 | 26 | 102 | 0 | 0 | 0 | 420 | 0 | 17 | 280 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 0 | 13 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 50 | 0 | 40 | 26 | 20 | 355 | 0 | 0 | 27 | 0 | 88 | 226 | 0 | 0 | 0 | 590 | 0 | 100 | 0 | 235 | 0 | 280 | 51 | 0 | 221 | 0 | 0 | 108 | 73 | 0 | 14 | 0 | 128 | 0 | 0 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 0 | 13 | 0 | 81 | 30 | 0 | 16 | 158 | 0 | 59 | 19 | 73 | 0 | 0 | 12 | 5444 | 678 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 1045 | 0 | 5449 | 10893 | 99.36
19:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 50.7 | 17 | 42 | 45 | 195 | 0 | 35 | 104 | 0 | 0 | 0 | 408 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 25 | 50 | 0 | 40 | 38 | 26 | 355 | 0 | 0 | 33 | 0 | 100 | 227 | 0 | 0 | 0 | 567 | 0 | 70 | 0 | 235 | 0 | 280 | 51 | 0 | 190 | 0 | 0 | 109 | 84 | 0 | 18 | 0 | 116 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 16 | 158 | 0 | 59 | 19 | 72 | 0 | 0 | 12 | 5299.7 | 771 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 0 | 0 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 70 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 506 | 1085 | 0 | 5703 | 11002.7 | 99.36
19:30 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 39 | 17 | 46 | 16 | 95 | 0 | 35 | 53 | 0 | 0 | 0 | 402 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 15 | 25 | 355 | 0 | 0 | 33.3 | 0 | 92 | 227 | 0 | 0 | 0 | 580 | 0 | 10 | 0 | 245 | 0 | 280 | 51 | 0 | 201 | 0 | 0 | 109 | 81 | 0 | 18 | 0 | 118 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 16 | 158 | 0 | 59 | 19 | 74 | 0 | 0 | 12 | 4986.3 | 771 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 0 | 0 | 1440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 506 | 1080 | 0 | 5708 | 10694.3
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 36.7 | 17 | 53 | 0 | 95 | 0 | 35 | 17 | 0 | 0 | 0 | 403 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 28 | 355 | 0 | 0 | 33 | 0 | 51 | 227 | 0 | 0 | 0 | 580 | 0 | 10 | 0 | 250 | 0 | 280 | 51 | 0 | 198 | 0 | 0 | 109 | 51 | 0 | 18 | 0 | 100 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 16 | 159 | 0 | 59 | 19 | 72 | 0 | 0 | 12 | 4781.7 | 771 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 506 | 1085 | 0 | 5730 | 10511.7 | 99.36
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 32.5 | 17 | 60 | 0 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 31 | 355 | 0 | 0 | 0 | 0 | 50 | 227 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 290 | 0 | 280 | 51 | 0 | 194 | 0 | 0 | 109 | 48 | 0 | 18 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 16 | 159 | 0 | 59 | 19 | 72 | 0 | 0 | 12 | 4664.5 | 777 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599 | 0 | 0 | 0 | 1455.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 1085 | 0 | 5649.46 | 10313.96 | 99.36
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 15.8 | 17 | 60 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 33 | 248 | 0 | 0 | 0 | 0 | 17 | 232 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 300 | 0 | 280 | 51 | 0 | 197 | 0 | 0 | 110 | 17 | 0 | 18 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 16 | 158 | 0 | 59 | 19 | 74 | 0 | 0 | 0 | 4430.8 | 783 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 0 | 0 | 0 | 1314.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 503 | 1085 | 0 | 5494.98 | 9925.78 | 99.36
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 230 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 207 | 0 | 0 | 110 | 0 | 0 | 18 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 16 | 158 | 0 | 25 | 8 | 72 | 0 | 0 | 0 | 4226 | 741 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 1222.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 355 | 1020 | 0 | 5100.68 | 9326.68 | 99.36
Total KWH | 0 | 385920 | 65760 | 0 | 0 | 0 | 0 | 0 | 8449200 | 0 | 0 | 177480 | 293400 | 255744 | 229920 | 564295 | 0 | 168871 | 267840 | 0 | 0 | 0 | 9221761 | 0 | 67087 | 6750921 | 0 | 0 | 164104 | 30000 | 426600 | 471600 | 0 | 0 | 33873 | 0 | 0 | 0 | 213600 | 0 | 0 | 0 | 33600 | 231360 | 18684 | 976000 | 97000 | 427200 | 5490909.09 | 0 | 0 | 104160 | 0 | 408145 | 5107918 | 0 | 0 | 0 | 12545453 | 2295 | 331200 | 0 | 6786500 | 0 | 6902000 | 925392 | 0 | 4974000 | 0 | 0 | 2199077 | 321120 | 0 | 311660 | 0 | 2220680 | 0 | 427173 | 0 | 7602000 | 0 | 5025000 | 0 | 669000 | 0 | 62127 | 304752 | 0 | 1417920 | 601248 | 0 | 404000 | 3723370 | 0 | 721200 | 276000 | 2057280 | 11200 | 273910 | 55200 | 102283709.09 | 16462545 | 6099840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455040 | 11789090 | 0 | 0 | 0 | 23775272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308280 | 570350 | 0 | 0 | 304512 | 4455727 | 0 | 0 | 0 | 0 | 0 | 9745309 | 0 | 4350 | 0 | 632290 | 284263 | 156006 | 208492 | 0 | 0 | 0 | 30113.04 | 895680 | 2206 | 0 | 0 | 2659000 | 5320891 | 0 | 7750466 | 19198545.45 | 0 | 111108267.49 | 213391976.58

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 8880.84 | MW | 12:00 Hr. | Energy Generated |  |  | 213.392 |  | MKWHr.
| Day Peak Demand |  |  | 8880.84 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11002.7 | MW | 19:00 Hr. | Energy Demand |  |  | 213.392 |  | MKWHr.
| Evening Peak Demand |  |  | 11002.7 | MW | 19:00 Hr. | Maximum Temperature |  |  | 26.5 |  | °C
| Minimum Generation of the Day |  |  | 6972.96 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 756.07 |  | MMCFD
| Maximum Generation of the Day |  |  | 11002.7 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.348 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.3201 | 0 | 2.5063 | 0 | 0 | 0.1641 | 0 | 0 | 27.9905 | Gas | 103.0392 | Gas | 360063252.24
| Chattogram Zone |  |  | 5.5351 | 18.0364 | 0.90814 | 0 | 0.976 | 0.020979 | 0 | 0.2136 | 25.6902 | Coal | 57.4068 | Coal | 365839899.0708
| Cumilla Zone |  |  | 22.0986 | 0 | 0.65232 | 0 | 0 | 0.42717 | 2.2207 | 0 | 25.3988 | HFO | 5.6119 | HFO | 96093490.1
| Mymensingh Zone |  |  | 2.0573 | 0 | 1.0524 | 0 | 0 | 0.28511 | 0 | 0 | 3.3948 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.7473 | 0 | 0 | 0 | 0 | 0.062127 | 0 | 0 | 19.8094 | Hydro | 0.976 | Hydro | 97600
| Khulna Zone |  |  | 6.0998 | 11.7891 | 0 | 0 | 0 | 0.45504 | 16.4625 | 0 | 34.8065 | Solar | 3.686 | Solar | 57702944.3184
| Barishal Zone |  |  | 7.9799 | 26.949 | 0 | 0 | 0 | 0.002206 | 0 | 0 | 34.9311 | Import | 42.4585 | Import | 258283563.41
| Rajshahi Zone |  |  | 14.201 | 0 | 0 | 0 | 0 | 1.1875 | 23.7753 | 0 | 39.1638 | Wind | 0.2136 | Wind | 3142056
| Rangpur Zone |  |  | 0 | 0.63229 | 0.49275 | 0 | 0 | 1.0818 | 0 | 0 | 2.2068
| Total |  |  | 103.0392 | 57.4068 | 5.6119 | 0 | 0.976 | 3.686 | 42.4585 | 0.2136 | 213.392
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 360063252.24 |  | Hydro | 97600
|  |  |  | Coal | 365839899.0708 |  | Solar | 57702944.3184
|  |  |  | HFO | 96093490.1 |  | Import | 258283563.41
|  |  |  | HSD | 0 |  | Wind | 3142056
[5 empty] | Total: | 114,12,22,805 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 16.4625 | Peak Hr Flow | 771.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42132981.83 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.7753 | Peak Hr Flow | 1452.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2253 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2207 | Peak Hr Flow | 116.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2449 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.4585 | Peak Hr Flow | 2339.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3929
|  |  |  | Chattogram |  | 0 |  | 1193
|  |  |  | Cumilla |  | 0 |  | 939
|  |  |  | Mymensingh |  | 0 |  | 820
|  |  |  | Sylhet |  | 0 |  | 394
|  |  |  | Khulna |  | 0 |  | 1218
|  |  |  | Barishal |  | 0 |  | 318
|  |  |  | Rajshahi |  | 0 |  | 946
|  |  |  | Rangpur |  | 0 |  | 708
|  |  |  | Total |  | 0 |  | 10465
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 | 14:32 | Gopalganj (O) - Gopalgan (N) Ckt-1 Project Work S/D from Gopalganj 132/33kV end Due to
T-3 jack bus installation and from Gopalganj 400/132kV end Due to G2G project work
| 08:06 | 16:11 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) LT Scheduled S/D Due to Annual
Maintenance.
| 08:07 | 16:10 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) HT Scheduled S/D Due to Annual
Maintenance.
| 08:20 | 17:58 | Natore 132/33kV S/S TR-3 (425 T) LT Scheduled S/D Due to Annual maintenance work
| 08:22 | 17:58 | Natore 132/33kV S/S TR-3 (425 T) HT Scheduled S/D Due to Annual maintenance work
| 08:24 | 14:35 | Gopalganj 132/33kV S/S T1 HT Project Work S/D Due to T3 jack bus installation. | [7 empty] | 25.0MW load
interrup.
| 08:24 | 14:36 | Gopalganj 132/33kV S/S T1 LT Project Work S/D Due to T3 jack bus installation. | [7 empty] | 25.0MW load
interrup.
| 08:24 | 14:52 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Project Work S/D from Gopalganj 132/33kV end Due to | [7 empty] | 30.0MW load
|  |  | T3 jack bus installation. and from Gopalganj 400/132kV end Due to G2G Project work | [7 empty] | interrup. Gopalganj
132/33kV end
| 08:25 | 14:39 | Gopalganj 132/33kV S/S T2 LT Project Work S/D Due to T3 jack bus installation. | [7 empty] | 35.0MW load
interrup.
| 08:26 | 14:56 | Rampur 230/132/33 S/S Halishahar-2 Scheduled S/D Due to Annual maintenance of Halishahar
ckt-02 line.
| 08:26 | 14:39 | Gopalganj 132/33kV S/S T2 HT Project Work S/D Due to T3 jack bus installation. | [7 empty] | 35.0MW load
interrup.
| 08:28 | 14:59 | Halishahar-Khulshi 132kV Ckt-2 Scheduled S/D from Halishahar 132/33kV end Due to Due to
Annual Maintenance
| 08:29 | 13:54 | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance work by pbs.
| 08:29 | 13:54 | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance work by pbs.
| 08:29 | 13:54 | Keranigonj 230/132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance work by pbs.
| 08:33 | 13:52 | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D
| 08:34 | 11:56 | Chauddagram-Feni 132 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to X-link
cable clamping works by project
| 08:34 | 15:59 | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Jashore 132/33kV end Due to Annual
Maintenance
| 08:35 | 14:32 | Gopalganj 132/33kV S/S Main Bus Project Work S/D Due to T3 jack bus installation | [7 empty] | 60.0MW load
interrup.
| 08:38 | 17:12 | Bhulta 400/230kV S/S ATR-02 HT Scheduled S/D
| 08:40 | 16:37 | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Annual Maintenance of PBS-3 | [7 empty] | 20.0MW load
interrup.
| 08:42 | 14:01 | Daudkandi 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance of PBS-3 | [7 empty] | 20.0MW load
interrup.
| 08:42 | 16:25 | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to Annual maintenance & CT
replacement work
| 08:42 | 16:36 | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Annual Maintenance of PBS-3 | [7 empty] | 20.0MW load
interrup.
| 08:42 | 14:43 | Daudkandi 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance of PBS-3 | [7 empty] | 20.0MW load
interrup.
| 08:43 | 17:04 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to Annual
maintenance.
| 08:44 | 11:56 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Chauddagram 132/33kV end Due to Yearly
Maintenance at Feni 230 kv Grid
| 08:51 | 18:31 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual maintenance work and from Bogura 400/230kV end Due to Annual Maintenance
| 08:58 | 18:27 | Fenchuganj 230/132/33kV S/S AT-01 LT Project Work S/D Due to G to G project work
| 08:58 | 17:44 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
Maintenance of Doh-cox's Ckt-2 (Dohazari Side) and from Dohazari 132/33kV end Due to
Annual Maintenance
| 09:02 | 16:50 | Rahanpur 132/33kV S/S Rahanpur-2 Scheduled S/D Due to Annual Maintenance
| 09:04 | 17:36 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 LT Scheduled S/D Due to Annual Maintenance.
| 09:05 | 17:35 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 HT Scheduled S/D Due to Annual maintenance
| 09:06 | 16:17 | Baroirhat 132/33kV S/S TR-2, 416T LT Scheduled S/D
| 09:06 | 16:17 | Baroirhat 132/33kV S/S TR-2, 416T HT Scheduled S/D Due to PBS Bus maintenance works
| 09:06 | 16:50 | Chauddagram 132/33kV S/S 132 kv bus-1 Scheduled S/D Due to Yearly Maintenance.
| 09:07 | 12:23 | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance
| 09:08 | 12:23 | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance
| 09:09 | 18:30 | Fenchuganj 230/132/33kV S/S AT-01 HT Project Work S/D Due to G To G project work
| 09:11 | 17:08 | Chuadanga-Jhenaidah 132 kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end Due to Annual
maintenance and from Chuadanga 132/33kV end Due to Annual Maintenance.
| 09:12 | 16:36 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR-01(A,B) shutdown for Tan-Delta
test purpose
| 09:12 | 16:35 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR-01(A,B) shutdown for Tan-Delta
test purpose
| 09:12 | 16:52 | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Deadline
Checking
| 09:14 | 16:08 | Madanganj 132/33kV S/S Madanganj -Summit 55 MW 132 kv Ckt Scheduled S/D Due to Annual
Maintenance work
| 09:15 | 17:17 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Scheduled S/D Due to Annual Maintenance.
| 09:18 | 16:47 | Rahanpur 400/132kV S/S Rahanpur-Chowdala 132 KV Line Ckt-02 Scheduled S/D Due to Annual
maintenance
| 09:25 | 16:21 | Borhanuddin 230/33kV S/S Tr-Load HT Scheduled S/D Due to Annual Grid Maintenance | [7 empty] | 50.0MW load
interrup.
| 09:27 | 12:36 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Scheduled S/D Due to Annual Maintenance
| 09:27 | 12:36 | Mirzapur 132/33kV S/S Transformer-02(E07) HT Scheduled S/D Due to Annual Maintenace
| 09:32 | 16:21 | Borhanuddin 230/33kV S/S Tr-Load HT Scheduled S/D Due to Annual Maintenance. | [7 empty] | 50.0MW load
interrup.
| 09:37 | 16:24 | Borhanuddin 230/33kV S/S Tr-Load LT Scheduled S/D Due to Annual Maintenance. | [7 empty] | 50.0MW load
interrup.
| 09:55 | 16:50 | Hathazari-Raozan 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
Maintenance Work
|  | 10:54 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 is restored.
| 12:04 | 17:02 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end. and from Ishurdi
132/33kV end Due to annual maintenance at natore grid substation
| 12:31 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Load
management purpose ( order of NLDC)
| 12:31 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Load
management purpose ( order of NLDC)
| 13:46 | 16:45 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT Scheduled S/D Due to Red hot problem solution
| 13:46 | 16:45 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Scheduled S/D Due to Red hot problem solution
|  | 13:53 | Keranigonj 230/132/33kV S/S TR-2 HT is restored.
|  | 13:53 | Keranigonj 230/132/33kV S/S TR-2 LT is restored.
| 14:15 | 17:01 | Baroirhat 132/33kV S/S TR-1, 406T HT Scheduled S/D
| 14:15 | 17:01 | Baroirhat 132/33kV S/S TR-1, 406T LT Scheduled S/D Due to PBS annual maintenance work
| 14:15 | 17:01 | Baroirhat 132/33kV S/S TR-1, 406T LT Scheduled S/D Due to PBS annual maintenance work
|  | 14:32 | Gopalganj (O) - Gopalgan (N) Ckt-1 is restored.
| 14:38 | 19:18 | Rajendrapur 132/33kV S/S MTR-3 LT Project Work S/D Due to PBS cable termination work on
H-22 feeder.
| 14:44 | 16:39 | Daudkandi 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 132/33 KV Transformer-1 | [7 empty] | 35.0MW load
|  |  | shutdown for PBS-3 switching station maintenance work | [7 empty] | interrup.
| 14:46 | 16:36 | Daudkandi 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 132/33 KV Transformer-1 | [7 empty] | 35.0MW load
|  |  | shutdown for PBS-3 switching station maintenance work | [7 empty] | interrup.
| 14:53 | 19:17 | Rajendrapur 132/33kV S/S MTR-3 HT Project Work S/D Due to PBS cable termination work on
H-22 feeder.
|  | 14:56 | Gulshan 132/33kV S/S MT-1 HT is restored.
|  | 15:08 | Gopalganj 132/33kV S/S Gallamari-1 is restored.
|  | 15:12 | Gulshan 132/33kV S/S MT-1 LT is restored.
|  | 15:14 | Gopalganj 132/33kV S/S Gallamari-2 is restored.
|  | 15:16 | Gopalganj-Madhumati 132kV Ckt-1 is restored.
|  | 15:22 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS is restored.
|  | 15:24 | Bakulia 132/33kV S/S T-2 (412T) HT is restored.
| 15:46 | 17:30 | Kaliakoir 400/230/132kV S/S 132kV Bus 1 Scheduled S/D Due to Annual Maintenance
|  | 16:19 | Barishal-Barishal(N) 132 kV Ckt-1 is restored.
|  | 17:20 | Shyampur 230/132kV S/S 230 kV APR (D04) is restored.
|  | 17:21 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 17:21 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 17:22 | APR-Hasnabad 230kV Ckt-2 is restored.
|  | 17:27 | Madunaghat 400/230kV S/S ATR-1 7006T LT is restored.
|  | 17:27 | Madunaghat 400/230kV S/S ATR-1 7006T HT is restored.
|  | 17:56 | Mymensingh 132/33kV S/S Bus B is restored.
| 19:00 |  | Evening Peak Generation is 11002 MW.
|  | 22:52 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
|  | 22:53 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
| 00:33 | 00:38 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Sudden temperature rise in TR-01(B)
LT side
| 00:33 | 00:38 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Sudden temperature rise in TR-01(B)
LT side
| 06:19 | 06:41 | Savar 132/33kV S/S T-2 HT Tripped showing Over Current Relay relays Due to L-35 | [7 empty] | 22.0MW load
interrup.
| 06:19 | 06:41 | Savar 132/33kV S/S T-1 HT Tripped showing Over Current Relay relays Due to L-35 | [7 empty] | 22.0MW load
interrup.
| 06:32 |  | Khulna(C )-Noapara 132kV Ckt-1 Project Work S/D from Khulna (C) end Due to Due to piling
work and from Noapara 132/33kVend.
| 07:00 |  | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to By direction
of NLDC
| 07:01 |  | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to by direction
of NLDC
| 07:09 |  | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to Annual
Maintenance and from Barishal 132/33kV end Due to Annual maintenance work.
| 07:20 |  | Meghnaghat 400/230kV S/S ATR - 2 LT Scheduled S/D Due to For maintenance work
| 07:21 |  | Bhulta 400/230kV S/S ATR-02 HT Scheduled S/D Due to Annual Maintenance Works
| 07:50 |  | Bhulta-Rampura 230 kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Dead line
checking. and from Bhulta 400/230kVend.
| 07:50 |  | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D
| 07:50 |  | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) LT Scheduled S/D Due to Annual
Maintenance.
| 07:51 |  | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Dead line
checking. and from Bhulta 400/230kVend.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 312 | 8449200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6750921 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 50.7 | 177480 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 45 | 229920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 168871 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 67087 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 426600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 471600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 65760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 564295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 42 | 255744 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 385920 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 104 | 267840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 164104 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 293400 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 408 | 9221761 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 30000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1634.7 | 27990503
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 2295 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 104160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 976000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5107918 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 100 | 408145 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 33600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 26 | 427200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18684 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 38 | 97000 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 231360 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 33873 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 567 | 12545453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 16 | 213600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 355 | 5490909.09 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1494 | 25690197.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4974000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 280 | 6902000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 235 | 6786500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 925392 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 331200 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 109 | 2199077 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 84 | 321120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 116 | 2220680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 311660 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 427173 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1153 | 25398802
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 72 | 2057280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 276000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 721200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 273910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 55200 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 162 | 3394790
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 62127 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 669000 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 601248 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1417920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3723370 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 404000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 304752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7602000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5025000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 856 | 19809417
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 771 | 16462545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6099840 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 455040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 597 | 11789090 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1618 | 34806515
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 506 | 7750466 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2659000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1085 | 19198545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5320891 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2206 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1926 | 34931108.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 308280 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4455727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 407 | 9745309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 4350 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1452 | 23775272 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 304512 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 570350 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2041 | 39163800
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 632290 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 48 | 208492 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30113.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 284263 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 156006 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 895680 | -
Rangpur Area Total |  |  |  |  | 950 | 118 | 2206844.04
Eastern Grid Total |  |  |  |  | 17395.105 | 5299.7 | 102283709.09
Western Grid Total |  |  |  |  | 10821.56 | 5703 | 111108267.49
National Grid Total |  |  |  |  | 28216.665 | 11002.7 | 213391976.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-12-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7275.22 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3190 | MW
i) Dhaka area |  |  | 3929.22 |  | MW | i) Khulna area |  |  |  | 1217.6 | MW
ii) Chattogram area |  |  | 1193 |  | MW | ii) Barishal area |  |  |  | 318.2 | MW
iii) Cumilla area |  |  | 939 |  | MW | iii) Rajshahi area |  |  |  | 946.2 | MW
iv) Mymensingh area |  |  | 820 |  | MW | iv) Rangpur area |  |  |  | 708 | MW
v) Sylhet area |  |  | 394 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10465.22 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 55 | 18:30 | 133 | Niamatpur | 42 | 08:00
2 | AKSML | 145 | 16:00 | 68 | Ishurdi | 50 | 18:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jaldhaka | 56 | 18:00 | 135 | PHP | 6 | 03:00
4 | Agargaon | 76 | 13:00 | 70 | Jamalpur | 91 | 18:00 | 136 | Pabna | 75 | 18:00
5 | Agrabad | 66 | 18:30 | 71 | Jashore | 97 | 18:30 | 137 | Palashbari | 86 | 18:30
6 | Amnura | 18 | 08:00 | 72 | Jhenaidah | 97 | 18:00 | 138 | Panchagarh | 44 | 18:00
7 | Ashuganj | 57 | 13:00 | 73 | Joydebpur | 89 | 18:00 | 139 | Patiya | 7 | 18:00
8 | BSRM | 198 | 02:00 | 74 | Joypurhat | 46 | 18:00 | 140 | Patuakhali | 43 | 21:00
9 | Bagerhat | 70 | 18:00 | 75 | Juldah | 14.5 | 16:00 | 141 | Payra | 22 | 19:30
10 | Bajitpur | 63 | 18:00 | 76 | KSRM | 25 | 16:00 | 142 | Postogola | 48 | 12:00
11 | Bakulia | 62 | 18:00 | 77 | Kabirpur | 202 | 18:00 | 143 | Purbachal | 26 | 13:00
12 | Banani | 38.4 | 13:00 | 78 | Kachua | 51 | 18:00 | 144 | Purbasadipur | 108 | 18:00
13 | Bangabhaban | 6 | 10:00 | 79 | Kallyanpur | 75 | 12:00 | 145 | Rahanpur | 21 | 18:00
14 | Barapukuria | 51 | 18:00 | 80 | Kalurghat | 38 | 12:00 | 146 | Rahim | 38 | 10:00
15 | Barguna | 14 | 20:00 | 81 | Kamrangirchar | 56 | 18:00 | 147 | Rajbari | 58 | 18:00
16 | Barishal | 94 | 15:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 95 | 18:30
17 | Barishal-230 | 68 | 18:00 | 83 | Kasba | 24 | 13:00 | 149 | Rajshahi | 69 | 18:00
18 | Baroaulia | 61 | 12:00 | 84 | Kazla | 84 | 18:00 | 150 | Rajshahi-230 | 71 | 13:00
19 | Baroirhat | 34 | 07:00 | 85 | Keranigonj | 66 | 17:00 | 151 | Ramganj | 70 | 20:00
20 | Bashundhara | 137 | 12:00 | 86 | Khagrachori | 28 | 18:00 | 152 | Rampur | 0 | 00:00
21 | BashundharaCement | 3 | 18:30 | 87 | Khulna | 43 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 146 | 23:00 | 154 | Rangpur | 92 | 18:00
23 | Benapole | 46 | 13:00 | 89 | Kishoreganj | 83 | 19:00 | 155 | Ruppur | 1.8 | 09:00
24 | Bhaluka | 119 | 19:30 | 90 | Kodda | 268 | 17:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 41.6 | 18:30 | 91 | Kulaura | 27 | 19:00 | 157 | Saidpur | 86 | 18:30
26 | Bhangura | 24 | 13:00 | 92 | Kurigram | 52 | 18:30 | 158 | Satkhira | 84 | 18:00
27 | Bheramara(GK) | 44 | 18:00 | 93 | Kushtia | 111 | 18:00 | 159 | Satmasjid | 80 | 13:00
28 | Bhulta | 149 | 06:00 | 94 | Laksam | 22 | 13:00 | 160 | Savar | 164 | 12:00
29 | Bog-Sherpur | 60 | 18:00 | 95 | Lakshmipur | 24 | 18:00 | 161 | SevenRings | 13.92 | 17:00
30 | Bogura | 115 | 18:00 | 96 | Lalbag | 53 | 18:00 | 162 | ShahCement | 31 | 23:00
31 | Borhanuddin | 78 | 18:00 | 97 | Lalmonirhat | 43 | 18:00 | 163 | Shahjadpur | 55 | 18:00
32 | Brahmanbaria | 84 | 19:30 | 98 | MI_Cement | 7.2 | 15:00 | 164 | Shahjibazar | 74 | 18:30
33 | Cantonment | 74 | 13:00 | 99 | Madanganj | 36 | 09:00 | 165 | Shahmirpur | 39 | 18:00
34 | Chandina | 6 | 01:00 | 100 | Madaripur | 71 | 19:00 | 166 | Shariatpur | 53 | 19:00
35 | Chandpur | 50 | 20:00 | 101 | Madartek | 60 | 12:00 | 167 | Sherpur | 106 | 17:00
36 | Chandraghona | 27 | 19:00 | 102 | Madunaghat | 38 | 17:00 | 168 | Shikalbaha | 21.5 | 00:00
37 | Chapai | 45 | 12:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 57.7 | 12:00
38 | Charsaidpur | 33 | 00:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 38 | 15:00
39 | Chauddagram | 44 | 18:00 | 105 | Maijdee | 26 | 18:00 | 171 | Shyampur | 140 | 13:00
40 | Chhatak | 21 | 18:00 | 106 | Manikganj | 86 | 18:00 | 172 | Siddhirganj | 93 | 12:00
41 | Chowmuhani | 100 | 18:30 | 107 | Maniknagar | 44 | 13:00 | 173 | Sirajganj | 75 | 18:30
42 | Chuadanga | 76 | 18:00 | 108 | Matarbari | 40 | 18:30 | 174 | Sonargaon | 86 | 20:00
43 | Coxsbazar | 106 | 20:00 | 109 | Matuail | 60 | 12:00 | 175 | Sreemongol | 61 | 18:00
44 | Cumilla(N) | 84 | 17:00 | 110 | Metrorail_Motijheel | 20 | 15:00 | 176 | Sreepur | 93 | 18:30
45 | Cumilla(S) | 125 | 18:00 | 111 | Metrorail_Uttara | 4 | 09:00 | 177 | Srinagar | 31.3 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 106 | 18:00 | 178 | Sunamganj | 41 | 18:00
47 | Daudkandi | 126 | 18:00 | 113 | Mirpur | 106 | 13:00 | 179 | Sylhet | 49 | 18:00
48 | DhakaUniversity | 52 | 13:00 | 114 | Mirsorai | 22 | 09:00 | 180 | Sylhet-132 | 66 | 18:30
49 | Dhamrai | 98 | 18:00 | 115 | Mirzapur | 37 | 17:00 | 181 | TK | 17 | 18:30
50 | Dhanmondi | 79 | 13:00 | 116 | Mithapukur | 48 | 18:00 | 182 | Tangail | 118 | 18:00
51 | Dohazari | 68 | 19:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 27 | 08:00
52 | Faridpur | 111 | 18:30 | 118 | Mogbazar | 59.7 | 13:00 | 184 | Tasnim | 31 | 16:00
53 | Fatullah | 92 | 12:00 | 119 | Mongla | 35 | 18:00 | 185 | Thakurgaon | 76 | 19:00
54 | Fenchuganj | 25 | 18:00 | 120 | Motijheel | 26 | 12:00 | 186 | Tongi | 92 | 18:00
55 | Feni | 86 | 18:30 | 121 | Muktagacha | 26 | 18:00 | 187 | Ullahpara | 26 | 18:00
56 | GPH | 89 | 11:00 | 122 | Munshiganj | 76 | 21:00 | 188 | Ullon | 48 | 18:00
57 | Ghatail | 56 | 18:30 | 123 | Muradnagar | 25 | 19:30 | 189 | Uttara | 57 | 13:00
58 | Ghorashal | N/A | N/A | 124 | Mymensingh | 138 | 18:30 | 190 | UttaraNew | 13 | 13:00
59 | Ghorashal-230 | 83 | 21:00 | 125 | Naogaon | 89 | 18:00 | 191 | Zigatola | 53 | 14:00
60 | Goalpara | 27 | 18:30 | 126 | Narail | 43 | 18:00
61 | Gollamari | 70 | 18:00 | 127 | Narinda | 55 | 13:00
62 | Gopalganj | 87.2 | 18:00 | 128 | Narshingdi | 151 | 18:30
63 | Gulshan | 66 | 13:00 | 129 | Natore | 90 | 19:30
64 | Halishahar | 60 | 17:00 | 130 | Nawabganj | 29.2 | 19:30
65 | HaripurSBU | 136 | 12:00 | 131 | Netrakona | 102 | 18:00
66 | Hasnabad | 108 | 14:00 | 132 | New | 59 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8402.97 | 0 |  | 8402.97
1:00 | 7859.72 | 0 |  | 7859.72
2:00 | 7445.71 | 0 |  | 7445.71
3:00 | 7256.99 | 0 |  | 7256.99
4:00 | 6996.54 | 0 |  | 6996.54
5:00 | 6972.96 | 0 |  | 6972.96
6:00 | 7468.62 | 0 |  | 7468.62
7:00 | 8081.26 | 0 |  | 8081.26
8:00 | 8825.53 | 0 |  | 8825.53
9:00 | 8222.43 | 0 |  | 8222.43
10:00 | 7934.11 | 0 |  | 7934.11
11:00 | 8157.54 | 0 |  | 8157.54
12:00 | 8880.84 | 0 |  | 8880.84
13:00 | 9209.02 | 0 |  | 9209.02
14:00 | 8992.17 | 0 |  | 8992.17
15:00 | 8802.59 | 0 |  | 8802.59
16:00 | 8868.83 | 0 |  | 8868.83
17:00 | 9608.4 | 0 |  | 9608.4
18:00 | 10893 | 0 |  | 10893
19:00 | 11002.7 | 0 |  | 11002.7
19:30 | 10694.3 | 0 |  | 10694.3
20:00 | 10511.7 | 0 |  | 10511.7
21:00 | 10313.96 | 0 |  | 10313.96
22:00 | 9925.78 | 0 |  | 9925.78
23:00 | 9326.68 | 0 |  | 9326.68
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4135 | 4267.97 | 8402.97 | DAILY GENERATION CURVE
00:30 | 3939 | 4192.345 | 8131.345
01:00 | 3743 | 4116.72 | 7859.72 | 06-12-2025
01:30 | 3639.5 | 4013.215 | 7652.715
02:00 | 3536 | 3909.71 | 7445.71
02:30 | 3500.5 | 3850.85 | 7351.35
03:00 | 3465 | 3791.99 | 7256.99
03:30 | 3426.5 | 3700.265 | 7126.765
04:00 | 3388 | 3608.54 | 6996.54
04:30 | 3384 | 3600.75 | 6984.75
05:00 | 3380 | 3592.96 | 6972.96
05:30 | 3583 | 3637.79 | 7220.79
06:00 | 3786 | 3682.62 | 7468.62
06:30 | 3956.395 | 3818.545 | 7774.94
07:00 | 4126.79 | 3954.47 | 8081.26
07:30 | 4251.37 | 4202.025 | 8453.395
08:00 | 4375.95 | 4449.58 | 8825.53
08:30 | 4222.125 | 4301.855 | 8523.98
09:00 | 4068.3 | 4154.13 | 8222.43
09:30 | 3925.975 | 4152.295 | 8078.27
10:00 | 3783.65 | 4150.46 | 7934.11
10:30 | 3827.565 | 4218.26 | 8045.825
11:00 | 3871.48 | 4286.06 | 8157.54
11:30 | 4158.37 | 4360.82 | 8519.19
12:00 | 4445.26 | 4435.58 | 8880.84
12:30 | 4481.505 | 4563.425 | 9044.93
13:00 | 4517.75 | 4691.27 | 9209.02
13:30 | 4433.465 | 4667.13 | 9100.595
14:00 | 4349.18 | 4642.99 | 8992.17
14:30 | 4326.135 | 4571.245 | 8897.38
15:00 | 4303.09 | 4499.5 | 8802.59
15:30 | 4370.73 | 4464.98 | 8835.71
16:00 | 4438.37 | 4430.46 | 8868.83
16:30 | 4579.805 | 4658.81 | 9238.615
17:00 | 4721.24 | 4887.16 | 9608.4
17:30 | 5082.62 | 5168.08 | 10250.7
18:00 | 5444 | 5449 | 10893
18:30 | 5371.85 | 5576 | 10947.85
19:00 | 5299.7 | 5703 | 11002.7
19:30 | 4986.3 | 5708 | 10694.3
20:00 | 4781.7 | 5730 | 10511.7
20:30 | 4723.1 | 5689.73 | 10412.83 |  | Executive Engineer
21:00 | 4664.5 | 5649.46 | 10313.96 |  | Network Operation Division
21:30 | 4547.65 | 5572.22 | 10119.87
22:00 | 4430.8 | 5494.98 | 9925.78
22:30 | 4328.4 | 5297.83 | 9626.23
23:00 | 4226 | 5100.68 | 9326.68

## En-Curve
QF-LDC-12
Date | 06-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3156 | 1228 | 752 | 0 | 80 | 830.97 | 40 | 2297 | 0 | 0 | 17 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 3101.5 | 1135 | 798.5 | 0 | 80 | 831.845 | 40 | 2120.5 | 0 | 0 | 17 | 0 | 0 | 7 | 0 | 06-12-2025
01:00 | 3047 | 1042 | 845 | 0 | 80 | 832.72 | 40 | 1944 | 0 | 0 | 17 | 0 | 0 | 12 | 0
01:30 | 2968 | 1006.5 | 798 | 0 | 79 | 831.215 | 40 | 1900.5 | 0 | 0 | 17 | 0 | 0 | 12.5 | 0 | Energy Generated | 213.392 |  | MKWHr
02:00 | 2889 | 971 | 751 | 0 | 78 | 829.71 | 40 | 1857 | 0 | 0 | 17 | 0 | 0 | 13 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2891.5 | 938.5 | 688.5 | 0 | 76 | 830.35 | 40 | 1853 | 0 | 0 | 17 | 0 | 0 | 16.5 | 0 | Total Energy Requirement | 213.392 |  | MKWHr
03:00 | 2894 | 906 | 626 | 0 | 74 | 830.99 | 40 | 1849 | 0 | 0 | 17 | 0 | 0 | 20 | 0
03:30 | 2883.5 | 876 | 547 | 0 | 74 | 832.765 | 40 | 1842.5 | 0 | 0 | 17 | 0 | 0 | 14 | 0
04:00 | 2873 | 846 | 468 | 0 | 74 | 834.54 | 40 | 1836 | 0 | 0 | 17 | 0 | 0 | 8 | 0
04:30 | 2863.5 | 838.5 | 468 | 0 | 75 | 833.25 | 40 | 1843 | 0 | 0 | 17 | 0 | 0 | 6.5 | 0
05:00 | 2854 | 831 | 468 | 0 | 76 | 831.96 | 40 | 1850 | 0 | 0 | 17 | 0 | 0 | 5 | 0
05:30 | 2987 | 942.5 | 468.5 | 0 | 78 | 830.29 | 40 | 1850 | 0 | 0 | 17 | 0 | 0 | 7.5 | 0
06:00 | 3120 | 1054 | 469 | 0 | 80 | 828.62 | 40 | 1850 | 0 | 0 | 17 | 0 | 0 | 10 | 0
06:30 | 3228 | 1089.5 | 468.5 | 0 | 79 | 880.805 | 40 | 1935 | 16.135 | 0 | 27.5 | 0 | 0 | 10.5 | 0
07:00 | 3336 | 1125 | 468 | 0 | 78 | 932.99 | 40 | 2020 | 32.27 | 0 | 38 | 0 | 0 | 11 | 0
07:30 | 3419.5 | 1110.25 | 562.5 | 0 | 80 | 934.56 | 40 | 2144.5 | 104.085 | 0 | 49 | 0 | 0 | 9 | 0
08:00 | 3503 | 1095.5 | 657 | 0 | 82 | 936.13 | 40 | 2269 | 175.9 | 0 | 60 | 0 | 0 | 7 | 0
08:30 | 3349.5 | 1039.5 | 656.5 | 0 | 77 | 882.06 | 40 | 2143.5 | 268.92 | 6 | 55.5 | 0 | 0 | 5.5 | 0
09:00 | 3196 | 983.5 | 656 | 0 | 72 | 827.99 | 40 | 2018 | 361.94 | 12 | 51 | 0 | 0 | 4 | 0
09:30 | 3055.5 | 958 | 656.5 | 0 | 76 | 833.28 | 40 | 1956 | 432.49 | 26 | 41.5 | 0 | 0 | 3 | 0
10:00 | 2915 | 932.5 | 657 | 0 | 80 | 838.57 | 40 | 1894 | 503.04 | 40 | 32 | 0 | 0 | 2 | 0
10:30 | 2999 | 939.25 | 657 | 0 | 81 | 834.745 | 40 | 1907 | 533.83 | 28.5 | 24 | 0 | 0 | 1.5 | 0
11:00 | 3083 | 946 | 657 | 0 | 82 | 830.92 | 40 | 1920 | 564.62 | 17 | 16 | 0 | 0 | 1 | 0
11:30 | 3248 | 1044.25 | 680.5 | 0 | 90 | 838.72 | 40 | 1957.5 | 584.22 | 17 | 16 | 0 | 0 | 3 | 0
12:00 | 3413 | 1142.5 | 704 | 0 | 98 | 846.52 | 40 | 1995 | 603.82 | 17 | 16 | 0 | 0 | 5 | 0
12:30 | 3408 | 1149 | 727 | 0 | 96 | 885.325 | 40 | 2111 | 579.605 | 17 | 29.5 | 0 | 0 | 2.5 | 0
13:00 | 3403 | 1155.5 | 750 | 0 | 94 | 924.13 | 40 | 2227 | 555.39 | 17 | 43 | 0 | 0 | 0 | 0
13:30 | 3340 | 1107 | 797 | 0 | 98 | 876.065 | 40 | 2283 | 489.03 | 17 | 53.5 | 0 | 0 | 0 | 0
14:00 | 3277 | 1058.5 | 844 | 0 | 102 | 828 | 40 | 2339 | 422.67 | 17 | 64 | 0 | 0 | 0 | 0
14:30 | 3253 | 1092.75 | 784.5 | 0 | 104 | 832 | 40 | 2349 | 361.13 | 17 | 64 | 0 | 0 | 0 | 0
15:00 | 3229 | 1127 | 725 | 0 | 106 | 836 | 40 | 2359 | 299.59 | 17 | 64 | 0 | 0 | 0 | 0
15:30 | 3221.5 | 1142 | 678 | 0 | 104 | 879 | 40 | 2450.5 | 207.71 | 32.5 | 71 | 0 | 0 | 9.5 | 0
16:00 | 3214 | 1157 | 631 | 0 | 102 | 922 | 40 | 2542 | 115.83 | 48 | 78 | 0 | 0 | 19 | 0
16:30 | 3211.5 | 1157 | 631 | 0 | 106 | 1030.5 | 40 | 2693.5 | 60.615 | 89.5 | 203 | 0 | 0 | 16 | 0
17:00 | 3209 | 1157 | 631 | 0 | 110 | 1139 | 40 | 2845 | 5.4 | 131 | 328 | 0 | 0 | 13 | 0
17:30 | 3201.5 | 1170 | 654.5 | 0 | 119 | 1256 | 40 | 2970 | 2.7 | 184.5 | 639 | 0 | 0 | 13.5 | 0
18:00 | 3194 | 1183 | 678 | 0 | 128 | 1373 | 40 | 3095 | 0 | 238 | 950 | 0 | 0 | 14 | 0
18:30 | 3147 | 1182 | 724.5 | 0 | 122 | 1412.5 | 40 | 3102.5 | 0 | 184.5 | 1017.85 | 0 | 0 | 15 | 0
19:00 | 3100 | 1181 | 771 | 0 | 116 | 1452 | 40 | 3110 | 0 | 131 | 1085.7 | 0 | 0 | 16 | 0
19:30 | 3156 | 1174 | 771 | 0 | 118 | 1440 | 40 | 3116 | 0 | 50 | 813.3 | 0 | 0 | 16 | 0
20:00 | 3147 | 1169 | 771 | 0 | 100 | 1454 | 40 | 3123 | 0 | 0 | 695.7 | 0 | 0 | 12 | 0
20:30 | 3170.5 | 1170.5 | 774 | 0 | 103 | 1454.73 | 40 | 3121 | 0 | 0 | 569.1 | 0 | 0 | 10 | 0
21:00 | 3194 | 1172 | 777 | 0 | 106 | 1455.46 | 40 | 3119 | 0 | 0 | 442.5 | 0 | 0 | 8 | 0
21:30 | 3208 | 1175.5 | 780 | 0 | 107 | 1385.22 | 40 | 3054 | 0 | 0 | 363.15 | 0 | 0 | 7 | 0
22:00 | 3222 | 1179 | 783 | 0 | 108 | 1314.98 | 40 | 2989 | 0 | 0 | 283.8 | 0 | 0 | 6 | 0
22:30 | 3218.5 | 1188 | 762 | 0 | 108 | 1268.83 | 40 | 2862 | 0 | 0 | 166.9 | 0 | 0 | 12 | 0
23:00 | 3215 | 1197 | 741 | 0 | 108 | 1222.68 | 40 | 2735 | 0 | 0 | 50 | 0 | 0 | 18 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 05:00 | 396 | 12:00 | Meghnaghat | 413 | 06:00 | 395 | 13:00
Ashuganj | 417 | 6:00 | 400 | 18:00 | Payra | 419 | 05:00 | 410 | 17:00
Bhulta | 413 | 06:00 | 395 | 18:00 | Rahanpur | 424 | 04:00 | 406 | 18:00
Bibiana | 406 | 03:00 | 396 | 21:00 | Rampal | 415 | 04:00 | 398 | 20:00
BIPTC | 408 | 03:00 | 395 | 14:00
Bogura | 420 | 04:00 | 395 | 18:30
Gopalganj | 416 | 05:00 | 400 | 18:00
Kaliakoir | 408 | 02:00 | 369 | 19:00
Korerhat | 413 | 06:00 | 401 | 11:00
Madunaghat | 405 | 04:00 | 396 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 01:00 | 229 | 13:00 | Kachua | 240 | 05:00 | 231 | 14:00
AKSML | 244 | 06:00 | 231 | 15:00 | Kaliakoir | 241 | 01:00 | 229 | 15:00
Aminbazar | 245 | 00:00 | 230 | 12:00 | Keranigonj | 242 | 01:00 | 228 | 13:00
Ashuganj | 243 | 05:00 | 235 | 14:00 | Khulna(S) | 242 | 03:00 | 229 | 18:00
Ashuganj-400 | 243 | 6:00 | 233 | 20:00 | Korerhat | 242 | 03:00 | 236 | 11:00
Baghabari | 241 | 04:00 | 229 | 18:00 | Madunaghat | 241 | 04:00 | 232 | 15:00
Barapukuria | 228 | 05:00 | 195 | 18:00 | Madunaghat-400 | 242 | 06:00 | 234 | 13:00
Barapukuria-230 | 205 | 5:00 | 195 | 17:00 | Maniknagar | 239 | 01:00 | 229 | 12:00
Barishal | 246 | 03:00 | 238 | 17:00 | Meghnaghat | 244 | 01:00 | 236 | 13:00
Bheramara | 240 | 06:00 | 225 | 18:00 | Meghnaghat-400 | 242 | 06:00 | 230 | 13:00
Bhulta | 241 | 05:00 | 229 | 12:00 | Mirsorai | 241 | 04:00 | 230 | 14:00
Bibiana | 238 | 05:00 | 232 | 21:00 | Rajshahi | 240 | 04:00 | 224 | 18:00
BIPTC | 242 | 04:00 | 225 | 18:00 | Rampal | 239 | 03:00 | 228 | 21:00
Bogura | 239 | 04:00 | 222 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 238 | 04:00 | 224 | 18:00 | Rampura | 241 | 06:00 | 228 | 13:00
Borhanuddin | 246 | 02:00 | 240 | 22:00 | Shikalbaha | 239 | 06:00 | 231 | 14:00
BSRM | 240 | 03:00 | 231 | 13:00 | Shyampur | 241 | 01:00 | 227 | 15:00
Cumilla(N) | 241 | 05:00 | 232 | 15:00 | Siddhirganj | 241 | 05:00 | 231 | 12:00
Faridpur | 246 | 04:00 | 236 | 18:00 | Sirajgonj | 245 | 03:00 | 235 | 18:00
Fenchuganj | 239 | 06:00 | 233 | 20:00 | Sreepur | 238 | 00:00 | 228 | 20:00
Feni | 241 | 06:00 | 231 | 13:00 | Tongi | 237 | 04:00 | 226 | 15:00
Ghorashal | N/A | N/A | N/A | N/A
Ghorashal-230 | 236 | 04:00 | 218 | 19:30
Gopalganj | 246 | 04:00 | 237 | 13:00
GPH | 237 | 07:00 | 230 | 05:00
Haripur | 241 | 05:00 | 230 | 13:00
Hasnabad | 241 | 00:00 | 228 | 12:00
Hathazari | 240 | 05:00 | 232 | 15:00
Ishurdi | 242 | 04:00 | 228 | 18:00
Jhenaidah | 241 | 04:00 | 225 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 01:00 | 128 | 11:00 | Lalbag | 137 | 00:00 | 128 | 12:00
Agargaon | 140 | 00:00 | 131 | 12:00 | Lalmonirhat | 133 | 05:00 | 118 | 18:00
Agrabad | 140 | 06:00 | 133 | 14:00 | Madanganj | 139 | 05:00 | 131 | 13:00
AKS | 137 | 06:00 | 132 | 13:00 | Madaripur | 140 | 05:00 | 136 | 18:00
Aminbazar | 138 | 00:00 | 131 | 15:00 | Madartek | 136 | 04:00 | 128 | 12:00
Amnura | 140 | 01:00 | 130 | 18:00 | Madunaghat | 141 | 06:00 | 136 | 12:00
Ashuganj | 144 | 03:00 | 104 | 20:00 | Magura | 141 | 01:00 | 127 | 18:00
Bagerhat | 140 | 04:00 | 126 | 18:00 | Mahasthangarh | 136 | 04:00 | 127 | 17:00
Bajitpur | 139 | 09:00 | 132 | 18:30 | Maijdee | 137 | 05:00 | 129 | 13:00
Bakulia | 141 | 06:00 | 135 | 13:00 | Manikganj | 134 | 06:00 | 126 | 15:00
Banani | 137 | 04:00 | 127 | 13:00 | Maniknagar | 142 | 00:00 | 131 | 12:00
Bangabhaban | 142 | 00:00 | 131 | 12:00 | Matarbari | 133 | 08:00 | 123 | 17:00
Barapukuria | 139 | 05:00 | 119 | 18:00 | Matuail | 141 | 02:00 | 134 | 12:00
Barguna | 137 | 01:00 | 134 | 18:00 | Metrorail_Motijheel | 140 | 00:00 | 131 | 12:00
Barishal | 142 | 03:00 | 136 | 18:00 | Metrorail_Uttara | 137 | 03:00 | 127 | 15:00
Barishal-230 | 142 | 03:00 | 136 | 18:00 | Millgate | 136 | 01:00 | 127 | 15:00
Baroaulia | 139 | 06:00 | 135 | 14:00 | Mirpur | 139 | 01:00 | 130 | 13:00
Baroirhat | 138 | 01:00 | 133 | 17:00 | Mirzapur | 138 | 03:00 | 131 | 12:00
Bashundhara | 137 | 03:00 | 127 | 16:00 | Mithapukur | 136 | 04:00 | 122 | 18:00
BashundharaCement | 139 | 05:00 | 131 | 13:00 | MI_Cement | 140 | 03:00 | 131 | 13:00
Beanibazar | 136 | 04:00 | 131 | 18:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 140 | 04:00 | 124 | 18:30 | Mogbazar | 138 | 00:00 | 129 | 13:00
Bhaluka | 137 | 04:00 | 131 | 18:00 | Mongla | 138 | 05:00 | 127 | 18:00
Bhandaria | 140 | 09:00 | 132 | 18:30 | Motijheel | 142 | 00:00 | 131 | 13:00
Bhangura | 140 | 04:00 | 131 | 18:00 | Muktagacha | 135 | 09:00 | 129 | 00:00
Bheramara | 141 | 03:00 | 136 | 18:00 | Munshiganj | 139 | 01:00 | 132 | 12:00
Bheramara(GK) | 141 | 04:00 | 136 | 18:00 | Muradnagar | 141 | 09:00 | 134 | 18:00
Bhulta | 137 | 01:00 | 130 | 13:00 | Mymensingh | 134 | 09:00 | 126 | 18:00
Bog-Sherpur | 138 | 04:00 | 126 | 18:00 | Naogaon | 134 | 04:00 | 123 | 18:00
Bogura | 137 | 06:00 | 129 | 17:00 | Narail | 143 | 04:00 | 128 | 18:30
Bogura-230 | 137 | 04:00 | 126 | 18:00 | Narinda | 0 | 00:00 | N/A | N/A
Brahmanbaria | 140 | 06:00 | 133 | 18:00 | Narshingdi | 139 | 06:00 | 130 | 18:30
Cantonment | 140 | 01:00 | 131 | 12:00 | Natore | 137 | 01:00 | 130 | 18:00
Chandina | 142 | 04:00 | 136 | 13:00 | Nawabganj | 139 | 00:00 | 128 | 13:00
Chandpur | 141 | 04:00 | 137 | 12:00 | Netrakona | 132 | 04:00 | 127 | 18:00
Chandraghona | 141 | 06:00 | 136 | 14:00 | New | 138 | 03:00 | 127 | 15:00
Chapai | 141 | 03:00 | 135 | 19:00 | Niamatpur | 142 | 04:00 | 134 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 141 | 05:00 | 133 | 12:00 | Noapara | 140 | 03:00 | 127 | 18:00
Chauddagram | 139 | 02:00 | 134 | 13:00 | Pabna | 140 | 03:00 | 133 | 18:00
Chhatak | 135 | 04:00 | 129 | 18:00 | Palashbari | 135 | 05:00 | 120 | 18:00
Chowmuhani | 137 | 06:00 | 132 | 13:00 | Panchagarh | 138 | 05:00 | 121 | 12:00
Chuadanga | 142 | 05:00 | 127 | 18:00 | Patiya | 140 | 06:00 | 134 | 13:00
Coxsbazar | 132 | 08:00 | 117 | 17:00 | Patuakhali | 137 | 07:00 | 134 | 13:00
Cumilla(N) | 142 | 05:00 | 136 | 14:00 | Payra | 138 | 01:00 | 135 | 13:00
Cumilla(S) | 141 | 05:00 | 124 | 15:00 | PHP | 138 | 06:00 | 132 | 13:00
Daganbhuiyan | 138 | 05:00 | 133 | 13:00 | Postogola | 141 | 01:00 | 133 | 12:00
Daudkandi | 140 | 04:00 | 131 | 18:00 | Purbachal | 136 | 01:00 | 128 | 12:00
DhakaUniversity | 137 | 06:00 | 128 | 13:00 | Purbasadipur | 134 | 05:00 | 115 | 18:00
Dhamrai | 140 | 02:00 | 131 | 15:00 | Rahanpur | 142 | 04:00 | 135 | 18:00
Dhanmondi | 142 | 06:00 | 135 | 12:00 | Rahanpur-400 | 143 | 05:00 | 136 | 18:00
Dohazari | 137 | 05:00 | 132 | 17:00 | Rahim | 140 | 02:00 | 133 | 13:00
Faridpur | 141 | 02:00 | 132 | 07:00 | Rajbari | 143 | 05:00 | 134 | 17:00
Fatullah | 142 | 00:00 | 132 | 12:00 | Rajendrapur | 139 | 06:00 | 132 | 12:00
Fenchuganj | 142 | 06:00 | 137 | 14:00 | Rajshahi | 139 | 06:00 | 130 | 18:00
Feni | 135 | 01:00 | 132 | 12:00 | Rajshahi-230 | 139 | 05:00 | 129 | 18:00
Feni-230 | 138 | 06:00 | 132 | 13:00 | Ramganj | 137 | 04:00 | 133 | 12:00
Ghatail | 133 | 01:00 | 129 | 00:00 | Rampur | 140 | 06:00 | 133 | 14:00
Ghorashal | N/A | N/A | N/A | N/A | Rampura | 136 | 01:00 | 128 | 12:00
Goalpara | 141 | 03:00 | 132 | 18:00 | Rangamati | 140 | 04:00 | 135 | 11:00
Gollamari | 141 | 04:00 | 132 | 18:00 | Rangpur | 134 | 03:00 | 123 | 08:00
Gopalganj | 142 | 04:00 | 130 | 23:00 | Ruppur | 141 | 03:00 | 135 | 18:00
Gopalganj-400 | 143 | 03:00 | 137 | 17:00 | Saidpur | 134 | 03:00 | 120 | 18:00
Gulshan | 136 | 04:00 | 128 | 12:00 | Satkhira | 139 | 05:00 | 127 | 18:00
Halishahar | 141 | 06:00 | 134 | 14:00 | Satmasjid | 141 | 01:00 | 130 | 13:00
Haripur | 141 | 04:00 | 134 | 13:00 | Savar | 138 | 06:00 | 129 | 12:00
HaripurSBU | 141 | 04:00 | 135 | 12:00 | SevenRings | 140 | 00:00 | 132 | 18:30
Hasnabad | 140 | 01:00 | 133 | 12:00 | ShahCement | 141 | 05:00 | 133 | 12:00
Hathazari | 141 | 04:00 | 136 | 12:00 | Shahjadpur | 141 | 03:00 | 135 | 18:00
Ishurdi | 143 | 04:00 | 136 | 18:00 | Shahjibazar | 141 | 01:00 | 135 | 18:00
Jaldhaka | 134 | 05:00 | 114 | 18:00 | Shahmirpur | 140 | 06:00 | 135 | 14:00
Jamalpur | 134 | 09:00 | 118 | 00:00 | Shariatpur | 141 | 03:00 | 135 | 17:00
Jashore | 141 | 02:00 | 125 | 18:00 | Sherpur | 130 | 09:00 | 116 | 00:00
Jhenaidah | 143 | 05:00 | 120 | 18:00 | Shikalbaha | 129 | 04:00 | 124 | 13:00
Jhenaidah-230 | 144 | 04:00 | 130 | 18:00 | Shikalbaha-230 | 141 | 05:00 | 136 | 14:00
Joydebpur | 138 | 01:00 | 129 | 18:00 | Shitalakhya | 140 | 03:00 | 131 | 13:00
Joypurhat | 132 | 00:00 | 121 | 18:00 | Sholosohor | 140 | 03:00 | 135 | 13:00
Juldah | 140 | 04:00 | 135 | 13:00 | Shyampur | 141 | 00:00 | 132 | 12:00
Kabirpur | 139 | 03:00 | 126 | 15:00 | Shyampur-230 | 143 | 00:00 | 133 | 12:00
Kachua | 142 | 05:00 | 137 | 14:00 | Siddhirganj | 140 | 01:00 | 134 | 12:00
Kaliakoir | 143 | 04:00 | 134 | 15:00 | Sirajganj | 136 | 00:00 | 129 | 18:00
Kallyanpur | 140 | 01:00 | 131 | 12:00 | Sonargaon | 140 | 06:00 | 135 | 12:00
Kalurghat | 141 | 06:00 | 135 | 14:00 | Sreemongol | 140 | 06:00 | 134 | 18:00
Kamrangirchar | 139 | 00:00 | 128 | 12:00 | Sreepur | 139 | 00:00 | 132 | 18:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 139 | 00:00 | 128 | 13:00
Kasba | 140 | 04:00 | 134 | 18:00 | SSM | 142 | 00:00 | 138 | 14:00
Kazla | 141 | 00:00 | 131 | 13:00 | Sunamganj | 133 | 08:00 | 128 | 18:00
Keranigonj | 140 | 00:00 | 128 | 13:00 | Sylhet | 136 | 06:00 | 131 | 18:30
Khagrachori | 140 | 04:00 | 134 | 14:00 | Sylhet-132 | 135 | 04:00 | 132 | 13:00
Khulna | 140 | 06:00 | 129 | 18:00 | Tangail | 134 | 05:00 | 128 | 12:00
Khulna(S) | 141 | 03:00 | 131 | 18:00 | Taraganj | 134 | 04:00 | 116 | 18:00
Khulshi | 138 | 05:00 | 132 | 16:00 | Tasnim | 140 | 06:00 | 135 | 12:00
Kishoreganj | 136 | 00:00 | 127 | 18:00 | Thakurgaon | 137 | 19:30 | 119 | 18:00
Kodda | 138 | 18:00 | 126 | 15:00 | TK | 140 | 05:00 | 135 | 13:00
KSRM | 141 | 04:00 | 134 | 14:00 | Tongi | 137 | 04:00 | 130 | 11:00
Kulaura | 140 | 01:00 | 136 | 12:00 | Ullahpara | 139 | 04:00 | 130 | 18:00
Kurigram | 133 | 04:00 | 117 | 18:00 | Ullon | 136 | 04:00 | 128 | 12:00
Kushtia | 138 | 04:00 | 130 | 18:00 | Uttara | 137 | 02:00 | 127 | 14:00
Laksam | 168 | 17:00 | 137 | 13:00 | UttaraNew | 137 | 03:00 | 127 | 15:00
Lakshmipur | 137 | 04:00 | 132 | 13:00 | Zigatola | 140 | 00:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division