## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-12-2025 | [28 empty] | Date: | 07-12-2025 | [28 empty] | Date: | 07-12-2025 | [28 empty] | Date: | 07-12-2025 | [28 empty] | Date: | 07-12-2025 | [17 empty] | Date: | 07-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 515 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 190 | 0 | 0 | 111 | 0 | 0 | 13 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 16 | 158 | 0 | 8 | 8 | 74 | 0 | 0 | 0 | 4126 | 740 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537 | 0 | 0 | 0 | 1129.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 305 | 950 | 0 | 4845.41 | 8971.41 | 99.36
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 195 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 94 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 41 | 30 | 0 | 16 | 159 | 0 | 8 | 8 | 92 | 0 | 0 | 0 | 4018 | 845 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 0 | 0 | 912.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 306 | 850 | 0 | 4466.84 | 8484.84 | 99.35
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 200 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 20 | 0 | 16 | 159 | 0 | 8 | 0 | 92 | 0 | 0 | 0 | 3921 | 752 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 855.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 306 | 750 | 0 | 4157.11 | 8078.11 | 99.35
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 206 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 205 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 3895 | 556 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 825.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 306 | 700 | 0 | 3884.37 | 7779.37 | 99.35
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 205 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 3839 | 468 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 834.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 256 | 665 | 0 | 3720.63 | 7559.63 | 99.35
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 210 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 201 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 3822 | 468 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 837.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 257 | 605 | 0 | 3641.86 | 7463.86 | 99.34
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 210 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 455 | 0 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 205 | 10 | 0 | 110 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 20 | 0 | 16 | 158 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 4021 | 468 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 306 | 696 | 0 | 3855 | 7876 | 99.34
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 280 | 0 | 0 | 2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0.1 | 40 | 0 | 39 | 210 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 563 | 2 | 0 | 0 | 360 | 0 | 280 | 51 | 0 | 214 | 20 | 0 | 111 | 0 | 0 | 11 | 0 | 84 | 0 | 5 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 16 | 158 | 0 | 7 | 16 | 94 | 0 | 1.7 | 0 | 4302.8 | 469 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 460 | 0 | 0 | 0 | 934.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.68 | 5 | 0 | 0 | 2.83 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 11 | 0.02 | 0 | 0 | 115 | 220 | 0 | 403 | 850 | 0 | 4316.9 | 8619.7 | 99.34
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 12 | 0.71 | 40 | 0 | 15 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 9 | 0 | 0 | 260 | 0 | 280 | 51 | 0 | 190 | 20 | 0 | 112 | 3 | 0 | 11 | 0 | 96 | 0 | 25 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 3 | 16 | 0 | 79 | 30 | 0 | 16 | 158 | 0 | 18 | 35 | 63 | 0 | 11 | 0 | 4337.71 | 657 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 566 | 0 | 0 | 0 | 1156.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.86 | 21 | 0 | 0 | 9.42 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.89 | 0 | 0 | 30 | 7 | 0 | 0 | 0 | 0 | 1 | 29 | 0.13 | 0 | 0 | 120 | 220 | 0 | 505 | 990 | 0 | 5259.08 | 9596.79 | 99.34
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 451 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 2.15 | 40 | 0 | 6 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 14 | 0 | 0 | 235 | 0 | 280 | 51 | 0 | 194 | 20 | 0 | 111 | 16 | 0 | 11 | 0 | 98 | 0 | 46 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 7 | 16 | 0 | 79 | 30 | 0 | 16 | 158 | 0 | 18 | 35 | 64 | 1 | 28.05 | 0 | 4311.2 | 657 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 596 | 0 | 0 | 0 | 1177.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.87 | 48 | 0 | 0 | 31 | 191 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 2.63 | 0 | 0 | 35 | 14 | 0 | 0 | 0 | 0 | 3.3 | 84 | 0.28 | 0 | 0 | 120 | 220 | 0 | 505 | 1010 | 0 | 5395.42 | 9706.62 | 99.34
10:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 23 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 2.87 | 40 | 0 | 6 | 210 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 18 | 0 | 0 | 393 | 0 | 0 | 51 | 0 | 198 | 20 | 0 | 109 | 0 | 0 | 11 | 0 | 98 | 0 | 57 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 9 | 16 | 0 | 79 | 30 | 0 | 16 | 158 | 0 | 18 | 16 | 64 | 2 | 38.48 | 0 | 4118.35 | 657 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 584 | 0 | 0 | 0 | 1167.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.07 | 72 | 0 | 0 | 42.9 | 169 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 3.58 | 0 | 0 | 17 | 21 | 0 | 0 | 0 | 0 | 4.1 | 125 | 0.4 | 0 | 0 | 115 | 220 | 0 | 408 | 970 | 0 | 5123.14 | 9241.49 | 99.33
11:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445 | 0 | 0 | 280 | 0 | 0 | 26 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 3.28 | 40 | 0 | 7 | 210 | 0 | 0 | 0 | 0 | 1 | 224 | 0 | 0 | 0 | 612 | 19 | 0 | 5 | 393 | 0 | 0 | 43 | 2 | 213 | 31 | 0 | 108 | 0 | 0 | 14 | 0 | 102 | 0 | 65 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 82 | 30 | 0 | 15 | 159 | 0 | 8 | 8 | 64 | 2 | 43.79 | 0 | 4255.07 | 657 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 555 | 0 | 0 | 0 | 1170.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.27 | 87 | 0 | 0 | 49.22 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.31 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 4.6 | 146 | 0.45 | 0 | 0 | 115 | 220 | 0 | 405 | 950 | 0 | 5196.61 | 9451.68 | 99.33
12:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 54 | 17 | 1 | 0 | 135 | 0 | 12 | 35 | 0 | 0 | 0 | 470 | 0 | 0 | 280 | 0 | 0 | 27 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 3.35 | 40 | 0 | 7 | 210 | 0 | 0 | 2 | 0 | 47 | 223 | 0 | 0 | 0 | 580 | 19 | 10 | 26 | 393 | 0 | 0 | 43 | 5 | 205 | 38 | 0 | 105 | 27 | 0 | 14 | 0 | 118 | 0 | 66 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 82 | 30 | 0 | 15 | 159 | 0 | 8 | 12 | 66 | 2 | 46 | 0 | 4634.35 | 704 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 580 | 0 | 0 | 0 | 1177.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.08 | 91 | 0 | 0 | 48.03 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.32 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 5.2 | 156 | 0.51 | 0 | 0 | 115 | 220 | 0 | 501 | 1006 | 0 | 5449.56 | 10083.91 | 99.33
13:00 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 17 | 14 | 0 | 210 | 0 | 35 | 45 | 0 | 0 | 0 | 450 | 0 | 0 | 250 | 0 | 0 | 26 | 0 | 0 | 14 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 12 | 3.11 | 40 | 11 | 12 | 354 | 0 | 0 | 41 | 0 | 51 | 226 | 0 | 0 | 0 | 580 | 18 | 50 | 70 | 355 | 0 | 0 | 43 | 14 | 199 | 39 | 1 | 105 | 51 | 0 | 14 | 0 | 114 | 0 | 59 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 10 | 16 | 0 | 84 | 30 | 0 | 15 | 159 | 0 | 19 | 24 | 61 | 2 | 42.66 | 0 | 4974.77 | 750 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 580 | 0 | 0 | 0 | 1179.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.95 | 82 | 0 | 0 | 41.29 | 190 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 4.12 | 0 | 0 | 35 | 26 | 34 | 0 | 0 | 0 | 5.1 | 135 | 0.45 | 0 | 0 | 115 | 220 | 0 | 501 | 1020 | 0 | 5461.97 | 10436.74 | 99.32
14:00 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 17 | 19 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 451 | 0 | 0 | 250 | 0 | 0 | 20 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 12 | 2.51 | 40 | 0 | 12 | 354 | 0 | 0 | 6 | 0 | 17 | 226 | 0 | 0 | 0 | 580 | 15 | 85 | 71 | 340 | 0 | 0 | 43 | 35 | 205 | 39 | 14 | 105 | 17 | 0 | 14 | 0 | 116 | 0 | 48 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 8 | 16 | 0 | 84 | 30 | 0 | 15 | 159 | 0 | 19 | 8 | 60 | 1 | 35.63 | 0 | 4590.14 | 843 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 580 | 0 | 0 | 0 | 1110.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.04 | 67 | 0 | 0 | 39.68 | 175 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 3.31 | 0 | 0 | 35 | 21 | 12 | 0 | 0 | 0 | 4 | 102 | 0.35 | 0 | 0 | 115 | 220 | 0 | 463 | 1020 | 0 | 5387.24 | 9977.38 | 99.32
15:00 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 17 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 328 | 0 | 0 | 15 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 12 | 1.69 | 40 | 0 | 6 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 505 | 11 | 150 | 71 | 370 | 0 | 0 | 43 | 35 | 192 | 38 | 0 | 106 | 0 | 0 | 14 | 0 | 114 | 0 | 32 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 5 | 16 | 0 | 84 | 30 | 0 | 15 | 158 | 0 | 19 | 8 | 60 | 1 | 24.64 | 0 | 4521.33 | 843 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 728 | 0 | 0 | 0 | 970.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.92 | 43 | 0 | 0 | 19.11 | 174 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 1.57 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 2.7 | 85 | 0.25 | 0 | 0 | 115 | 180 | 0 | 250 | 950 | 0 | 5025.21 | 9546.54 | 99.32
16:00 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 54 | 17 | 18 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 330 | 0 | 0 | 6 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 12 | 0.75 | 40 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 500 | 6 | 150 | 75 | 393 | 0 | 0 | 43 | 35 | 205 | 39 | 0 | 106 | 0 | 0 | 14 | 0 | 108 | 0 | 14 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 2 | 16 | 0 | 84 | 30 | 0 | 15 | 158 | 0 | 19 | 8 | 64 | 0 | 9.2 | 0 | 4494.95 | 844 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 840 | 0 | 0 | 0 | 867.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.75 | 17 | 0 | 0 | 7.28 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.55 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 29 | 0.1 | 0 | 0 | 115 | 220 | 0 | 250 | 900 | 0 | 4963.54 | 9458.49 | 99.31
17:00 | 0 | 10 | 43 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 54 | 17 | 60 | 0 | 95 | 0 | 25 | 116 | 0 | 0 | 0 | 326 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 13 | 354 | 0 | 0 | 11 | 0 | 14 | 226 | 0 | 0 | 0 | 565 | 0 | 150 | 71 | 340 | 0 | 0 | 43 | 36 | 188 | 39 | 0 | 108 | 18 | 3 | 14 | 0 | 106 | 0 | 1 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 20 | 0 | 84 | 30 | 0 | 15 | 158 | 0 | 19 | 56 | 64 | 0 | 0.26 | 4 | 4795.26 | 844 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 952 | 0 | 0 | 0 | 1228.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 0 | 0 | 0 | 0.46 | 182 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0.05 | 0 | 0 | 35 | 0 | 10 | 0 | 0 | 0 | 0.1 | 3 | 0.01 | 0 | 0 | 100 | 180 | 0 | 400 | 980 | 0 | 5508.01 | 10303.27 | 99.31
18:00 | 0 | 34 | 43 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 44 | 17 | 62 | 0 | 60 | 0 | 35 | 152 | 0 | 0 | 0 | 403 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 150 | 81 | 393 | 0 | 80 | 51 | 35 | 203 | 39 | 0 | 108 | 0 | 6 | 14 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 15 | 158 | 0 | 19 | 56 | 62 | 0 | 0 | 12 | 5093 | 843 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1420.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 65 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 510 | 1050 | 0 | 6242.61 | 11335.61 | 99.31
19:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 62 | 0 | 15 | 0 | 35 | 162 | 0 | 0 | 0 | 406 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 0 | 150 | 16 | 393 | 0 | 18 | 51 | 0 | 197 | 36 | 0 | 109 | 0 | 9 | 14 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 15 | 157 | 0 | 19 | 56 | 62 | 0 | 0 | 0 | 4758 | 843 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 1354.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 35 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 400 | 1070 | 0 | 6022.64 | 10780.64 | 99.3
19:30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 62 | 0 | 0 | 0 | 35 | 108 | 0 | 0 | 0 | 420 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 580 | 0 | 150 | 16 | 360 | 0 | 18 | 51 | 0 | 207 | 40 | 0 | 109 | 0 | 0 | 18 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 15 | 157 | 0 | 19 | 56 | 65 | 0 | 0 | 0 | 4690 | 843 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 1327.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 400 | 1080 | 0 | 5976.15 | 10666.15 | 99.3
20:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 62 | 0 | 0 | 0 | 35 | 98 | 0 | 0 | 0 | 405 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 580 | 0 | 150 | 16 | 340 | 0 | 18 | 51 | 0 | 194 | 40 | 0 | 109 | 0 | 0 | 18 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 84 | 30 | 0 | 15 | 157 | 0 | 19 | 58 | 67 | 0 | 0 | 0 | 4636 | 843 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 0 | 0 | 0 | 1332.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 400 | 1080 | 0 | 5997.16 | 10633.16 | 99.3
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 72 | 0 | 0 | 0 | 405 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 585 | 0 | 0 | 10 | 320 | 0 | 33 | 51 | 0 | 204 | 0 | 0 | 110 | 0 | 0 | 18 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 85 | 30 | 0 | 15 | 157 | 0 | 19 | 58 | 67 | 0 | 0 | 0 | 4352 | 843 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 350 | 1080 | 0 | 5925 | 10277 | 99.3
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 393 | 0 | 47 | 51 | 0 | 196 | 0 | 0 | 110 | 0 | 0 | 18 | 0 | 106 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 85 | 30 | 0 | 17 | 157 | 0 | 19 | 57 | 65 | 0 | 0 | 0 | 4289 | 844 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1131 | 0 | 0 | 0 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 250 | 1080 | 0 | 5671 | 9960 | 99.29
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 385 | 0 | 62 | 51 | 0 | 188 | 0 | 0 | 109 | 0 | 0 | 18 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 84 | 30 | 0 | 17 | 157 | 0 | 19 | 16 | 65 | 0 | 0 | 0 | 4217.2 | 843 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 0 | 0 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 254 | 1000 | 0 | 5274 | 9491.2 | 99.29
Total KWH | 0 | 66240 | 371520 | 0 | 0 | 0 | 0 | 0 | 8182800 | 0 | 0 | 368280 | 433800 | 382032 | 0 | 493286 | 0 | 341841 | 691200 | 0 | 0 | 0 | 9963272 | 0 | 6857 | 7137112 | 0 | 0 | 149433 | 7200 | 235200 | 481320 | 0 | 0 | 13800 | 0 | 0 | 0 | 362880 | 0 | 0 | 0 | 12480 | 120960 | 20879 | 980000 | 28400 | 611040 | 6763636.36 | 0 | 0 | 92160 | 0 | 214109 | 5155630 | 0 | 0 | 0 | 12976362 | 128385 | 1125745 | 518545 | 8143000 | 0 | 2902000 | 1216260 | 210240 | 4855000 | 485208 | 29760 | 2516849 | 235200 | 21840 | 311030 | 0 | 2401920 | 0 | 418600 | 0 | 7522500 | 0 | 5037000 | 0 | 719280 | 0 | 66009 | 426504 | 0 | 1602240 | 707328 | 0 | 394000 | 3685630 | 0 | 324000 | 566400 | 1706880 | 11200 | 282750 | 26640 | 105261672.36 | 17440727 | 5695200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439920 | 17338182 | 0 | 0 | 0 | 25918909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548449 | 0 | 0 | 289488 | 4413909 | 0 | 0 | 0 | 0 | 0 | 9340509 | 0 | 25080 | 0 | 0 | 360284 | 165698 | 201811 | 0 | 0 | 0 | 30901.8 | 901440 | 2989 | 0 | 0 | 2757000 | 5352969 | 0 | 8811535 | 22900363.64 | 0 | 122935364.44 | 228197036.8

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-12-2025 | during | 08-12-2025 | during | 08-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 354 | 332 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 44 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 12 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 20 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 43 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 135 | 60 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 1 | 62 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 152 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 470 | 403 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0.01 | 0.01 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1433 | 1559 | 5765.15 | 5734.15 | 2654.38 | 2632.38
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 2 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 226 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 47 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 48 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 20 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.35 | 0 | 3.35 | 0 | 3.35 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 0 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 13 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 210 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1147.35 | 1265 | 2582.07 | 2573.72 | 2086.85 | 2094.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 205 | 203 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 80 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 39 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 35 | 55 | 55 | 55 | 55 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 81 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 108 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 27 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 118 | 110 | 160 | 160 | 128 | 128 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 6 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1050 | 1270 | 2432.21 | 2372.21 | 2224.21 | 2173.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-12-2025 | during | 08-12-2025 | during | 08-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 66 | 62 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 12 | 56 | 20 | 20 | 20 | 20 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 19 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46 | 0 | 47.8 | 0 | 47.8 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 134 | 149 | 363.8 | 314 | 316.3 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 158 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 207 | 207 | 195 | 195 | 195 | 195 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 870 | 850 | 885 | 885 | 851 | 851
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 704 | 843 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 68 | 300 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 580 | 1055 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1422 | 2198 | 2024 | 1942 | 1599.1 | 1517.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 501 | 510 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 1006 | 1050 | 1085.32 | 1085.32 | 1025.32 | 1025.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant shutdown as per NLDC requirement.
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1842.51 | 1895 | 1993.32 | 1993.32 | 1493.32 | 1493.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 53.08 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 207 | 186 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.32 | 0 | 4.9 | 0 | 4.9 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1177.42 | 1420.61 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.03 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 91 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1994.85 | 2020.61 | 3076.77 | 2910.87 | 2462.11 | 2296.21
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 64 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 65 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 156 | 0 | 164.79 | 0 | 164.79 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 190.2 | 129 | 441.99 | 262 | 427.99 | 228
System Total |  |  |  |  | 28823.2 | 28216.665 | 10083.91 | 11335.61 | 19564.31 | 18987.27 | 14115.26 | 13552.22
Forecast Scenario (08-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9200 |  | 0 |  | 9200
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 8090 |  | 0 |  | 8090
|  |  |  | 3:00 | 7800 |  | 0 |  | 7800
|  |  |  | 4:00 | 7590 |  | 0 |  | 7590
|  |  |  | 5:00 | 7550 |  | 0 |  | 7550
|  |  |  | 6:00 | 7950 |  | 0 |  | 7950
|  |  |  | 7:00 | 8700 |  | 0 |  | 8700
|  |  |  | 8:00 | 9400 |  | 0 |  | 9400
|  |  |  | 9:00 | 9570 |  | 0 |  | 9570
|  |  |  | 10:00 | 9370 |  | 0 |  | 9370
|  |  |  | 11:00 | 9640 |  | 0 |  | 9640
|  |  |  | 12:00 | 10180 |  | 0 |  | 10180
|  |  |  | 13:00 | 10510 |  | 0 |  | 10510
|  |  |  | 14:00 | 10120 |  | 0 |  | 10120
|  |  |  | 15:00 | 9810 |  | 0 |  | 9810
|  |  |  | 16:00 | 9670 |  | 0 |  | 9670
|  |  |  | 17:00 | 10160 |  | 0 |  | 10160
|  |  |  | 18:00 | 11200 |  | 0 |  | 11200
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 10830 |  | 0 |  | 10830
|  |  |  | 19:30 | 10690 |  | 0 |  | 10690
|  |  |  | 20:00 | 10590 |  | 0 |  | 10590
|  |  |  | 21:00 | 10370 |  | 0 |  | 10370
|  |  |  | 22:00 | 10070 |  | 0 |  | 10070
|  |  |  | 23:00 | 9602 |  | 0 |  | 9602
Probable Maximum Temperature: |  |  | 25.50°C
Probable Maximum Demand at Day Peak: |  |  | 10180.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 226.472 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:28 hrs on 08-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10083.91 | MW | 12:00 Hr. | Energy Generated |  |  | 228.197 |  | MKWHr.
| Day Peak Demand |  |  | 10083.91 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11335.61 | MW | 18:00 Hr. | Energy Demand |  |  | 228.197 |  | MKWHr.
| Evening Peak Demand |  |  | 11335.61 | MW | 18:00 Hr. | Maximum Temperature |  |  | 26.3 |  | °C
| Minimum Generation of the Day |  |  | 7463.86 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 751.53 |  | MMCFD
| Maximum Generation of the Day |  |  | 11335.61 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.4868 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.9997 | 0 | 3.1623 | 0 | 0 | 0.14943 | 0 | 0 | 29.3114 | Gas | 102.2855 | Gas | 360585992.4
| Chattogram Zone |  |  | 5.7667 | 19.74 | 0.48191 | 0 | 0.98 | 0.14926 | 0 | 0.36288 | 27.4807 | Coal | 68.7901 | Coal | 439175435.6564
| Cumilla Zone |  |  | 21.1581 | 0 | 1.4125 | 0 | 0 | 0.4186 | 2.4019 | 0 | 25.3912 | HFO | 6.5358 | HFO | 112044417.66
| Mymensingh Zone |  |  | 1.7069 | 0 | 0.91704 | 0 | 0 | 0.29395 | 0 | 0 | 2.9179 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 20.0945 | 0 | 0 | 0 | 0 | 0.066009 | 0 | 0 | 20.1605 | Hydro | 0.98 | Hydro | 98000
| Khulna Zone |  |  | 5.6952 | 17.3382 | 0 | 0 | 0 | 0.43992 | 17.4407 | 0 | 40.914 | Solar | 3.4812 | Solar | 55612284.908
| Barishal Zone |  |  | 8.11 | 31.7119 | 0 | 0 | 0 | 0.002989 | 0 | 0 | 39.8249 | Import | 45.7616 | Import | 279224389.9
| Rajshahi Zone |  |  | 13.7544 | 0 | 0 | 0 | 0 | 0.86302 | 25.9189 | 0 | 40.5363 | Wind | 0.36288 | Wind | 5337964.8
| Rangpur Zone |  |  | 0 | 0 | 0.5621 | 0 | 0 | 1.098 | 0 | 0 | 1.6601
| Total |  |  | 102.2855 | 68.7901 | 6.5358 | 0 | 0.98 | 3.4812 | 45.7616 | 0.36288 | 228.197
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 360585992.4 |  | Hydro | 98000
|  |  |  | Coal | 439175435.6564 |  | Solar | 55612284.908
|  |  |  | HFO | 112044417.66 |  | Import | 279224389.9
|  |  |  | HSD | 0 |  | Wind | 5337964.8
[5 empty] | Total: | 125,20,78,485 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.4407 | Peak Hr Flow | 843.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49066127.28 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.9189 | Peak Hr Flow | 1420.61 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2743 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4019 | Peak Hr Flow | 110.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2773 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.7616 | Peak Hr Flow | 2373.61 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4178
|  |  |  | Chattogram |  | 0 |  | 1248
|  |  |  | Cumilla |  | 0 |  | 932
|  |  |  | Mymensingh |  | 0 |  | 878
|  |  |  | Sylhet |  | 0 |  | 399
|  |  |  | Khulna |  | 0 |  | 1264
|  |  |  | Barishal |  | 0 |  | 307
|  |  |  | Rajshahi |  | 0 |  | 1001
|  |  |  | Rangpur |  | 0 |  | 795
|  |  |  | Total |  | 0 |  | 11002
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 15:10 | Chhatak 132/33kV S/S Bus-B Scheduled S/D Due to Annual Maintanance
|  | 08:10 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 08:20 | 17:59 | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to Annual maintenance
| 08:20 | 17:59 | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to Annual maintenance
| 08:20 | 17:59 | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to Annual maintenance
| 08:21 | 16:55 | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to annul
maintenance
| 08:34 | 15:45 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to Annual
maintenance
| 08:37 | 17:10 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
Maintenance Doh-Cox Ckt-2 (Dohazari Side) and from Dohazari 132/33kV end Due to Annual
Maintenance
| 08:41 | 18:31 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Scheduled S/D Due to Scheduled shutdown
| 08:41 | 18:23 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT Scheduled S/D Due to Scheduled shutdown
| 08:51 | 18:22 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual maintenance and from Bogura 400/230kV end Due to Annual Maintenance
| 08:54 | 16:15 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end Due to annual
maintenance and from Natore 132/33kV end Due to Annual maintenance work
| 08:59 | 17:36 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to Annual
maintenance work (Dead line checking).
| 09:02 | 16:30 | Rahanpur 132/33kV S/S Rahanpur-2 Scheduled S/D
| 09:03 | 16:28 | Rahanpur 400/132kV S/S Rahanpur-Chowdala 132 KV Line Ckt-02 Scheduled S/D Due to Due to
anual maintenance work.
| 09:07 | 17:27 | UttaraNew 132/33kV S/S GT-01 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 9.0MW load
interrup.
| 09:09 | 16:51 | Chuadanga-Jhenaidah 132 kV Ckt-1 Scheduled S/D from Chuadanga 132/33kV end Due to Annual
Maintenance. and from Jhenaidah 230/132kV end Due to Annual maintanance
| 09:09 | 16:38 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Scheduled S/D Due to Annual Maintenance
| 09:11 | 16:29 | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D Due to Annual Maintenance Work
| 09:12 | 16:28 | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D Due to Annual Maintenance Work
| 09:12 |  | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 LT Scheduled S/D Due to Yearly maintenance
| 09:13 | 15:57 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 HT Scheduled S/D Due to Annual Maintenance
| 09:13 |  | Rampur 230/132/33 S/S Halishahar-2 Scheduled S/D Due to Annual maintenance of Halishahar
Ckt-02 line
| 09:14 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- Plant
| 09:17 | 16:23 | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 HT Scheduled S/D
| 09:17 | 16:24 | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 LT Scheduled S/D Due to Annual Maintenance.
| 09:18 | 16:29 | Halishahar-Khulshi 132kV Ckt-2 Scheduled S/D from Halishahar 132/33kV end.
| 09:19 | 15:00 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) HT Scheduled S/D Due to Annual meainteance
| 09:20 | 15:01 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) LT Scheduled S/D Due to Annual Meainteance
| 09:24 | 09:29 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Sudden temperature rise in TR-01(B)
LT side
| 09:24 | 09:29 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Sudden temperature rise in TR-01(B)
LT side
| 09:24 |  | Chowmuhani-Ramganj 132 kV Ckt-2 Project Work S/D from Chowmuhani 132/33kV end Due to
Project work shutdown for 132kV CRP panel replacement work.
| 09:46 | 13:49 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance (Tan-Delta test) of
TR-02
| 09:47 | 13:48 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintenance (Tan-Delta test) of
TR-02
| 09:55 | 10:54 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to T-1 Bus DS Cleaning
| 09:55 | 10:54 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to T-1 Bus DS Cleaning
| 09:56 | 16:07 | Hathazari-Raozan 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
maintenance
| 10:00 | 16:41 | Beanibazar 132/33kV S/S 132 KV BUS-1 Scheduled S/D Due to Annual Maintenance
| 10:01 |  | Bheramara 410 MW CCPP Tripped with remarks:- ST
| 10:05 | 16:03 | Gulshan 132/33kV S/S MT-1 HT Scheduled S/D Due to Annual Maintenance
| 10:05 | 16:07 | Gulshan 132/33kV S/S MT-1 LT Scheduled S/D Due to Annual Maintenance
| 10:10 |  | Bheramara 410 MW CCPP Synchronized
| 10:12 | 15:38 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D
| 10:12 | 15:38 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D
| 10:55 | 13:09 | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to 132 kv T-2 DS Cleaning
| 10:55 | 13:09 | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to 132 kv T-2 DS Cleaning
| 11:16 |  | Kaliakoir 400/230/132kV S/S 230kV Bus 2 Forced S/D Due to Loop open To Separate 230/132kV
Transformer from 230Kv bUS-2 .
| 12:00 |  | Day Peak Generation: 10082 MW.
| 12:05 | 17:26 | Natore 132/33kV S/S TR-3 (425 T) LT Scheduled S/D Due to Annual maintenance work
| 12:05 | 17:25 | Natore 132/33kV S/S TR-3 (425 T) HT Scheduled S/D Due to Annual maintenance work
|  | 12:40 | Sherpur 132/33kV S/S Transformer- 01 HT is restored.
|  | 12:41 | Sherpur 132/33kV S/S Transformer- 01 LT is restored.
|  | 12:46 | Meghnaghat 400/230kV S/S ATR - 2 LT is restored.
| 12:56 | 17:43 | Meghnaghat 400/230kV S/S ATR-1 LT Scheduled S/D
| 12:58 | 17:42 | Meghnaghat 400/230kV S/S ATR-1 HT Scheduled S/D
|  | 13:07 | Chauddagram-Feni 132 kV Ckt-2 is restored.
| 13:27 | 15:37 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Feni ckt -3 S/D
taken by Feni 230Kv SS work purpose and from Feni 230/132kV end Due to XLPE Cable
Earthing and clamping works
| 13:45 | 15:07 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Shutdown by
Chhatak Grid Sub-Station
| 13:55 |  | Bheramara 410 MW CCPP Synchronized with remarks:- ST
| 14:09 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 15:33 |  | Ghorashal 230kV bus-4 was charged on for the first time after the earthquake of 21st
November through Ashuganj (south)-Ghorashal 230kV ckt-1.
|  | 16:38 | Barishal-Barishal(N) 132 kV Ckt-1 is restored.
|  | 16:47 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 16:47 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 17:08 | Bhulta-Rampura 230 kV Ckt-1 is restored.
|  | 17:09 | Bhulta-Rampura 230 kV Ckt-2 is restored.
|  | 17:18 | Bhulta 400/230kV S/S ATR-02 HT is restored.
|  | 17:19 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) HT is restored.
|  | 17:30 | Fenchuganj- Fenchuganj-Khusiara 16 230kV Ckt-1 is restored.
| 17:31 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
|  | 17:40 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) LT is restored.
| 18:00 |  | Chandpur 132/33kV S/S 402T (T-01) LT Forced S/D
| 18:00 |  | Evening peak Generation is 11335 MW
|  | 18:13 | Rangpur 132/33kV S/S Rangpur-GTPS is restored.
|  | 19:07 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
|  | 19:07 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
| 05:00 |  | Minimum Generation is 7511 MW.
| 06:23 |  | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end. and from Khulna
(C) end Due to Due to piling work
| 07:01 |  | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end.
| 07:03 |  | Ghorashal - Ashuganj (S) 230 kv L-2 was shut down (taken by Ghorashal P.P)
| 07:03 |  | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
| 07:16 |  | Barishal-Barishal(N) 132 kV Ckt-2 Scheduled S/D from Barishal 132/33kV end Due to Annual
Maintenance work and from Barishal 230/132kV end Due to Annual Maintenance
| 07:21 |  | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to Annual maintenance
| 07:21 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to Annual maintenance
| 07:36 |  | Bhulta 400/230kV S/S ATR-02 HT Scheduled S/D
| 07:38 |  | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance and from Coxsbazar 132/33kV end Due to Annual maintenance Doh-Cox Ckt-2
(Cox's Bazar Side)
| 07:42 |  | Gopalganj 132/33kV S/S T1 HT Project Work S/D Due to Ccc project work | [7 empty] | 8.0MW load
interrup.
| 07:42 |  | Gopalganj 132/33kV S/S T1 LT Project Work S/D Due to Ccc project work | [7 empty] | 8.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 332 | 8182800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7137112 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44 | 368280 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 341841 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 6857 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 235200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 481320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 43 | 371520 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 60 | 493286 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 62 | 382032 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 66240 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 152 | 691200 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 149433 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 433800 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 403 | 9963272 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 7200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1559 | 29311393
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128385 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 92160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 980000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5155630 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 214109 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 12480 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 611040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 28400 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 120960 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 13800 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12976362 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 362880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 6763636.36 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1265 | 27480721.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 203 | 4855000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 80 | 2902000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8143000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 485208 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 35 | 210240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 81 | 518545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1216260 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1125745 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2516849 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 235200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 110 | 2401920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 311030 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 6 | 21840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 29760 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 418600 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1270 | 25391197
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 62 | 1706880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 56 | 566400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 324000 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 282750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 26640 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 149 | 2917870
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 66009 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719280 | GT#4 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 707328 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1602240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3685630 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 394000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 426504 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7522500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5037000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 850 | 20160491
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 843 | 17440727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 300 | 5695200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 439920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1055 | 17338182 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2198 | 40914029
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 510 | 8811535 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2757000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1050 | 22900363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5352969 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2989 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1895 | 39824856.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4413909 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9340509 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1420.61 | 25918909 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 289488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 548449 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2020.61 | 40536344
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 64 | 201811 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30901.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 65 | 360284 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 165698 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 901440 | -
Rangpur Area Total |  |  |  |  | 950 | 129 | 1660134.8
Eastern Grid Total |  |  |  |  | 17395.105 | 5093 | 105261672.36
Western Grid Total |  |  |  |  | 10821.56 | 6242.61 | 122935364.44
National Grid Total |  |  |  |  | 28216.665 | 11335.61 | 228197036.8
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7635.49 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3367.5 | MW
i) Dhaka area |  |  | 4178.49 |  | MW | i) Khulna area |  |  |  | 1264 | MW
ii) Chattogram area |  |  | 1248 |  | MW | ii) Barishal area |  |  |  | 307.3 | MW
iii) Cumilla area |  |  | 932 |  | MW | iii) Rajshahi area |  |  |  | 1001.2 | MW
iv) Mymensingh area |  |  | 878 |  | MW | iv) Rangpur area |  |  |  | 795 | MW
v) Sylhet area |  |  | 399 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11002.99 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 56 | 18:30 | 133 | Niamatpur | 42 | 18:00
2 | AKSML | 114 | 00:00 | 68 | Ishurdi | 49 | 18:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 26 | 14:00 | 69 | Jaldhaka | 60 | 18:00 | 135 | PHP | 6 | 04:00
4 | Agargaon | 78 | 13:00 | 70 | Jamalpur | 92 | 08:00 | 136 | Pabna | 75 | 18:00
5 | Agrabad | 62 | 18:00 | 71 | Jashore | 100 | 13:00 | 137 | Palashbari | 86 | 18:00
6 | Amnura | 17 | 08:00 | 72 | Jhenaidah | 96 | 18:00 | 138 | Panchagarh | 50 | 18:00
7 | Ashuganj | 54 | 00:00 | 73 | Joydebpur | 96 | 18:00 | 139 | Patiya | 6.3 | 19:00
8 | BSRM | 202 | 15:00 | 74 | Joypurhat | 43 | 18:00 | 140 | Patuakhali | 43.4 | 21:00
9 | Bagerhat | 65 | 18:30 | 75 | Juldah | 13 | 00:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 52 | 19:30 | 76 | KSRM | 35 | 13:00 | 142 | Postogola | 45 | 12:00
11 | Bakulia | 56 | 13:00 | 77 | Kabirpur | 179 | 17:00 | 143 | Purbachal | 25 | 13:00
12 | Banani | 44 | 13:00 | 78 | Kachua | 54 | 19:00 | 144 | Purbasadipur | 107 | 18:00
13 | Bangabhaban | 13 | 10:00 | 79 | Kallyanpur | 78 | 13:00 | 145 | Rahanpur | 22 | 18:30
14 | Barapukuria | 55 | 18:00 | 80 | Kalurghat | 38 | 12:00 | 146 | Rahim | 54 | 17:00
15 | Barguna | 14 | 18:00 | 81 | Kamrangirchar | 57 | 13:00 | 147 | Rajbari | 60 | 18:00
16 | Barishal | 81 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 105 | 18:30
17 | Barishal-230 | 64 | 19:00 | 83 | Kasba | 21 | 13:00 | 149 | Rajshahi | 65 | 19:30
18 | Baroaulia | 53 | 13:00 | 84 | Kazla | 73 | 23:00 | 150 | Rajshahi-230 | 66 | 13:00
19 | Baroirhat | 52 | 18:00 | 85 | Keranigonj | 64 | 13:00 | 151 | Ramganj | 78 | 13:00
20 | Bashundhara | 145 | 13:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 0 | 00:00
21 | BashundharaCement | 8 | 19:30 | 87 | Khulna | 47 | 13:00 | 153 | Rangamati | 12 | 18:00
22 | Beanibazar | 48 | 18:00 | 88 | Khulshi | 185 | 12:00 | 154 | Rangpur | 91 | 18:00
23 | Benapole | 44 | 08:00 | 89 | Kishoreganj | 82 | 19:30 | 155 | Ruppur | 3 | 16:00
24 | Bhaluka | 127 | 18:00 | 90 | Kodda | 300 | 11:00 | 156 | SSM | 5 | 23:00
25 | Bhandaria | 36 | 21:00 | 91 | Kulaura | 24 | 18:00 | 157 | Saidpur | 89 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 49 | 18:00 | 158 | Satkhira | 85 | 18:00
27 | Bheramara(GK) | 42 | 18:00 | 93 | Kushtia | 114 | 18:00 | 159 | Satmasjid | 80 | 13:00
28 | Bhulta | 153 | 18:00 | 94 | Laksam | 20 | 18:00 | 160 | Savar | 158 | 17:00
29 | Bog-Sherpur | 56 | 08:00 | 95 | Lakshmipur | 26 | 13:00 | 161 | SevenRings | 13.74 | 01:00
30 | Bogura | 115 | 18:30 | 96 | Lalbag | 58 | 13:00 | 162 | ShahCement | 32 | 10:00
31 | Borhanuddin | 63 | 20:00 | 97 | Lalmonirhat | 48 | 18:00 | 163 | Shahjadpur | 56 | 18:30
32 | Brahmanbaria | 80 | 18:00 | 98 | MI_Cement | 8.8 | 23:00 | 164 | Shahjibazar | 77 | 18:00
33 | Cantonment | 73 | 13:00 | 99 | Madanganj | 27 | 21:00 | 165 | Shahmirpur | 38 | 18:00
34 | Chandina | 10 | 18:00 | 100 | Madaripur | 73 | 13:00 | 166 | Shariatpur | 52 | 21:00
35 | Chandpur | 48 | 18:00 | 101 | Madartek | 60 | 13:00 | 167 | Sherpur | 118 | 18:00
36 | Chandraghona | 27 | 18:00 | 102 | Madunaghat | 36 | 12:00 | 168 | Shikalbaha | 18 | 19:00
37 | Chapai | 49 | 12:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 59.9 | 13:00
38 | Charsaidpur | 31 | 00:00 | 104 | Mahasthangarh | 50 | 18:00 | 170 | Sholosohor | 37 | 18:00
39 | Chauddagram | 47 | 13:00 | 105 | Maijdee | 27 | 18:00 | 171 | Shyampur | 136 | 12:00
40 | Chhatak | 18 | 17:00 | 106 | Manikganj | 90 | 17:00 | 172 | Siddhirganj | 94 | 16:00
41 | Chowmuhani | 97 | 20:00 | 107 | Maniknagar | 46 | 13:00 | 173 | Sirajganj | 81 | 18:30
42 | Chuadanga | 73 | 18:00 | 108 | Matarbari | 35 | 18:00 | 174 | Sonargaon | 107 | 17:00
43 | Coxsbazar | 105 | 18:00 | 109 | Matuail | 59 | 13:00 | 175 | Sreemongol | 53 | 18:30
44 | Cumilla(N) | 81 | 13:00 | 110 | Metrorail_Motijheel | 30 | 19:00 | 176 | Sreepur | 94 | 12:00
45 | Cumilla(S) | 121 | 12:00 | 111 | Metrorail_Uttara | 7 | 11:00 | 177 | Srinagar | 30.36 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 86 | 15:00 | 178 | Sunamganj | 38 | 17:00
47 | Daudkandi | 104 | 18:30 | 113 | Mirpur | 106 | 14:00 | 179 | Sylhet | 41 | 18:00
48 | DhakaUniversity | 60 | 13:00 | 114 | Mirsorai | 26 | 14:00 | 180 | Sylhet-132 | 75 | 14:00
49 | Dhamrai | 96 | 16:00 | 115 | Mirzapur | 37 | 18:00 | 181 | TK | 15 | 09:00
50 | Dhanmondi | 80.2 | 13:00 | 116 | Mithapukur | 52 | 18:00 | 182 | Tangail | 120 | 18:00
51 | Dohazari | 63 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 26 | 18:00
52 | Faridpur | 111 | 18:00 | 118 | Mogbazar | 67.1 | 14:00 | 184 | Tasnim | 33 | 16:00
53 | Fatullah | 92 | 10:00 | 119 | Mongla | 32 | 18:00 | 185 | Thakurgaon | 82 | 18:00
54 | Fenchuganj | 28 | 18:00 | 120 | Motijheel | 27 | 13:00 | 186 | Tongi | 101 | 13:00
55 | Feni | 74 | 18:00 | 121 | Muktagacha | 26 | 08:00 | 187 | Ullahpara | 26 | 18:00
56 | GPH | 84 | 09:00 | 122 | Munshiganj | 76 | 13:00 | 188 | Ullon | 52 | 13:00
57 | Ghatail | 60 | 18:00 | 123 | Muradnagar | 23 | 18:30 | 189 | Uttara | 57 | 12:00
58 | Ghorashal | N/A | N/A | 124 | Mymensingh | 127 | 20:00 | 190 | UttaraNew | 13 | 13:00
59 | Ghorashal-230 | 85 | 21:00 | 125 | Naogaon | 89 | 18:30 | 191 | Zigatola | 50 | 14:00
60 | Goalpara | 33 | 13:00 | 126 | Narail | 42 | 18:00
61 | Gollamari | 70 | 13:00 | 127 | Narinda | 56 | 13:00
62 | Gopalganj | 75 | 18:00 | 128 | Narshingdi | 133 | 18:30
63 | Gulshan | 76 | 13:00 | 129 | Natore | 99 | 18:00
64 | Halishahar | 53 | 19:30 | 130 | Nawabganj | 28.2 | 13:00
65 | HaripurSBU | 156 | 10:00 | 131 | Netrakona | 104 | 18:00
66 | Hasnabad | 74 | 12:00 | 132 | New | 60 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8971.41 | 0 |  | 8971.41
1:00 | 8484.84 | 0 |  | 8484.84
2:00 | 8078.11 | 0 |  | 8078.11
3:00 | 7779.37 | 0 |  | 7779.37
4:00 | 7559.63 | 0 |  | 7559.63
5:00 | 7463.86 | 0 |  | 7463.86
6:00 | 7876 | 0 |  | 7876
7:00 | 8619.7 | 0 |  | 8619.7
8:00 | 9596.79 | 0 |  | 9596.79
9:00 | 9706.62 | 0 |  | 9706.62
10:00 | 9241.49 | 0 |  | 9241.49
11:00 | 9451.68 | 0 |  | 9451.68
12:00 | 10083.91 | 0 |  | 10083.91
13:00 | 10436.74 | 0 |  | 10436.74
14:00 | 9977.38 | 0 |  | 9977.38
15:00 | 9546.54 | 0 |  | 9546.54
16:00 | 9458.49 | 0 |  | 9458.49
17:00 | 10303.27 | 0 |  | 10303.27
18:00 | 11335.61 | 0 |  | 11335.61
19:00 | 10780.64 | 0 |  | 10780.64
19:30 | 10666.15 | 0 |  | 10666.15
20:00 | 10633.16 | 0 |  | 10633.16
21:00 | 10277 | 0 |  | 10277
22:00 | 9960 | 0 |  | 9960
23:00 | 9491.2 | 0 |  | 9491.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4126 | 4845.41 | 8971.41 | DAILY GENERATION CURVE
00:30 | 4072 | 4656.125 | 8728.125
01:00 | 4018 | 4466.84 | 8484.84 | 07-12-2025
01:30 | 3969.5 | 4311.975 | 8281.475
02:00 | 3921 | 4157.11 | 8078.11
02:30 | 3908 | 4020.74 | 7928.74
03:00 | 3895 | 3884.37 | 7779.37
03:30 | 3867 | 3802.5 | 7669.5
04:00 | 3839 | 3720.63 | 7559.63
04:30 | 3830.5 | 3681.245 | 7511.745
05:00 | 3822 | 3641.86 | 7463.86
05:30 | 3921.5 | 3748.43 | 7669.93
06:00 | 4021 | 3855 | 7876
06:30 | 4161.9 | 4085.95 | 8247.85
07:00 | 4302.8 | 4316.9 | 8619.7
07:30 | 4320.255 | 4787.99 | 9108.245
08:00 | 4337.71 | 5259.08 | 9596.79
08:30 | 4324.455 | 5327.25 | 9651.705
09:00 | 4311.2 | 5395.42 | 9706.62
09:30 | 4214.775 | 5259.28 | 9474.055
10:00 | 4118.35 | 5123.14 | 9241.49
10:30 | 4186.71 | 5159.875 | 9346.585
11:00 | 4255.07 | 5196.61 | 9451.68
11:30 | 4444.71 | 5323.085 | 9767.795
12:00 | 4634.35 | 5449.56 | 10083.91
12:30 | 4804.56 | 5455.765 | 10260.325
13:00 | 4974.77 | 5461.97 | 10436.74
13:30 | 4782.455 | 5424.605 | 10207.06
14:00 | 4590.14 | 5387.24 | 9977.38
14:30 | 4555.735 | 5206.225 | 9761.96
15:00 | 4521.33 | 5025.21 | 9546.54
15:30 | 4508.14 | 4994.375 | 9502.515
16:00 | 4494.95 | 4963.54 | 9458.49
16:30 | 4645.105 | 5235.775 | 9880.88
17:00 | 4795.26 | 5508.01 | 10303.27
17:30 | 4944.13 | 5875.31 | 10819.44
18:00 | 5093 | 6242.61 | 11335.61
18:30 | 4925.5 | 6132.625 | 11058.125
19:00 | 4758 | 6022.64 | 10780.64
19:30 | 4690 | 5976.15 | 10666.15
20:00 | 4636 | 5997.16 | 10633.16
20:30 | 4494 | 5961.08 | 10455.08 |  | Executive Engineer
21:00 | 4352 | 5925 | 10277 |  | Network Operation Division
21:30 | 4320.5 | 5798 | 10118.5
22:00 | 4289 | 5671 | 9960
22:30 | 4253.1 | 5472.5 | 9725.6
23:00 | 4217.2 | 5274 | 9491.2

## En-Curve
QF-LDC-12
Date | 07-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3179 | 1218 | 740 | 0 | 94 | 1129.41 | 40 | 2517 | 0 | 0 | 33 | 0 | 0 | 21 | 0 | DAILY ENERGY CURVE
00:30 | 3159 | 1164 | 792.5 | 0 | 94 | 1021.125 | 40 | 2399.5 | 0 | 0 | 33 | 0 | 0 | 25 | 0 | 07-12-2025
01:00 | 3139 | 1110 | 845 | 0 | 94 | 912.84 | 40 | 2282 | 0 | 0 | 33 | 0 | 0 | 29 | 0
01:30 | 3127 | 1084.5 | 798.5 | 0 | 91 | 883.975 | 40 | 2197 | 0 | 0 | 29 | 0 | 0 | 30.5 | 0 | Energy Generated | 228.197 |  | MKWHr
02:00 | 3115 | 1059 | 752 | 0 | 88 | 855.11 | 40 | 2112 | 0 | 0 | 25 | 0 | 0 | 32 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3122 | 1044 | 654 | 0 | 87 | 840.24 | 40 | 2082 | 0 | 0 | 21 | 0 | 0 | 38.5 | 0 | Total Energy Requirement | 228.197 |  | MKWHr
03:00 | 3129 | 1029 | 556 | 0 | 86 | 825.37 | 40 | 2052 | 0 | 0 | 17 | 0 | 0 | 45 | 0
03:30 | 3111 | 1029 | 512 | 0 | 86 | 830 | 40 | 2006 | 0 | 0 | 17 | 0 | 0 | 38.5 | 0
04:00 | 3093 | 1029 | 468 | 0 | 86 | 834.63 | 40 | 1960 | 0 | 0 | 17 | 0 | 0 | 32 | 0
04:30 | 3074 | 1039.5 | 468 | 0 | 85 | 836.245 | 40 | 1925 | 0 | 0 | 17 | 0 | 0 | 27 | 0
05:00 | 3055 | 1050 | 468 | 0 | 84 | 837.86 | 40 | 1890 | 0 | 0 | 17 | 0 | 0 | 22 | 0
05:30 | 3103 | 1110 | 468 | 0 | 86 | 840.93 | 40 | 1981.5 | 0 | 0 | 17 | 0 | 0 | 23.5 | 0
06:00 | 3151 | 1170 | 468 | 0 | 88 | 844 | 40 | 2073 | 0 | 0 | 17 | 0 | 0 | 25 | 0
06:30 | 3241.5 | 1171.5 | 468.5 | 0 | 86 | 889.135 | 40 | 2279.5 | 18.715 | 0 | 28.5 | 0 | 0 | 24.5 | 0
07:00 | 3332 | 1173 | 469 | 0 | 84 | 934.27 | 40 | 2486 | 37.43 | 0 | 40 | 0 | 0 | 24 | 0
07:30 | 3300 | 1196 | 563 | 0 | 90 | 1045.525 | 40 | 2684.5 | 92.72 | 0 | 78 | 0 | 0 | 18.5 | 0
08:00 | 3268 | 1219 | 657 | 0 | 96 | 1156.78 | 40 | 2883 | 148.01 | 0 | 116 | 0 | 0 | 13 | 0
08:30 | 3199.5 | 1192.5 | 657 | 0 | 97 | 1167.06 | 40 | 2908 | 249.145 | 0 | 133 | 0 | 0 | 8.5 | 0
09:00 | 3131 | 1166 | 657 | 0 | 98 | 1177.34 | 40 | 2933 | 350.28 | 0 | 150 | 0 | 0 | 4 | 0
09:30 | 2960 | 1134 | 657 | 0 | 98 | 1172.215 | 40 | 2858.5 | 433.84 | 4 | 109 | 0 | 0 | 7.5 | 0
10:00 | 2789 | 1102 | 657 | 0 | 98 | 1167.09 | 40 | 2784 | 517.4 | 8 | 68 | 0 | 0 | 11 | 0
10:30 | 2845 | 1130 | 657 | 0 | 100 | 1168.925 | 40 | 2758 | 562.66 | 16.5 | 57 | 0 | 0 | 11.5 | 0
11:00 | 2901 | 1158 | 657 | 0 | 102 | 1170.76 | 40 | 2732 | 607.92 | 25 | 46 | 0 | 0 | 12 | 0
11:30 | 2905 | 1187.5 | 680.5 | 0 | 110 | 1174.09 | 40 | 2804.5 | 619.705 | 29.5 | 209 | 0 | 0 | 8 | 0
12:00 | 2909 | 1217 | 704 | 0 | 118 | 1177.42 | 40 | 2877 | 631.49 | 34 | 372 | 0 | 0 | 4 | 0
12:30 | 2826.5 | 1232 | 727 | 0 | 116 | 1178.24 | 40 | 2956 | 598.585 | 38.5 | 545 | 0 | 0 | 2.5 | 0
13:00 | 2744 | 1247 | 750 | 0 | 114 | 1179.06 | 40 | 3035 | 565.68 | 43 | 718 | 0 | 0 | 1 | 0
13:30 | 2755.5 | 1256 | 796.5 | 0 | 115 | 1144.96 | 40 | 3016 | 514.1 | 43 | 525 | 0 | 0 | 1 | 0
14:00 | 2767 | 1265 | 843 | 0 | 116 | 1110.86 | 40 | 2997 | 462.52 | 43 | 332 | 0 | 0 | 1 | 0
14:30 | 2867 | 1213 | 843 | 0 | 115 | 1040.76 | 40 | 2892 | 389.7 | 43 | 313 | 0 | 0 | 5.5 | 0
15:00 | 2967 | 1161 | 843 | 0 | 114 | 970.66 | 40 | 2787 | 316.88 | 43 | 294 | 0 | 0 | 10 | 0
15:30 | 3033.5 | 1173 | 843.5 | 0 | 111 | 919.26 | 40 | 2815.5 | 219.755 | 43 | 294.5 | 0 | 0 | 9.5 | 0
16:00 | 3100 | 1185 | 844 | 0 | 108 | 867.86 | 40 | 2844 | 122.63 | 43 | 295 | 0 | 0 | 9 | 0
16:30 | 3001 | 1159.5 | 844 | 0 | 107 | 1048.32 | 40 | 3047.5 | 65.06 | 56.5 | 503.5 | 0 | 0 | 8.5 | 0
17:00 | 2902 | 1134 | 844 | 0 | 106 | 1228.78 | 40 | 3251 | 7.49 | 70 | 712 | 0 | 0 | 8 | 0
17:30 | 3067.5 | 1205 | 843.5 | 0 | 108 | 1324.695 | 40 | 3416 | 3.745 | 73.5 | 727 | 0 | 0 | 10.5 | 0
18:00 | 3233 | 1276 | 843 | 0 | 110 | 1420.61 | 40 | 3581 | 0 | 77 | 742 | 0 | 0 | 13 | 0
18:30 | 3160.5 | 1229.5 | 843 | 0 | 111 | 1387.625 | 40 | 3548.5 | 0 | 51 | 673.5 | 0 | 0 | 13.5 | 0
19:00 | 3088 | 1183 | 843 | 0 | 112 | 1354.64 | 40 | 3516 | 0 | 25 | 605 | 0 | 0 | 14 | 0
19:30 | 3059 | 1218 | 843 | 0 | 110 | 1327.15 | 40 | 3534 | 0 | 8 | 516 | 0 | 0 | 11 | 0
20:00 | 3068 | 1205 | 843 | 0 | 110 | 1332.16 | 40 | 3540 | 0 | 8 | 474 | 0 | 0 | 13 | 0
20:30 | 3057.5 | 1200.5 | 843 | 0 | 110 | 1332.08 | 40 | 3518.5 | 0 | 4 | 337.5 | 0 | 0 | 12 | 0
21:00 | 3047 | 1196 | 843 | 0 | 110 | 1332 | 40 | 3497 | 0 | 0 | 201 | 0 | 0 | 11 | 0
21:30 | 3088.5 | 1187 | 843.5 | 0 | 108 | 1252.5 | 40 | 3443.5 | 0 | 0 | 147 | 0 | 0 | 8.5 | 0
22:00 | 3130 | 1178 | 844 | 0 | 106 | 1173 | 40 | 3390 | 0 | 0 | 93 | 0 | 0 | 6 | 0
22:30 | 3107.5 | 1169.1 | 843.5 | 0 | 108 | 1091 | 40 | 3285 | 0 | 0 | 72.5 | 0 | 0 | 9 | 0
23:00 | 3085 | 1160.2 | 843 | 0 | 110 | 1009 | 40 | 3180 | 0 | 0 | 52 | 0 | 0 | 12 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 411 | 04:00 | 388 | 11:00 | Meghnaghat | 412 | 05:00 | 389 | 11:00
Ashuganj | 415 | 5:00 | 392 | 11:00 | Payra | 418 | 03:00 | 409 | 12:00
Bhulta | 412 | 04:00 | 389 | 12:00 | Rahanpur | 424 | 05:00 | 402 | 18:00
Bibiana | 405 | 04:00 | 393 | 11:00 | Rampal | 414 | 04:00 | 395 | 13:00
BIPTC | 407 | 03:00 | 397 | 10:00
Bogura | 420 | 04:00 | 393 | 18:00
Gopalganj | 415 | 04:00 | 395 | 12:00
Kaliakoir | 406 | 04:00 | 383 | 11:00
Korerhat | 413 | 05:00 | 396 | 11:00
Madunaghat | 405 | 04:00 | 393 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 05:00 | 225 | 11:00 | Kachua | 240 | 03:00 | 230 | 11:00
AKSML | 240 | 03:00 | 232 | 11:00 | Kaliakoir | 241 | 04:00 | 224 | 11:00
Aminbazar | 240 | 05:00 | 225 | 11:00 | Keranigonj | 240 | 05:00 | 223 | 11:00
Ashuganj | 242 | 03:00 | 228 | 12:00 | Khulna(S) | 241 | 03:00 | 227 | 13:00
Ashuganj-400 | 242 | 03:00 | 228 | 12:00 | Korerhat | 243 | 05:00 | 233 | 11:00
Baghabari | 242 | 03:00 | 229 | 12:00 | Madunaghat | 240 | 01:00 | 233 | 11:00
Barapukuria | 227 | 05:00 | 205 | 11:00 | Madunaghat-400 | 242 | 03:00 | 234 | 12:00
Barapukuria-230 | 227 | 05:00 | 205 | 11:00 | Maniknagar | 238 | 05:00 | 223 | 12:00
Barishal | 246 | 02:00 | 236 | 12:00 | Meghnaghat | 245 | 06:00 | 230 | 12:00
Bheramara | 240 | 05:00 | 223 | 13:00 | Meghnaghat-400 | 242 | 05:00 | 226 | 11:00
Bhulta | 241 | 04:00 | 224 | 11:00 | Mirsorai | 241 | 05:00 | 230 | 16:00
Bibiana | 240 | 03:00 | 230 | 11:00 | Rajshahi | 239 | 04:00 | 222 | 12:00
BIPTC | 240 | 03:00 | 223 | 13:00 | Rampal | 239 | 04:00 | 224 | 13:00
Bogura | 239 | 03:00 | 222 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 238 | 03:00 | 222 | 18:00 | Rampura | 240 | 04:00 | 221 | 12:00
Borhanuddin | 246 | 03:00 | 241 | 00:00 | Shikalbaha | 238 | 03:00 | 230 | 18:00
BSRM | 240 | 04:00 | 228 | 11:00 | Shyampur | 240 | 04:00 | 224 | 11:00
Cumilla(N) | 239 | 06:00 | 228 | 11:00 | Siddhirganj | 239 | 01:00 | 225 | 12:00
Faridpur | 246 | 04:00 | 234 | 12:00 | Sirajgonj | 245 | 04:00 | 235 | 18:00
Fenchuganj | 237 | 03:00 | 231 | 10:00 | Sreepur | 239 | 05:00 | 224 | 12:00
Feni | 240 | 05:00 | 227 | 11:00 | Tongi | 236 | 04:00 | 219 | 17:00
Ghorashal | 237 | 23:00 | 214 | 12:00
Ghorashal-230 | 237 | 23:00 | 214 | 12:00
Gopalganj | 246 | 05:00 | 234 | 12:00
GPH | 236 | 01:00 | 230 | 18:30
Haripur | 241 | 04:00 | 224 | 12:00
Hasnabad | 240 | 04:00 | 223 | 22:00
Hathazari | 239 | 05:00 | 231 | 11:00
Ishurdi | 242 | 04:00 | 226 | 13:00
Jhenaidah | 241 | 04:00 | 222 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 124 | 12:00 | Lalbag | 135 | 04:00 | 124 | 11:00
Agargaon | 138 | 04:00 | 128 | 11:00 | Lalmonirhat | 133 | 04:00 | 120 | 11:00
Agrabad | 139 | 02:00 | 133 | 15:00 | Madanganj | 136 | 00:00 | 131 | 14:00
AKS | 135 | 00:00 | 132 | 11:00 | Madaripur | 141 | 02:00 | 135 | 12:00
Aminbazar | 138 | 04:00 | 127 | 11:00 | Madartek | 136 | 05:00 | 124 | 11:00
Amnura | 141 | 03:00 | 129 | 12:00 | Madunaghat | 140 | 01:00 | 135 | 11:00
Ashuganj | 143 | 06:00 | 137 | 11:00 | Magura | 138 | 03:00 | 125 | 13:00
Bagerhat | 139 | 04:00 | 128 | 18:00 | Mahasthangarh | 136 | 03:00 | 125 | 18:00
Bajitpur | 138 | 05:00 | 131 | 12:00 | Maijdee | 137 | 05:00 | 130 | 11:00
Bakulia | 139 | 04:00 | 134 | 16:00 | Manikganj | 135 | 05:00 | 121 | 16:00
Banani | 137 | 04:00 | 124 | 13:00 | Maniknagar | 139 | 04:00 | 128 | 12:00
Bangabhaban | 138 | 04:00 | 128 | 12:00 | Matarbari | 131 | 02:00 | 121 | 17:00
Barapukuria | 138 | 05:00 | 125 | 11:00 | Matuail | 140 | 05:00 | 131.5 | 12:00
Barguna | 137 | 05:00 | 134 | 10:00 | Metrorail_Motijheel | 139 | 04:00 | 119 | 14:00
Barishal | 142 | 03:00 | 135 | 12:00 | Metrorail_Uttara | 135 | 01:00 | 123 | 16:00
Barishal-230 | 142 | 02:00 | 135 | 12:00 | Millgate | 136 | 03:00 | 123 | 16:00
Baroaulia | 138 | 00:00 | 135 | 16:00 | Mirpur | 138 | 06:00 | 126 | 11:00
Baroirhat | 138 | 03:00 | 131 | 18:00 | Mirzapur | 138 | 04:00 | 126 | 12:00
Bashundhara | 136 | 03:00 | 123 | 12:00 | Mithapukur | 136 | 03:00 | 122 | 18:00
BashundharaCement | 139 | 11:00 | 131 | 15:00 | MI_Cement | 140 | 05:00 | 128 | 12:00
Beanibazar | 135 | 04:00 | 132 | 10:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 138 | 03:00 | 120 | 13:00 | Mogbazar | 139 | 05:00 | 125 | 12:00
Bhaluka | 136 | 04:00 | 128 | 12:00 | Mongla | 137 | 06:00 | 129 | 12:00
Bhandaria | 139 | 06:00 | 133 | 12:00 | Motijheel | 138 | 04:00 | 128 | 12:00
Bhangura | 139 | 04:00 | 132 | 12:00 | Muktagacha | 133 | 09:00 | 127 | 18:00
Bheramara | 142 | 03:00 | 135 | 12:00 | Munshiganj | 138 | 01:00 | 130 | 11:00
Bheramara(GK) | 142 | 04:00 | 134 | 12:00 | Muradnagar | 141 | 05:00 | 131 | 12:00
Bhulta | 132 | 00:00 | 125 | 12:00 | Mymensingh | 133 | 12:00 | 125 | 08:00
Bog-Sherpur | 138 | 03:00 | 128 | 18:00 | Naogaon | 134 | 04:00 | 123 | 18:00
Bogura | 136 | 05:00 | 128 | 18:00 | Narail | 138 | 06:00 | 125 | 13:00
Bogura-230 | 137 | 03:00 | 126 | 18:00 | Narinda | 139 | 04:00 | 128 | 12:00
Brahmanbaria | 139 | 05:00 | 132 | 12:00 | Narshingdi | 134 | 00:00 | 128 | 11:00
Cantonment | 138 | 03:00 | 128 | 11:00 | Natore | 137 | 02:00 | 129 | 12:00
Chandina | 142 | 05:00 | 134 | 11:00 | Nawabganj | 136 | 04:00 | 125 | 11:00
Chandpur | 141 | 04:00 | 135 | 18:00 | Netrakona | 132 | 01:00 | 122 | 08:00
Chandraghona | 140 | 02:00 | 136 | 11:00 | New | 138 | 06:00 | 125 | 11:00
Chapai | 140 | 05:00 | 134 | 18:00 | Niamatpur | 141 | 01:00 | 133 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 140 | 03:00 | 131 | 11:00 | Noapara | 140 | 04:00 | 130 | 12:00
Chauddagram | 139 | 02:00 | 132 | 11:00 | Pabna | 141 | 03:00 | 132 | 18:00
Chhatak | 134 | 04:00 | 130 | 18:00 | Palashbari | 133 | 05:00 | 123 | 08:00
Chowmuhani | 135 | 03:00 | 130 | 11:00 | Panchagarh | 141 | 18:30 | 122 | 11:00
Chuadanga | 140 | 03:00 | 122 | 13:00 | Patiya | 139 | 03:00 | 132 | 18:00
Coxsbazar | 130 | 03:00 | 118 | 17:00 | Patuakhali | 136 | 00:00 | 133 | 18:00
Cumilla(N) | 142 | 06:00 | 134 | 10:00 | Payra | 138 | 02:00 | 135 | 10:00
Cumilla(S) | 142 | 05:00 | 125 | 12:00 | PHP | 138 | 03:00 | 131 | 12:00
Daganbhuiyan | 138 | 05:00 | 131 | 11:00 | Postogola | 140 | 04:00 | 130 | 11:00
Daudkandi | 138 | 04:00 | 129 | 11:00 | Purbachal | 136 | 02:00 | 123 | 12:00
DhakaUniversity | 137 | 03:00 | 124 | 12:00 | Purbasadipur | 133 | 05:00 | 119 | 11:00
Dhamrai | 140 | 02:00 | 131 | 11:00 | Rahanpur | 142 | 05:00 | 135 | 18:00
Dhanmondi | 141.6 | 06:00 | 132.6 | 12:00 | Rahanpur-400 | 143 | 04:00 | 135 | 18:00
Dohazari | 137 | 05:00 | 130 | 18:00 | Rahim | 140 | 03:00 | 131 | 12:00
Faridpur | 140 | 04:00 | 135 | 10:00 | Rajbari | 141 | 04:00 | 133 | 12:00
Fatullah | 140 | 04:00 | 129 | 11:00 | Rajendrapur | 139 | 04:00 | 129 | 12:00
Fenchuganj | 141 | 05:00 | 137 | 11:00 | Rajshahi | 138 | 05:00 | 129 | 12:00
Feni | 137 | 05:00 | 130 | 11:00 | Rajshahi-230 | 139 | 03:00 | 128 | 12:00
Feni-230 | 138 | 05:00 | 131 | 11:00 | Ramganj | 137 | 05:00 | 132 | 11:00
Ghatail | 133 | 05:00 | 125 | 18:00 | Rampur | 140 | 04:00 | 132 | 17:00
Ghorashal | N/A | N/A | N/A | N/A | Rampura | 136 | 04:00 | 124 | 11:00
Goalpara | 141 | 04:00 | 131 | 13:00 | Rangamati | 140 | 04:00 | 134 | 18:00
Gollamari | 140 | 05:00 | 131 | 14:00 | Rangpur | 134 | 18:30 | 121 | 18:00
Gopalganj | 141 | 03:00 | 132 | 12:00 | Ruppur | 141 | 04:00 | 135 | 12:00
Gopalganj-400 | 143 | 04:00 | 135 | 12:00 | Saidpur | 135 | 04:00 | 118 | 18:00
Gulshan | 135 | 04:00 | 123 | 12:00 | Satkhira | 139 | 04:00 | 128 | 13:00
Halishahar | 140 | 03:00 | 133 | 18:00 | Satmasjid | 138 | 04:00 | 128 | 11:00
Haripur | 140 | 04:00 | 132 | 11:00 | Savar | 137 | 03:00 | 125 | 11:00
HaripurSBU | 141 | 04:00 | 131 | 17:00 | SevenRings | 139 | 05:00 | 132 | 11:00
Hasnabad | 140 | 05:00 | 130 | 11:00 | ShahCement | 140 | 03:00 | 131 | 11:00
Hathazari | 140 | 06:00 | 135 | 11:00 | Shahjadpur | 140 | 00:00 | 134 | 18:30
Ishurdi | 143 | 03:00 | 135 | 12:00 | Shahjibazar | 140 | 06:00 | 134 | 12:00
Jaldhaka | 134 | 04:00 | 120 | 07:00 | Shahmirpur | 138 | 08:00 | 134 | 18:00
Jamalpur | 130 | 20:00 | 120 | 00:00 | Shariatpur | 142 | 04:00 | 134 | 12:00
Jashore | 138 | 03:00 | 121 | 13:00 | Sherpur | 130 | 20:00 | 116 | 00:00
Jhenaidah | 139 | 06:00 | 121 | 18:00 | Shikalbaha | 128 | 03:00 | 122 | 18:00
Jhenaidah-230 | 140 | 03:00 | 127 | 12:00 | Shikalbaha-230 | 141 | 04:00 | 111 | 03:00
Joydebpur | 138 | 05:00 | 129 | 21:00 | Shitalakhya | 140 | 05:00 | 128 | 12:00
Joypurhat | 133 | 01:00 | 122 | 18:00 | Sholosohor | 139 | 03:00 | 135 | 11:00
Juldah | 139 | 04:00 | 134 | 15:00 | Shyampur | 138 | 02:00 | 128 | 12:00
Kabirpur | 136 | 17:00 | 122 | 10:00 | Shyampur-230 | 139 | 04:00 | 129 | 11:00
Kachua | 142 | 03:00 | 136 | 11:00 | Siddhirganj | 141 | 04:00 | 131 | 12:00
Kaliakoir | 142 | 03:00 | 133 | 11:00 | Sirajganj | 138 | 04:00 | 129 | 17:00
Kallyanpur | 139 | 03:00 | 127 | 11:00 | Sonargaon | 138 | 00:00 | 130 | 12:00
Kalurghat | 139 | 02:00 | 135 | 10:00 | Sreemongol | 140 | 06:00 | 134 | 12:00
Kamrangirchar | 135 | 04:00 | 124 | 11:00 | Sreepur | 139 | 03:00 | 131 | 11:00
Kaptai | 141 | 2:00 | 137 | 12:00 | Srinagar | 135 | 04:00 | 125 | 11:00
Kasba | 140 | 04:00 | 131 | 12:00 | SSM | 141 | 04:00 | 140 | 00:00
Kazla | 139 | 04:00 | 128 | 12:00 | Sunamganj | 134 | 06:00 | 128 | 14:00
Keranigonj | 136 | 05:00 | 124 | 12:00 | Sylhet | 136 | 04:00 | 132 | 12:00
Khagrachori | 139 | 02:00 | 134 | 11:00 | Sylhet-132 | 134 | 00:00 | 132 | 15:00
Khulna | 139 | 05:00 | 130 | 11:00 | Tangail | 134 | 04:00 | 126 | 07:00
Khulna(S) | 140 | 03:00 | 132 | 12:00 | Taraganj | 135 | 03:00 | 120 | 18:00
Khulshi | 139 | 02:00 | 132 | 11:00 | Tasnim | 138 | 00:00 | 129 | 10:00
Kishoreganj | 136 | 05:00 | 129 | 08:00 | Thakurgaon | 141 | 18:30 | 119 | 11:00
Kodda | 136 | 03:00 | 125 | 08:00 | TK | 139 | 00:00 | 135 | 16:00
KSRM | 139 | 00:00 | 134 | 10:00 | Tongi | 136 | 04:00 | 126 | 11:00
Kulaura | 140 | 03:00 | 136 | 12:00 | Ullahpara | 139 | 05:00 | 129 | 18:00
Kurigram | 134 | 04:00 | 119 | 08:00 | Ullon | 136 | 04:00 | 124 | 12:00
Kushtia | 137 | 02:00 | 126 | 13:00 | Uttara | 135 | 04:00 | 123 | 11:00
Laksam | 142 | 04:00 | 135 | 18:00 | UttaraNew | 135 | 01:00 | 123 | 16:00
Lakshmipur | 136 | 02:00 | 131 | 10:00 | Zigatola | 135 | 03:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division