## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-12-2025 | during | 10-12-2025 | during | 10-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 365 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 359 | 351 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 32 | 35 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 52 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 27 | 21 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 18 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 175 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 59 | 24 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 52 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 12 | 85 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 405 | 340 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1299 | 1577 | 5869.15 | 5839.15 | 2537.07 | 2516.07
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 12 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 50 | 50 | 50 | 50 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 226 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 27 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 64 | 64 | 40 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 33 | 33 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 10 | 10 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 6 | 21 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.31 | 0 | 3.46 | 0 | 3.46 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 550 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 6 | 0 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1221.31 | 1310 | 2494.18 | 2481.72 | 2049.96 | 2061.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 210 | 211 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 255 | 230 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 330 | 325 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 33 | 33 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 53 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 108 | 163 | 163 | 112 | 112 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 44 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 106 | 114 | 160 | 160 | 124 | 124 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 17 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 61 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1121 | 1166 | 2437.21 | 2372.21 | 2012.21 | 1956.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-12-2025 | during | 10-12-2025 | during | 10-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 35 | 34 | 157.5 | 157.5 | 74 | 74 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 64 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.25 | 0 | 45.5 | 0 | 45.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 158.25 | 117 | 361.6 | 314 | 230.6 | 183
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 156 | 159 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 206 | 207 | 200 | 200 | 200 | 200 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 847 | 853 | 888 | 888 | 854 | 854
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 844 | 844 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 225 | 201 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 34 | 0 | 71 | 0 | 71 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 860 | 1093 | 0 | 0 | 1050 | 1050 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1963 | 2138 | 2343 | 2272 | 2638.1 | 2567.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 350 | 504 | 0 | 0 | 500 | 500 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 115 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 830 | 1030 | 1085.32 | 1085.32 | 1025.32 | 1025.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1500.52 | 1869 | 1993.32 | 1993.32 | 1993.32 | 1993.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 49.86 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 171 | 174 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 381 | 401 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.45 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 938 | 1329.92 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.33 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 91 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1691.64 | 1904.92 | 3083.87 | 2917.87 | 2542.09 | 2376.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 4.2 | 0 | 4.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 105 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 168 | 0 | 170.16 | 0 | 170.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 234.6 | 218 | 446.36 | 262 | 432.36 | 228
System Total |  |  |  |  | 28823.2 | 28216.665 | 10036.32 | 11152.92 | 19916.69 | 19340.27 | 15289.71 | 14735.29
Forecast Scenario (10-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9260 |  | 0 |  | 9260
|  |  |  | 1:00 | 8670 |  | 0 |  | 8670
|  |  |  | 2:00 | 8260 |  | 0 |  | 8260
|  |  |  | 3:00 | 7880 |  | 0 |  | 7880
|  |  |  | 4:00 | 7700 |  | 0 |  | 7700
|  |  |  | 5:00 | 7710 |  | 0 |  | 7710
|  |  |  | 6:00 | 8120 |  | 0 |  | 8120
|  |  |  | 7:00 | 8910 |  | 0 |  | 8910
|  |  |  | 8:00 | 9700 |  | 0 |  | 9700
|  |  |  | 9:00 | 9740 |  | 0 |  | 9740
|  |  |  | 10:00 | 9400 |  | 0 |  | 9400
|  |  |  | 11:00 | 9570 |  | 0 |  | 9570
|  |  |  | 12:00 | 10130 |  | 0 |  | 10130
|  |  |  | 13:00 | 10460 |  | 0 |  | 10460
|  |  |  | 14:00 | 10120 |  | 0 |  | 10120
|  |  |  | 15:00 | 9740 |  | 0 |  | 9740
|  |  |  | 16:00 | 9590 |  | 0 |  | 9590
|  |  |  | 17:00 | 10040 |  | 0 |  | 10040
|  |  |  | 18:00 | 11250 |  | 0 |  | 11250
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 10960 |  | 0 |  | 10960
|  |  |  | 19:30 | 10810 |  | 0 |  | 10810
|  |  |  | 20:00 | 10720 |  | 0 |  | 10720
|  |  |  | 21:00 | 10470 |  | 0 |  | 10470
|  |  |  | 22:00 | 10180 |  | 0 |  | 10180
|  |  |  | 23:00 | 9600 |  | 0 |  | 9600
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 10130.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11250.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11250.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 228.18 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:17 hrs on 10-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10036.32 | MW | 12:00 Hr. | Energy Generated |  |  | 227.8014 |  | MKWHr.
| Day Peak Demand |  |  | 10036.32 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11152.92 | MW | 18:00 Hr. | Energy Demand |  |  | 227.8014 |  | MKWHr.
| Evening Peak Demand |  |  | 11152.92 | MW | 18:00 Hr. | Maximum Temperature |  |  | 27.2 |  | °C
| Minimum Generation of the Day |  |  | 7603.12 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 740.42 |  | MMCFD
| Maximum Generation of the Day |  |  | 11152.92 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.4483 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.3442 | 0 | 3.3743 | 0 | 0 | 0 | 0 | 0 | 29.7185 | Gas | 101.0646 | Gas | 352831320.23
| Chattogram Zone |  |  | 5.6458 | 19.8127 | 0.26575 | 0 | 1.0766 | 0.11544 | 0 | 0.00864 | 26.9249 | Coal | 70.8056 | Coal | 453291521.7114
| Cumilla Zone |  |  | 21.3488 | 0 | 0.23527 | 0 | 0 | 0.39121 | 2.3683 | 0 | 24.3436 | HFO | 6.333 | HFO | 108491293.26
| Mymensingh Zone |  |  | 0.92736 | 0 | 1.2972 | 0 | 0 | 0.27801 | 0 | 0 | 2.5026 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 20.0348 | 0 | 0 | 0 | 0 | 0.05736 | 0 | 0 | 20.0922 | Hydro | 1.0766 | Hydro | 107658
| Khulna Zone |  |  | 5.3392 | 21.9273 | 0 | 0 | 0 | 0.38664 | 19.1425 | 0 | 46.7957 | Solar | 3.712 | Solar | 58557419.8724
| Barishal Zone |  |  | 7.9489 | 29.0656 | 0 | 0 | 0 | 0.002478 | 0 | 0 | 37.017 | Import | 44.8011 | Import | 267734900.85
| Rajshahi Zone |  |  | 13.4755 | 0 | 0 | 0 | 0 | 1.2366 | 23.2902 | 0 | 38.0023 | Wind | 0.00864 | Wind | 127094.4
| Rangpur Zone |  |  | 0 | 0 | 1.1604 | 0 | 0 | 1.2443 | 0 | 0 | 2.4047
| Total |  |  | 101.0646 | 70.8056 | 6.333 | 0 | 1.0766 | 3.712 | 44.8011 | 0.00864 | 227.8014
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 352831320.23 |  | Hydro | 107658
|  |  |  | Coal | 453291521.7114 |  | Solar | 58557419.8724
|  |  |  | HFO | 108491293.26 |  | Import | 267734900.85
|  |  |  | HSD | 0 |  | Wind | 127094.4
[5 empty] | Total: | 124,11,41,208 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.1425 | Peak Hr Flow | 844.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50005836.37 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.2902 | Peak Hr Flow | 1329.92 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2516 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3683 | Peak Hr Flow | 114.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2807 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.8011 | Peak Hr Flow | 2287.92 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4097
|  |  |  | Chattogram |  | 0 |  | 1146
|  |  |  | Cumilla |  | 0 |  | 921
|  |  |  | Mymensingh |  | 0 |  | 890
|  |  |  | Sylhet |  | 0 |  | 401
|  |  |  | Khulna |  | 0 |  | 1260
|  |  |  | Barishal |  | 0 |  | 309
|  |  |  | Rajshahi |  | 0 |  | 1013
|  |  |  | Rangpur |  | 0 |  | 778
|  |  |  | Total |  | 0 |  | 10815
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:07 | 20:22 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT Scheduled S/D Due to Annual maintenance
| 08:07 | 20:24 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT Scheduled S/D Due to Annual maintenance
| 08:21 | 16:32 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Annual Maintenance.
| 08:22 | 16:31 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Annual Maintenance.
| 08:23 | 10:12 | Feni 230/132kV S/S ATR-1 HT Project Work S/D Due to GIB EARTHING WORK
| 08:23 | 16:55 | Jhenaidah 132/33kV S/S Jhenaidah-Chuadanga, 132kV Circuit-2(L8) Scheduled S/D Due to
Annual maintenance
| 08:24 | 16:43 | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Annual Maintenance
| 08:24 | 16:43 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Annual Maintenance
| 08:29 |  | Bibiyana-III 400 MW CCPP, FGMO is OFF with remarks:-
| 08:31 | 17:09 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to Khulna
Central Ckt-2 SD Due ALDC's Instruction. and from Khulna (C) end Due to Project & bay
annual maintenance work
| 08:37 | 17:05 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance.
| 08:38 | 18:00 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to
annual maintenance
| 08:40 | 17:48 | Natore 132/33kV S/S TR-4 (435 T) LT Scheduled S/D
| 08:40 | 16:18 | Bogura-Natore 132 kV Ckt-1 Scheduled S/D from Bogura 132/33kV end Due to Annual
Maintenance work. and from Natore 132/33kVend.
| 08:41 | 17:47 | Natore 132/33kV S/S TR-4 (435 T) HT Scheduled S/D
| 08:42 | 17:31 | Gopalganj 400/132kV S/S ATR-03 LT Scheduled S/D Due to None
| 08:42 | 17:30 | Gopalganj 400/132kV S/S ATR-03 HT Scheduled S/D
| 08:48 | 14:51 | Sirajganj 132/33kV S/S T1-(415) HT Scheduled S/D Due to Annual maintenance work
| 08:48 | 14:51 | Sirajganj 132/33kV S/S T1-(415) LT Scheduled S/D Due to Annual maintenance work
| 08:50 | 14:10 | Ramganj 132/33kV S/S 132 Kv Bus- A Scheduled S/D Due to Annual Maintenance
| 08:51 | 16:45 | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to For
annual maintenance
| 08:51 |  | Naogaon-Niyamatpur 132kV Ckt-1 Scheduled S/D from Niamatpur 132/33kV end Due to Annual
Maintenance and from Naogaon 132/33kV end Due to Annual maintenance
| 08:55 | 14:24 | Barishal-Barishal(N) 132 kV Ckt-2 Scheduled S/D from Barishal 230/132kV end Due to Annual
maintenance and from Barishal 132/33kV end Due to Annual maintenance work.
| 08:55 | 19:24 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to ANNUAL MAINTENANCE.
| 08:55 | 19:23 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance.
| 08:56 | 19:43 | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to Annual maintenance
| 08:57 | 15:50 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end.
| 08:59 | 15:52 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D
| 09:04 | 18:00 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 09:09 | 17:02 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end.
| 09:12 | 16:58 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Annual maintenance
| 09:17 | 16:53 | Satmasjid 132/33kV S/S Auxiliary Tr-2 LT Scheduled S/D Due to Annual maintenance
| 09:22 | 16:56 | Chuadanga 132/33kV S/S Jhenaidah-Chuadanga Ckt-2 Scheduled S/D Due to Annual Maintenance.
| 09:28 | 17:43 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to Annual Maintenance
| 09:28 | 17:44 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to Annual Maintenance
| 09:33 | 16:44 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 HT Scheduled S/D Due to Annual Maintenance
|  | 09:33 | Sirajganj 132/33kV S/S T4-(445) HT is restored.
|  | 09:33 | Sirajganj 132/33kV S/S T4-(445) LT is restored.
| 09:38 | 16:27 | Hathazari 230/132/33kV S/S Raojan-02 Scheduled S/D Due to Annual maintenance (Dead line
checking)
| 09:40 | 15:10 | Bajitpur 132/33kV S/S Tr-2(414T) LT Scheduled S/D
| 09:40 | 15:09 | Bajitpur 132/33kV S/S Tr-2(414T) HT Scheduled S/D
| 09:52 | 17:26 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Muktagacha 132/33kV end. and from
Ghatail 132/33kV end Due to Annual Maintenance and from Ghatail 132/33kV end Due to
Annual Maintenance
| 09:58 | 15:51 | Brahmanbaria 132/33kV S/S 402T LT Scheduled S/D
| 09:58 | 15:51 | Brahmanbaria 132/33kV S/S 402T HT Scheduled S/D
| 10:06 | 17:29 | Ghatail 132/33kV S/S Main Bus-1 Scheduled S/D Due to Annual Maintenance
| 10:27 | 13:49 | Feni 230/132kV S/S ATR-2 LT Project Work S/D Due to GIB EARTHING WORK
| 10:29 | 13:48 | Feni 230/132kV S/S ATR-2 HT Project Work S/D Due to GIB Earthing.
| 12:12 |  | Rampur 230/132/33 S/S Halishahar-1 Scheduled S/D Due to S/D on Demand of Halishahar
| 12:15 | 18:12 | Halishahar-Khulshi 132kV Ckt-1 Project Work S/D from Halishahar 132/33kV end.
|  | 12:17 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
|  | 12:18 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
|  | 12:21 | Rampur 230/132/33 S/S TR 02 (417T) HT is restored.
| 12:34 | 18:22 | Halishahar-Khulshi 132kV Ckt-2 Project Work S/D from Halishahar 132/33kV end Due to
ESPNER project work
| 12:34 |  | Rampur 230/132/33 S/S Halishahar-2 Scheduled S/D Due to S/D on demand of halishahar
| 12:42 | 19:48 | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to Annual Maintenance
| 12:42 | 19:47 | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to Annual Maintenance
| 13:37 | 16:44 | Chandina-Cumilla(N) 132 kV Ckt-1 Project Work S/D from Chandina 132/33kV end Due to NLDC
-SAS Intrigation by CNEEC
| 14:20 | 16:45 | Ramganj 132/33kV S/S 132 Kv Bus-B Scheduled S/D Due to Annual Maintenance
| 15:04 | 15:39 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D
| 15:05 | 15:38 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D
| 15:09 | 16:20 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-1 Scheduled S/D Due to Work on 132 KV
Bhulta-2 DS-232S.
| 15:10 | 16:07 | Nawabganj 132/33kV S/S TR-2 HT Forced S/D Due to Red hot maintenance at 33kV incomer-2, | [7 empty] | 9.0MW load
|  |  | 33kV Bus side. | [7 empty] | interrup.
| 15:15 | 18:18 | Feni 230/132kV S/S ATR-3 LT Project Work S/D Due to GIB boanding earthing connection by
project
| 15:16 | 18:17 | Feni 230/132kV S/S ATR-3 HT Project Work S/D Due to GIB boanding earthing connection by
project
| 15:55 |  | Full interruption (240MW) occurred from 15:55 hrs to 16:16 hrs at Kodda 132/33kV
substation due to the tripping of Kabirpur-Kodda 132kV ckt-1. Ckt-2 was in shut down
condition. Now, no interruption is occurring.
|  | 16:10 | Nawabganj 132/33kV S/S TR-2 LT is restored.
|  | 16:47 | Cox'sbazar-Dohazari 132 kV Ckt-2 is restored.
|  | 16:50 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 LT is restored.
|  | 17:42 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
|  | 17:42 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
| 18:00 |  | Evening Peak Generation is 11152 MW.
| 18:26 |  | Barguna 132/33kV S/S Transformer-2 LT Tripped showing ABB REF615 (33 kV Incomer-2) relays | [7 empty] | 14.0MW load
|  |  | Due to 33 kV BREB-2( Betagi PBS) feeder has tripped due to earth fault (Earth wire | [7 empty] | interrup.
cutoff)
| 18:26 |  | Barguna 132/33kV S/S Transformer-2 HT Tripped showing ABB REC650, ABB RET670, ABB | [7 empty] | 14.0MW load
|  |  | RET650. relays Due to 33 kV CB Failure(33 kV Incomer-2) | [7 empty] | interrup.
| 18:26 | 19:35 | Barguna 132/33kV S/S Transformer-1 LT Tripped showing ABB(REF615) relays Due to 33 kV | [7 empty] | 14.0MW load
|  |  | BREB-2( Betagi PBS) feeder has tripped due to earth fault (Earth wire cutoff) | [7 empty] | interrup.
|  | 21:07 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
|  | 21:11 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
|  | 23:03 | Bhulta-Haripur 132 kV Ckt-1 is restored.
| 05:00 |  | Minimum Generation: 7556 MW.
| 05:10 |  | Halishahar-Khulshi 132kV Ckt-1 Project Work S/D from Halishahar 132/33kV end Due to Due
to LILO Cable Connection work at Anandabaza Grid S/S.
| 05:11 |  | Halishahar-Khulshi 132kV Ckt-2 Project Work S/D from Halishahar 132/33kV end Due to Due
to LILO Cable Connection work at Anandabaza Grid S/S.
| 07:14 |  | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Annual
Maintenance and from Bhandaria 132/33kV end Due to Annual maintenance
| 07:17 |  | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to annual maintenance
| 07:17 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to annual maintenance
| 07:50 |  | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual
Maintenance Doh-Cox Ckt-2 (Cox's Bazar Side)
| 07:59 |  | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Annual Maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8618400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 6778103 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 328680 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 52 | 83520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 482851 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 72041 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 455400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 495000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 18 | 187680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 175 | 499560 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 24 | 749808 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 322560 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 85 | 302400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 345240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 340 | 9997273 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1577 | 29718516
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 95040 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 24480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1076580 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5317960 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 27 | 95345 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 50880 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 327840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20398 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 95040 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 550 | 11732726 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 8640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 8080000 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1310 | 26924929
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 211 | 4974000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 230 | 5766000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 325 | 6803000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1113776 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 53 | 93672 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2379648 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 44 | 81120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 114 | 2368320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 312370 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 20160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 40320 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 391209 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1166 | 24343595
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 927360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 314400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 64 | 982800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 266910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 117 | 2502570
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 57360 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 718440 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 709440 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1575360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 159 | 3689750 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 384000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 431328 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7493500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5033000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 853 | 20092178
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 844 | 19142545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 201 | 5339232 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 386640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1093 | 21927280 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2138 | 46795697
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 504 | 8147749 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2668000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1030 | 20917818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5280909 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2478 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1869 | 37016954.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 300656 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4265455 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 401 | 9210036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1329.92 | 23290200 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 335248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 571100 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1904.92 | 38002275
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 865728 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32992.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 105 | 294682 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 181660 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1029600 | -
Rangpur Area Total |  |  |  |  | 950 | 218 | 2404662.44
Eastern Grid Total |  |  |  |  | 17395.105 | 5023 | 103581788
Western Grid Total |  |  |  |  | 10821.56 | 6129.92 | 124219588.62
National Grid Total |  |  |  |  | 28216.665 | 11152.92 | 227801376.62
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7455.03 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3360 | MW
i) Dhaka area |  |  | 4096.93 |  | MW | i) Khulna area |  |  |  | 1260 | MW
ii) Chattogram area |  |  | 1146.1 |  | MW | ii) Barishal area |  |  |  | 309 | MW
iii) Cumilla area |  |  | 921 |  | MW | iii) Rajshahi area |  |  |  | 1013 | MW
iv) Mymensingh area |  |  | 890 |  | MW | iv) Rangpur area |  |  |  | 778 | MW
v) Sylhet area |  |  | 401 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10815.03 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 61 | 17:00 | 133 | Niamatpur | 44 | 08:00
2 | AKSML | 99.9 | 06:00 | 68 | Ishurdi | 50 | 18:30 | 134 | Noapara | 39 | 18:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jaldhaka | 58 | 18:00 | 135 | PHP | 6 | 19:00
4 | Agargaon | 88 | 13:00 | 70 | Jamalpur | 93 | 18:00 | 136 | Pabna | 76 | 18:00
5 | Agrabad | 56 | 11:00 | 71 | Jashore | 101 | 13:00 | 137 | Palashbari | 88 | 18:00
6 | Amnura | 20 | 08:00 | 72 | Jhenaidah | 95 | 18:00 | 138 | Panchagarh | 50 | 18:00
7 | Ashuganj | 62 | 13:00 | 73 | Joydebpur | 105 | 18:30 | 139 | Patiya | 6 | 18:30
8 | BSRM | 206 | 19:30 | 74 | Joypurhat | 44 | 18:00 | 140 | Patuakhali | 47 | 21:00
9 | Bagerhat | 64 | 18:00 | 75 | Juldah | 13 | 11:00 | 141 | Payra | 20 | 00:00
10 | Bajitpur | 57 | 18:00 | 76 | KSRM | 37 | 00:00 | 142 | Postogola | 47 | 18:00
11 | Bakulia | 59 | 18:00 | 77 | Kabirpur | 205 | 14:00 | 143 | Purbachal | 26 | 13:00
12 | Banani | 46.8 | 13:00 | 78 | Kachua | 58 | 18:00 | 144 | Purbasadipur | 111 | 18:30
13 | Bangabhaban | 14 | 11:00 | 79 | Kallyanpur | 75 | 14:00 | 145 | Rahanpur | 22 | 18:30
14 | Barapukuria | 51 | 18:00 | 80 | Kalurghat | 38 | 11:00 | 146 | Rahim | 49 | 14:00
15 | Barguna | 16 | 17:00 | 81 | Kamrangirchar | 60 | 13:00 | 147 | Rajbari | 59 | 18:00
16 | Barishal | 86 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 99 | 18:00
17 | Barishal-230 | 66 | 18:00 | 83 | Kasba | 22 | 18:00 | 149 | Rajshahi | 67 | 20:00
18 | Baroaulia | 51 | 08:00 | 84 | Kazla | 91 | 13:00 | 150 | Rajshahi-230 | 74 | 13:00
19 | Baroirhat | 47 | 19:00 | 85 | Keranigonj | 64 | 13:00 | 151 | Ramganj | 66 | 17:00
20 | Bashundhara | 139 | 13:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 27 | 18:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 54 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 17:00 | 88 | Khulshi | 170 | 19:30 | 154 | Rangpur | 87 | 12:00
23 | Benapole | 42 | 18:00 | 89 | Kishoreganj | 82 | 18:30 | 155 | Ruppur | 3 | 11:00
24 | Bhaluka | 134 | 18:00 | 90 | Kodda | 260 | 11:00 | 156 | SSM | 2 | 02:00
25 | Bhandaria | 36 | 21:00 | 91 | Kulaura | 31 | 18:00 | 157 | Saidpur | 92 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 52 | 18:00 | 158 | Satkhira | 85 | 18:00
27 | Bheramara(GK) | 44 | 18:00 | 93 | Kushtia | 116 | 18:00 | 159 | Satmasjid | 79 | 14:00
28 | Bhulta | 154 | 07:00 | 94 | Laksam | 20 | 18:00 | 160 | Savar | 156 | 18:00
29 | Bog-Sherpur | 58 | 18:00 | 95 | Lakshmipur | 26 | 21:00 | 161 | SevenRings | 12.38 | 21:00
30 | Bogura | 114 | 20:00 | 96 | Lalbag | 59 | 19:30 | 162 | ShahCement | 34 | 23:00
31 | Borhanuddin | 65 | 20:00 | 97 | Lalmonirhat | 40 | 18:30 | 163 | Shahjadpur | 59 | 18:00
32 | Brahmanbaria | 84 | 19:00 | 98 | MI_Cement | 15.7 | 23:00 | 164 | Shahjibazar | 77 | 18:00
33 | Cantonment | 74 | 13:00 | 99 | Madanganj | 29 | 13:00 | 165 | Shahmirpur | 37 | 18:00
34 | Chandina | 15 | 07:00 | 100 | Madaripur | 70 | 20:00 | 166 | Shariatpur | 54 | 19:30
35 | Chandpur | 56 | 13:00 | 101 | Madartek | 62 | 13:00 | 167 | Sherpur | 108 | 18:00
36 | Chandraghona | 25 | 18:00 | 102 | Madunaghat | 44 | 20:00 | 168 | Shikalbaha | 15 | 13:00
37 | Chapai | 52 | 18:30 | 103 | Magura | 50 | 18:00 | 169 | Shitalakhya | 62.7 | 12:00
38 | Charsaidpur | 31 | 00:00 | 104 | Mahasthangarh | 54 | 18:00 | 170 | Sholosohor | 34 | 12:00
39 | Chauddagram | 48 | 13:00 | 105 | Maijdee | 24 | 18:30 | 171 | Shyampur | 132 | 13:00
40 | Chhatak | 20 | 18:00 | 106 | Manikganj | 98 | 18:00 | 172 | Siddhirganj | 97 | 12:00
41 | Chowmuhani | 104 | 20:00 | 107 | Maniknagar | 46 | 13:00 | 173 | Sirajganj | 84 | 19:00
42 | Chuadanga | 75 | 18:00 | 108 | Matarbari | 38 | 19:00 | 174 | Sonargaon | 127 | 18:30
43 | Coxsbazar | 101 | 18:00 | 109 | Matuail | 58 | 10:00 | 175 | Sreemongol | 50 | 18:00
44 | Cumilla(N) | 85 | 18:30 | 110 | Metrorail_Motijheel | 25 | 10:00 | 176 | Sreepur | 87 | 18:30
45 | Cumilla(S) | 114 | 18:30 | 111 | Metrorail_Uttara | 9 | 09:00 | 177 | Srinagar | 30.6 | 21:00
46 | Daganbhuiyan | 0 | 05:00 | 112 | Millgate | 88 | 11:00 | 178 | Sunamganj | 39 | 18:00
47 | Daudkandi | 108 | 19:00 | 113 | Mirpur | 108 | 14:00 | 179 | Sylhet | 40 | 14:00
48 | DhakaUniversity | 58 | 13:00 | 114 | Mirsorai | 36 | 15:00 | 180 | Sylhet-132 | 74 | 16:00
49 | Dhamrai | 98 | 16:00 | 115 | Mirzapur | 38 | 12:00 | 181 | TK | 16 | 18:00
50 | Dhanmondi | 64 | 14:00 | 116 | Mithapukur | 50 | 18:00 | 182 | Tangail | 114 | 18:00
51 | Dohazari | 65 | 17:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 26 | 08:00
52 | Faridpur | 109 | 21:00 | 118 | Mogbazar | 64.6 | 14:00 | 184 | Tasnim | 32 | 15:00
53 | Fatullah | 92 | 10:00 | 119 | Mongla | 32 | 07:00 | 185 | Thakurgaon | 83 | 18:00
54 | Fenchuganj | 25 | 18:00 | 120 | Motijheel | 29 | 13:00 | 186 | Tongi | 99 | 17:00
55 | Feni | 71 | 18:00 | 121 | Muktagacha | 26 | 07:00 | 187 | Ullahpara | 25 | 18:00
56 | GPH | 92 | 10:00 | 122 | Munshiganj | 74 | 13:00 | 188 | Ullon | 51 | 13:00
57 | Ghatail | 62 | 18:00 | 123 | Muradnagar | 26 | 19:30 | 189 | Uttara | 60 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 133 | 18:00 | 190 | UttaraNew | 14 | 18:00
59 | Ghorashal-230 | 83 | 19:00 | 125 | Naogaon | 91 | 18:00 | 191 | Zigatola | 52 | 13:00
60 | Goalpara | 27 | 12:00 | 126 | Narail | 42 | 18:00
61 | Gollamari | 72 | 13:00 | 127 | Narinda | 56 | 13:00
62 | Gopalganj | 77 | 18:30 | 128 | Narshingdi | 138 | 18:30
63 | Gulshan | 82 | 13:00 | 129 | Natore | 103 | 18:00
64 | Halishahar | 54 | 12:00 | 130 | Nawabganj | 30 | 13:00
65 | HaripurSBU | 125 | 09:00 | 131 | Netrakona | 108 | 18:00
66 | Hasnabad | 71 | 12:00 | 132 | New | 58.6 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9167.25 | 0 |  | 9167.25
1:00 | 8572.34 | 0 |  | 8572.34
2:00 | 8162.77 | 0 |  | 8162.77
3:00 | 7780.32 | 0 |  | 7780.32
4:00 | 7603.12 | 0 |  | 7603.12
5:00 | 7612.95 | 0 |  | 7612.95
6:00 | 8019.56 | 0 |  | 8019.56
7:00 | 8817.38 | 0 |  | 8817.38
8:00 | 9608.37 | 0 |  | 9608.37
9:00 | 9645.09 | 0 |  | 9645.09
10:00 | 9304.7 | 0 |  | 9304.7
11:00 | 9472.67 | 0 |  | 9472.67
12:00 | 10036.32 | 0 |  | 10036.32
13:00 | 10369.11 | 0 |  | 10369.11
14:00 | 10023.15 | 0 |  | 10023.15
15:00 | 9642.63 | 0 |  | 9642.63
16:00 | 9499.3 | 0 |  | 9499.3
17:00 | 9947.16 | 0 |  | 9947.16
18:00 | 11152.92 | 0 |  | 11152.92
19:00 | 10864.94 | 0 |  | 10864.94
19:30 | 10715.54 | 0 |  | 10715.54
20:00 | 10621.11 | 0 |  | 10621.11
21:00 | 10377.11 | 0 |  | 10377.11
22:00 | 10083.78 | 0 |  | 10083.78
23:00 | 9525.33 | 0 |  | 9525.33
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4160.5 | 5006.75 | 9167.25 | DAILY GENERATION CURVE
00:30 | 4093.75 | 4776.045 | 8869.795
01:00 | 4027 | 4545.34 | 8572.34 | 09-12-2025
01:30 | 3975.25 | 4392.305 | 8367.555
02:00 | 3923.5 | 4239.27 | 8162.77
02:30 | 3801.5 | 4170.045 | 7971.545
03:00 | 3679.5 | 4100.82 | 7780.32
03:30 | 3636 | 4055.72 | 7691.72
04:00 | 3592.5 | 4010.62 | 7603.12
04:30 | 3595 | 4013.035 | 7608.035
05:00 | 3597.5 | 4015.45 | 7612.95
05:30 | 3719 | 4097.255 | 7816.255
06:00 | 3840.5 | 4179.06 | 8019.56
06:30 | 3990.45 | 4428.02 | 8418.47
07:00 | 4140.4 | 4676.98 | 8817.38
07:30 | 4272.6 | 4940.275 | 9212.875
08:00 | 4404.8 | 5203.57 | 9608.37
08:30 | 4359.79 | 5266.94 | 9626.73
09:00 | 4314.78 | 5330.31 | 9645.09
09:30 | 4263.395 | 5211.5 | 9474.895
10:00 | 4212.01 | 5092.69 | 9304.7
10:30 | 4288.57 | 5100.115 | 9388.685
11:00 | 4365.13 | 5107.54 | 9472.67
11:30 | 4505.845 | 5248.65 | 9754.495
12:00 | 4646.56 | 5389.76 | 10036.32
12:30 | 4659.1 | 5543.615 | 10202.715
13:00 | 4671.64 | 5697.47 | 10369.11
13:30 | 4571.655 | 5624.475 | 10196.13
14:00 | 4471.67 | 5551.48 | 10023.15
14:30 | 4415.25 | 5417.64 | 9832.89
15:00 | 4358.83 | 5283.8 | 9642.63
15:30 | 4401.47 | 5169.495 | 9570.965
16:00 | 4444.11 | 5055.19 | 9499.3
16:30 | 4421.51 | 5301.72 | 9723.23
17:00 | 4398.91 | 5548.25 | 9947.16
17:30 | 4710.955 | 5839.085 | 10550.04
18:00 | 5023 | 6129.92 | 11152.92
18:30 | 4902.65 | 6106.28 | 11008.93
19:00 | 4782.3 | 6082.64 | 10864.94
19:30 | 4693.3 | 6022.24 | 10715.54
20:00 | 4635.7 | 5985.41 | 10621.11
20:30 | 4570.85 | 5928.26 | 10499.11 |  | Executive Engineer
21:00 | 4506 | 5871.11 | 10377.11 |  | Network Operation Division
21:30 | 4460 | 5770.445 | 10230.445
22:00 | 4414 | 5669.78 | 10083.78
22:30 | 4358 | 5446.555 | 9804.555
23:00 | 4302 | 5223.33 | 9525.33

## En-Curve
QF-LDC-12
Date | 09-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3027 | 1179.5 | 750 | 0 | 92 | 964.75 | 44 | 3058 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3065.5 | 1182.75 | 732 | 0 | 88 | 927.045 | 44 | 2795 | 0 | 0 | 34.5 | 0 | 0 | 1 | 0 | 09-12-2025
01:00 | 3104 | 1186 | 714 | 0 | 84 | 889.34 | 44 | 2532 | 0 | 0 | 17 | 0 | 0 | 2 | 0
01:30 | 3080.5 | 1160.25 | 684.5 | 0 | 85 | 862.305 | 44 | 2431 | 0 | 0 | 17 | 0 | 0 | 3 | 0 | Energy Generated | 227.8014 |  | MKWHr
02:00 | 3057 | 1134.5 | 655 | 0 | 86 | 835.27 | 44 | 2330 | 0 | 0 | 17 | 0 | 0 | 4 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2997 | 1074.5 | 655 | 0 | 87 | 835.045 | 44 | 2259.5 | 0 | 0 | 17 | 0 | 0 | 2.5 | 0 | Total Energy Requirement | 227.8014 |  | MKWHr
03:00 | 2937 | 1014.5 | 655 | 0 | 88 | 834.82 | 44 | 2189 | 0 | 0 | 17 | 0 | 0 | 1 | 0
03:30 | 2902.5 | 1020.5 | 608.5 | 0 | 86 | 833.22 | 44 | 2179.5 | 0 | 0 | 17 | 0 | 0 | 0.5 | 0
04:00 | 2868 | 1026.5 | 562 | 0 | 84 | 831.62 | 44 | 2170 | 0 | 0 | 17 | 0 | 0 | 0 | 0
04:30 | 2870 | 1026.5 | 562 | 0 | 82 | 834.535 | 44 | 2172 | 0 | 0 | 17 | 0 | 0 | 0 | 0
05:00 | 2872 | 1026.5 | 562 | 0 | 80 | 837.45 | 44 | 2174 | 0 | 0 | 17 | 0 | 0 | 0 | 0
05:30 | 2917.5 | 1118.5 | 585 | 0 | 83 | 836.255 | 44 | 2215 | 0 | 0 | 17 | 0 | 0 | 0 | 0
06:00 | 2963 | 1210.5 | 608 | 0 | 86 | 835.06 | 44 | 2256 | 0 | 0 | 17 | 0 | 0 | 0 | 0
06:30 | 3001.5 | 1205 | 631.5 | 0 | 87 | 888.285 | 44 | 2516.5 | 10.685 | 0 | 34 | 0 | 0 | 0 | 0
07:00 | 3040 | 1199.5 | 655 | 0 | 88 | 941.51 | 44 | 2777 | 21.37 | 0 | 51 | 0 | 0 | 0 | 0
07:30 | 3119 | 1162.5 | 703 | 0 | 82 | 986.755 | 44 | 2943 | 100.62 | 0 | 72 | 0 | 0 | 0 | 0
08:00 | 3198 | 1125.5 | 751 | 0 | 76 | 1032 | 44 | 3109 | 179.87 | 0 | 93 | 0 | 0 | 0 | 0
08:30 | 3110.5 | 1109.25 | 797.5 | 0 | 85 | 993.5 | 45 | 3100.5 | 279.48 | 12.5 | 93.5 | 0 | 0 | 0 | 0
09:00 | 3023 | 1093 | 844 | 0 | 94 | 955 | 46 | 3092 | 379.09 | 25 | 94 | 0 | 0 | 0 | 0
09:30 | 3016 | 1062.5 | 844 | 0 | 94 | 896 | 46 | 2923 | 448.895 | 37.5 | 107 | 0 | 0 | 0 | 0
10:00 | 3009 | 1032 | 844 | 0 | 94 | 837 | 46 | 2754 | 518.7 | 50 | 120 | 0 | 0 | 0 | 0
10:30 | 3022.5 | 1064 | 844 | 0 | 97 | 835 | 46 | 2730 | 552.985 | 50 | 147.2 | 0 | 0 | 0 | 0
11:00 | 3036 | 1096 | 844 | 0 | 100 | 833 | 46 | 2706 | 587.27 | 50 | 174.4 | 0 | 0 | 0 | 0
11:30 | 3074.5 | 1111 | 844 | 0 | 103 | 885.5 | 46 | 2840 | 589.295 | 41.5 | 219.7 | 0 | 0 | 0 | 0
12:00 | 3113 | 1126 | 844 | 0 | 106 | 938 | 46 | 2974 | 591.32 | 33 | 265 | 0 | 0 | 0 | 0
12:30 | 3062.5 | 1125.5 | 844 | 0 | 109 | 1006.5 | 46 | 3038.5 | 595.215 | 33 | 342.5 | 0 | 0 | 0 | 0
13:00 | 3012 | 1125 | 844 | 0 | 112 | 1075 | 46 | 3103 | 599.11 | 33 | 420 | 0 | 0 | 0 | 0
13:30 | 2959 | 1121.5 | 844 | 0 | 113 | 1048.025 | 46 | 3077 | 550.12 | 33 | 404.485 | 0 | 0 | 0 | 0
14:00 | 2906 | 1118 | 844 | 0 | 114 | 1021.05 | 46 | 3051 | 501.13 | 33 | 388.97 | 0 | 0 | 0 | 0
14:30 | 2905.5 | 1093.25 | 844 | 0 | 111 | 1020.6 | 46 | 2969 | 425.705 | 33 | 384.835 | 0 | 0 | 0 | 0
15:00 | 2905 | 1068.5 | 844 | 0 | 108 | 1020.15 | 46 | 2887 | 350.28 | 33 | 380.7 | 0 | 0 | 0 | 0
15:30 | 3023.5 | 1093.15 | 844 | 0 | 109 | 961.01 | 46 | 2887.5 | 242.705 | 25 | 338.6 | 0 | 0 | 0.5 | 0
16:00 | 3142 | 1117.8 | 844 | 0 | 110 | 901.87 | 46 | 2888 | 135.13 | 17 | 296.5 | 0 | 0 | 1 | 0
16:30 | 3141.5 | 1103.15 | 844 | 0 | 106 | 998.225 | 46 | 3061 | 72.605 | 9 | 340.75 | 0 | 0 | 1 | 0
17:00 | 3141 | 1088.5 | 844 | 0 | 102 | 1094.58 | 46 | 3234 | 10.08 | 1 | 385 | 0 | 0 | 1 | 0
17:30 | 3145.5 | 1094.25 | 844 | 0 | 108 | 1212.25 | 46 | 3382.5 | 5.04 | 61.5 | 650.5 | 0 | 0 | 0.5 | 0
18:00 | 3150 | 1100 | 844 | 0 | 114 | 1329.92 | 46 | 3531 | 0 | 122 | 916 | 0 | 0 | 0 | 0
18:30 | 3110.5 | 1132.85 | 844 | 0 | 110 | 1331.78 | 46 | 3543 | 0 | 94 | 796.8 | 0 | 0 | 0 | 0
19:00 | 3071 | 1165.7 | 844 | 0 | 106 | 1333.64 | 46 | 3555 | 0 | 66 | 677.6 | 0 | 0 | 0 | 0
19:30 | 3080 | 1158.7 | 844 | 0 | 110 | 1321.24 | 46 | 3558 | 0 | 40 | 557.6 | 0 | 0 | 0 | 0
20:00 | 3089 | 1159.7 | 844 | 0 | 108 | 1333.41 | 46 | 3557 | 0 | 40 | 444 | 0 | 0 | 0 | 0
20:30 | 3093 | 1166.85 | 844 | 0 | 109 | 1271.76 | 46 | 3563 | 0 | 36 | 369.5 | 0 | 0 | 0 | 0
21:00 | 3097 | 1174 | 844 | 0 | 110 | 1210.11 | 46 | 3569 | 0 | 32 | 295 | 0 | 0 | 0 | 0
21:30 | 3099.5 | 1177 | 844.5 | 0 | 105 | 1174.445 | 46 | 3529.5 | 0 | 16 | 238.5 | 0 | 0 | 0 | 0
22:00 | 3102 | 1180 | 845 | 0 | 100 | 1138.78 | 46 | 3490 | 0 | 0 | 182 | 0 | 0 | 0 | 0
22:30 | 3100.5 | 1183 | 849 | 0 | 102 | 1074.555 | 46 | 3328.5 | 0 | 0 | 121 | 0 | 0 | 0 | 0
23:00 | 3099 | 1186 | 853 | 0 | 104 | 1010.33 | 46 | 3167 | 0 | 0 | 60 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 411 | 04:00 | 40 | 00:00 | Meghnaghat | 412 | 04:00 | 391 | 13:00
Ashuganj | 419 | 02:00 | 395 | 18:00 | Payra | 418 | 02:00 | 410 | 18:00
Bhulta | 410 | 04:00 | 389 | 12:00 | Rahanpur | 423 | 02:00 | 405 | 18:00
Bibiana | 404 | 04:00 | 393 | 12:00 | Rampal | 415 | 05:00 | 399 | 13:00
BIPTC | 409 | 02:00 | 393 | 18:00
Bogura | 419 | 02:00 | 395 | 18:00
Gopalganj | 414 | 03:00 | 397 | 13:00
Kaliakoir | 403 | 04:00 | 382 | 15:00
Korerhat | 417 | 04:00 | 399 | 13:00
Madunaghat | 414 | 05:00 | 400 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 227 | 12:00 | Kachua | 242 | 06:00 | 233 | 13:00
AKSML | 234 | 05:00 | 221 | 13:00 | Kaliakoir | 240 | 04:00 | 226 | 15:00
Aminbazar | 238 | 04:00 | 228 | 12:00 | Keranigonj | 240 | 05:00 | 225 | 13:00
Ashuganj | 240 | 03:00 | 230 | 13:00 | Khulna(S) | 247 | 01:00 | 232 | 12:00
Ashuganj-400 | 240 | 03:00 | 230 | 13:00 | Korerhat | 245 | 04:00 | 234 | 12:00
Baghabari | 240 | 06:00 | 231 | 18:00 | Madunaghat | 233 | 21:00 | 221 | 13:00
Barapukuria | 230 | 15:00 | 218 | 07:00 | Madunaghat-400 | 232 | 00:00 | 222 | 13:00
Barapukuria-230 | 230 | 15:00 | 218 | 07:00 | Maniknagar | 236 | 04:00 | 227 | 12:00
Barishal | 245 | 02:00 | 238 | 12:00 | Meghnaghat | 246 | 06:00 | 234 | 15:00
Bheramara | 239 | 03:00 | 227 | 18:00 | Meghnaghat-400 | 241 | 04:00 | 223 | 20:00
Bhulta | 241 | 05:00 | 227 | 12:00 | Mirsorai | 235 | 05:00 | 221 | 13:00
Bibiana | 238 | 02:00 | 230 | 11:00 | Rajshahi | 240 | 05:00 | 227 | 18:00
BIPTC | 242 | 03:00 | 227 | 18:30 | Rampal | 240 | 03:00 | 228 | 13:00
Bogura | 242 | 03:00 | 232 | 08:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 241 | 04:00 | 232 | 08:00 | Rampura | 240 | 04:00 | 224 | 13:00
Borhanuddin | 247 | 05:00 | 242 | 11:00 | Shikalbaha | 227 | 08:00 | 220 | 12:00
BSRM | 234 | 04:00 | 221 | 12:00 | Shyampur | 240 | 04:00 | 226 | 13:00
Cumilla(N) | 239 | 04:00 | 226 | 14:00 | Siddhirganj | 238 | 00:00 | 227 | 12:00
Faridpur | 246 | 04:00 | 236 | 12:00 | Sirajgonj | 246 | 03:00 | 238 | 19:00
Fenchuganj | 238 | 06:00 | 231 | 13:00 | Sreepur | 238 | 04:00 | 229 | 12:00
Feni | 236 | 04:00 | 225 | 12:00 | Tongi | 233 | 19:30 | 225 | 09:00
Ghorashal | 240 | 08:00 | 235 | 00:00
Ghorashal-230 | 233 | 03:00 | 217 | 19:00
Gopalganj | 245 | 02:00 | 236 | 13:00
GPH | 234 | 00:00 | 220 | 13:00
Haripur | 241 | 04:00 | 227 | 13:00
Hasnabad | 240 | 02:00 | 227 | 13:00
Hathazari | 225 | 00:00 | 217 | 12:00
Ishurdi | 242 | 03:00 | 230 | 18:00
Jhenaidah | 240 | 02:00 | 227 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 127 | 12:00 | Lalbag | 135 | 04:00 | 125 | 12:00
Agargaon | 138 | 03:00 | 129 | 12:00 | Lalmonirhat | 135 | 04:00 | 127 | 08:00
Agrabad | 134 | 04:00 | 128 | 11:00 | Madanganj | 138 | 04:00 | 132 | 13:00
AKS | 134 | 10:00 | 128 | 18:00 | Madaripur | 141 | 04:00 | 136 | 13:00
Aminbazar | 137 | 04:00 | 130 | 12:00 | Madartek | 136 | 06:00 | 126 | 13:00
Amnura | 141 | 01:00 | 132 | 08:00 | Madunaghat | 133 | 00:00 | 129 | 13:00
Ashuganj | 143 | 01:00 | 138 | 12:00 | Magura | 138 | 01:00 | 129 | 18:00
Bagerhat | 138 | 04:00 | 130 | 18:30 | Mahasthangarh | 137 | 04:00 | 129 | 08:00
Bajitpur | 138 | 05:00 | 130 | 18:00 | Maijdee | 137 | 04:00 | 129 | 13:00
Bakulia | 134 | 04:00 | 127 | 13:00 | Manikganj | 134 | 18:00 | 124 | 21:00
Banani | 136 | 04:00 | 126 | 13:00 | Maniknagar | 139 | 03:00 | 130 | 12:00
Bangabhaban | 139 | 04:00 | 129 | 13:00 | Matarbari | 127 | 05:00 | 117 | 17:00
Barapukuria | 139 | 05:00 | 130 | 19:30 | Matuail | 141.3 | 06:00 | 134 | 12:00
Barguna | 137 | 05:00 | 133 | 17:00 | Metrorail_Motijheel | 139 | 03:00 | 120 | 19:00
Barishal | 141 | 02:00 | 136 | 12:00 | Metrorail_Uttara | 134 | 01:00 | 127 | 09:00
Barishal-230 | 142 | 04:00 | 136 | 12:00 | Millgate | 136 | 04:00 | 126 | 10:00
Baroaulia | 134 | 04:00 | 128 | 13:00 | Mirpur | 138 | 03:00 | 129 | 12:00
Baroirhat | 135 | 00:00 | 128 | 13:00 | Mirzapur | 137 | 04:00 | 129 | 12:00
Bashundhara | 137 | 05:00 | 127 | 12:00 | Mithapukur | 136 | 04:00 | 127 | 08:00
BashundharaCement | 138 | 04:00 | 132 | 13:00 | MI_Cement | 139.3 | 06:00 | 129 | 12:00
Beanibazar | 135 | 01:00 | 132 | 11:00 | Modern | 0 | 00:00 | 0 | 00:00
Benapole | 137 | 02:00 | 124 | 13:00 | Mogbazar | 136 | 01:00 | 126 | 13:00
Bhaluka | 137 | 04:00 | 128 | 18:00 | Mongla | 138 | 06:00 | 130 | 18:00
Bhandaria | 139 | 05:00 | 8 | 10:00 | Motijheel | 139 | 04:00 | 129 | 13:00
Bhangura | 138 | 05:00 | 133 | 18:30 | Muktagacha | 134 | 10:00 | 122 | 18:00
Bheramara | 142 | 02:00 | 137 | 08:00 | Munshiganj | 139 | 05:00 | 132 | 11:00
Bheramara(GK) | 142 | 03:00 | 136 | 18:00 | Muradnagar | 140 | 04:00 | 131 | 13:00
Bhulta | 135 | 06:00 | 128 | 15:00 | Mymensingh | 133 | 10:00 | 120 | 18:00
Bog-Sherpur | 140 | 23:00 | 132 | 08:00 | Naogaon | 135 | 03:00 | 128 | 08:00
Bogura | 138 | 03:00 | 132 | 07:00 | Narail | 139 | 02:00 | 128 | 18:00
Bogura-230 | 138 | 03:00 | 132 | 08:00 | Narinda | 139 | 03:00 | 130 | 12:00
Brahmanbaria | 137 | 02:00 | 132 | 12:00 | Narshingdi | 138 | 04:00 | 128 | 12:00
Cantonment | 138 | 03:00 | 129 | 12:00 | Natore | 138 | 06:00 | 133 | 08:00
Chandina | 141 | 02:00 | 133 | 13:00 | Nawabganj | 135 | 04:00 | 125 | 13:00
Chandpur | 140 | 03:00 | 135 | 13:00 | Netrakona | 131 | 06:00 | 121 | 18:00
Chandraghona | 136 | 05:00 | 129 | 12:00 | New | 135 | 05:00 | 127 | 09:00
Chapai | 141 | 02:00 | 134 | 19:30 | Niamatpur | 140 | 00:00 | 134 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 140 | 04:00 | 133 | 12:00 | Noapara | 140 | 03:00 | 130 | 12:00
Chauddagram | 137 | 02:00 | 131 | 13:00 | Pabna | 141 | 03:00 | 134 | 18:00
Chhatak | 132 | 00:00 | 130 | 00:00 | Palashbari | 134 | 04:00 | 124 | 08:00
Chowmuhani | 136 | 03:00 | 129 | 12:00 | Panchagarh | 139 | 18:30 | 125 | 14:00
Chuadanga | 140 | 04:00 | 126 | 13:00 | Patiya | 135 | 04:00 | 128 | 12:00
Coxsbazar | 127 | 05:00 | 115 | 16:00 | Patuakhali | 136 | 06:00 | 134 | 11:00
Cumilla(N) | 141 | 04:00 | 134 | 12:00 | Payra | 137 | 02:00 | 134 | 18:30
Cumilla(S) | 140 | 06:00 | 125 | 09:00 | PHP | 135 | 04:00 | 129 | 12:00
Daganbhuiyan | 136 | 05:00 | 129 | 12:00 | Postogola | 140 | 02:00 | 131 | 12:00
Daudkandi | 137 | 04:00 | 131 | 12:00 | Purbachal | 137 | 04:00 | 126 | 12:00
DhakaUniversity | 136 | 05:00 | 127 | 12:00 | Purbasadipur | 132 | 18:30 | 122 | 08:00
Dhamrai | 138 | 05:00 | 130 | 12:00 | Rahanpur | 141 | 01:00 | 136 | 08:00
Dhanmondi | 142 | 04:00 | 135 | 13:00 | Rahanpur-400 | 142 | 01:00 | 136 | 18:00
Dohazari | 134 | 06:00 | 126 | 13:00 | Rahim | 140 | 01:00 | 128 | 08:00
Faridpur | 140 | 04:00 | 135 | 12:00 | Rajbari | 141 | 03:00 | 134 | 13:00
Fatullah | 140 | 05:00 | 130 | 13:00 | Rajendrapur | 138 | 02:00 | 130 | 18:30
Fenchuganj | 141 | 06:00 | 137 | 12:00 | Rajshahi | 138 | 02:00 | 132 | 13:00
Feni | 134 | 05:00 | 128 | 13:00 | Rajshahi-230 | 138 | 03:00 | 131 | 13:00
Feni-230 | 136 | 04:00 | 129 | 13:00 | Ramganj | 137 | 02:00 | 131 | 12:00
Ghatail | 130 | 03:00 | 120 | 18:00 | Rampur | 135 | 05:00 | 127 | 15:00
Ghorashal | 136 | 03:00 | 132 | 15:00 | Rampura | 136 | 04:00 | 126 | 13:00
Goalpara | 141 | 02:00 | 131 | 17:00 | Rangamati | 135 | 04:00 | 128 | 13:00
Gollamari | 140 | 02:00 | 134 | 12:00 | Rangpur | 136 | 04:00 | 127 | 08:00
Gopalganj | 141 | 03:00 | 134 | 13:00 | Ruppur | 142 | 04:00 | 136 | 18:00
Gopalganj-400 | 143 | 04:00 | 136 | 12:00 | Saidpur | 134 | 04:00 | 127 | 19:30
Gulshan | 136 | 05:00 | 126 | 13:00 | Satkhira | 139 | 04:00 | 130 | 18:00
Halishahar | 135 | 04:00 | 127 | 12:00 | Satmasjid | 138 | 05:00 | 129 | 13:00
Haripur | 141 | 03:00 | 134 | 13:00 | Savar | 136 | 05:00 | 129 | 12:00
HaripurSBU | 141 | 03:00 | 134 | 13:00 | SevenRings | 138 | 04:00 | 130 | 19:00
Hasnabad | 140 | 04:00 | 131 | 12:00 | ShahCement | 140 | 04:00 | 133 | 12:00
Hathazari | 134 | 01:00 | 128 | 12:00 | Shahjadpur | 140 | 23:00 | 136 | 16:00
Ishurdi | 143 | 02:00 | 137 | 18:00 | Shahjibazar | 141 | 06:00 | 133 | 11:00
Jaldhaka | 134 | 04:00 | 125 | 22:00 | Shahmirpur | 135 | 00:00 | 128 | 13:00
Jamalpur | 131 | 09:00 | 116 | 18:00 | Shariatpur | 141 | 02:00 | 135 | 13:00
Jashore | 137 | 02:00 | 125 | 13:00 | Sherpur | 129 | 10:00 | 112 | 18:00
Jhenaidah | 140 | 03:00 | 123 | 18:00 | Shikalbaha | 125 | 06:00 | 117 | 17:00
Jhenaidah-230 | 140 | 02:00 | 131 | 13:00 | Shikalbaha-230 | 137 | 03:00 | 129 | 12:00
Joydebpur | 136 | 04:00 | 128 | 13:00 | Shitalakhya | 139.3 | 06:00 | 129 | 12:00
Joypurhat | 134 | 03:00 | 127 | 18:00 | Sholosohor | 135 | 04:00 | 129 | 12:00
Juldah | 136 | 08:00 | 128 | 17:00 | Shyampur | 139 | 06:00 | 129 | 13:00
Kabirpur | 139 | 04:00 | 125 | 10:00 | Shyampur-230 | 139 | 04:00 | 130 | 13:00
Kachua | 142 | 06:00 | 136 | 13:00 | Siddhirganj | 141 | 04:00 | 134 | 12:00
Kaliakoir | 141 | 03:00 | 133 | 12:00 | Sirajganj | 137 | 02:00 | 8 | 05:00
Kallyanpur | 138 | 05:00 | 130 | 12:00 | Sonargaon | 140 | 02:00 | 133 | 12:00
Kalurghat | 135 | 04:00 | 129 | 12:00 | Sreemongol | 139 | 01:00 | 133 | 11:00
Kamrangirchar | 136 | 04:00 | 125 | 12:00 | Sreepur | 138 | 02:00 | 132 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 135 | 05:00 | 126 | 12:00
Kasba | 138 | 01:00 | 132 | 12:00 | SSM | 138 | 04:00 | 130 | 15:00
Kazla | 140 | 07:00 | 129 | 13:00 | Sunamganj | 132 | 00:00 | 129 | 17:00
Keranigonj | 135 | 04:00 | 126 | 12:00 | Sylhet | 135 | 01:00 | 132 | 15:00
Khagrachori | 135 | 05:00 | 128 | 12:00 | Sylhet-132 | 134 | 00:00 | 132 | 11:00
Khulna | 140 | 03:00 | 132 | 13:00 | Tangail | 132 | 06:00 | 123 | 18:00
Khulna(S) | 141 | 04:00 | 134 | 12:00 | Taraganj | 134 | 04:00 | 124 | 08:00
Khulshi | 133 | 06:00 | 126 | 17:00 | Tasnim | 140 | 04:00 | 133 | 12:00
Kishoreganj | 135 | 02:00 | 128 | 18:00 | Thakurgaon | 138 | 18:30 | 125 | 08:00
Kodda | 136 | 18:00 | 126 | 12:00 | TK | 135 | 06:00 | 129 | 12:00
KSRM | 135 | 04:00 | 128 | 12:00 | Tongi | 135 | 19:30 | 130 | 09:00
Kulaura | 139 | 00:00 | 136 | 13:00 | Ullahpara | 138 | 01:00 | 133 | 17:00
Kurigram | 133 | 13:00 | 123 | 08:00 | Ullon | 136 | 04:00 | 127 | 13:00
Kushtia | 138 | 04:00 | 129 | 18:00 | Uttara | 136 | 04:00 | 127 | 21:00
Laksam | 141 | 04:00 | 135 | 12:00 | UttaraNew | 134 | 01:00 | 127 | 09:00
Lakshmipur | 136 | 04:00 | 130 | 12:00 | Zigatola | 136 | 05:00 | 126 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-12-2025 | [28 empty] | Date: | 09-12-2025 | [28 empty] | Date: | 09-12-2025 | [28 empty] | Date: | 09-12-2025 | [28 empty] | Date: | 09-12-2025 | [17 empty] | Date: | 09-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 1 | 350 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 393 | 0 | 143 | 51 | 0 | 196 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 15 | 160 | 0 | 16 | 19 | 34 | 0 | 0 | 0 | 4160.5 | 750 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 0 | 0 | 0 | 964.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 300 | 900 | 0 | 5006.75 | 9167.25 | 99.21
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 360 | 0 | 220 | 51 | 0 | 199 | 0 | 0 | 111 | 0 | 0 | 17 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 4027 | 714 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 844 | 0 | 0 | 0 | 889.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 250 | 750 | 0 | 4545.34 | 8572.34 | 99.2
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 260 | 0 | 260 | 51 | 0 | 200 | 0 | 0 | 111 | 0 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 41 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 3923.5 | 655 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 835.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 250 | 640 | 0 | 4239.27 | 8162.77 | 99.2
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 200 | 0 | 0 | 111 | 0 | 0 | 10 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 3679.5 | 655 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 834.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 560 | 0 | 4100.82 | 7780.32 | 99.2
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 3592.5 | 562 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 0 | 0 | 831.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 570 | 0 | 4010.62 | 7603.12 | 99.19
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 230 | 0 | 230 | 10 | 0 | 207 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 3597.5 | 562 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 837.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 564 | 0 | 4015.45 | 7612.95 | 99.19
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 37 | 294 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 230 | 0 | 230 | 44 | 0 | 200 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 3840.5 | 608 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786 | 0 | 0 | 0 | 835.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 260 | 586 | 0 | 4179.06 | 8019.56 | 99.19
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 44 | 0 | 23 | 355 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 490 | 2 | 0 | 0 | 250 | 0 | 250 | 51 | 0 | 212 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 88 | 0 | 1 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 15 | 159 | 0 | 15 | 19 | 53 | 0 | 1.67 | 0 | 4140.4 | 655 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 866 | 0 | 0 | 0 | 941.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 2 | 0 | 0 | 1.16 | 174 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 7 | 0.01 | 0 | 0 | 115 | 220 | 0 | 350 | 716 | 0 | 4676.98 | 8817.38 | 99.18
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 260 | 0 | 0 | 8 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 44 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 554 | 11 | 0 | 0 | 393 | 0 | 230 | 51 | 0 | 208 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 76 | 0 | 21 | 0 | 305 | 0 | 205 | 0 | 30 | 0 | 1 | 16 | 0 | 79 | 30 | 0 | 15 | 160 | 0 | 57 | 19 | 53 | 1 | 13.05 | 0 | 4404.8 | 751 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 971 | 0 | 0 | 0 | 1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.27 | 22 | 0 | 0 | 12.4 | 184 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 1.41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.4 | 52 | 0.09 | 0 | 0 | 115 | 180 | 0 | 350 | 880 | 0 | 5203.57 | 9608.37 | 99.18
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 260 | 0 | 0 | 17 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.89 | 46 | 0 | 6 | 354 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 515 | 16 | 0 | 0 | 300 | 0 | 230 | 51 | 0 | 189 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 94 | 0 | 43 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 3 | 16 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 57 | 19 | 45 | 1 | 25.89 | 0 | 4314.78 | 844 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 983 | 0 | 0 | 0 | 955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.66 | 54 | 0 | 0 | 33.44 | 175 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 2.81 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3.2 | 99 | 0.2 | 0 | 0 | 115 | 180 | 0 | 300 | 940 | 0 | 5330.31 | 9645.09 | 99.18
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 1 | 0 | 8 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 260 | 0 | 0 | 15 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 46 | 0 | 10 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 420 | 11 | 0 | 0 | 300 | 0 | 260 | 43 | 0 | 203 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 94 | 0 | 56 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 10 | 16 | 0 | 22 | 30 | 0 | 15 | 157 | 0 | 57 | 19 | 35 | 1 | 37.27 | 0 | 4212.01 | 844 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 830 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.75 | 84 | 0 | 0 | 46.21 | 171 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 4.24 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.3 | 136 | 0.19 | 0 | 0 | 100 | 180 | 0 | 300 | 850 | 0 | 5092.69 | 9304.7 | 99.17
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 24.4 | 0 | 29 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 230 | 0 | 0 | 28 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 46 | 0 | 10 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 440 | 8 | 0 | 0 | 330 | 0 | 280 | 43 | 0 | 202 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 100 | 0 | 62 | 0 | 315 | 0 | 206 | 0 | 30 | 0 | 12 | 16 | 0 | 22 | 30 | 0 | 15 | 157 | 0 | 57 | 19 | 35 | 2 | 42.46 | 0 | 4365.13 | 844 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 812 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.92 | 91 | 0 | 0 | 57.25 | 174 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 4.98 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 4.9 | 161 | 0.49 | 0 | 0 | 100 | 220 | 0 | 300 | 800 | 0 | 5107.54 | 9472.67 | 99.17
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 32 | 0 | 59 | 0 | 15 | 0 | 35 | 12 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 28 | 0 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.31 | 46 | 0 | 6 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 580 | 7 | 0 | 0 | 330 | 0 | 255 | 43 | 0 | 210 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 106 | 0 | 61 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 10 | 16 | 0 | 79 | 30 | 0 | 15 | 156 | 0 | 59 | 19 | 35 | 2 | 43.25 | 0 | 4646.56 | 844 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 860 | 0 | 0 | 0 | 938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.86 | 91 | 0 | 0 | 56.33 | 171 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 4.45 | 0 | 0 | 0 | 27 | 34 | 0 | 0 | 0 | 5.6 | 168 | 0.52 | 0 | 0 | 100 | 220 | 0 | 350 | 830 | 0 | 5389.76 | 10036.32 | 99.17
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 41 | 6 | 60 | 0 | 45 | 0 | 35 | 48 | 0 | 0 | 0 | 430 | 0 | 0 | 250 | 0 | 0 | 26 | 0 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.05 | 46 | 0 | 20 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 580 | 18 | 0 | 0 | 280 | 0 | 250 | 43 | 0 | 195 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 112 | 0 | 55 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 5 | 16 | 0 | 79 | 30 | 0 | 15 | 156 | 0 | 58 | 19 | 34 | 1 | 43.59 | 0 | 4671.64 | 844 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 969 | 0 | 0 | 0 | 1075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.79 | 90 | 0 | 0 | 50.33 | 174 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 4.72 | 0 | 0 | 0 | 23 | 108 | 0 | 0 | 0 | 5.4 | 152 | 0.23 | 0 | 0 | 115 | 180 | 0 | 300 | 900 | 0 | 5697.47 | 10369.11 | 99.16
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 53.97 | 17 | 60 | 0 | 15 | 0 | 35 | 17 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 22 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 46 | 0 | 13 | 354 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 530 | 11 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 182 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 114 | 0 | 47 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 9 | 16 | 0 | 78 | 30 | 0 | 15 | 156 | 0 | 59 | 19 | 34 | 1 | 33.19 | 0 | 4471.67 | 844 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 967 | 0 | 0 | 0 | 1021.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.04 | 73 | 0 | 0 | 45.97 | 177 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 4.19 | 0 | 0 | 0 | 22 | 113 | 0 | 0 | 0 | 4.1 | 133 | 0.13 | 0 | 0 | 115 | 180 | 0 | 300 | 900 | 0 | 5551.48 | 10023.15 | 99.16
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 47.7 | 17 | 60 | 0 | 15 | 0 | 35 | 15 | 0 | 0 | 0 | 370 | 0 | 0 | 250 | 0 | 0 | 15 | 0 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 46 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 515 | 15 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 205 | 0 | 0 | 105 | 0 | 0 | 13 | 0 | 108 | 0 | 28 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 5 | 16 | 0 | 81 | 20 | 0 | 15 | 156 | 0 | 59 | 19 | 34 | 1 | 21.95 | 0 | 4358.83 | 844 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 868 | 0 | 0 | 0 | 1020.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.68 | 52 | 0 | 0 | 29.05 | 171 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 2.88 | 0 | 0 | 0 | 17 | 113 | 0 | 0 | 0 | 2.8 | 93 | 0.24 | 0 | 0 | 115 | 180 | 0 | 300 | 850 | 0 | 5283.8 | 9642.63 | 99.16
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 18.5 | 17 | 0 | 0 | 15 | 0 | 35 | 16 | 0 | 0 | 0 | 370 | 0 | 0 | 331 | 0 | 0 | 7 | 0 | 25.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.79 | 46 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 568 | 6 | 0 | 0 | 300 | 0 | 230 | 51 | 0 | 197 | 0 | 0 | 105 | 0 | 4 | 13 | 0 | 110 | 0 | 13 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 1 | 16 | 0 | 81 | 30 | 0 | 15 | 160 | 0 | 59 | 19 | 34 | 0 | 4.02 | 0 | 4444.11 | 844 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 831 | 0 | 0 | 0 | 901.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.04 | 28 | 0 | 0 | 4.71 | 180 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0.36 | 0 | 0 | 0 | 6 | 113 | 0 | 0 | 0 | 1.1 | 36 | 0.11 | 0 | 0 | 115 | 220 | 0 | 300 | 835 | 0 | 5055.19 | 9499.3 | 99.16
17:00 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 0 | 0 | 15 | 0 | 35 | 25 | 0 | 0 | 0 | 325 | 0 | 17 | 280 | 0 | 0 | 1 | 0 | 25.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 15 | 0 | 0 | 46 | 0 | 15 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 350 | 0 | 230 | 51 | 0 | 196 | 0 | 0 | 107 | 2 | 12 | 13 | 0 | 102 | 0 | 1 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 63 | 19 | 34 | 0 | 0.41 | 0 | 4398.91 | 844 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 988 | 0 | 0 | 0 | 1094.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.68 | 180 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0.07 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 115 | 220 | 0 | 407 | 935 | 0 | 5548.25 | 9947.16 | 99.15
18:00 | 0 | 52 | 18 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 35 | 17 | 24 | 52 | 175 | 0 | 35 | 85 | 0 | 0 | 0 | 340 | 0 | 17 | 333 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 24 | 0 | 46 | 0 | 21 | 354 | 0 | 0 | 12 | 0 | 27 | 226 | 0 | 0 | 0 | 550 | 0 | 53 | 0 | 325 | 0 | 230 | 51 | 0 | 211 | 0 | 17 | 108 | 44 | 0 | 13 | 0 | 114 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 159 | 0 | 64 | 19 | 34 | 0 | 0 | 0 | 5023 | 844 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 1329.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 105 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 504 | 1030 | 0 | 6129.92 | 11152.92 | 99.15
19:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 47.6 | 17 | 81 | 15 | 95 | 0 | 35 | 35 | 0 | 0 | 0 | 400 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 21.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 25 | 352 | 0 | 0 | 6 | 0 | 17 | 228 | 0 | 0 | 0 | 560 | 0 | 17 | 0 | 255 | 0 | 230 | 51 | 0 | 213 | 0 | 0 | 109 | 17 | 0 | 19 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 61 | 19 | 34 | 0 | 0 | 0 | 4782.3 | 844 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 1333.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 1045 | 0 | 6082.64 | 10864.94 | 99.15
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 15.6 | 17 | 98 | 15 | 95 | 0 | 35 | 32 | 0 | 0 | 0 | 400 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 21.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 18 | 354 | 0 | 0 | 0 | 0 | 15 | 228 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 250 | 0 | 230 | 51 | 0 | 213 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 110 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 65 | 19 | 34 | 0 | 0 | 0 | 4693.3 | 844 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 1321.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 1046 | 0 | 6022.24 | 10715.54 | 99.15
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 17 | 96 | 15 | 95 | 0 | 35 | 31 | 0 | 0 | 0 | 399 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 21.7 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 250 | 0 | 230 | 51 | 0 | 217 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 67 | 19 | 34 | 0 | 0 | 0 | 4635.7 | 844 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 1333.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 1045 | 0 | 5985.41 | 10621.11 | 99.15
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 95 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 408 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 250 | 0 | 230 | 51 | 0 | 219 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 157 | 0 | 62 | 19 | 34 | 0 | 0 | 0 | 4506 | 844 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1210.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 505 | 1050 | 0 | 5871.11 | 10377.11 | 99.14
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 260 | 0 | 230 | 51 | 0 | 216 | 0 | 0 | 110 | 0 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 15 | 158 | 0 | 68 | 19 | 34 | 0 | 0 | 0 | 4414 | 845 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 0 | 0 | 1138.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 441 | 1050 | 0 | 5669.78 | 10083.78 | 99.14
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 255 | 0 | 230 | 51 | 0 | 216 | 0 | 0 | 110 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 81 | 30 | 0 | 17 | 158 | 0 | 24 | 19 | 34 | 0 | 0 | 0 | 4302 | 853 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 0 | 0 | 0 | 1010.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 305 | 1020 | 0 | 5223.33 | 9525.33 | 99.14
Total KWH | 0 | 322560 | 187680 | 0 | 0 | 0 | 0 | 0 | 8618400 | 0 | 0 | 328680 | 345240 | 749808 | 83520 | 499560 | 0 | 482851 | 302400 | 0 | 0 | 0 | 9997273 | 0 | 72041 | 6778103 | 0 | 0 | 0 | 0 | 455400 | 495000 | 0 | 0 | 0 | 0 | 0 | 0 | 8640 | 0 | 0 | 0 | 50880 | 95040 | 20398 | 1076580 | 0 | 327840 | 8080000 | 0 | 0 | 24480 | 0 | 95345 | 5317960 | 0 | 0 | 0 | 11732726 | 95040 | 93672 | 0 | 6803000 | 0 | 5766000 | 1113776 | 0 | 4974000 | 0 | 40320 | 2379648 | 81120 | 20160 | 312370 | 0 | 2368320 | 0 | 391209 | 0 | 7493500 | 0 | 5033000 | 0 | 718440 | 0 | 57360 | 431328 | 0 | 1575360 | 709440 | 0 | 384000 | 3689750 | 0 | 982800 | 314400 | 927360 | 11100 | 266910 | 0 | 103581788 | 19142545 | 5339232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386640 | 21927280 | 0 | 0 | 0 | 23290200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300656 | 571100 | 0 | 0 | 335248 | 4265455 | 0 | 0 | 0 | 0 | 0 | 9210036 | 0 | 29580 | 0 | 0 | 294682 | 181660 | 865728 | 0 | 0 | 0 | 32992.44 | 1029600 | 2478 | 0 | 0 | 2668000 | 5280909 | 0 | 8147749 | 20917818.18 | 0 | 124219588.62 | 227801376.62