## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-12-2025 | during | 14-12-2025 | during | 14-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 356 | 370 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 334 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.6 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 27.1 | 9 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 180 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 44 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 101 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 410 | 460 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | ST under maint. & Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1174.1 | 1626.6 | 5781.35 | 5749.35 | 2519.06 | 2496.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 34 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 224 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 40 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 49 | 64 | 64 | 40 | 60 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 33 | 33 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 11 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.25 | 0 | 3.23 | 0 | 3.23 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 9 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 397 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 2 | 0 | 6 | 0 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1048.25 | 1449 | 2573.95 | 2561.72 | 2039.73 | 2047.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 194 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 260 | 300 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 250 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 10 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 60 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 102 | 105 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 47 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 102 | 118 | 160 | 160 | 116 | 116 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 10 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1151 | 1148 | 2437.21 | 2372.21 | 1934.51 | 1869.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-12-2025 | during | 14-12-2025 | during | 14-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 73 | 74 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.01 | 0 | 45.15 | 0 | 45.15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 197.01 | 164 | 361.25 | 314 | 313.75 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 53 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 156 | 130 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 13 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 207 | 207 | 205 | 205 | 205 | 205 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 830 | 828 | 859 | 859 | 825 | 825
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 777 | 870 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 339 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 76.96 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 780 | 1060 | 0 | 0 | 1050 | 1050 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1883.96 | 2275 | 2347 | 2272 | 2642.1 | 2567.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 250 | 504 | 0 | 0 | 500 | 500 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 110 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 640 | 996 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1170.54 | 1830 | 1993.32 | 1993.32 | 2053.32 | 2053.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 57.74 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 0 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.4 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 837 | 1297.29 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.85 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1649.99 | 1711.29 | 3083.87 | 2918.87 | 2549.09 | 2384.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 50 | 50 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 174 | 0 | 172.78 | 0 | 172.78 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 210.5 | 84 | 519.98 | 312 | 435.98 | 228
System Total |  |  |  |  | 28823.2 | 28379.108 | 9315.35 | 11115.89 | 19956.93 | 19352.47 | 15312.54 | 14737.08
Forecast Scenario (14-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9070 |  | 0 |  | 9070
|  |  |  | 1:00 | 8580 |  | 0 |  | 8580
|  |  |  | 2:00 | 8170 |  | 0 |  | 8170
|  |  |  | 3:00 | 7870 |  | 0 |  | 7870
|  |  |  | 4:00 | 7660 |  | 0 |  | 7660
|  |  |  | 5:00 | 7560 |  | 0 |  | 7560
|  |  |  | 6:00 | 7970 |  | 0 |  | 7970
|  |  |  | 7:00 | 8720 |  | 0 |  | 8720
|  |  |  | 8:00 | 9690 |  | 0 |  | 9690
|  |  |  | 9:00 | 9800 |  | 0 |  | 9800
|  |  |  | 10:00 | 9340 |  | 0 |  | 9340
|  |  |  | 11:00 | 9550 |  | 0 |  | 9550
|  |  |  | 12:00 | 10180 |  | 0 |  | 10180
|  |  |  | 13:00 | 10530 |  | 0 |  | 10530
|  |  |  | 14:00 | 10070 |  | 0 |  | 10070
|  |  |  | 15:00 | 9640 |  | 0 |  | 9640
|  |  |  | 16:00 | 9550 |  | 0 |  | 9550
|  |  |  | 17:00 | 10400 |  | 0 |  | 10400
|  |  |  | 18:00 | 11430 |  | 0 |  | 11430
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 10880 |  | 0 |  | 10880
|  |  |  | 19:30 | 10760 |  | 0 |  | 10760
|  |  |  | 20:00 | 10730 |  | 0 |  | 10730
|  |  |  | 21:00 | 10370 |  | 0 |  | 10370
|  |  |  | 22:00 | 10060 |  | 0 |  | 10060
|  |  |  | 23:00 | 9590 |  | 0 |  | 9590
Probable Maximum Temperature: |  |  | 29.00°C
Probable Maximum Demand at Day Peak: |  |  | 10180.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11430.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11430.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.41 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:11 hrs on 14-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-12-2025 | [28 empty] | Date: | 13-12-2025 | [28 empty] | Date: | 13-12-2025 | [28 empty] | Date: | 13-12-2025 | [28 empty] | Date: | 13-12-2025 | [17 empty] | Date: | 13-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 155 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 230 | 0 | 250 | 5 | 0 | 199 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 88 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 5 | 30 | 0 | 17 | 154 | 0 | 16 | 0 | 93 | 0 | 0 | 0 | 3817 | 783 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 250 | 700 | 0 | 4556 | 8373 | 98.98
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 152 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 230 | 0 | 250 | 5 | 0 | 195 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 205 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 17 | 154 | 0 | 8 | 0 | 105 | 0 | 0 | 0 | 3666 | 732 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 220 | 0 | 256 | 600 | 0 | 4312 | 7978 | 98.98
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 153 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 230 | 0 | 240 | 5 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 5 | 20 | 0 | 17 | 154 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3349 | 732 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 180 | 0 | 250 | 500 | 0 | 4143 | 7492 | 98.97
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 202 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 17 | 154 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 3260 | 661 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3925 | 7185 | 98.97
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 315 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 17 | 154 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3295 | 497 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3739 | 7034 | 98.97
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 17 | 154 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3251 | 497 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3727 | 6978 | 98.97
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 280 | 0 | 310 | 10 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 320 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 17 | 20 | 0 | 17 | 153 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3542 | 497 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 220 | 0 | 250 | 520 | 0 | 3939 | 7481 | 98.97
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 300 | 0 | 0 | 1 | 0 | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 34 | 155 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 500 | 2 | 0 | 0 | 300 | 0 | 310 | 47 | 0 | 205 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 78 | 0 | 4 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 1 | 16 | 0 | 82 | 30 | 0 | 17 | 155 | 0 | 8 | 3 | 110 | 0 | 1.75 | 0 | 3926.08 | 497 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 842 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 3 | 0 | 0 | 1.52 | 153 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0.16 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0 | 0 | 0 | 115 | 220 | 0 | 250 | 615 | 0 | 4167.99 | 8094.07 | 98.97
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 10 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.89 | 40 | 0 | 15 | 155 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 584 | 9 | 0 | 0 | 300 | 0 | 310 | 51 | 0 | 201 | 0 | 0 | 110 | 0 | 0 | 6 | 0 | 86 | 0 | 26 | 0 | 310 | 0 | 205 | 0 | 30 | 0 | 4 | 16 | 0 | 82 | 30 | 0 | 17 | 155 | 0 | 24 | 8 | 108 | 1 | 13.51 | 0 | 4110.4 | 645 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 900 | 0 | 0 | 0 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.41 | 25 | 0 | 0 | 14.01 | 168 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 1.8 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.4 | 54 | 0.06 | 0 | 0 | 115 | 180 | 0 | 256 | 800 | 0 | 4734.68 | 8845.08 | 98.97
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 20 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.05 | 40 | 0 | 13 | 155 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 475 | 0 | 0 | 0 | 260 | 0 | 250 | 51 | 0 | 198 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 84 | 0 | 47 | 0 | 300 | 0 | 205 | 0 | 30 | 0 | 8 | 16 | 0 | 82 | 20 | 0 | 18 | 155 | 0 | 24 | 8 | 109 | 1 | 30.14 | 0 | 3858.19 | 681 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 830 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.16 | 56 | 0 | 0 | 38.37 | 163 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 3.47 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3.8 | 105 | 0.14 | 0 | 0 | 115 | 180 | 0 | 250 | 720 | 0 | 4658.94 | 8517.13 | 98.96
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 27 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.78 | 40 | 0 | 11 | 250 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 346 | 17 | 0 | 0 | 250 | 0 | 250 | 10 | 0 | 156 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 98 | 0 | 60 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 10 | 16 | 0 | 5 | 20 | 0 | 18 | 156 | 0 | 8 | 8 | 72 | 2 | 40 | 0 | 3592.78 | 681 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.3 | 765 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.09 | 78 | 0 | 0 | 51.08 | 164 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 4.74 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 4.6 | 145 | 0.2 | 0 | 0 | 115 | 180 | 0 | 250 | 600 | 0 | 4493.01 | 8085.79 | 98.96
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 250 | 0 | 0 | 30 | 0 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3.14 | 40 | 0 | 11 | 354 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 307 | 19 | 0 | 0 | 260 | 0 | 260 | 10 | 0 | 197 | 0 | 0 | 103 | 0 | 0 | 15 | 0 | 94 | 0 | 66 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 5 | 20 | 0 | 17 | 156 | 0 | 20 | 19 | 72 | 2 | 45.84 | 0 | 4002.98 | 680 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.35 | 780 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.37 | 93 | 0 | 0 | 56.87 | 170 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 5.33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.4 | 168 | 0.38 | 0 | 0 | 115 | 220 | 0 | 250 | 600 | 0 | 4736.7 | 8739.68 | 98.96
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 300 | 0 | 0 | 29 | 0 | 27.1 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.25 | 40 | 0 | 12 | 354 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 397 | 19 | 0 | 0 | 393 | 0 | 260 | 10 | 0 | 208 | 0 | 0 | 102 | 0 | 0 | 9 | 0 | 102 | 0 | 67 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 53 | 30 | 0 | 17 | 156 | 0 | 56 | 19 | 73 | 2 | 47.01 | 0 | 4400.36 | 777 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.96 | 780 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.74 | 95 | 0 | 0 | 59.85 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.4 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 5.5 | 174 | 0.54 | 0 | 0 | 100 | 180 | 0 | 250 | 640 | 0 | 4914.99 | 9315.35 | 98.96
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 300 | 0 | 0 | 27 | 0 | 27.1 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 4 | 354 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 425 | 18 | 0 | 0 | 393 | 0 | 300 | 42 | 0 | 196 | 0 | 0 | 102 | 0 | 0 | 13 | 0 | 98 | 0 | 63 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 82 | 30 | 0 | 17 | 156 | 0 | 56 | 19 | 72 | 2 | 44.48 | 0 | 4509.58 | 775 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.59 | 850 | 0 | 6 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.83 | 89 | 0 | 0 | 56.91 | 196 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.19 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5.4 | 163 | 0.51 | 0 | 0 | 115 | 220 | 0 | 256 | 760 | 0 | 5154.43 | 9664.01 | 98.96
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 300 | 0 | 0 | 21 | 0 | 27.1 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 427 | 15 | 0 | 0 | 340 | 0 | 300 | 51 | 0 | 202 | 0 | 0 | 107 | 0 | 0 | 13 | 0 | 104 | 0 | 53 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 9 | 16 | 0 | 81 | 30 | 0 | 17 | 156 | 0 | 59 | 19 | 72 | 2 | 37.99 | 0 | 4436.09 | 770 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.85 | 854 | 0 | 5 | 0 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.88 | 79 | 0 | 0 | 46.31 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 4.35 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.5 | 135 | 0.42 | 0 | 0 | 115 | 220 | 0 | 257 | 800 | 0 | 4893.31 | 9329.4 | 98.96
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 300 | 0 | 0 | 13 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1.66 | 40 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 502 | 11 | 0 | 0 | 360 | 0 | 300 | 51 | 0 | 201 | 0 | 0 | 103 | 0 | 0 | 13 | 0 | 118 | 0 | 39 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 5 | 16 | 0 | 81 | 30 | 0 | 17 | 158 | 0 | 59 | 19 | 74 | 1 | 26.8 | 0 | 4483.46 | 775 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.98 | 798 | 0 | 6 | 0 | 822.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.25 | 49 | 0 | 0 | 27.34 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 3.01 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3.1 | 97 | 0.29 | 0 | 0 | 115 | 220 | 0 | 300 | 660 | 0 | 4623.11 | 9106.57 | 98.95
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 328 | 0 | 0 | 6 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.76 | 40 | 0 | 2 | 354 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 530 | 6 | 0 | 0 | 345 | 0 | 300 | 51 | 0 | 193 | 0 | 0 | 104 | 0 | 0 | 13 | 0 | 108 | 0 | 18 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 2 | 16 | 0 | 81 | 30 | 0 | 17 | 130 | 0 | 59 | 19 | 74 | 0 | 10.83 | 8 | 4474.59 | 681 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.65 | 806 | 0 | 6 | 0 | 901.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.79 | 22 | 0 | 0 | 11.24 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.5 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 32 | 0.12 | 0 | 0 | 110 | 220 | 0 | 325 | 660 | 0 | 4475.91 | 8950.5 | 98.95
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 1 | 0 | 13 | 0 | 40 | 0 | 55 | 16 | 0 | 0 | 0 | 455 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 16 | 0 | 0 | 12 | 0.02 | 40 | 0 | 6 | 354 | 0 | 0 | 1 | 0 | 4 | 223 | 0 | 0 | 0 | 580 | 0 | 10 | 0 | 270 | 0 | 300 | 51 | 0 | 188 | 0 | 0 | 105 | 3 | 0 | 13 | 0 | 112 | 0 | 1 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 0 | 17 | 130 | 0 | 59 | 19 | 74 | 0 | 0.37 | 12 | 4540.39 | 681 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.79 | 946 | 0 | 6 | 0 | 1096.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 1 | 0 | 0 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.07 | 0 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0.1 | 2 | 0.01 | 0 | 0 | 110 | 220 | 0 | 402 | 790 | 0 | 5073.76 | 9614.15 | 98.95
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17.6 | 0 | 44 | 0 | 180 | 0 | 55 | 101 | 0 | 0 | 0 | 460 | 0 | 17 | 334 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 49 | 0 | 24 | 50 | 0 | 40 | 9 | 11 | 354 | 0 | 0 | 34 | 0 | 40 | 224 | 0 | 0 | 0 | 612 | 0 | 60 | 0 | 250 | 0 | 300 | 51 | 0 | 194 | 0 | 10 | 105 | 47 | 0 | 13 | 0 | 118 | 0 | 0 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 0 | 13 | 0 | 81 | 30 | 0 | 17 | 130 | 0 | 59 | 19 | 74 | 0 | 0 | 12 | 5215.6 | 870 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 6 | 0 | 1297.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 504 | 996 | 0 | 5900.29 | 11115.89 | 98.94
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 35 | 0 | 60 | 0 | 95 | 0 | 55 | 17 | 0 | 0 | 0 | 385 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 18 | 354 | 0 | 0 | 0 | 0 | 98 | 225 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 255 | 0 | 270 | 51 | 0 | 205 | 0 | 0 | 106 | 120 | 0 | 19 | 0 | 114 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 13 | 0 | 82 | 30 | 0 | 17 | 129 | 0 | 59 | 19 | 73 | 0 | 0 | 12 | 4880 | 870 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 8 | 0 | 1439.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 501 | 1056 | 0 | 6016.98 | 10896.98 | 98.94
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 61 | 0 | 30 | 0 | 35 | 0 | 0 | 0 | 0 | 405 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 18 | 354 | 0 | 0 | 0 | 0 | 93 | 228 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 270 | 0 | 270 | 51 | 0 | 202 | 0 | 0 | 108 | 83 | 0 | 19 | 0 | 110 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 13 | 0 | 82 | 30 | 0 | 17 | 130 | 0 | 59 | 19 | 74 | 0 | 0 | 6 | 4730 | 870 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 1445.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 502 | 1062 | 0 | 6098.52 | 10828.52
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 390 | 0 | 17 | 334 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 20 | 354 | 0 | 0 | 0 | 0 | 34 | 229 | 0 | 0 | 0 | 568 | 0 | 0 | 0 | 275 | 0 | 270 | 51 | 0 | 202 | 0 | 0 | 108 | 85 | 0 | 19 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 13 | 0 | 82 | 30 | 0 | 19 | 128 | 0 | 59 | 19 | 76 | 0 | 0 | 0 | 4598 | 869 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 1452.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 435 | 1064 | 0 | 6029.39 | 10627.39 | 98.93
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 400 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 40 | 0 | 31 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 275 | 0 | 270 | 51 | 0 | 202 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 19 | 129 | 0 | 59 | 19 | 75 | 0 | 0 | 0 | 4472 | 869 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1445.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 303 | 1080 | 0 | 5944.44 | 10416.44 | 98.93
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 275 | 0 | 270 | 51 | 0 | 202 | 0 | 0 | 110 | 0 | 0 | 19 | 0 | 100 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 19 | 130 | 0 | 59 | 19 | 75 | 0 | 0 | 0 | 4349 | 870 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 0 | 0 | 0 | 1443.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 255 | 1050 | 0 | 5806.44 | 10155.44 | 98.92
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 585 | 0 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 206 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 102 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 13 | 0 | 82 | 30 | 0 | 18 | 130 | 0 | 35 | 0 | 76 | 0 | 0 | 0 | 4159 | 775 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 1319.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 950 | 0 | 5364.73 | 9523.73 | 98.92
Total KWH | 0 | 27840 | 0 | 0 | 0 | 0 | 0 | 0 | 8496000 | 0 | 0 | 72720 | 0 | 259200 | 0 | 348513 | 0 | 461134 | 144000 | 0 | 0 | 0 | 8689958 | 0 | 72173 | 7119967 | 0 | 0 | 184465 | 0 | 360600 | 530280 | 0 | 0 | 0 | 0 | 0 | 0 | 33600 | 0 | 41280 | 0 | 28800 | 195840 | 16684 | 824000 | 20909 | 407040 | 6472727.27 | 0 | 0 | 68160 | 0 | 239200 | 5239698 | 0 | 0 | 0 | 11050908 | 108945 | 132145 | 0 | 6804500 | 0 | 6594000 | 907520 | 0 | 4855000 | 0 | 24960 | 2102603 | 296640 | 0 | 339010 | 0 | 2278080 | 0 | 448291 | 0 | 7556000 | 0 | 5039000 | 0 | 719160 | 0 | 68780 | 398280 | 0 | 1245120 | 636384 | 0 | 422000 | 3109670 | 0 | 834000 | 249600 | 2032320 | 13150 | 297530 | 52080 | 98970464.27 | 17012363 | 6985728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477360 | 21163640 | 0 | 57958 | 0 | 24070305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340512 | 599930 | 0 | 0 | 360000 | 2224727 | 0 | 66000 | 0 | 0 | 0 | 8888872 | 0 | 34020 | 0 | 0 | 201123 | 189968 | 76329 | 0 | 0 | 0 | 34493.16 | 1089360 | 2670 | 0 | 0 | 2628000 | 5284057 | 0 | 7254527 | 18775272.73 | 0 | 117817214.89 | 216787679.16

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9315.35 | MW | 12:00 Hr. | Energy Generated |  |  | 216.7877 |  | MKWHr.
| Day Peak Demand |  |  | 9315.35 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11115.89 | MW | 18:00 Hr. | Energy Demand |  |  | 216.7877 |  | MKWHr.
| Evening Peak Demand |  |  | 11115.89 | MW | 18:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 6978 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 735.37 |  | MMCFD
| Maximum Generation of the Day |  |  | 11115.89 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.3362 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.1968 | 0 | 1.3856 | 0 | 0 | 0.18446 | 0 | 0 | 26.7669 | Gas | 99.7395 | Gas | 347232142.14
| Chattogram Zone |  |  | 5.6467 | 17.5236 | 0.59419 | 0 | 0.824 | 0.12563 | 0 | 0.0336 | 24.7478 | Coal | 64.7171 | Coal | 414540369.7598
| Cumilla Zone |  |  | 21.6026 | 0 | 0.45375 | 0 | 0 | 0.44829 | 2.2781 | 0 | 24.7827 | HFO | 3.8466 | HFO | 63913547.28
| Mymensingh Zone |  |  | 2.0323 | 0 | 1.1357 | 0 | 0 | 0.31068 | 0 | 0 | 3.4787 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 19.1256 | 0 | 0 | 0 | 0 | 0.06878 | 0 | 0 | 19.1944 | Hydro | 0.824 | Hydro | 82400
| Khulna Zone |  |  | 7.0437 | 21.1636 | 0 | 0 | 0 | 0.47736 | 17.0124 | 0 | 45.697 | Solar | 4.2662 | Solar | 67323103.4536
| Barishal Zone |  |  | 7.9121 | 26.0298 | 0 | 0 | 0 | 0.00267 | 0 | 0 | 33.9445 | Import | 43.3607 | Import | 263246740.62
| Rajshahi Zone |  |  | 11.1796 | 0 | 0 | 0 | 0 | 1.3345 | 24.0703 | 0 | 36.5844 | Wind | 0.0336 | Wind | 494256
| Rangpur Zone |  |  | 0 | 0 | 0.27745 | 0 | 0 | 1.3138 | 0 | 0 | 1.5913
| Total |  |  | 99.7395 | 64.7171 | 3.8466 | 0 | 0.824 | 4.2662 | 43.3607 | 0.0336 | 216.7877
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 347232142.14 |  | Hydro | 82400
|  |  |  | Coal | 414540369.7598 |  | Solar | 67323103.4536
|  |  |  | HFO | 63913547.28 |  | Import | 263246740.62
|  |  |  | HSD | 0 |  | Wind | 494256
[5 empty] | Total: | 115,68,32,559 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.0124 | Peak Hr Flow | 870.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47924763.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.0703 | Peak Hr Flow | 1297.29 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2397 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2781 | Peak Hr Flow | 118.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2726 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.3607 | Peak Hr Flow | 2285.29 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3965
|  |  |  | Chattogram |  | 0 |  | 1275
|  |  |  | Cumilla |  | 0 |  | 959
|  |  |  | Mymensingh |  | 0 |  | 885
|  |  |  | Sylhet |  | 0 |  | 407
|  |  |  | Khulna |  | 0 |  | 1287
|  |  |  | Barishal |  | 0 |  | 321
|  |  |  | Rajshahi |  | 0 |  | 1019
|  |  |  | Rangpur |  | 0 |  | 764
|  |  |  | Total |  | 0 |  | 10882
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 08:55 | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D
| 08:01 | 10:18 | Chandpur 132/33kV S/S 402T (T-01) HT Forced S/D Due to Bus section 1 maintenance | [7 empty] | 8.0MW load
interrup.
| 08:01 | 10:18 | Chandpur 132/33kV S/S 33 kV T-1 Section Forced S/D Due to Maintenance | [7 empty] | 8.0MW load
interrup.
| 08:07 | 17:28 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Annual Maintenance
| 08:08 | 17:28 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Annual maintenance
| 08:10 | 15:34 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to A/M
| 08:10 | 17:04 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) LT Scheduled S/D Due to Annual
Maintenance.
| 08:11 | 17:02 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) HT Scheduled S/D Due to Annual
Maintenance.
| 08:12 | 15:50 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Scheduled S/D Due to Annual maintance
| 08:13 | 15:49 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Scheduled S/D Due to annual
maintanance
| 08:16 | 11:28 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Scheduled S/D Due to Annual maintenance PBS | [7 empty] | 10.0MW load
|  |  | Side.(33kv Bus) | [7 empty] | interrup.
| 08:16 | 11:29 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Scheduled S/D Due to Annual maintenance PBS | [7 empty] | 10.0MW load
|  |  | side. (33kv Bus) | [7 empty] | interrup.
| 08:16 | 17:31 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Annual maintenance.
| 08:16 | 17:30 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Annual maintenance.
| 08:17 | 16:59 | Bhulta 400/230kV S/S 230kV Bus-02 Scheduled S/D
| 08:19 | 14:31 | Bogura 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Maintenance work. | [7 empty] | 25.0MW load
interrup.
| 08:19 | 10:10 | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Maintenance work.
| 08:19 | 14:31 | Bogura 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Maintenance work. | [7 empty] | 25.0MW load
interrup.
| 08:19 | 10:10 | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Maintenance Work. | [7 empty] | 25.0MW load
interrup.
| 08:21 | 14:29 | Sirajganj 132/33kV S/S T2-(425) LT Scheduled S/D Due to Annual Maintenance
| 08:22 | 14:29 | Sirajganj 132/33kV S/S T2-(425) HT Scheduled S/D Due to Annual Maintenance. all
operations have been conducted by the instruction of ALDC,Bogura, according to QF-GMD-18
| 08:22 | 10:11 | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to Red hot spot maintenance work for | [7 empty] | 13.0MW load
|  |  | N-4 feeder source side DS. | [7 empty] | interrup.
| 08:22 | 16:51 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to
Annual Maintenance and from Fenchuganj 230/132/33kV end Due to Annual maintenance
| 08:24 | 10:13 | Narail 132/33kV S/S TR1 (403-T) HT Scheduled S/D Due to Red hot spot maintenance work for | [7 empty] | 13.0MW load
|  |  | N-4 feeder source side DS | [7 empty] | interrup.
| 08:27 | 16:54 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end Due to Annual
maintenance and from Barishal 132/33kV end Due to Annual maontenance work
| 08:28 | 16:54 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Annual
maontenance work
| 08:28 | 16:43 | Rajshahi 230/132/33kV S/S 132 kV Main BUS-02 Scheduled S/D Due to Annual Maintenance
| 08:28 |  | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D Due to Annual maintenance.
| 08:29 |  | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D Due to Annual Maintenance
| 08:30 | 18:02 | Amnura-Rajshahi 132kV Ckt-1 Scheduled S/D from Rajshahi 230/132/33kV end Due to Annual
Maintenance. and from Amnura 132/33kV end Due to Annual Maintenance
| 08:30 | 09:58 | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D Due to 33 kV BUS B Phase conductor | [7 empty] | 24.0MW load
|  |  | repair | [7 empty] | interrup.
| 08:31 | 16:50 | Chapai 132/33kV S/S T-4 (435T) LT Scheduled S/D Due to Annual maintenance
| 08:32 | 16:42 | Chapai 132/33kV S/S T-4 (435T) HT Scheduled S/D Due to Annual maintenance
| 08:34 | 14:00 | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance
| 08:34 | 14:00 | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance
| 08:36 | 17:51 | Madanganj 132/33kV S/S GT-1 LT Scheduled S/D Due to Annual maintenance
| 08:37 | 16:15 | Patuakhali-Payra 132kV Ckt-2 Scheduled S/D from Payra 400/132/33kV end Due to | [7 empty] | 19.0MW load
|  |  | Maintenance | [7 empty] | interrup. Payra
400/132/33kV end
| 08:38 | 17:43 | Madanganj 132/33kV S/S GT-1 HT Scheduled S/D Due to Annual maintenance
| 08:41 | 13:35 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual maintenance
| 08:42 | 13:34 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance
| 08:44 | 15:19 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Scheduled S/D Due to Annual maintenance
| 08:46 | 17:19 | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Annual
Maintenance. and from Natore 132/33kV end Due to Annual maintenance work
| 09:04 | 13:38 | Kodda 132/33kV S/S RPCL 100 MW PS Scheduled S/D
| 09:13 | 13:13 | Jashore 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
| 09:14 | 13:12 | Jashore 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
| 09:15 | 17:38 | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Dead line
checking by Siddhirganj S/S and from Sonargaon 132/33kV end Due to Annual maintenance
| 09:22 | 13:32 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual maintenance
| 09:25 | 16:02 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Annual Maintenance
| 09:25 | 16:02 | Beanibazar 132/33kV S/S 132 KV BUS-2 Scheduled S/D Due to Annual Maintenance
| 09:26 | 16:01 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Annual Maintenance
| 09:30 | 11:59 | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to Due to under ground Cable moving
work.
| 09:30 | 11:58 | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to Due to under ground Cable moving
work.
| 09:40 | 15:54 | Rangpur 132/33kV S/S 132KV Bus B Project Work S/D
|  | 09:41 | Mymensingh-Netrokona 132kV Ckt-1 is restored.
| 09:44 | 13:50 | Mymensingh-Netrokona 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to NLDC
AE.
| 09:50 | 16:00 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Scheduled S/D Due to Annual
Maintenance
| 09:50 | 15:58 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Annual
Maintenance
| 10:06 | 12:01 | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Kodda 132/33kV end.
| 10:07 | 12:00 | Kodda-Rajendrapur 132kV Ckt-2 Scheduled S/D from Kodda 132/33kV end.
| 10:37 | 15:58 | Tangail 132/33kV S/S Kaliakair-1 Scheduled S/D Due to SPS installation by SPMD
| 10:37 | 15:58 | Kaliakoir-Tangail 132kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual maintenance at Tangail End.
| 11:31 | 15:31 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Scheduled S/D Due to Annual maintenance | [7 empty] | 10.0MW load
|  |  | PBS side. (33kv Bus) | [7 empty] | interrup.
| 11:31 | 15:30 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Scheduled S/D Due to Annua maintenance PBS | [7 empty] | 10.0MW load
|  |  | side. (33kb Bus) | [7 empty] | interrup.
| 11:45 |  | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Annual maintenance
| 12:00 |  | Day peak generation 9311 MW
| 12:08 | 12:38 | Kodda 132/33kV S/S Tr-1 (406T) LT Scheduled S/D
| 12:09 | 12:36 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D
| 12:39 | 13:12 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D
| 12:39 | 13:12 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D
| 12:39 | 13:12 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D
|  | 13:07 | Keranigonj 230/132/33kV S/S ATR-2 HT is restored.
|  | 13:08 | Keranigonj 230/132/33kV S/S ATR-2 LT is restored.
|  | 13:10 | Munshiganj 132/33kV S/S Transformer-1 LT is restored.
|  | 13:10 | Munshiganj 132/33kV S/S Transformer-1 HT is restored.
| 13:12 | 13:50 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D
| 13:14 | 13:49 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D
| 13:31 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 13:34 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 14:23 | 14:59 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to Bus1 annual maintenance
| 14:23 | 14:57 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to 132KV Bus 1 Annual maintenance
work
| 14:29 |  | Mymensingh-Netrokona 132kV Ckt-1 Project Work S/D from Mymensingh 132/33kV end Due to G
to G project work.
| 15:01 |  | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to 132KV BUS1 SHUTDOWN FOR ANNUAL
MAINTENANCE
| 15:01 | 15:29 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to Bus1 shutdown for annual
maintenance
| 15:42 | 17:05 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Forced S/D from Rajshahi 230/132/33kV end Due to
Emergency DS maintenance
|  | 15:42 | Gulshan 132/33kV S/S MT-2 HT is restored.
| 15:42 |  | Niamatpur 132/33kV S/S Transformer-3(426T) LT Scheduled S/D Due to PBS 33kV Bus
| 15:42 |  | Niamatpur 132/33kV S/S Transformer-3(426T) HT Scheduled S/D Due to PBS 33kV Bus
|  | 15:50 | Gulshan 132/33kV S/S MT-2 LT is restored.
| 16:01 | 17:13 | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to SPS installation by SPMD
| 16:03 | 17:12 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Scheduled S/D Due to Shutdown taken by
Tangail grid.
| 16:03 | 17:12 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Scheduled S/D Due to Shutdown taken by
Tangail grid.
|  | 16:10 | Daudkandi 132/33kV S/S Transformer-2 HT is restored.
|  | 16:16 | Patuakhali 132/33kV S/S Main Bus is restored.
|  | 16:16 | Patuakhali-Payra 132kV Ckt-1 is restored.
|  | 16:16 | Patuakhali-Payra 132kV Ckt-2 is restored.
|  | 16:17 | Patuakhali 132/33kV S/S 405T (T-1) LT is restored.
|  | 16:17 | Patuakhali 132/33kV S/S 405T (T-1) HT is restored.
|  | 16:20 | Daudkandi 132/33kV S/S Transformer-2 LT is restored.
|  | 16:22 | Patuakhali 132/33kV S/S UPPL (150MW) 132kV LINE is restored.
|  | 16:24 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
|  | 16:24 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
|  | 16:24 | Patuakhali 132/33kV S/S 415T (T-2) LT is restored.
|  | 16:24 | Patuakhali 132/33kV S/S 415T (T-2) HT is restored.
|  | 16:34 | Barguna 132/33kV S/S Transformer-1 HT is restored.
|  | 16:36 | Barguna 132/33kV S/S Transformer-1 LT is restored.
|  | 16:37 | Barguna 132/33kV S/S Transformer-2 HT is restored.
|  | 16:38 | Barguna 132/33kV S/S Transformer-2 LT is restored.
|  | 16:48 | Munshiganj 132/33kV S/S Transformer-2 LT is restored.
|  | 16:48 | Munshiganj 132/33kV S/S Transformer-2 HT is restored.
|  | 16:53 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
|  | 17:01 | Khulna(C )-Khulna (S) 132kV Ckt-2 is restored.
|  | 17:13 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT is restored.
|  | 17:13 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) LT is restored.
|  | 17:15 | Hasnabad-Keraniganj 230kV Ckt-1 is restored.
| 17:25 |  | Khulna (C) S/S Tr-2 415 T HT Tripped showing no relay relays Due to unknown
| 17:58 |  | Khulna (C) S/S Tr-2 415 T LT Forced S/D Due to for tr2 HT site trip
| 18:00 |  | Evening Peak Generation: 11115 MW.
| 19:13 |  | Bhulta-Ghorashal 230 ckt-1 tripped, showing SOTF and distance relay.
|  | 19:13 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
|  | 19:22 | Ghorasal-Tongi 230kV Ckt-2 is restored.
|  | 19:23 | Ghorasal-Tongi 230kV Ckt-1 is restored.
| 20:26 |  | Sirajganj unit-2 GT was synchronized.
| 00:39 |  | Sirajganj unit-2 ST was sync.
| 05:00 |  | Minimum Generation: 7490 MW
| 05:00 | 05:29 | Cumilla(S) 132/33kV S/S TR-4 LT Tripped showing REF 615 relays Due to 33KV SAS Still Mill | [7 empty] | 25.0MW load
|  |  | . | [7 empty] | interrup.
| 05:00 | 05:26 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF 615 relays Due to 33KV SAS Still Mill | [7 empty] | 25.0MW load
|  |  | . | [7 empty] | interrup.
| 07:04 |  | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from Feni 230/132kV end Due to korerhat ss
commisionning
| 07:04 |  | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to korerhat ss
commisionning
| 07:13 |  | Maniknagar 230/132kV S/S Auto Transformer-01(705T) LT Scheduled S/D Due to Annual
Maintenance
| 07:14 |  | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT Scheduled S/D Due to Annual
Maintenance
| 07:16 |  | Maniknagar-Siddhirganj 230kV Ckt-1 Scheduled S/D from Siddhirganj 230/132kV end Due to
Annual maintenance work for Maniknagar ss end
| 07:27 |  | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Rampura 230/132kV end Due to Deadline Line
Checking. and from Bhulta 400/230kVend.
| 07:27 |  | Bhulta-Rampura 230 kV Ckt-3 Scheduled S/D from Rampura 230/132kV end Due to Deadline
Checking work and from Bhulta 400/230kVend.
| 07:58 |  | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 370 | 8496000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 334 | 7119967 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.6 | 72720 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 461134 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 72173 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 9 | 360600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 530280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 180 | 348513 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 44 | 259200 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 27840 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 101 | 144000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 184465 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 460 | 8689958 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1626.6 | 26766850
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 108945 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 34 | 68160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 824000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5239698 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 40 | 239200 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 49 | 41280 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 28800 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 407040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16684 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 9 | 20909 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 195840 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 11050908 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 33600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 6472727.27 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1449 | 24747791.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 194 | 4855000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 300 | 6594000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 250 | 6804500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 907520 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 60 | 132145 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2102603 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 47 | 296640 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 118 | 2278080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 339010 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 10 | 24960 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 448291 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1148 | 24782749
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 74 | 2032320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 249600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 834000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 297530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 52080 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 164 | 3478680
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 68780 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719160 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 636384 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1245120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 130 | 3109670 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 422000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 398280 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7556000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5039000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 828 | 19194394
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 6 | 57958 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 870 | 17012363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 339 | 6985728 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 477360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1060 | 21163640 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2275 | 45697049
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 504 | 7254527 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2628000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 996 | 18775272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5284057 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2670 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1830 | 33944526.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 340512 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 2224727 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 66000 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8888872 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1297.29 | 24070305 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 360000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 599930 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1711.29 | 36584366
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 76329 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34493.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 201123 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189968 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1089360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 84 | 1591273.16
Eastern Grid Total |  |  |  |  | 17395.105 | 5215.6 | 98970464.27
Western Grid Total |  |  |  |  | 10984.003 | 5900.29 | 117817214.89
National Grid Total |  |  |  |  | 28379.108 | 11115.89 | 216787679.16
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7491.22 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3391.2 | MW
i) Dhaka area |  |  | 3964.82 |  | MW | i) Khulna area |  |  |  | 1287 | MW
ii) Chattogram area |  |  | 1275.4 |  | MW | ii) Barishal area |  |  |  | 321 | MW
iii) Cumilla area |  |  | 959 |  | MW | iii) Rajshahi area |  |  |  | 1019.2 | MW
iv) Mymensingh area |  |  | 885 |  | MW | iv) Rangpur area |  |  |  | 764 | MW
v) Sylhet area |  |  | 407 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10882.42 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 53 | 18:30 | 133 | Niamatpur | 49 | 18:00
2 | AKSML | 92 | 08:00 | 68 | Ishurdi | 55 | 18:00 | 134 | Noapara | 38 | 18:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 53 | 18:00 | 135 | PHP | 9 | 09:00
4 | Agargaon | 85 | 13:00 | 70 | Jamalpur | 93 | 18:00 | 136 | Pabna | 72 | 18:00
5 | Agrabad | 44 | 19:00 | 71 | Jashore | 95 | 18:00 | 137 | Palashbari | 80 | 08:00
6 | Amnura | 25 | 08:00 | 72 | Jhenaidah | 99 | 18:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 66 | 13:00 | 73 | Joydebpur | 96 | 18:00 | 139 | Patiya | 6.4 | 18:00
8 | BSRM | 203 | 17:00 | 74 | Joypurhat | 41 | 18:00 | 140 | Patuakhali | 56.5 | 18:30
9 | Bagerhat | 65 | 18:00 | 75 | Juldah | 14 | 11:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 55 | 22:00 | 76 | KSRM | 21 | 11:00 | 142 | Postogola | 40 | 13:00
11 | Bakulia | 66 | 18:30 | 77 | Kabirpur | 178 | 12:00 | 143 | Purbachal | 26 | 13:00
12 | Banani | 39.2 | 14:00 | 78 | Kachua | 54 | 19:30 | 144 | Purbasadipur | 109 | 18:30
13 | Bangabhaban | 6 | 11:00 | 79 | Kallyanpur | 78 | 14:00 | 145 | Rahanpur | 22 | 12:00
14 | Barapukuria | 49 | 19:00 | 80 | Kalurghat | 30 | 18:00 | 146 | Rahim | 21 | 09:00
15 | Barguna | 12 | 17:00 | 81 | Kamrangirchar | 55 | 12:00 | 147 | Rajbari | 60 | 18:00
16 | Barishal | 84 | 21:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 92 | 19:00
17 | Barishal-230 | 68 | 18:00 | 83 | Kasba | 21 | 19:00 | 149 | Rajshahi | 90 | 13:00
18 | Baroaulia | 51 | 13:00 | 84 | Kazla | 84 | 13:00 | 150 | Rajshahi-230 | 48 | 18:00
19 | Baroirhat | 47 | 18:00 | 85 | Keranigonj | 53 | 13:00 | 151 | Ramganj | 68 | 18:00
20 | Bashundhara | 142 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 30 | 18:00
21 | BashundharaCement | 7 | 11:00 | 87 | Khulna | 51 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 54 | 18:00 | 88 | Khulshi | 174 | 16:00 | 154 | Rangpur | 89 | 18:00
23 | Benapole | 42 | 18:00 | 89 | Kishoreganj | 86 | 18:00 | 155 | Ruppur | 1.6 | 14:00
24 | Bhaluka | 119 | 18:30 | 90 | Kodda | 252 | 17:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 37 | 21:00 | 91 | Kulaura | 28 | 19:30 | 157 | Saidpur | 96 | 18:00
26 | Bhangura | 24 | 13:00 | 92 | Kurigram | 47 | 18:00 | 158 | Satkhira | 94 | 18:00
27 | Bheramara(GK) | 46 | 18:00 | 93 | Kushtia | 116 | 13:00 | 159 | Satmasjid | 79 | 14:00
28 | Bhulta | 164 | 07:00 | 94 | Laksam | 20 | 18:00 | 160 | Savar | 175 | 18:00
29 | Bog-Sherpur | 56 | 18:00 | 95 | Lakshmipur | 24 | 20:00 | 161 | SevenRings | 11.74 | 13:00
30 | Bogura | 123 | 18:00 | 96 | Lalbag | 56 | 13:00 | 162 | ShahCement | 27 | 21:00
31 | Borhanuddin | 63 | 21:00 | 97 | Lalmonirhat | 46 | 18:00 | 163 | Shahjadpur | 54 | 18:00
32 | Brahmanbaria | 80 | 18:00 | 98 | MI_Cement | 15.2 | 07:00 | 164 | Shahjibazar | 79 | 18:00
33 | Cantonment | 75 | 13:00 | 99 | Madanganj | 30 | 18:00 | 165 | Shahmirpur | 37 | 18:00
34 | Chandina | 12 | 09:00 | 100 | Madaripur | 68 | 13:00 | 166 | Shariatpur | 55 | 18:00
35 | Chandpur | 53 | 19:00 | 101 | Madartek | 58 | 13:00 | 167 | Sherpur | 106 | 18:00
36 | Chandraghona | 27 | 18:00 | 102 | Madunaghat | 40 | 18:00 | 168 | Shikalbaha | 21 | 14:00
37 | Chapai | 46 | 08:00 | 103 | Magura | 48 | 18:00 | 169 | Shitalakhya | 63.8 | 12:00
38 | Charsaidpur | 38 | 09:00 | 104 | Mahasthangarh | 54 | 18:00 | 170 | Sholosohor | 37 | 12:00
39 | Chauddagram | 54 | 17:00 | 105 | Maijdee | 27 | 20:00 | 171 | Shyampur | 136 | 12:00
40 | Chhatak | 24 | 15:00 | 106 | Manikganj | 86 | 21:00 | 172 | Siddhirganj | 98 | 12:00
41 | Chowmuhani | 100 | 19:30 | 107 | Maniknagar | 47 | 13:00 | 173 | Sirajganj | 77 | 18:30
42 | Chuadanga | 79 | 18:00 | 108 | Matarbari | 39 | 18:00 | 174 | Sonargaon | 124 | 21:00
43 | Coxsbazar | 104 | 19:00 | 109 | Matuail | 57 | 12:00 | 175 | Sreemongol | 55 | 18:00
44 | Cumilla(N) | 89 | 19:30 | 110 | Metrorail_Motijheel | 22 | 13:00 | 176 | Sreepur | 89 | 18:00
45 | Cumilla(S) | 120 | 18:00 | 111 | Metrorail_Uttara | 5 | 10:00 | 177 | Srinagar | 30 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 80 | 12:00 | 178 | Sunamganj | 36 | 18:00
47 | Daudkandi | 104 | 18:00 | 113 | Mirpur | 107 | 13:00 | 179 | Sylhet | 48 | 18:00
48 | DhakaUniversity | 52 | 12:00 | 114 | Mirsorai | 41 | 11:00 | 180 | Sylhet-132 | 71 | 18:00
49 | Dhamrai | 98 | 15:00 | 115 | Mirzapur | 36 | 18:00 | 181 | TK | 17 | 18:00
50 | Dhanmondi | 78 | 14:00 | 116 | Mithapukur | 50 | 18:00 | 182 | Tangail | 116 | 18:00
51 | Dohazari | 77 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 26 | 18:00
52 | Faridpur | 112 | 18:00 | 118 | Mogbazar | 56 | 14:00 | 184 | Tasnim | 26 | 12:00
53 | Fatullah | 93 | 15:00 | 119 | Mongla | 28 | 18:00 | 185 | Thakurgaon | 82 | 18:30
54 | Fenchuganj | 24 | 13:00 | 120 | Motijheel | 25 | 18:00 | 186 | Tongi | 95 | 15:00
55 | Feni | 71 | 18:00 | 121 | Muktagacha | 28 | 18:00 | 187 | Ullahpara | 25 | 18:00
56 | GPH | 94 | 07:00 | 122 | Munshiganj | 72 | 19:00 | 188 | Ullon | 55 | 14:00
57 | Ghatail | 62 | 18:00 | 123 | Muradnagar | 29 | 17:00 | 189 | Uttara | 60 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 136 | 18:00 | 190 | UttaraNew | 11 | 13:00
59 | Ghorashal-230 | 74 | 21:00 | 125 | Naogaon | 91 | 18:00 | 191 | Zigatola | 56 | 13:00
60 | Goalpara | 30 | 13:00 | 126 | Narail | 44 | 18:00
61 | Gollamari | 62 | 19:00 | 127 | Narinda | 54 | 13:00
62 | Gopalganj | 74 | 18:00 | 128 | Narshingdi | 136 | 21:00
63 | Gulshan | 68 | 13:00 | 129 | Natore | 103 | 18:00
64 | Halishahar | 52 | 15:00 | 130 | Nawabganj | 31 | 13:00
65 | HaripurSBU | 84 | 11:00 | 131 | Netrakona | 107 | 18:00
66 | Hasnabad | 77 | 18:30 | 132 | New | 66.6 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8373 | 0 |  | 8373
1:00 | 7978 | 0 |  | 7978
2:00 | 7492 | 0 |  | 7492
3:00 | 7185 | 0 |  | 7185
4:00 | 7034 | 0 |  | 7034
5:00 | 6978 | 0 |  | 6978
6:00 | 7481 | 0 |  | 7481
7:00 | 8094.07 | 0 |  | 8094.07
8:00 | 8845.08 | 0 |  | 8845.08
9:00 | 8517.13 | 0 |  | 8517.13
10:00 | 8085.79 | 0 |  | 8085.79
11:00 | 8739.68 | 0 |  | 8739.68
12:00 | 9315.35 | 0 |  | 9315.35
13:00 | 9664.01 | 0 |  | 9664.01
14:00 | 9329.4 | 0 |  | 9329.4
15:00 | 9106.57 | 0 |  | 9106.57
16:00 | 8950.5 | 0 |  | 8950.5
17:00 | 9614.15 | 0 |  | 9614.15
18:00 | 11115.89 | 0 |  | 11115.89
19:00 | 10896.98 | 0 |  | 10896.98
19:30 | 10828.52 | 0 |  | 10828.52
20:00 | 10627.39 | 0 |  | 10627.39
21:00 | 10416.44 | 0 |  | 10416.44
22:00 | 10155.44 | 0 |  | 10155.44
23:00 | 9523.73 | 0 |  | 9523.73
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 3817 | 4556 | 8373 | DAILY GENERATION CURVE
00:30 | 3741.5 | 4434 | 8175.5
01:00 | 3666 | 4312 | 7978 | 13-12-2025
01:30 | 3507.5 | 4227.5 | 7735
02:00 | 3349 | 4143 | 7492
02:30 | 3304.5 | 4034 | 7338.5
03:00 | 3260 | 3925 | 7185
03:30 | 3277.5 | 3832 | 7109.5
04:00 | 3295 | 3739 | 7034
04:30 | 3273 | 3733 | 7006
05:00 | 3251 | 3727 | 6978
05:30 | 3396.5 | 3833 | 7229.5
06:00 | 3542 | 3939 | 7481
06:30 | 3734.04 | 4053.495 | 7787.535
07:00 | 3926.08 | 4167.99 | 8094.07
07:30 | 4018.24 | 4451.335 | 8469.575
08:00 | 4110.4 | 4734.68 | 8845.08
08:30 | 3984.295 | 4696.81 | 8681.105
09:00 | 3858.19 | 4658.94 | 8517.13
09:30 | 3725.485 | 4575.975 | 8301.46
10:00 | 3592.78 | 4493.01 | 8085.79
10:30 | 3797.88 | 4614.855 | 8412.735
11:00 | 4002.98 | 4736.7 | 8739.68
11:30 | 4201.67 | 4825.845 | 9027.515
12:00 | 4400.36 | 4914.99 | 9315.35
12:30 | 4454.97 | 5034.71 | 9489.68
13:00 | 4509.58 | 5154.43 | 9664.01
13:30 | 4472.835 | 5023.87 | 9496.705
14:00 | 4436.09 | 4893.31 | 9329.4
14:30 | 4459.775 | 4758.21 | 9217.985
15:00 | 4483.46 | 4623.11 | 9106.57
15:30 | 4479.025 | 4549.51 | 9028.535
16:00 | 4474.59 | 4475.91 | 8950.5
16:30 | 4507.49 | 4774.835 | 9282.325
17:00 | 4540.39 | 5073.76 | 9614.15
17:30 | 4877.995 | 5487.025 | 10365.02
18:00 | 5215.6 | 5900.29 | 11115.89
18:30 | 5047.8 | 5958.635 | 11006.435
19:00 | 4880 | 6016.98 | 10896.98
19:30 | 4730 | 6098.52 | 10828.52
20:00 | 4598 | 6029.39 | 10627.39
20:30 | 4535 | 5986.915 | 10521.915 |  | Executive Engineer
21:00 | 4472 | 5944.44 | 10416.44 |  | Network Operation Division
21:30 | 4410.5 | 5875.44 | 10285.94
22:00 | 4349 | 5806.44 | 10155.44
22:30 | 4254 | 5585.585 | 9839.585
23:00 | 4159 | 5364.73 | 9523.73

## En-Curve
QF-LDC-12
Date | 13-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3218 | 1046 | 783 | 0 | 88 | 825 | 40 | 2357 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3174.5 | 1007 | 757.5 | 0 | 84 | 828.5 | 40 | 2272 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 13-12-2025
01:00 | 3131 | 968 | 732 | 0 | 80 | 832 | 40 | 2187 | 0 | 0 | 8 | 0 | 0 | 0 | 0
01:30 | 3040.5 | 928 | 732 | 0 | 75 | 834 | 40 | 2081.5 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | Energy Generated | 216.7877 |  | MKWHr
02:00 | 2950 | 888 | 732 | 0 | 70 | 836 | 40 | 1976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2853.5 | 871.5 | 696.5 | 0 | 70 | 833.5 | 40 | 1973.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 216.7877 |  | MKWHr
03:00 | 2757 | 855 | 661 | 0 | 70 | 831 | 40 | 1971 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2739 | 862.5 | 579 | 0 | 72 | 834.5 | 40 | 1981.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:00 | 2721 | 870 | 497 | 0 | 74 | 838 | 40 | 1992 | 0 | 0 | 0 | 0 | 0 | 2 | 0
04:30 | 2717.5 | 867.5 | 497 | 0 | 78 | 835.5 | 20 | 1987 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0
05:00 | 2714 | 865 | 497 | 0 | 82 | 833 | 0 | 1982 | 0 | 0 | 0 | 0 | 0 | 5 | 0
05:30 | 2874 | 903.5 | 497 | 0 | 81 | 829.5 | 0 | 2040 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0
06:00 | 3034 | 942 | 497 | 0 | 80 | 826 | 0 | 2098 | 0 | 0 | 0 | 0 | 0 | 4 | 0
06:30 | 3119.5 | 1012 | 497 | 0 | 79 | 829 | 0 | 2230 | 13.035 | 0 | 5.5 | 0 | 0 | 2.5 | 0
07:00 | 3205 | 1082 | 497 | 0 | 78 | 832 | 0 | 2362 | 26.07 | 0 | 11 | 0 | 0 | 1 | 0
07:30 | 3192.5 | 1062 | 571 | 0 | 82 | 877 | 20 | 2528.5 | 113.575 | 0 | 21.5 | 0 | 0 | 1.5 | 0
08:00 | 3180 | 1042 | 645 | 0 | 86 | 922 | 40 | 2695 | 201.08 | 0 | 32 | 0 | 0 | 2 | 0
08:30 | 3109 | 1013.5 | 663 | 0 | 85 | 871 | 40 | 2562.5 | 303.605 | 0 | 32 | 0 | 0 | 1.5 | 0
09:00 | 3038 | 985 | 681 | 0 | 84 | 820 | 40 | 2430 | 406.13 | 0 | 32 | 0 | 0 | 1 | 0
09:30 | 2905 | 927.5 | 681 | 0 | 91 | 822 | 40 | 2320.5 | 489.46 | 0 | 24 | 0 | 0 | 1 | 0
10:00 | 2772 | 870 | 681 | 0 | 98 | 824 | 40 | 2211 | 572.79 | 0 | 16 | 0 | 0 | 1 | 0
10:30 | 2910.5 | 959.5 | 680.5 | 0 | 96 | 828.5 | 40 | 2251 | 617.735 | 0 | 27.5 | 0 | 0 | 1.5 | 0
11:00 | 3049 | 1049 | 680 | 0 | 94 | 833 | 40 | 2291 | 662.68 | 0 | 39 | 0 | 0 | 2 | 0
11:30 | 3174.5 | 1049.05 | 728.5 | 0 | 98 | 835 | 40 | 2356 | 673.465 | 0 | 72 | 0 | 0 | 1 | 0
12:00 | 3300 | 1049.1 | 777 | 0 | 102 | 837 | 40 | 2421 | 684.25 | 0 | 105 | 0 | 0 | 0 | 0
12:30 | 3329 | 1095.1 | 776 | 0 | 100 | 836.5 | 40 | 2533 | 663.08 | 0 | 117 | 0 | 0 | 0 | 0
13:00 | 3358 | 1141.1 | 775 | 0 | 98 | 836 | 40 | 2645 | 641.91 | 0 | 129 | 0 | 0 | 0 | 0
13:30 | 3208 | 1136.6 | 772.5 | 0 | 101 | 848 | 40 | 2668.5 | 591.105 | 0 | 131 | 0 | 0 | 0 | 0
14:00 | 3058 | 1132.1 | 770 | 0 | 104 | 860 | 40 | 2692 | 540.3 | 0 | 133 | 0 | 0 | 0 | 0
14:30 | 3089.5 | 1122.55 | 772.5 | 0 | 111 | 841.07 | 40 | 2653 | 453.865 | 0 | 133 | 0 | 0 | 1.5 | 0
15:00 | 3121 | 1113 | 775 | 0 | 118 | 822.14 | 40 | 2614 | 367.43 | 0 | 133 | 0 | 0 | 3 | 0
15:30 | 3117 | 1127.5 | 728 | 0 | 113 | 861.875 | 40 | 2644.5 | 256.66 | 0 | 137 | 0 | 0 | 3 | 0
16:00 | 3113 | 1142 | 681 | 0 | 108 | 901.61 | 40 | 2675 | 145.89 | 0 | 141 | 0 | 0 | 3 | 0
16:30 | 3103.5 | 1160.5 | 681 | 0 | 110 | 999.015 | 40 | 2873.5 | 77.81 | 8 | 225.5 | 0 | 0 | 3.5 | 0
17:00 | 3094 | 1179 | 681 | 0 | 112 | 1096.42 | 40 | 3072 | 9.73 | 16 | 310 | 0 | 0 | 4 | 0
17:30 | 3114 | 1189.5 | 775.5 | 0 | 115 | 1196.855 | 40 | 3299 | 4.865 | 41 | 586.3 | 0 | 0 | 3 | 0
18:00 | 3134 | 1200 | 870 | 0 | 118 | 1297.29 | 40 | 3526 | 0 | 66 | 862.6 | 0 | 0 | 2 | 0
18:30 | 3078 | 1171.5 | 870 | 0 | 116 | 1368.635 | 40 | 3552.5 | 0 | 41.5 | 767.3 | 0 | 0 | 1 | 0
19:00 | 3022 | 1143 | 870 | 0 | 114 | 1439.98 | 40 | 3579 | 0 | 17 | 672 | 0 | 0 | 0 | 0
19:30 | 3127 | 1162 | 870 | 0 | 110 | 1445.52 | 40 | 3586 | 0 | 0 | 488 | 0 | 0 | 0 | 0
20:00 | 3107 | 1144 | 869 | 0 | 112 | 1452.39 | 40 | 3511 | 0 | 0 | 392 | 0 | 0 | 0 | 0
20:30 | 3128 | 1160 | 869 | 0 | 108 | 1448.915 | 40 | 3466.5 | 0 | 0 | 301.5 | 0 | 0 | 0 | 0
21:00 | 3149 | 1176 | 869 | 0 | 104 | 1445.44 | 40 | 3422 | 0 | 0 | 211 | 0 | 0 | 0 | 0
21:30 | 3139 | 1156.5 | 869.5 | 0 | 102 | 1444.44 | 40 | 3375 | 0 | 0 | 158.5 | 0 | 0 | 1 | 0
22:00 | 3129 | 1137 | 870 | 0 | 100 | 1443.44 | 40 | 3328 | 0 | 0 | 106 | 0 | 0 | 2 | 0
22:30 | 3076 | 1110.5 | 822.5 | 0 | 101 | 1381.585 | 40 | 3235 | 0 | 0 | 70.5 | 0 | 0 | 2.5 | 0
23:00 | 3023 | 1084 | 775 | 0 | 102 | 1319.73 | 40 | 3142 | 0 | 0 | 35 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 413 | 05:00 | 391 | 11:00 | Meghnaghat | 412 | 05:00 | 392 | 13:00
Ashuganj | 416 | 6:00 | 396 | 19:30 | Payra | 419 | 04:00 | 409 | 18:00
Bhulta | 412 | 04:00 | 393 | 12:00 | Rahanpur | 420 | 04:00 | 399 | 18:00
Bibiana | 407 | 06:00 | 395 | 13:00 | Rampal | 415 | 03:00 | 398 | 20:00
BIPTC | 409 | 03:00 | 392 | 18:00
Bogura | 416 | 05:00 | 389 | 18:00
Gopalganj | 415 | 04:00 | 397 | 19:30
Kaliakoir | 407 | 04:00 | 386 | 11:00
Korerhat | 414 | 06:00 | 400 | 12:00
Madunaghat | 409 | 04:00 | 397 | 17:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 242 | 04:00 | 226 | 13:00 | Kachua | 238 | 00:00 | 231 | 13:00
AKSML | 235 | 03:00 | 227 | 16:00 | Kaliakoir | 241 | 04:00 | 226 | 11:00
Aminbazar | 241 | 05:00 | 226 | 11:00 | Keranigonj | 241 | 05:00 | 225 | 13:00
Ashuganj | 240 | 01:00 | 231 | 20:00 | Khulna(S) | 243 | 02:00 | 228 | 18:00
Ashuganj-400 | 240 | 01:00 | 231 | 20:00 | Korerhat | 243 | 02:00 | 231 | 11:00
Baghabari | 242 | 02:00 | 229 | 18:30 | Madunaghat | 236 | 03:00 | 228 | 16:00
Barapukuria | 234 | 05:00 | 212 | 18:00 | Madunaghat-400 | 237 | 04:00 | 229 | 17:00
Barapukuria-230 | 234 | 05:00 | 212 | 18:00 | Maniknagar | 240 | 06:00 | 226 | 13:00
Barishal | 247 | 04:00 | 237 | 19:30 | Meghnaghat | 245 | 04:00 | 235 | 13:00
Bheramara | 240 | 05:00 | 222 | 18:00 | Meghnaghat-400 | 242 | 05:00 | 229 | 13:00
Bhulta | 241 | 04:00 | 229 | 12:00 | Mirsorai | 238 | 05:00 | 227 | 17:00
Bibiana | 238 | 04:00 | 231 | 13:00 | Rajshahi | 240 | 05:00 | 223 | 18:00
BIPTC | 241 | 04:00 | 224 | 18:00 | Rampal | 241 | 04:00 | 227 | 18:00
Bogura | 244 | 04:00 | 227 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 243 | 04:00 | 226 | 18:00 | Rampura | 240 | 04:00 | 226 | 13:00
Borhanuddin | 246 | 01:00 | 241 | 18:00 | Shikalbaha | 234 | 03:00 | 226 | 14:00
BSRM | 237 | 05:00 | 225 | 17:00 | Shyampur | 241 | 04:00 | 227 | 13:00
Cumilla(N) | 239 | 05:00 | 229 | 13:00 | Siddhirganj | 242 | 05:00 | 231 | 17:00
Faridpur | 246 | 03:00 | 235 | 18:00 | Sirajgonj | 248 | 04:00 | 235 | 18:00
Fenchuganj | 239 | 06:00 | 232 | 13:00 | Sreepur | 239 | 05:00 | 226 | 19:00
Feni | 238 | 05:00 | 226 | 13:00 | Tongi | 235 | 04:00 | 223 | 15:00
Ghorashal | 245 | 07:00 | 235 | 11:00
Ghorashal-230 | 235 | 04:00 | 219 | 18:00
Gopalganj | 246 | 04:00 | 236 | 13:00
GPH | 237 | 05:00 | 227 | 17:00
Haripur | 241 | 04:00 | 229 | 13:00
Hasnabad | 242 | 05:00 | 228 | 15:00
Hathazari | 233 | 00:00 | 226 | 16:00
Ishurdi | 243 | 05:00 | 226 | 18:00
Jhenaidah | 242 | 05:00 | 222 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 128 | 13:00 | Lalbag | 140 | 05:00 | 128 | 13:00
Agargaon | 139 | 04:00 | 129 | 13:00 | Lalmonirhat | 134 | 03:00 | 117 | 18:00
Agrabad | 137 | 03:00 | 130 | 16:00 | Madanganj | 139 | 00:00 | 134 | 07:00
AKS | 134 | 00:00 | 130 | 12:00 | Madaripur | 140 | 02:00 | 136 | 13:00
Aminbazar | 139 | 05:00 | 129 | 11:00 | Madartek | 136 | 04:00 | 128 | 12:00
Amnura | 139 | 05:00 | 131 | 18:30 | Madunaghat | 137 | 01:00 | 132 | 16:00
Ashuganj | 144 | 09:00 | 139 | 18:00 | Magura | 138 | 02:00 | 125 | 18:00
Bagerhat | 139 | 03:00 | 126 | 18:00 | Mahasthangarh | 138 | 06:00 | 126 | 18:00
Bajitpur | 138 | 03:00 | 131 | 19:00 | Maijdee | 136 | 04:00 | 130 | 13:00
Bakulia | 136 | 03:00 | 132 | 14:00 | Manikganj | 134 | 05:00 | 124 | 12:00
Banani | 136 | 02:00 | 127 | 12:00 | Maniknagar | 139 | 02:00 | 125 | 13:00
Bangabhaban | 139 | 01:00 | 125 | 13:00 | Matarbari | 130 | 09:00 | 120 | 18:00
Barapukuria | 137 | 05:00 | 125 | 18:00 | Matuail | 142 | 04:00 | 135 | 17:00
Barguna | 137 | 01:00 | 133 | 18:00 | Metrorail_Motijheel | 139 | 02:00 | 125 | 13:00
Barishal | 141 | 04:00 | 136 | 18:00 | Metrorail_Uttara | 139 | 03:00 | 129 | 13:00
Barishal-230 | 143 | 04:00 | 136 | 18:00 | Millgate | 137 | 04:00 | 124 | 12:00
Baroaulia | 136 | 00:00 | 131 | 16:00 | Mirpur | 138 | 04:00 | 129 | 12:00
Baroirhat | 136 | 01:00 | 130 | 17:00 | Mirzapur | 139 | 05:00 | 130 | 13:00
Bashundhara | 136 | 03:00 | 127 | 12:00 | Mithapukur | 137 | 05:00 | 122 | 18:00
BashundharaCement | 139 | 00:00 | 134 | 07:00 | MI_Cement | 140 | 04:00 | 128 | 12:00
Beanibazar | 135 | 00:00 | 132 | 18:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 137 | 05:00 | 119 | 18:00 | Mogbazar | 138 | 01:00 | 130 | 12:00
Bhaluka | 136 | 00:00 | 127 | 18:00 | Mongla | 138 | 04:00 | 127 | 18:00
Bhandaria | 137 | 05:00 | 125 | 18:30 | Motijheel | 139 | 01:00 | 125 | 13:00
Bhangura | 138 | 02:00 | 131 | 18:00 | Muktagacha | 134 | 09:00 | 128 | 18:00
Bheramara | 141 | 04:00 | 134 | 18:00 | Munshiganj | 140 | 04:00 | 133 | 20:00
Bheramara(GK) | 141 | 03:00 | 134 | 18:00 | Muradnagar | 141 | 05:00 | 129 | 16:00
Bhulta | 135 | 00:00 | 130 | 16:00 | Mymensingh | 133 | 07:00 | 123 | 19:00
Bog-Sherpur | 139 | 04:00 | 129 | 18:00 | Naogaon | 135 | 01:00 | 126 | 18:00
Bogura | 138 | 05:00 | 128 | 17:00 | Narail | 140 | 04:00 | 124 | 18:00
Bogura-230 | 139 | 04:00 | 128 | 18:00 | Narinda | 139 | 02:00 | 125 | 13:00
Brahmanbaria | 139 | 09:00 | 133 | 18:00 | Narshingdi | 139 | 02:00 | 131 | 13:00
Cantonment | 139 | 04:00 | 129 | 12:00 | Natore | 138 | 01:00 | 129 | 18:00
Chandina | 142 | 05:00 | 133 | 17:00 | Nawabganj | 138 | 04:00 | 127 | 13:00
Chandpur | 139 | 00:00 | 135 | 13:00 | Netrakona | 130 | 03:00 | 116 | 18:00
Chandraghona | 138 | 04:00 | 133 | 16:00 | New | 138 | 04:00 | 126 | 12:00
Chapai | 139 | 00:00 | 133 | 18:30 | Niamatpur | 139 | 00:00 | 133 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 141 | 01:00 | 134 | 13:00 | Noapara | 138 | 05:00 | 120 | 18:00
Chauddagram | 138 | 02:00 | 131 | 17:00 | Pabna | 141 | 04:00 | 132 | 18:00
Chhatak | 132 | 00:00 | 130 | 00:00 | Palashbari | 136 | 05:00 | 121 | 18:00
Chowmuhani | 134 | 04:00 | 129 | 13:00 | Panchagarh | 139 | 04:00 | 126 | 08:00
Chuadanga | 138 | 05:00 | 125 | 18:00 | Patiya | 137 | 04:00 | 131 | 17:00
Coxsbazar | 129 | 08:00 | 120 | 17:00 | Patuakhali | 138 | 04:00 | 131 | 18:30
Cumilla(N) | 141 | 06:00 | 133 | 16:00 | Payra | 137 | 00:00 | 134 | 18:00
Cumilla(S) | 140 | 05:00 | 124 | 15:00 | PHP | 136 | 02:00 | 130 | 13:00
Daganbhuiyan | 137 | 05:00 | 130 | 17:00 | Postogola | 141 | 03:00 | 131 | 12:00
Daudkandi | 139 | 05:00 | 123 | 17:00 | Purbachal | 136 | 02:00 | 127 | 13:00
DhakaUniversity | 136 | 01:00 | 128 | 12:00 | Purbasadipur | 133 | 01:00 | 119 | 18:00
Dhamrai | 141 | 06:00 | 132 | 12:00 | Rahanpur | 141 | 04:00 | 134 | 18:00
Dhanmondi | 143 | 05:00 | 136 | 16:00 | Rahanpur-400 | 141 | 01:00 | 134 | 18:00
Dohazari | 135 | 09:00 | 129 | 17:00 | Rahim | 141 | 01:00 | 127 | 11:00
Faridpur | 140 | 00:00 | 135 | 17:00 | Rajbari | 142 | 05:00 | 134 | 18:00
Fatullah | 140 | 05:00 | 129 | 12:00 | Rajendrapur | 139 | 04:00 | 130 | 19:00
Fenchuganj | 141 | 06:00 | 137 | 18:00 | Rajshahi | 139 | 05:00 | 130 | 18:00
Feni | 135 | 04:00 | 129 | 13:00 | Rajshahi-230 | 139 | 04:00 | 129 | 18:00
Feni-230 | 137 | 05:00 | 130 | 12:00 | Ramganj | 138 | 03:00 | 132 | 14:00
Ghatail | 133 | 02:00 | 128 | 13:00 | Rampur | 137 | 02:00 | 130 | 16:00
Ghorashal | 138 | 00:00 | 131 | 18:00 | Rampura | 136 | 03:00 | 127 | 13:00
Goalpara | 141 | 04:00 | 131 | 18:00 | Rangamati | 137 | 00:00 | 132 | 17:00
Gollamari | 141 | 04:00 | 132 | 18:00 | Rangpur | 136 | 06:00 | 125 | 18:00
Gopalganj | 142 | 05:00 | 133 | 18:00 | Ruppur | 141 | 04:00 | 133 | 18:00
Gopalganj-400 | 143 | 04:00 | 136 | 18:00 | Saidpur | 134 | 03:00 | 123 | 18:00
Gulshan | 135 | 05:00 | 127 | 13:00 | Satkhira | 139 | 04:00 | 127 | 18:00
Halishahar | 137 | 01:00 | 131 | 16:00 | Satmasjid | 138 | 01:00 | 128 | 13:00
Haripur | 142 | 03:00 | 135 | 13:00 | Savar | 136 | 01:00 | 128 | 12:00
HaripurSBU | 142 | 03:00 | 135 | 13:00 | SevenRings | 138 | 01:00 | 131 | 18:00
Hasnabad | 140 | 02:00 | 131 | 16:00 | ShahCement | 141 | 01:00 | 134 | 13:00
Hathazari | 137 | 00:00 | 134 | 12:00 | Shahjadpur | 143 | 04:00 | 136 | 13:00
Ishurdi | 143 | 05:00 | 134 | 18:00 | Shahjibazar | 140 | 07:00 | 135 | 10:00
Jaldhaka | 134 | 04:00 | 120 | 18:00 | Shahmirpur | 137 | 05:00 | 132 | 13:00
Jamalpur | 132 | 11:00 | 123 | 08:00 | Shariatpur | 142 | 02:00 | 135 | 17:00
Jashore | 137 | 04:00 | 120 | 18:00 | Sherpur | 130 | 11:00 | 120 | 08:00
Jhenaidah | 139 | 05:00 | 120 | 18:00 | Shikalbaha | 127 | 03:00 | 121 | 15:00
Jhenaidah-230 | 141 | 05:00 | 126 | 18:00 | Shikalbaha-230 | 138 | 02:00 | 133 | 12:00
Joydebpur | 136 | 02:00 | 128 | 18:00 | Shitalakhya | 140 | 04:00 | 128 | 12:00
Joypurhat | 134 | 01:00 | 123 | 18:00 | Sholosohor | 138 | 04:00 | 133 | 12:00
Juldah | 138 | 03:00 | 132 | 15:00 | Shyampur | 139 | 06:00 | 131 | 13:00
Kabirpur | 139 | 02:00 | 123 | 16:00 | Shyampur-230 | 140 | 04:00 | 131 | 12:00
Kachua | 141 | 02:00 | 136 | 13:00 | Siddhirganj | 141 | 01:00 | 135 | 13:00
Kaliakoir | 143 | 03:00 | 134 | 06:00 | Sirajganj | 139 | 04:00 | 128 | 18:00
Kallyanpur | 138 | 06:00 | 130 | 12:00 | Sonargaon | 138 | 00:00 | 125 | 10:00
Kalurghat | 137 | 01:00 | 133 | 12:00 | Sreemongol | 139 | 04:00 | 134 | 11:00
Kamrangirchar | 138 | 04:00 | 127 | 13:00 | Sreepur | 140 | 04:00 | 131 | 19:00
Kaptai | 137 | 5:00 | 130 | 12:00 | Srinagar | 139 | 04:00 | 126 | 13:00
Kasba | 140 | 05:00 | 129 | 13:00 | SSM | 140 | 00:00 | 136 | 13:00
Kazla | 139 | 03:00 | 125 | 13:00 | Sunamganj | 133 | 01:00 | 129 | 12:00
Keranigonj | 139 | 05:00 | 126 | 13:00 | Sylhet | 136 | 03:00 | 133 | 12:00
Khagrachori | 138 | 03:00 | 131 | 13:00 | Sylhet-132 | 134 | 00:00 | 133 | 12:00
Khulna | 140 | 04:00 | 130 | 18:00 | Tangail | 135 | 05:00 | 126 | 13:00
Khulna(S) | 141 | 02:00 | 132 | 18:00 | Taraganj | 134 | 03:00 | 121 | 18:00
Khulshi | 136 | 04:00 | 130 | 15:00 | Tasnim | 138 | 00:00 | 134 | 21:00
Kishoreganj | 135 | 03:00 | 126 | 18:00 | Thakurgaon | 139 | 04:00 | 125 | 08:00
Kodda | 137 | 02:00 | 127 | 15:00 | TK | 137 | 00:00 | 133 | 12:00
KSRM | 136 | 00:00 | 130 | 16:00 | Tongi | 135 | 00:00 | 127 | 11:00
Kulaura | 140 | 02:00 | 137 | 19:30 | Ullahpara | 140 | 03:00 | 130 | 18:00
Kurigram | 131 | 03:00 | 118 | 18:00 | Ullon | 136 | 04:00 | 127 | 12:00
Kushtia | 137 | 05:00 | 126 | 18:00 | Uttara | 136 | 03:00 | 122 | 12:00
Laksam | 142 | 05:00 | 135 | 13:00 | UttaraNew | 139 | 03:00 | 129 | 13:00
Lakshmipur | 137 | 05:00 | 130 | 13:00 | Zigatola | 138 | 01:00 | 126 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division