## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-12-2025 | during | 15-12-2025 | during | 15-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 334 | 358 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 40.2 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 27 | 25 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 76 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 30 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 86 | 164 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 408 | 417 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1318 | 1781.2 | 5780.35 | 5749.35 | 2938.06 | 2916.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 30 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 0 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 223 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 11 | 90 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 40 | 60 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 33 | 33 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 10 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.21 | 0 | 3.24 | 0 | 3.24 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 33 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 31 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 585 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 7 | 0 | 5 | 0 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 345 | 345 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1239.21 | 1366 | 2557.96 | 2560.72 | 2039.74 | 2046.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 211 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 240 | 99 | 318.81 | 318.81 | 318.81 | 318.81
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 380 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 103 | 106 | 163 | 163 | 112 | 112 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 10 | 70 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 114 | 106 | 160 | 160 | 118 | 118 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 13 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1054 | 1136 | 2437.21 | 2372.21 | 1885.51 | 1820.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-12-2025 | during | 15-12-2025 | during | 15-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 61 | 60 | 157.5 | 157.5 | 110 | 110 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.69 | 0 | 45.15 | 0 | 45.15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 3 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 151.69 | 141 | 361.25 | 314 | 266.25 | 219
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 207 | 207 | 205 | 205 | 205 | 205 | GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 709 | 698 | 732 | 732 | 698 | 698
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 874 | 875 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 12 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 74 | 0 | 74 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 968 | 1100 | 0 | 0 | 1050 | 1050 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2170 | 2256 | 2346 | 2272 | 2481 | 2407
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 350 | 504 | 0 | 0 | 500 | 500 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 120 | 120 | 55 | 55 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 837 | 1000 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1517.54 | 1834 | 1993.32 | 1993.32 | 1988 | 1988
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 53.01 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Under Maintenance
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 165 | 176 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.13 | 0 | 4.6 | 0 | 4.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1047.42 | 1387 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.88 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 101 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1842.44 | 1977 | 3083.47 | 2918.87 | 2554 | 2389.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 25 | 50 | 50 | 50 | 50 | Machine problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 167 | 0 | 140 | 0 | 160.96 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 202.8 | 124 | 487.2 | 312 | 474.16 | 278
System Total |  |  |  |  | 28823.2 | 28379.108 | 10204.68 | 11313.2 | 19778.76 | 19224.47 | 15325.54 | 14762.27
Forecast Scenario (15-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9310 |  | 0 |  | 9310
|  |  |  | 1:00 | 8590 |  | 0 |  | 8590
|  |  |  | 2:00 | 8210 |  | 0 |  | 8210
|  |  |  | 3:00 | 7860 |  | 0 |  | 7860
|  |  |  | 4:00 | 7640 |  | 0 |  | 7640
|  |  |  | 5:00 | 7590 |  | 0 |  | 7590
|  |  |  | 6:00 | 8050 |  | 0 |  | 8050
|  |  |  | 7:00 | 8640 |  | 0 |  | 8640
|  |  |  | 8:00 | 9550 |  | 0 |  | 9550
|  |  |  | 9:00 | 9710 |  | 0 |  | 9710
|  |  |  | 10:00 | 9510 |  | 0 |  | 9510
|  |  |  | 11:00 | 9760 |  | 0 |  | 9760
|  |  |  | 12:00 | 10300 |  | 0 |  | 10300
|  |  |  | 13:00 | 10790 |  | 0 |  | 10790
|  |  |  | 14:00 | 10290 |  | 0 |  | 10290
|  |  |  | 15:00 | 9980 |  | 0 |  | 9980
|  |  |  | 16:00 | 9800 |  | 0 |  | 9800
|  |  |  | 17:00 | 10230 |  | 0 |  | 10230
|  |  |  | 18:00 | 11410 |  | 0 |  | 11410
|  |  |  | 18:30 | 11200 |  | 0 |  | 11200
|  |  |  | 19:00 | 11190 |  | 0 |  | 11190
|  |  |  | 19:30 | 11020 |  | 0 |  | 11020
|  |  |  | 20:00 | 10950 |  | 0 |  | 10950
|  |  |  | 21:00 | 10680 |  | 0 |  | 10680
|  |  |  | 22:00 | 10270 |  | 0 |  | 10270
|  |  |  | 23:00 | 9600 |  | 0 |  | 9600
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 10300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11410.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11410.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 229.91 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:04 hrs on 15-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-12-2025 | [28 empty] | Date: | 14-12-2025 | [28 empty] | Date: | 14-12-2025 | [28 empty] | Date: | 14-12-2025 | [28 empty] | Date: | 14-12-2025 | [17 empty] | Date: | 14-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 191 | 0 | 0 | 110 | 0 | 0 | 19 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 18 | 130 | 0 | 16 | 0 | 92 | 0 | 0 | 0 | 4111 | 775 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 919 | 0 | 0 | 0 | 1192.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 940 | 0 | 5104.32 | 9215.32 | 98.91
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 545 | 0 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 205 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 205 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 18 | 130 | 0 | 8 | 0 | 92 | 0 | 0 | 0 | 4044 | 721 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 922.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 700 | 0 | 4446.11 | 8490.11 | 98.91
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 195 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 205 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 18 | 130 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 3917 | 686 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 834.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 560 | 0 | 4201.52 | 8118.52 | 98.91
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 203 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 205 | 0 | 30 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 18 | 130 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 3598 | 686 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 834.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 556 | 0 | 4162.72 | 7760.72 | 98.91
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 205 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 305 | 0 | 205 | 0 | 30 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 18 | 130 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 3478 | 592 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 842.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 560 | 0 | 4064.45 | 7542.45 | 98.91
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 355 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 230 | 0 | 230 | 5 | 0 | 197 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 26 | 0 | 0 | 0 | 305 | 0 | 205 | 0 | 30 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 18 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 3456 | 592 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 834.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 560 | 0 | 4034.77 | 7490.77 | 98.9
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 355 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 230 | 0 | 230 | 10 | 0 | 197 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 320 | 0 | 205 | 0 | 30 | 0 | 0 | 0 | 0 | 82 | 30 | 0 | 18 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 3765 | 638 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 779 | 0 | 0 | 0 | 838.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 580 | 0 | 4187.88 | 7952.88 | 98.9
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 355 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 460 | 2 | 0 | 0 | 370 | 0 | 230 | 48 | 0 | 214 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 78 | 0 | 3 | 0 | 315 | 0 | 205 | 0 | 30 | 0 | 1 | 16 | 0 | 82 | 30 | 0 | 18 | 130 | 0 | 2 | 3 | 88 | 0 | 1.73 | 0 | 4186.73 | 685 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 776 | 0 | 0 | 0 | 838.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.43 | 3 | 0 | 0 | 1.29 | 0 | 0 | 168 | 0 | 0 | 0 | 394 | 0 | 0.14 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 652 | 0 | 4359.09 | 8545.82 | 98.9
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 335 | 0 | 0 | 10 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 40 | 0 | 14 | 355 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 580 | 9 | 0 | 0 | 350 | 0 | 330 | 51 | 0 | 208 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 86 | 0 | 29 | 0 | 315 | 0 | 205 | 0 | 30 | 0 | 4 | 8 | 0 | 82 | 30 | 0 | 18 | 83 | 0 | 24 | 19 | 75 | 1 | 13.85 | 0 | 4444.95 | 779 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 861 | 0 | 0 | 0 | 1011.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.53 | 26 | 0 | 0 | 13.37 | 0 | 0 | 177 | 0 | 0 | 0 | 386 | 0 | 1.62 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.4 | 49 | 0.13 | 0 | 0 | 110 | 180 | 0 | 300 | 820 | 0 | 5009.43 | 9454.38 | 98.9
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 335 | 0 | 0 | 19 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.01 | 40 | 0 | 10 | 345 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 495 | 14 | 0 | 0 | 350 | 0 | 330 | 51 | 0 | 205 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 86 | 0 | 48 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 7 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 24 | 19 | 66 | 1 | 29.77 | 0 | 4313.78 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.94 | 911 | 0 | 0 | 0 | 1024.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.07 | 61 | 0 | 0 | 34.78 | 0 | 0 | 170 | 0 | 0 | 0 | 380 | 0 | 3.15 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 104 | 0.22 | 0 | 0 | 110 | 180 | 0 | 300 | 800 | 0 | 5299.83 | 9613.61 | 98.9
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 335 | 0 | 0 | 25 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 40 | 0 | 10 | 345 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 450 | 17 | 0 | 0 | 270 | 0 | 330 | 51 | 0 | 197 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 92 | 0 | 60 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 10 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 24 | 19 | 61 | 2 | 39.08 | 0 | 4209.82 | 874 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 906 | 0 | 0 | 0 | 869.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.11 | 83 | 0 | 0 | 47.36 | 0 | 0 | 168 | 0 | 0 | 0 | 390 | 0 | 4.29 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.7 | 141 | 0.45 | 0 | 0 | 110 | 220 | 0 | 300 | 705 | 0 | 5208.28 | 9418.1 | 98.89
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 410 | 0 | 0 | 335 | 0 | 0 | 28 | 0 | 6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.15 | 40 | 0 | 7 | 345 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 600 | 18 | 0 | 0 | 260 | 0 | 280 | 51 | 0 | 199 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 108 | 0 | 67 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 24 | 19 | 61 | 2 | 43.25 | 0 | 4346.4 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 902 | 0 | 0 | 0 | 873.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.81 | 97 | 0 | 0 | 55.14 | 0 | 0 | 168 | 0 | 0 | 0 | 414 | 0 | 4.94 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5.5 | 167 | 0.53 | 0 | 0 | 110 | 220 | 0 | 300 | 715 | 0 | 5313.88 | 9660.28 | 98.89
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 35 | 86 | 0 | 0 | 0 | 408 | 0 | 0 | 332 | 0 | 0 | 29 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.21 | 40 | 0 | 8 | 345 | 0 | 0 | 0 | 0 | 11 | 221 | 0 | 0 | 0 | 580 | 19 | 0 | 0 | 250 | 0 | 240 | 51 | 0 | 208 | 0 | 0 | 103 | 10 | 0 | 11 | 0 | 114 | 0 | 67 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 24 | 19 | 61 | 2 | 45.69 | 0 | 4471.9 | 874 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 968 | 0 | 0 | 0 | 1047.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.01 | 101 | 0 | 0 | 56.88 | 0 | 0 | 165 | 0 | 0 | 0 | 414 | 0 | 5.13 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 3.8 | 167 | 0.54 | 0 | 0 | 110 | 220 | 0 | 350 | 837 | 0 | 5732.78 | 10204.68 | 98.89
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 22 | 0 | 200 | 0 | 35 | 143 | 0 | 0 | 0 | 420 | 0 | 0 | 330 | 0 | 0 | 28 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 3 | 40 | 0 | 15 | 345 | 0 | 0 | 0 | 0 | 45 | 220 | 0 | 0 | 0 | 580 | 18 | 3 | 0 | 270 | 0 | 210 | 51 | 0 | 213 | 0 | 0 | 102 | 47 | 0 | 11 | 0 | 110 | 0 | 63 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 10 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 57 | 19 | 63 | 2 | 43.3 | 0 | 4854.3 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1033 | 0 | 0 | 0 | 1053.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.22 | 95 | 0 | 0 | 50.04 | 0 | 0 | 173 | 0 | 0 | 0 | 414 | 0 | 4.93 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 3.5 | 153 | 0.48 | 0 | 0 | 110 | 220 | 0 | 350 | 900 | 0 | 5836.38 | 10690.68 | 98.89
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 34.3 | 0 | 41 | 0 | 195 | 0 | 35 | 164 | 0 | 0 | 0 | 358 | 0 | 0 | 250 | 0 | 0 | 24 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2.46 | 40 | 0 | 7 | 345 | 0 | 0 | 0 | 0 | 34 | 222 | 0 | 0 | 0 | 580 | 15 | 50 | 0 | 270 | 0 | 88 | 51 | 0 | 195 | 0 | 0 | 50 | 34 | 0 | 11 | 0 | 106 | 0 | 52 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 8 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 56 | 19 | 62 | 2 | 36.38 | 0 | 4509.14 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1082 | 0 | 0 | 0 | 1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.38 | 82 | 0 | 0 | 41.31 | 0 | 0 | 162 | 0 | 0 | 0 | 360 | 0 | 4 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 2.8 | 134 | 0.4 | 0 | 0 | 110 | 180 | 0 | 300 | 906 | 0 | 5683.89 | 10193.03 | 98.89
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 16 | 0 | 17 | 0 | 195 | 0 | 35 | 164 | 0 | 0 | 0 | 359 | 0 | 0 | 250 | 0 | 0 | 17 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 1.65 | 40 | 0 | 4 | 345 | 0 | 0 | 0 | 0 | 32 | 220 | 0 | 0 | 0 | 580 | 12 | 12 | 0 | 280 | 0 | 88 | 51 | 0 | 200 | 0 | 0 | 50 | 34 | 0 | 13 | 0 | 98 | 0 | 38 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 5 | 16 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 56 | 19 | 60 | 1 | 25.27 | 0 | 4412.92 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1041 | 0 | 12 | 0 | 972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.77 | 52 | 0 | 0 | 27.11 | 0 | 0 | 166 | 0 | 0 | 0 | 373 | 0 | 2.86 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 86 | 0.27 | 0 | 0 | 110 | 180 | 0 | 300 | 942 | 0 | 5475.01 | 9887.93 | 98.88
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 16.5 | 0 | 17 | 9 | 95 | 0 | 35 | 164 | 0 | 0 | 0 | 384 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 5 | 345 | 0 | 0 | 0 | 0 | 33 | 221 | 0 | 0 | 0 | 585 | 6 | 12 | 0 | 330 | 0 | 25 | 51 | 0 | 209 | 0 | 0 | 103 | 34 | 0 | 13 | 0 | 100 | 0 | 18 | 0 | 320 | 0 | 207 | 0 | 30 | 0 | 2 | 16 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 56 | 19 | 61 | 0 | 10.17 | 0 | 4392.67 | 874 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1005 | 0 | 12 | 0 | 972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.33 | 23 | 0 | 0 | 10.52 | 0 | 0 | 169 | 0 | 0 | 0 | 392 | 0 | 0.62 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.8 | 31 | 0.12 | 0 | 0 | 110 | 180 | 0 | 300 | 945 | 0 | 5310.39 | 9703.06 | 98.88
17:00 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 16.5 | 0 | 41 | 45 | 195 | 0 | 35 | 164 | 0 | 0 | 0 | 414 | 0 | 17 | 300 | 0 | 0 | 1 | 0 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 1 | 7 | 345 | 0 | 0 | 12 | 0 | 60 | 222 | 0 | 0 | 0 | 575 | 0 | 65 | 0 | 330 | 0 | 51 | 51 | 0 | 197 | 0 | 0 | 104 | 34 | 0 | 13 | 0 | 82 | 0 | 1 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 59 | 19 | 61 | 0 | 0.34 | 0 | 4658.84 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.68 | 1002 | 0 | 12 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.61 | 0 | 0 | 168 | 0 | 0 | 0 | 350 | 0 | 0.08 | 0 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 0 | 110 | 180 | 0 | 388 | 945 | 0 | 5472.18 | 10131.02 | 98.88
18:00 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 40.2 | 0 | 76 | 64 | 195 | 0 | 35 | 164 | 0 | 0 | 0 | 417 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 31 | 0 | 0 | 33 | 10 | 345 | 0 | 0 | 30 | 0 | 90 | 223 | 0 | 0 | 0 | 585 | 0 | 100 | 0 | 380 | 0 | 99 | 51 | 0 | 211 | 0 | 0 | 106 | 70 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 19 | 60 | 0 | 0 | 3 | 5122.2 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 12 | 19 | 0 | 1387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 25 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 504 | 1000 | 0 | 6191 | 11313.2 | 98.88
19:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 40 | 0 | 80 | 32 | 80 | 0 | 17 | 164 | 0 | 0 | 0 | 400 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 33 | 0 | 40 | 0 | 11 | 345 | 0 | 0 | 32 | 0 | 88 | 225 | 0 | 0 | 0 | 589 | 0 | 10 | 0 | 380 | 0 | 99 | 51 | 0 | 195 | 0 | 0 | 106 | 83 | 0 | 19 | 0 | 102 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 30 | 0 | 0 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 19 | 62 | 0 | 0 | 12 | 4804 | 874 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 36 | 17 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 59 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 454 | 1010 | 0 | 6289 | 11093 | 98.88
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 15.6 | 0 | 90 | 15 | 15 | 0 | 17 | 164 | 0 | 0 | 0 | 413 | 0 | 35 | 300 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 40 | 0 | 13 | 348 | 0 | 0 | 0 | 0 | 79 | 226 | 0 | 0 | 0 | 580 | 0 | 10 | 0 | 380 | 0 | 103 | 51 | 0 | 202 | 0 | 0 | 108 | 80 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 19 | 62 | 0 | 0 | 12 | 4678.6 | 874 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 35 | 22 | 0 | 1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 57 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 400 | 1020 | 0 | 6243 | 10921.6
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 16.5 | 0 | 90 | 15 | 15 | 0 | 17 | 164 | 0 | 0 | 0 | 402 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 36 | 0 | 40 | 0 | 17 | 348 | 0 | 0 | 0 | 0 | 83 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 380 | 0 | 136 | 51 | 0 | 190 | 0 | 0 | 108 | 81 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 19 | 62 | 0 | 0 | 0 | 4639.5 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 35 | 19 | 0 | 1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 400 | 1010 | 0 | 6218 | 10857.5 | 98.87
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 15.8 | 0 | 90 | 0 | 15 | 0 | 17 | 54 | 0 | 0 | 0 | 405 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24 | 0 | 40 | 0 | 16 | 348 | 0 | 0 | 0 | 0 | 34 | 228 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 380 | 0 | 198 | 51 | 0 | 201 | 0 | 0 | 109 | 34 | 0 | 20 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 21 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 19 | 61 | 0 | 0 | 0 | 4494.8 | 874 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 17 | 20 | 0 | 1324.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 63 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 400 | 1010 | 0 | 6090.82 | 10585.62 | 98.87
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24 | 0 | 40 | 0 | 27 | 350 | 0 | 0 | 0 | 0 | 17 | 229 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 320 | 0 | 300 | 51 | 0 | 192 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 0 | 13 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 59 | 19 | 63 | 0 | 0 | 0 | 4331 | 874 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 10 | 0 | 1280.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 300 | 1010 | 0 | 5841.4 | 10172.4 | 98.87
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 250 | 0 | 310 | 51 | 0 | 186 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 0 | 10 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 24 | 19 | 63 | 0 | 0 | 0 | 4049 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1068 | 0 | 10 | 0 | 1277.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 950 | 0 | 5667.88 | 9716.88 | 98.87
Total KWH | 0 | 90240 | 0 | 0 | 0 | 0 | 0 | 0 | 8125200 | 0 | 0 | 207000 | 0 | 569808 | 133440 | 1218164 | 0 | 412675 | 1428480 | 0 | 0 | 0 | 8858194 | 0 | 139020 | 7378821 | 0 | 0 | 187225 | 0 | 480600 | 527400 | 0 | 0 | 0 | 0 | 0 | 0 | 105600 | 0 | 0 | 0 | 24000 | 273600 | 19898 | 864000 | 58545 | 424800 | 8247272.73 | 0 | 0 | 88800 | 0 | 613891 | 5168076 | 0 | 0 | 0 | 12338180 | 130005 | 414836 | 0 | 7076000 | 0 | 5042000 | 1112608 | 0 | 4927000 | 0 | 0 | 2493227 | 537600 | 0 | 317310 | 0 | 2245440 | 0 | 447873 | 0 | 7563000 | 0 | 5032000 | 0 | 720360 | 0 | 0 | 290760 | 0 | 1699200 | 683808 | 0 | 439000 | 1624410 | 0 | 794400 | 307200 | 1660800 | 12600 | 288690 | 28800 | 103871856.73 | 19872727 | 6585120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 491040 | 22756360 | 133440 | 25091 | 0 | 24789818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323264 | 639660 | 0 | 0 | 334496 | 0 | 0 | 4050073 | 0 | 0 | 0 | 9390690 | 0 | 31020 | 0 | 341236 | 269437 | 194040 | 135600 | 0 | 0 | 0 | 25653.72 | 1059840 | 3238 | 0 | 0 | 2622000 | 5300968 | 0 | 7680109 | 20580363.64 | 0 | 127635284.36 | 231507141.09

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10204.68 | MW | 12:00 Hr. | Energy Generated |  |  | 231.5071 |  | MKWHr.
| Day Peak Demand |  |  | 10204.68 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11313.2 | MW | 18:00 Hr. | Energy Demand |  |  | 231.5071 |  | MKWHr.
| Evening Peak Demand |  |  | 11313.2 | MW | 18:00 Hr. | Maximum Temperature |  |  | 28.1 |  | °C
| Minimum Generation of the Day |  |  | 7490.77 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 725.84 |  | MMCFD
| Maximum Generation of the Day |  |  | 11313.2 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.5726 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.3702 | 0 | 4.1988 | 0 | 0 | 0.18723 | 0 | 0 | 29.7563 | Gas | 99.6185 | Gas | 349445079.02
| Chattogram Zone |  |  | 5.5929 | 20.5855 | 1.0588 | 0 | 0.864 | 0.1499 | 0 | 0.1056 | 28.3567 | Coal | 71.9435 | Coal | 460164701.3453
| Cumilla Zone |  |  | 20.9681 | 0 | 0.95244 | 0 | 0 | 0.44787 | 2.2454 | 0 | 24.6139 | HFO | 7.879 | HFO | 131370949.41
| Mymensingh Zone |  |  | 1.6608 | 0 | 1.1304 | 0 | 0 | 0.30129 | 0 | 0 | 3.0925 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 18.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0525 | Hydro | 0.864 | Hydro | 86400
| Khulna Zone |  |  | 6.6102 | 22.7564 | 0.13344 | 0 | 0 | 0.49104 | 19.8727 | 0 | 49.8638 | Solar | 4.1885 | Solar | 67203591.8912
| Barishal Zone |  |  | 7.923 | 28.2605 | 0 | 0 | 0 | 0.003238 | 0 | 0 | 36.1867 | Import | 46.908 | Import | 280274284.97
| Rajshahi Zone |  |  | 13.4408 | 0 | 0 | 0 | 0 | 1.3284 | 24.7898 | 0 | 39.559 | Wind | 0.1056 | Wind | 1553376
| Rangpur Zone |  |  | 0 | 0.34124 | 0.40504 | 0 | 0 | 1.2795 | 0 | 0 | 2.0258
| Total |  |  | 99.6185 | 71.9435 | 7.879 | 0 | 0.864 | 4.1885 | 46.908 | 0.1056 | 231.5071
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 349445079.02 |  | Hydro | 86400
|  |  |  | Coal | 460164701.3453 |  | Solar | 67203591.8912
|  |  |  | HFO | 131370949.41 |  | Import | 280274284.97
|  |  |  | HSD | 0 |  | Wind | 1553376
[5 empty] | Total: | 129,00,98,382 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.8727 | Peak Hr Flow | 875.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51970236.37 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.7898 | Peak Hr Flow | 1387.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2712 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2454 | Peak Hr Flow | 106.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2894 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.908 | Peak Hr Flow | 2368.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4142
|  |  |  | Chattogram |  | 0 |  | 1242
|  |  |  | Cumilla |  | 0 |  | 939
|  |  |  | Mymensingh |  | 0 |  | 875
|  |  |  | Sylhet |  | 0 |  | 405
|  |  |  | Khulna |  | 0 |  | 1271
|  |  |  | Barishal |  | 0 |  | 310
|  |  |  | Rajshahi |  | 0 |  | 998
|  |  |  | Rangpur |  | 0 |  | 776
|  |  |  | Total |  | 0 |  | 10958
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 | 15:56 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Annual
maintenance.
| 08:12 | 15:13 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Scheduled S/D Due to Annual
Maintenance work
| 08:13 | 15:12 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Scheduled S/D Due to Annual
Maintenance work
| 08:14 | 15:48 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to For Annual
Maintenance.
| 08:15 | 15:54 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end Due to Annual
maintenance
| 08:16 | 08:43 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-2 Tripped showing Distance relays Due to EF
trip,SOTF ,21 trip,R,Y,B Phase trip
| 08:16 | 08:42 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-02 Tripped showing Distance Relay | [7 empty] | 7.0MW load
|  |  | relays Due to Distance Relay operate | [7 empty] | interrup.
| 08:19 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by NLDC
| 08:19 |  | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by NLDC
| 08:20 | 16:07 | Bakulia-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance Bakalia-shikalbaha CKT-01 Dead line checking.
| 08:22 | 20:46 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D Due to Annual Maintenance
| 08:22 | 20:46 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D Due to Annual Maintenance
| 08:25 | 17:22 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Annual maintenance
work
| 08:26 | 17:20 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Annual maintenance
work
| 08:29 | 15:52 | Sirajganj 132/33kV S/S T2-(425) LT Scheduled S/D Due to Annual Maintenance
| 08:30 | 15:51 | Sirajganj 132/33kV S/S T2-(425) HT Scheduled S/D Due to Annual Maintenance
| 08:30 | 16:41 | Bibiyana-Kaliakoir 400 kV Ckt-2 Forced S/D from Kaliakoir 400/230/132kV end Due to By
NLDC and from Bibiana 400/230kV end Due to Death line checking-in
| 08:31 |  | Sylhet 225MW CCPP was shutdown due to air filter change work
| 08:34 | 13:59 | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shahmirpur 132/33kV end Due to Annual
Maintenance
| 08:34 | 17:33 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual maintenance work and from Sreemongol 132/33kV end Due to Annual maintenance
| 08:35 | 15:40 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to
132 kV Main Bus -01 shutdown for annual maintenance work.
| 08:37 | 15:40 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Narshingdi 132/33kV end Due to
132 kV Main Bus -01 shutdown for annual maintenance work.
| 08:39 | 15:40 | Narshingdi 132/33kV S/S 132 kV Main Bus-1 Scheduled S/D Due to 132 kV Main Bus -01
shutdown for annual maintenance work.
| 08:42 | 14:53 | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Annual
maintenance and from Haripur 230/132kV end Due to Annual Dead Line Checking.
| 08:47 | 11:37 | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Annual
Maintenance and from Natore 132/33kV end Due to Annual maintenance work
| 08:56 | 16:19 | Amnura-Rajshahi 132kV Ckt-1 Scheduled S/D from Rajshahi 230/132/33kV end Due to A/M and
from Amnura 132/33kV end Due to Annual maintenance.
| 09:03 | 16:40 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to annual maintenance
| 09:03 | 15:34 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance
| 09:04 | 15:33 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance
| 09:10 | 13:55 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Annual Maintenance
| 09:10 | 13:54 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Annual Maintenance
| 09:22 | 10:00 | Full interruption (42 MW) occurred under Jigatola grid s/s (DPDC) due to tripping of
Kamrangirchar-Jigatola ckt-1 and 2 caused by 33 kV feeder fault at Jigatola grid
| 09:27 | 13:07 | BIPTC S/S 10CF23 Scheduled S/D Due to Annual Maintenance
| 09:34 | 13:52 | Barapukuria 230/132/33kV S/S 132 KV Bus A Project Work S/D Due to Rangpur circuit -01
Bus-01 upgradation work.
| 09:34 | 12:17 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to shutdown
taken by Bashundhara via NLDC
| 09:35 | 12:13 | Jashore 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance
| 09:36 | 12:12 | Jashore 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance
| 09:37 | 14:42 | Kazla 132/33kV S/S GT-1 LT Scheduled S/D Due to Maintenance purpose | [7 empty] | 28.0MW load
interrup.
| 09:47 | 16:54 | Tongi 230/132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance
| 09:47 | 16:50 | Tongi 230/132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance
| 09:51 | 13:39 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) LT Scheduled S/D Due to Annual
Maintenance.
| 09:52 | 13:38 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) HT Scheduled S/D Due to Annual
Maintenance.
| 09:53 | 16:03 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to Incomer 2 conductor
maintenance
| 09:54 | 16:02 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to Incomer 2 conductor
maintenance
| 10:07 | 16:08 | Ghatail 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance work
| 10:08 | 16:05 | Ghatail 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance work
| 10:22 | 14:22 | Gulshan 132/33kV S/S MT-2 LT Scheduled S/D
| 10:25 | 14:20 | Gulshan 132/33kV S/S MT-2 HT Scheduled S/D
| 11:33 | 13:11 | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to TCS
Failure
| 12:00 |  | Day Peak Generation is 10201 MW.
| 12:04 | 13:30 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to T5 shutdown due to PT fuse change
| 12:05 | 13:29 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to T5 shutdown due to PT fuse change
| 12:58 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- ST
| 14:00 |  | Ashuganj 450 MW CCPP(South) Synchronized
| 14:26 |  | Rupsha 800 MW CCPP (NWPGCL) GT-1 was sync for test purpose.
|  | 15:29 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 is restored.
| 15:35 | 18:17 | Rajendrapur 132/33kV S/S 132 kV BUS-2 Scheduled S/D Due to For Bus Bar Protection
Integration.
| 15:50 |  | Kodda-Rajendrapur 132kV Ckt-1 Project Work S/D from Rajendrapur 132/33kV end Due to Bus
Bar Protection Integration. Only Kodda End CB Open.
|  | 16:43 | Khulna (C) S/S Tr-2 415 T HT is restored.
|  | 16:44 | Khulna (C) S/S Tr-2 415 T LT is restored.
|  | 16:47 | Bhulta-Rampura 230 kV Ckt-3 is restored.
|  | 16:48 | Bhulta-Rampura 230 kV Ckt-4 is restored.
|  | 17:00 | Cumilla(S) 132/33kV S/S TR-4 HT is restored.
|  | 17:00 | Cumilla(S) 132/33kV S/S TR-4 LT is restored.
| 17:18 |  | Khulna (C) S/S Tr-2 415 T LT Forced S/D Due to maybe PT problem
| 17:19 |  | Khulna (C) S/S Tr-2 415 T HT Forced S/D Due to maybe PT problem
| 17:38 |  | Barapukuria unit-1 was synchronized.
| 17:40 |  | Hathazari–Kaptai circuit-2 is switched.
|  | 17:54 | Maniknagar-Siddhirganj 230kV Ckt-1 is restored.
| 18:00 |  | Evening Peak Generation: 11313 MW.
| 18:04 |  | Kaptai Unit-4 synchronized.
|  | 18:24 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
| 18:26 |  | Korerhat-Feni 230kV circuit-1 was switched on for the first time at 18:26 hrs.
| 18:42 |  | Korerhat-Feni 230kV circuit-2 was switched on for the first time.
| 19:15 |  | Korerhat-BSRMi 230kV circuit-1 was switched on for the first time.
| 19:26 |  | Ashuganj (South) 360 MW CCPP ST was sync.
| 19:26 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 19:32 |  | Korerhat-BSRMi 230kV circuit-2 was switched on for the first time.
| 21:51 |  | Kaptai–Chandroghona circuits-1 and -2 were switched on.
| 22:00 |  | Hathazari–Kaptai circuit-1 is charged from Hathazari Substation.
| 01:04 |  | Mirsorai 230/33kV S/S TR-2, 728T LT Scheduled S/D Due to annual maintenance
|  | 03:07 | Mirsorai 230/33kV S/S TR-1, 718T HT is restored.
| 04:00 |  | Minimum Generation: 7627 MW.
| 07:34 |  | Bhulta 400/230kV S/S 400kV Bus-1 Scheduled S/D
| 07:45 |  | Maniknagar 132/33kV S/S Motijheel Ckt-2 Scheduled S/D Due to Annual Maintenance.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 358 | 8125200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7378821 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 40.2 | 207000 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 133440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 412675 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 139020 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 480600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1218164 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 76 | 569808 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 30 | 90240 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 164 | 1428480 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 187225 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 417 | 8858194 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1781.2 | 29756267
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130005 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 88800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 0 | 864000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5168076 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 613891 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 24000 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 424800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19898 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 58545 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 31 | 273600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 585 | 12338180 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 105600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 345 | 8247272.73 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1366 | 28356667.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 211 | 4927000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 99 | 5042000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 380 | 7076000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1112608 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 414836 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 106 | 2493227 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 70 | 537600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 106 | 2245440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 317310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 447873 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1136 | 24613894
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 60 | 1660800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 307200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 794400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 288690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 3 | 28800 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 141 | 3092490
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 683808 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1699200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 1624410 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 439000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 290760 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7563000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5032000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 698 | 18052538
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 19 | 25091 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 875 | 19872727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6585120 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 12 | 133440 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 491040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1100 | 22756360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2256 | 49863778
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 504 | 7680109 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2622000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1000 | 20580363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5300968 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Under Maintenance
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3238 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1834 | 36186678.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 323264 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 176 | 4050073 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9390690 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1387 | 24789818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 334496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 639660 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1977 | 39559021
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 25 | 341236 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 135600 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25653.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 269437 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 194040 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1059840 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 124 | 2025806.72
Eastern Grid Total |  |  |  |  | 17395.105 | 5122.2 | 103871856.73
Western Grid Total |  |  |  |  | 10984.003 | 6191 | 127635284.36
National Grid Total |  |  |  |  | 28379.108 | 11313.2 | 231507141.09
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7602.46 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3354.7 | MW
i) Dhaka area |  |  | 4141.96 |  | MW | i) Khulna area |  |  |  | 1271 | MW
ii) Chattogram area |  |  | 1241.5 |  | MW | ii) Barishal area |  |  |  | 309.5 | MW
iii) Cumilla area |  |  | 939 |  | MW | iii) Rajshahi area |  |  |  | 998.2 | MW
iv) Mymensingh area |  |  | 875 |  | MW | iv) Rangpur area |  |  |  | 776 | MW
v) Sylhet area |  |  | 405 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10957.16 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 51 | 18:00 | 133 | Niamatpur | 53 | 08:00
2 | AKSML | 100 | 13:00 | 68 | Ishurdi | 55 | 18:00 | 134 | Noapara | 37 | 20:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 53 | 18:00 | 135 | PHP | 9 | 18:30
4 | Agargaon | 89 | 13:00 | 70 | Jamalpur | 97 | 18:00 | 136 | Pabna | 73 | 18:00
5 | Agrabad | 46 | 18:00 | 71 | Jashore | 108 | 13:00 | 137 | Palashbari | 86 | 18:00
6 | Amnura | 24 | 08:00 | 72 | Jhenaidah | 100 | 18:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 58 | 13:00 | 73 | Joydebpur | 96 | 18:00 | 139 | Patiya | 6 | 18:00
8 | BSRM | 197 | 18:30 | 74 | Joypurhat | 42 | 18:00 | 140 | Patuakhali | 46.5 | 20:00
9 | Bagerhat | 64 | 18:00 | 75 | Juldah | 14 | 18:00 | 141 | Payra | 22 | 19:00
10 | Bajitpur | 58 | 20:00 | 76 | KSRM | 25 | 16:00 | 142 | Postogola | 41 | 13:00
11 | Bakulia | 68 | 18:00 | 77 | Kabirpur | 186 | 18:30 | 143 | Purbachal | 28 | 13:00
12 | Banani | 48 | 13:00 | 78 | Kachua | 55 | 20:00 | 144 | Purbasadipur | 106 | 19:00
13 | Bangabhaban | 14 | 10:00 | 79 | Kallyanpur | 72 | 17:00 | 145 | Rahanpur | 22 | 08:00
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 30 | 10:00 | 146 | Rahim | 29 | 11:00
15 | Barguna | 10 | 18:00 | 81 | Kamrangirchar | 59 | 19:00 | 147 | Rajbari | 61 | 18:00
16 | Barishal | 89 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 94 | 18:00
17 | Barishal-230 | 66 | 19:00 | 83 | Kasba | 22 | 19:00 | 149 | Rajshahi | 76 | 18:00
18 | Baroaulia | 46 | 18:30 | 84 | Kazla | 76 | 22:00 | 150 | Rajshahi-230 | 58 | 13:00
19 | Baroirhat | 48 | 13:00 | 85 | Keranigonj | 53 | 18:30 | 151 | Ramganj | 68 | 18:30
20 | Bashundhara | 146 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 28 | 14:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 60 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 168 | 18:00 | 154 | Rangpur | 92 | 18:00
23 | Benapole | 38 | 18:00 | 89 | Kishoreganj | 86 | 18:30 | 155 | Ruppur | 2.6 | 10:00
24 | Bhaluka | 126 | 18:30 | 90 | Kodda | 265 | 17:00 | 156 | SSM | 2 | 03:00
25 | Bhandaria | 37 | 20:00 | 91 | Kulaura | 27 | 18:00 | 157 | Saidpur | 94 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 48 | 08:00 | 158 | Satkhira | 84 | 18:00
27 | Bheramara(GK) | 42 | 18:00 | 93 | Kushtia | 117 | 18:00 | 159 | Satmasjid | 81 | 13:00
28 | Bhulta | 172 | 12:00 | 94 | Laksam | 18 | 00:00 | 160 | Savar | 150 | 16:00
29 | Bog-Sherpur | 54 | 08:00 | 95 | Lakshmipur | 23 | 20:00 | 161 | SevenRings | 3.14 | 01:00
30 | Bogura | 125 | 18:00 | 96 | Lalbag | 54 | 17:00 | 162 | ShahCement | 34 | 16:00
31 | Borhanuddin | 63 | 21:00 | 97 | Lalmonirhat | 48 | 18:00 | 163 | Shahjadpur | 55 | 18:00
32 | Brahmanbaria | 84 | 18:00 | 98 | MI_Cement | 11.7 | 05:00 | 164 | Shahjibazar | 83 | 18:00
33 | Cantonment | 76 | 13:00 | 99 | Madanganj | 26 | 20:00 | 165 | Shahmirpur | 39.5 | 23:00
34 | Chandina | 11 | 13:00 | 100 | Madaripur | 69 | 14:00 | 166 | Shariatpur | 54 | 19:30
35 | Chandpur | 52 | 13:00 | 101 | Madartek | 57 | 13:00 | 167 | Sherpur | 110 | 18:00
36 | Chandraghona | 27 | 18:00 | 102 | Madunaghat | 40 | 18:00 | 168 | Shikalbaha | 16 | 18:00
37 | Chapai | 51 | 13:00 | 103 | Magura | 48 | 18:00 | 169 | Shitalakhya | 65.8 | 13:00
38 | Charsaidpur | 43 | 12:00 | 104 | Mahasthangarh | 56 | 08:00 | 170 | Sholosohor | 36 | 15:00
39 | Chauddagram | 51 | 13:00 | 105 | Maijdee | 27 | 19:00 | 171 | Shyampur | 142 | 12:00
40 | Chhatak | 26 | 18:00 | 106 | Manikganj | 95 | 18:00 | 172 | Siddhirganj | 97 | 12:00
41 | Chowmuhani | 100 | 13:00 | 107 | Maniknagar | 55 | 13:00 | 173 | Sirajganj | 86 | 18:30
42 | Chuadanga | 74 | 18:00 | 108 | Matarbari | 34 | 18:00 | 174 | Sonargaon | 140 | 17:00
43 | Coxsbazar | 105 | 18:00 | 109 | Matuail | 58 | 12:00 | 175 | Sreemongol | 50 | 18:30
44 | Cumilla(N) | 90 | 23:00 | 110 | Metrorail_Motijheel | 22 | 10:00 | 176 | Sreepur | 88 | 18:30
45 | Cumilla(S) | 116 | 12:00 | 111 | Metrorail_Uttara | 7 | 18:00 | 177 | Srinagar | 31.3 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 84 | 17:00 | 178 | Sunamganj | 40 | 18:00
47 | Daudkandi | 110 | 18:00 | 113 | Mirpur | 117 | 18:00 | 179 | Sylhet | 39 | 18:00
48 | DhakaUniversity | 64 | 13:00 | 114 | Mirsorai | 10 | 15:00 | 180 | Sylhet-132 | 77 | 21:00
49 | Dhamrai | 100 | 18:00 | 115 | Mirzapur | 39 | 18:30 | 181 | TK | 17 | 20:00
50 | Dhanmondi | 79 | 13:00 | 116 | Mithapukur | 47 | 18:00 | 182 | Tangail | 118 | 18:00
51 | Dohazari | 68 | 13:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 27 | 08:00
52 | Faridpur | 113 | 18:00 | 118 | Mogbazar | 67.3 | 14:00 | 184 | Tasnim | 31 | 16:00
53 | Fatullah | 92 | 12:00 | 119 | Mongla | 34 | 08:00 | 185 | Thakurgaon | 83 | 18:00
54 | Fenchuganj | 23 | 18:00 | 120 | Motijheel | 29 | 13:00 | 186 | Tongi | 104 | 11:00
55 | Feni | 70 | 13:00 | 121 | Muktagacha | 27 | 07:00 | 187 | Ullahpara | 25 | 18:30
56 | GPH | 96 | 04:00 | 122 | Munshiganj | 75 | 13:00 | 188 | Ullon | 53 | 13:00
57 | Ghatail | 64 | 08:00 | 123 | Muradnagar | 25 | 19:30 | 189 | Uttara | 63 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 140 | 18:00 | 190 | UttaraNew | 13 | 13:00
59 | Ghorashal-230 | 79 | 13:00 | 125 | Naogaon | 90 | 18:30 | 191 | Zigatola | 58 | 13:00
60 | Goalpara | 30 | 13:00 | 126 | Narail | 40 | 18:00
61 | Gollamari | 60 | 08:00 | 127 | Narinda | 56 | 13:00
62 | Gopalganj | 77 | 18:30 | 128 | Narshingdi | 136 | 18:00
63 | Gulshan | 80 | 13:00 | 129 | Natore | 98 | 18:00
64 | Halishahar | 55 | 14:00 | 130 | Nawabganj | 28.6 | 13:00
65 | HaripurSBU | 84 | 12:00 | 131 | Netrakona | 105 | 18:30
66 | Hasnabad | 78 | 12:00 | 132 | New | 68 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9215.32 | 0 |  | 9215.32
1:00 | 8490.11 | 0 |  | 8490.11
2:00 | 8118.52 | 0 |  | 8118.52
3:00 | 7760.72 | 0 |  | 7760.72
4:00 | 7542.45 | 0 |  | 7542.45
5:00 | 7490.77 | 0 |  | 7490.77
6:00 | 7952.88 | 0 |  | 7952.88
7:00 | 8545.82 | 0 |  | 8545.82
8:00 | 9454.38 | 0 |  | 9454.38
9:00 | 9613.61 | 0 |  | 9613.61
10:00 | 9418.1 | 0 |  | 9418.1
11:00 | 9660.28 | 0 |  | 9660.28
12:00 | 10204.68 | 0 |  | 10204.68
13:00 | 10690.68 | 0 |  | 10690.68
14:00 | 10193.03 | 0 |  | 10193.03
15:00 | 9887.93 | 0 |  | 9887.93
16:00 | 9703.06 | 0 |  | 9703.06
17:00 | 10131.02 | 0 |  | 10131.02
18:00 | 11313.2 | 0 |  | 11313.2
19:00 | 11093 | 0 |  | 11093
19:30 | 10921.6 | 0 |  | 10921.6
20:00 | 10857.5 | 0 |  | 10857.5
21:00 | 10585.62 | 0 |  | 10585.62
22:00 | 10172.4 | 0 |  | 10172.4
23:00 | 9716.88 | 0 |  | 9716.88
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4111 | 5104.32 | 9215.32 | DAILY GENERATION CURVE
00:30 | 4077.5 | 4775.215 | 8852.715
01:00 | 4044 | 4446.11 | 8490.11 | 14-12-2025
01:30 | 3980.5 | 4323.815 | 8304.315
02:00 | 3917 | 4201.52 | 8118.52
02:30 | 3757.5 | 4182.12 | 7939.62
03:00 | 3598 | 4162.72 | 7760.72
03:30 | 3538 | 4113.585 | 7651.585
04:00 | 3478 | 4064.45 | 7542.45
04:30 | 3467 | 4049.61 | 7516.61
05:00 | 3456 | 4034.77 | 7490.77
05:30 | 3610.5 | 4111.325 | 7721.825
06:00 | 3765 | 4187.88 | 7952.88
06:30 | 3975.865 | 4273.485 | 8249.35
07:00 | 4186.73 | 4359.09 | 8545.82
07:30 | 4315.84 | 4684.26 | 9000.1
08:00 | 4444.95 | 5009.43 | 9454.38
08:30 | 4379.365 | 5154.63 | 9533.995
09:00 | 4313.78 | 5299.83 | 9613.61
09:30 | 4261.8 | 5254.055 | 9515.855
10:00 | 4209.82 | 5208.28 | 9418.1
10:30 | 4278.11 | 5261.08 | 9539.19
11:00 | 4346.4 | 5313.88 | 9660.28
11:30 | 4409.15 | 5523.33 | 9932.48
12:00 | 4471.9 | 5732.78 | 10204.68
12:30 | 4663.1 | 5784.58 | 10447.68
13:00 | 4854.3 | 5836.38 | 10690.68
13:30 | 4681.72 | 5760.135 | 10441.855
14:00 | 4509.14 | 5683.89 | 10193.03
14:30 | 4461.03 | 5579.45 | 10040.48
15:00 | 4412.92 | 5475.01 | 9887.93
15:30 | 4402.795 | 5392.7 | 9795.495
16:00 | 4392.67 | 5310.39 | 9703.06
16:30 | 4525.755 | 5391.285 | 9917.04
17:00 | 4658.84 | 5472.18 | 10131.02
17:30 | 4890.52 | 5831.59 | 10722.11
18:00 | 5122.2 | 6191 | 11313.2
18:30 | 4963.1 | 6240 | 11203.1
19:00 | 4804 | 6289 | 11093
19:30 | 4678.6 | 6243 | 10921.6
20:00 | 4639.5 | 6218 | 10857.5
20:30 | 4567.15 | 6154.41 | 10721.56 |  | Executive Engineer
21:00 | 4494.8 | 6090.82 | 10585.62 |  | Network Operation Division
21:30 | 4412.9 | 5966.11 | 10379.01
22:00 | 4331 | 5841.4 | 10172.4
22:30 | 4190 | 5754.64 | 9944.64
23:00 | 4049 | 5667.88 | 9716.88

## En-Curve
QF-LDC-12
Date | 14-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2975 | 1072 | 775 | 0 | 100 | 1192.32 | 40 | 3043 | 0 | 0 | 16 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 3004.5 | 1060.5 | 748 | 0 | 96 | 1057.215 | 40 | 2829.5 | 0 | 0 | 12 | 0 | 0 | 5 | 0 | 14-12-2025
01:00 | 3034 | 1049 | 721 | 0 | 92 | 922.11 | 40 | 2616 | 0 | 0 | 8 | 0 | 0 | 8 | 0
01:30 | 3044 | 1054 | 703.5 | 0 | 88 | 878.315 | 40 | 2483.5 | 0 | 0 | 4 | 0 | 0 | 9 | 0 | Energy Generated | 231.5071 |  | MKWHr
02:00 | 3054 | 1059 | 686 | 0 | 84 | 834.52 | 40 | 2351 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3033.5 | 979 | 686 | 0 | 82 | 834.62 | 40 | 2273.5 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | Total Energy Requirement | 231.5071 |  | MKWHr
03:00 | 3013 | 899 | 686 | 0 | 80 | 834.72 | 40 | 2196 | 0 | 0 | 0 | 0 | 0 | 12 | 0
03:30 | 2980.5 | 876.5 | 639 | 0 | 83 | 838.585 | 40 | 2181 | 0 | 0 | 0 | 0 | 0 | 13 | 0
04:00 | 2948 | 854 | 592 | 0 | 86 | 842.45 | 40 | 2166 | 0 | 0 | 0 | 0 | 0 | 14 | 0
04:30 | 2929 | 854 | 592 | 0 | 56 | 838.61 | 40 | 2194 | 0 | 0 | 0 | 0 | 0 | 13 | 0
05:00 | 2910 | 854 | 592 | 0 | 26 | 834.77 | 40 | 2222 | 0 | 0 | 0 | 0 | 0 | 12 | 0
05:30 | 2937.5 | 946.5 | 615 | 0 | 52 | 836.825 | 40 | 2283 | 0 | 0 | 0 | 0 | 0 | 11 | 0
06:00 | 2965 | 1039 | 638 | 0 | 78 | 838.88 | 40 | 2344 | 0 | 0 | 0 | 0 | 0 | 10 | 0
06:30 | 3103 | 1090 | 661.5 | 0 | 78 | 838.505 | 40 | 2418.5 | 12.345 | 0 | 2.5 | 0 | 0 | 5 | 0
07:00 | 3241 | 1141 | 685 | 0 | 78 | 838.13 | 40 | 2493 | 24.69 | 0 | 5 | 0 | 0 | 0 | 0
07:30 | 3254.5 | 1114.5 | 732 | 0 | 82 | 924.755 | 40 | 2704.5 | 113.845 | 0 | 34 | 0 | 0 | 0 | 0
08:00 | 3268 | 1088 | 779 | 0 | 86 | 1011.38 | 40 | 2916 | 203 | 0 | 63 | 0 | 0 | 0 | 0
08:30 | 3216 | 1081.5 | 827 | 0 | 86 | 1018.025 | 40 | 2883.5 | 311.47 | 0 | 70.5 | 0 | 0 | 0 | 0
09:00 | 3164 | 1075 | 875 | 0 | 86 | 1024.67 | 40 | 2851 | 419.94 | 0 | 78 | 0 | 0 | 0 | 0
09:30 | 3115.5 | 1097.5 | 874.5 | 0 | 89 | 947.02 | 40 | 2778.5 | 495.835 | 0 | 78 | 0 | 0 | 0 | 0
10:00 | 3067 | 1120 | 874 | 0 | 92 | 869.37 | 40 | 2706 | 571.73 | 0 | 78 | 0 | 0 | 0 | 0
10:30 | 3049.5 | 1130 | 874.5 | 0 | 100 | 871.665 | 40 | 2784 | 615.025 | 0 | 74.5 | 0 | 0 | 0 | 0
11:00 | 3032 | 1140 | 875 | 0 | 108 | 873.96 | 40 | 2862 | 658.32 | 0 | 71 | 0 | 0 | 0 | 0
11:30 | 3002.5 | 1150 | 874.5 | 0 | 111 | 960.69 | 40 | 2971 | 666.29 | 0 | 156.5 | 0 | 0 | 0 | 0
12:00 | 2973 | 1160 | 874 | 0 | 114 | 1047.42 | 40 | 3080 | 674.26 | 0 | 242 | 0 | 0 | 0 | 0
12:30 | 2981.5 | 1168.5 | 874.5 | 0 | 112 | 1050.315 | 40 | 3144 | 649.865 | 0 | 427 | 0 | 0 | 0 | 0
13:00 | 2990 | 1177 | 875 | 0 | 110 | 1053.21 | 40 | 3208 | 625.47 | 0 | 612 | 0 | 0 | 0 | 0
13:30 | 2811.5 | 1109 | 875 | 0 | 108 | 1059.605 | 40 | 3210.5 | 579.1 | 0 | 649.15 | 0 | 0 | 0 | 0
14:00 | 2633 | 1041 | 875 | 0 | 106 | 1066 | 40 | 3213 | 532.73 | 0 | 686.3 | 0 | 0 | 0 | 0
14:30 | 2657.5 | 1048 | 875 | 0 | 102 | 1019 | 40 | 3210.5 | 443.33 | 0 | 645.15 | 0 | 0 | 0 | 0
15:00 | 2682 | 1055 | 875 | 0 | 98 | 972 | 40 | 3208 | 353.93 | 0 | 604 | 0 | 0 | 0 | 0
15:30 | 2747.5 | 1075.5 | 874.5 | 0 | 99 | 972 | 20 | 3194 | 249.745 | 4.5 | 554.75 | 0 | 0 | 4 | 0
16:00 | 2813 | 1096 | 874 | 0 | 100 | 972 | 0 | 3180 | 145.56 | 9 | 505.5 | 0 | 0 | 8 | 0
16:30 | 2799 | 1106.5 | 874.5 | 0 | 91 | 1046 | 0 | 3217.5 | 77.54 | 31 | 665.5 | 0 | 0 | 8.5 | 0
17:00 | 2785 | 1117 | 875 | 0 | 82 | 1120 | 0 | 3255 | 9.52 | 53 | 825.5 | 0 | 0 | 9 | 0
17:30 | 2888 | 1144 | 875 | 0 | 94 | 1253.5 | 0 | 3407 | 4.76 | 73.5 | 974.35 | 0 | 0 | 8 | 0
18:00 | 2991 | 1171 | 875 | 0 | 106 | 1387 | 0 | 3559 | 0 | 94 | 1123.2 | 0 | 0 | 7 | 0
18:30 | 2949.5 | 1154 | 874.5 | 0 | 104 | 1418 | 20 | 3583 | 0 | 80 | 1015.1 | 0 | 0 | 5 | 0
19:00 | 2908 | 1137 | 874 | 0 | 102 | 1449 | 40 | 3607 | 0 | 66 | 907 | 0 | 0 | 3 | 0
19:30 | 2983 | 1159 | 874 | 0 | 104 | 1457 | 40 | 3555 | 0 | 32 | 715.6 | 0 | 0 | 2 | 0
20:00 | 2985 | 1158 | 875 | 0 | 100 | 1447 | 40 | 3550 | 0 | 15 | 682.5 | 0 | 0 | 5 | 0
20:30 | 3031 | 1161.5 | 874.5 | 0 | 101 | 1385.91 | 40 | 3551.5 | 0 | 7.5 | 564.15 | 0 | 0 | 4.5 | 0
21:00 | 3077 | 1165 | 874 | 0 | 102 | 1324.82 | 40 | 3553 | 0 | 0 | 445.8 | 0 | 0 | 4 | 0
21:30 | 3089 | 1164.5 | 874 | 0 | 102 | 1302.61 | 40 | 3490.5 | 0 | 0 | 312.4 | 0 | 0 | 4 | 0
22:00 | 3101 | 1164 | 874 | 0 | 102 | 1280.4 | 40 | 3428 | 0 | 0 | 179 | 0 | 0 | 4 | 0
22:30 | 3063 | 1132.5 | 874.5 | 0 | 97 | 1279.14 | 40 | 3345 | 0 | 0 | 111 | 0 | 0 | 2.5 | 0
23:00 | 3025 | 1101 | 875 | 0 | 92 | 1277.88 | 40 | 3262 | 0 | 0 | 43 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 409 | 05:00 | 383 | 12:00 | Meghnaghat | 409 | 05:00 | 385 | 12:00
Ashuganj | 413 | 6:00 | 387 | 12:00 | Payra | 418 | 05:00 | 409 | 12:00
Bhulta | 409 | 05:00 | 381 | 12:00 | Rahanpur | 419 | 03:00 | 400 | 18:00
Bibiana | 405 | 04:00 | 391 | 12:00 | Rampal | 414 | 07:00 | 395 | 12:00
BIPTC | 408 | 03:00 | 393 | 13:00
Bogura | 414 | 05:00 | 390 | 18:00
Gopalganj | 414 | 05:00 | 393 | 12:00
Kaliakoir | 403 | 03:00 | 375 | 12:00
Korerhat | 414 | 05:00 | 394 | 12:00
Madunaghat | 408 | 05:00 | 393 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 05:00 | 222 | 12:00 | Kachua | 236 | 18:00 | 226 | 12:00
AKSML | 235 | 06:00 | 224 | 12:00 | Kaliakoir | 239 | 04:00 | 221 | 12:00
Aminbazar | 239 | 04:00 | 223 | 12:00 | Keranigonj | 239 | 05:00 | 220 | 12:00
Ashuganj | 240 | 04:00 | 228 | 12:00 | Khulna(S) | 242 | 03:00 | 228 | 12:00
Ashuganj-400 | 240 | 6:00 | 228 | 12:00 | Korerhat | 240 | 04:00 | 229 | 12:00
Baghabari | 241 | 03:00 | 229 | 18:00 | Madunaghat | 235 | 03:00 | 226 | 11:00
Barapukuria | 233 | 05:00 | 216 | 08:00 | Madunaghat-400 | 236 | 04:00 | 227 | 12:00
Barapukuria-230 | 233 | 6:00 | 217 | 12:00 | Maniknagar | 238 | 05:00 | 221 | 12:00
Barishal | 246 | 03:00 | 235 | 12:00 | Meghnaghat | 240 | 04:00 | 229 | 12:00
Bheramara | 238 | 05:00 | 222 | 12:00 | Meghnaghat-400 | 240 | 05:00 | 224 | 12:00
Bhulta | 240 | 06:00 | 222 | 12:00 | Mirsorai | 238 | 06:00 | 223 | 17:00
Bibiana | 237 | 06:00 | 229 | 12:00 | Rajshahi | 238 | 04:00 | 222 | 18:00
BIPTC | 240 | 02:00 | 222 | 13:00 | Rampal | 239 | 02:00 | 226 | 12:00
Bogura | 243 | 05:00 | 229 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 242 | 05:00 | 228 | 18:00 | Rampura | 239 | 05:00 | 219 | 12:00
Borhanuddin | 245 | 00:00 | 240 | 10:00 | Shikalbaha | 234 | 04:00 | 225 | 12:00
BSRM | 237 | 06:00 | 223 | 14:00 | Shyampur | 239 | 05:00 | 225 | 11:00
Cumilla(N) | 239 | 05:00 | 225 | 12:00 | Siddhirganj | 238 | 03:00 | 223 | 12:00
Faridpur | 245 | 03:00 | 233 | 12:00 | Sirajgonj | 246 | 04:00 | 236 | 18:00
Fenchuganj | 237 | 00:00 | 230 | 11:00 | Sreepur | 237 | 02:00 | 224 | 12:00
Feni | 238 | 06:00 | 225 | 12:00 | Tongi | 236 | 05:00 | 217 | 11:00
Ghorashal | 242 | 04:00 | 232 | 13:00
Ghorashal-230 | 232 | 05:00 | 211 | 12:00
Gopalganj | 245 | 04:00 | 233 | 12:00
GPH | 236 | 05:00 | 225 | 12:00
Haripur | 239 | 04:00 | 223 | 12:00
Hasnabad | 237 | 05:00 | 221 | 11:00
Hathazari | 230 | 08:00 | 226 | 00:00
Ishurdi | 241 | 02:00 | 225 | 18:00
Jhenaidah | 239 | 03:00 | 221 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 123 | 12:00 | Lalbag | 137 | 05:00 | 124 | 12:00
Agargaon | 138 | 05:00 | 127 | 12:00 | Lalmonirhat | 132 | 07:00 | 121 | 08:00
Agrabad | 136 | 04:00 | 129 | 12:00 | Madanganj | 139 | 06:00 | 133 | 15:00
AKS | 135 | 01:00 | 130 | 00:00 | Madaripur | 141 | 05:00 | 135 | 12:00
Aminbazar | 137 | 03:00 | 129 | 12:00 | Madartek | 135 | 05:00 | 125 | 12:00
Amnura | 139 | 05:00 | 130 | 18:00 | Madunaghat | 137 | 02:00 | 131 | 12:00
Ashuganj | 142 | 04:00 | 138 | 12:00 | Magura | 138 | 05:00 | 125 | 12:00
Bagerhat | 138 | 03:00 | 128 | 12:00 | Mahasthangarh | 137 | 05:00 | 128 | 08:00
Bajitpur | 137 | 04:00 | 129 | 13:00 | Maijdee | 135 | 05:00 | 128 | 12:00
Bakulia | 137 | 06:00 | 130 | 12:00 | Manikganj | 132 | 01:00 | 120 | 12:00
Banani | 135 | 03:00 | 121 | 12:00 | Maniknagar | 138 | 05:00 | 124 | 12:00
Bangabhaban | 139 | 00:00 | 123 | 12:00 | Matarbari | 129 | 06:00 | 119 | 18:00
Barapukuria | 136 | 02:00 | 124 | 10:00 | Matuail | 140 | 02:00 | 131 | 12:00
Barguna | 137 | 06:00 | 134 | 12:00 | Metrorail_Motijheel | 138 | 05:00 | 123 | 15:00
Barishal | 141 | 01:00 | 134 | 12:00 | Metrorail_Uttara | 137 | 01:00 | 125 | 15:00
Barishal-230 | 142 | 03:00 | 135 | 12:00 | Millgate | 136 | 04:00 | 121 | 12:00
Baroaulia | 136 | 06:00 | 130 | 12:00 | Mirpur | 137 | 03:00 | 128 | 12:00
Baroirhat | 135 | 02:00 | 128 | 12:00 | Mirzapur | 138 | 05:00 | 126 | 11:00
Bashundhara | 135 | 03:00 | 122 | 12:00 | Mithapukur | 136 | 04:00 | 125 | 08:00
BashundharaCement | 139 | 06:00 | 133 | 15:00 | MI_Cement | 139 | 06:00 | 125 | 12:00
Beanibazar | 136 | 05:00 | 132 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 135 | 03:00 | 118 | 13:00 | Mogbazar | 138 | 01:00 | 124 | 12:00
Bhaluka | 135 | 05:00 | 128 | 13:00 | Mongla | 137 | 06:00 | 128 | 12:00
Bhandaria | 135 | 05:00 | 125 | 18:00 | Motijheel | 139 | 00:00 | 123 | 12:00
Bhangura | 139 | 02:00 | 132 | 12:00 | Muktagacha | 132 | 03:00 | 128 | 08:00
Bheramara | 141 | 02:00 | 134 | 18:00 | Munshiganj | 139 | 02:00 | 130 | 12:00
Bheramara(GK) | 141 | 03:00 | 134 | 18:00 | Muradnagar | 139 | 05:00 | 127 | 13:00
Bhulta | 136 | 05:00 | 127 | 12:00 | Mymensingh | 132 | 00:00 | 122 | 12:00
Bog-Sherpur | 139 | 05:00 | 130 | 12:00 | Naogaon | 135 | 04:00 | 125 | 12:00
Bogura | 138 | 05:00 | 129 | 13:00 | Narail | 139 | 04:00 | 124 | 13:00
Bogura-230 | 138 | 02:00 | 130 | 12:00 | Narinda | 138 | 5:00 | 124 | 12:00
Brahmanbaria | 139 | 06:00 | 133 | 12:00 | Narshingdi | 136 | 01:00 | 126 | 12:00
Cantonment | 137 | 03:00 | 126 | 12:00 | Natore | 137 | 02:00 | 130 | 13:00
Chandina | 141 | 06:00 | 131 | 12:00 | Nawabganj | 137 | 05:00 | 125 | 12:00
Chandpur | 139 | 07:00 | 134 | 11:00 | Netrakona | 132 | 23:00 | 117 | 18:00
Chandraghona | 138 | 06:00 | 132 | 16:00 | New | 134 | 04:00 | 123 | 11:00
Chapai | 140 | 06:00 | 134 | 12:00 | Niamatpur | 140 | 05:00 | 133 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 140 | 04:00 | 132 | 12:00 | Noapara | 138 | 04:00 | 119 | 13:00
Chauddagram | 138 | 04:00 | 129 | 12:00 | Pabna | 140 | 02:00 | 132 | 13:00
Chhatak | 135 | 09:00 | 130 | 14:00 | Palashbari | 135 | 05:00 | 124 | 12:00
Chowmuhani | 135 | 03:00 | 128 | 15:00 | Panchagarh | 139 | 05:00 | 121 | 13:00
Chuadanga | 139 | 04:00 | 124 | 12:00 | Patiya | 137 | 05:00 | 130 | 12:00
Coxsbazar | 126 | 04:00 | 120 | 12:00 | Patuakhali | 136 | 05:00 | 132 | 12:00
Cumilla(N) | 141 | 05:00 | 132 | 12:00 | Payra | 137 | 01:00 | 134 | 12:00
Cumilla(S) | 140 | 04:00 | 124 | 12:00 | PHP | 136 | 06:00 | 128 | 11:00
Daganbhuiyan | 136 | 05:00 | 129 | 12:00 | Postogola | 139 | 05:00 | 127 | 12:00
Daudkandi | 137 | 05:00 | 121 | 12:00 | Purbachal | 135 | 04:00 | 122 | 12:00
DhakaUniversity | 136 | 05:00 | 123 | 12:00 | Purbasadipur | 134 | 03:00 | 122 | 13:00
Dhamrai | 139 | 05:00 | 127 | 11:00 | Rahanpur | 141 | 05:00 | 135 | 12:00
Dhanmondi | 142 | 06:00 | 132 | 12:00 | Rahanpur-400 | 141 | 02:00 | 134 | 18:00
Dohazari | 134 | 05:00 | 128 | 12:00 | Rahim | 140 | 05:00 | 131 | 12:00
Faridpur | 140 | 03:00 | 134 | 12:00 | Rajbari | 141 | 05:00 | 133 | 13:00
Fatullah | 138 | 04:00 | 125 | 12:00 | Rajendrapur | 139 | 05:00 | 128 | 12:00
Fenchuganj | 141 | 00:00 | 137 | 11:00 | Rajshahi | 138 | 05:00 | 129 | 13:00
Feni | 135 | 04:00 | 128 | 12:00 | Rajshahi-230 | 138 | 05:00 | 129 | 12:00
Feni-230 | 136 | 04:00 | 129 | 12:00 | Ramganj | 136 | 01:00 | 132 | 10:00
Ghatail | 133 | 04:00 | 125 | 12:00 | Rampur | 135 | 01:00 | 129 | 12:00
Ghorashal | 138 | 04:00 | 126 | 13:00 | Rampura | 135 | 03:00 | 122 | 12:00
Goalpara | 141 | 04:00 | 131 | 12:00 | Rangamati | 137 | 02:00 | 131 | 16:00
Gollamari | 141 | 06:00 | 131 | 12:00 | Rangpur | 133 | 01:00 | 125 | 13:00
Gopalganj | 141 | 05:00 | 133 | 12:00 | Ruppur | 140 | 01:00 | 134 | 13:00
Gopalganj-400 | 142 | 02:00 | 133 | 17:00 | Saidpur | 135 | 05:00 | 122 | 08:00
Gulshan | 135 | 05:00 | 124 | 11:00 | Satkhira | 138 | 04:00 | 129 | 12:00
Halishahar | 137 | 02:00 | 130 | 12:00 | Satmasjid | 138 | 05:00 | 127 | 12:00
Haripur | 141 | 05:00 | 132 | 12:00 | Savar | 138 | 18:30 | 128 | 11:00
HaripurSBU | 140 | 04:00 | 132 | 12:00 | SevenRings | 138 | 02:00 | 126 | 13:00
Hasnabad | 138 | 01:00 | 127 | 12:00 | ShahCement | 140 | 04:00 | 132 | 12:00
Hathazari | 136 | 00:00 | 133 | 11:00 | Shahjadpur | 143 | 05:00 | 135 | 16:00
Ishurdi | 142 | 02:00 | 134 | 18:00 | Shahjibazar | 141 | 06:00 | 135 | 12:00
Jaldhaka | 133 | 06:00 | 120 | 08:00 | Shahmirpur | 136 | 02:00 | 130 | 16:00
Jamalpur | 131 | 15:00 | 120 | 00:00 | Shariatpur | 141 | 03:00 | 134 | 12:00
Jashore | 136 | 02:00 | 132 | 19:00 | Sherpur | 130 | 15:00 | 116 | 07:00
Jhenaidah | 139 | 04:00 | 118 | 18:00 | Shikalbaha | 126 | 05:00 | 120 | 12:00
Jhenaidah-230 | 139 | 02:00 | 126 | 13:00 | Shikalbaha-230 | 138 | 06:00 | 131 | 12:00
Joydebpur | 136 | 04:00 | 125 | 18:00 | Shitalakhya | 139 | 06:00 | 125 | 12:00
Joypurhat | 135 | 04:00 | 125 | 12:00 | Sholosohor | 137 | 02:00 | 131 | 12:00
Juldah | 137 | 04:00 | 130 | 11:00 | Shyampur | 134 | 02:00 | 127 | 12:00
Kabirpur | 137 | 05:00 | 120 | 12:00 | Shyampur-230 | 139 | 05:00 | 129 | 11:00
Kachua | 141 | 05:00 | 134 | 12:00 | Siddhirganj | 140 | 02:00 | 131 | 12:00
Kaliakoir | 141 | 02:00 | 130 | 12:00 | Sirajganj | 138 | 03:00 | 130 | 12:00
Kallyanpur | 138 | 04:00 | 129 | 12:00 | Sonargaon | 136 | 19:00 | 120 | 11:00
Kalurghat | 136 | 01:00 | 132 | 11:00 | Sreemongol | 140 | 06:00 | 134 | 12:00
Kamrangirchar | 136 | 03:00 | 125 | 12:00 | Sreepur | 139 | 02:00 | 130 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 05:00 | 125 | 12:00
Kasba | 139 | 05:00 | 126 | 12:00 | SSM | 138 | 01:00 | 133 | 11:00
Kazla | 138 | 04:00 | 122 | 13:00 | Sunamganj | 134 | 10:00 | 130 | 00:00
Keranigonj | 137 | 05:00 | 125 | 12:00 | Sylhet | 136 | 09:00 | 133 | 12:00
Khagrachori | 136 | 00:00 | 131 | 12:00 | Sylhet-132 | 136 | 09:00 | 134 | 00:00
Khulna | 139 | 04:00 | 130 | 12:00 | Tangail | 133 | 05:00 | 123 | 12:00
Khulna(S) | 141 | 03:00 | 131 | 13:00 | Taraganj | 134 | 06:00 | 122 | 12:00
Khulshi | 135 | 04:00 | 129 | 12:00 | Tasnim | 136 | 19:00 | 129 | 11:00
Kishoreganj | 134 | 04:00 | 127 | 13:00 | Thakurgaon | 138 | 05:00 | 120 | 13:00
Kodda | 136 | 18:00 | 123 | 12:00 | TK | 137 | 04:00 | 131 | 12:00
KSRM | 138 | 00:00 | 131 | 12:00 | Tongi | 136 | 05:00 | 125 | 11:00
Kulaura | 141 | 05:00 | 137 | 00:00 | Ullahpara | 139 | 04:00 | 130 | 18:00
Kurigram | 133 | 04:00 | 119 | 08:00 | Ullon | 135 | 02:00 | 122 | 12:00
Kushtia | 137 | 05:00 | 126 | 18:00 | Uttara | 136 | 04:00 | 122 | 11:00
Laksam | 140 | 02:00 | 134 | 12:00 | UttaraNew | 137 | 01:00 | 129 | 11:00
Lakshmipur | 136 | 05:00 | 128 | 12:00 | Zigatola | 137 | 04:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division