## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-12-2025 | during | 16-12-2025 | during | 16-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 377 | 338 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 31.5 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 25.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 5 | 105 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 32 | 155 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | Gas shortage ST maint
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 408 | 433 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1305 | 1675 | 5779.35 | 5749.35 | 2517.06 | 2496.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 28 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 226 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 64 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 33 | 33 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 22 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.28 | 0 | 3.21 | 0 | 3.21 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 585 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 3 | 0 | 5 | 0 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1266.28 | 1374 | 2557.93 | 2560.72 | 2047.71 | 2050.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 210 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 250 | 250 | 250 | 250 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 250 | 330 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 300 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 8 | 20 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 103 | 108 | 163 | 163 | 112 | 112 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 12 | 100 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 110 | 112 | 160 | 160 | 116 | 116 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1052 | 1231 | 2687.21 | 2622.21 | 2133.51 | 2068.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-12-2025 | during | 16-12-2025 | during | 16-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 32 | 35 | 157.5 | 157.5 | 96 | 96 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 60 | 65 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.81 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 156.81 | 131 | 364.1 | 314 | 255.1 | 205
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 20 | 20 | 20 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 207 | 207 | 205 | 205 | 205 | 205 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 706 | 712 | 754 | 754 | 700 | 700
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 874 | 873 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 212 | 180 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 57 | 108 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 941 | 1112 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2166 | 2283 | 2356 | 2278 | 1595.1 | 1517.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 300 | 513 | 0 | 0 | 500 | 500 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 55 | 55 | 55 | 55 | 55 | 55 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 950 | 941 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant shutdown as per NLDC requirement.
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.44 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1525.44 | 1729 | 1928.32 | 1928.32 | 1988.32 | 1988.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 53.01 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 168 | 179 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 398 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.12 | 0 | 4.9 | 0 | 4.9 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 932 | 1399.44 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.46 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 89 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1715.59 | 1976.44 | 3083.77 | 2918.87 | 2554.39 | 2389.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 57 | 58 | 58 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.7 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 144 | 0 | 142 | 0 | 173 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 236.7 | 126 | 497.2 | 320 | 486.2 | 278
System Total |  |  |  |  | 28823.2 | 28379.108 | 10129.82 | 11237.44 | 20007.88 | 19445.47 | 14277.39 | 13692.98
Forecast Scenario (16-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9260 |  | 0 |  | 9260
|  |  |  | 1:00 | 8680 |  | 0 |  | 8680
|  |  |  | 2:00 | 8290 |  | 0 |  | 8290
|  |  |  | 3:00 | 7990 |  | 0 |  | 7990
|  |  |  | 4:00 | 7620 |  | 0 |  | 7620
|  |  |  | 5:00 | 7670 |  | 0 |  | 7670
|  |  |  | 6:00 | 7930 |  | 0 |  | 7930
|  |  |  | 7:00 | 8560 |  | 0 |  | 8560
|  |  |  | 8:00 | 9450 |  | 0 |  | 9450
|  |  |  | 9:00 | 9710 |  | 0 |  | 9710
|  |  |  | 10:00 | 9510 |  | 0 |  | 9510
|  |  |  | 11:00 | 9640 |  | 0 |  | 9640
|  |  |  | 12:00 | 10130 |  | 0 |  | 10130
|  |  |  | 13:00 | 10610 |  | 0 |  | 10610
|  |  |  | 14:00 | 10230 |  | 0 |  | 10230
|  |  |  | 15:00 | 9610 |  | 0 |  | 9610
|  |  |  | 16:00 | 9530 |  | 0 |  | 9530
|  |  |  | 17:00 | 9770 |  | 0 |  | 9770
|  |  |  | 18:00 | 11230 |  | 0 |  | 11230
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 10920 |  | 0 |  | 10920
|  |  |  | 19:30 | 10700 |  | 0 |  | 10700
|  |  |  | 20:00 | 10630 |  | 0 |  | 10630
|  |  |  | 21:00 | 10480 |  | 0 |  | 10480
|  |  |  | 22:00 | 10000 |  | 0 |  | 10000
|  |  |  | 23:00 | 9700 |  | 0 |  | 9700
Probable Maximum Temperature: |  |  | 26.90°C
Probable Maximum Demand at Day Peak: |  |  | 10130.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11230.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11230.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.15 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:58 hrs on 16-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-12-2025 | [28 empty] | Date: | 15-12-2025 | [28 empty] | Date: | 15-12-2025 | [28 empty] | Date: | 15-12-2025 | [28 empty] | Date: | 15-12-2025 | [17 empty] | Date: | 15-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 230 | 0 | 250 | 51 | 0 | 209 | 0 | 0 | 110 | 0 | 0 | 14 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 8 | 8 | 63 | 0 | 0 | 0 | 3984 | 780 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 0 | 10 | 0 | 1119.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 900 | 0 | 5280.42 | 9264.42 | 98.87
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 502 | 0 | 0 | 0 | 230 | 0 | 250 | 51 | 0 | 224 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 8 | 8 | 65 | 0 | 0 | 0 | 3943 | 765 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912 | 0 | 10 | 0 | 860.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 790 | 0 | 4744.15 | 8687.15 | 98.86
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 230 | 0 | 250 | 51 | 0 | 204 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 315 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 8 | 0 | 69 | 0 | 0 | 0 | 3884 | 685 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 0 | 10 | 0 | 828.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 655 | 0 | 4408.96 | 8292.96 | 98.86
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 230 | 0 | 250 | 51 | 0 | 191 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 3750.5 | 685 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 10 | 0 | 830.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 558 | 0 | 4243.58 | 7994.08 | 98.86
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 230 | 0 | 250 | 5 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 305 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 42 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 3510.5 | 591 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 10 | 0 | 841.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 500 | 0 | 4117.72 | 7628.22 | 98.86
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 230 | 0 | 250 | 5 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 295 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 42 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 3459.5 | 590 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 10 | 0 | 855.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 500 | 0 | 4210.92 | 7670.42 | 98.86
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 300 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 230 | 0 | 250 | 15 | 0 | 208 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 300 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 73 | 30 | 0 | 15 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 3634.5 | 637 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799 | 0 | 10 | 0 | 831.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 220 | 0 | 250 | 538 | 0 | 4301.99 | 7936.49 | 98.85
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 260 | 0 | 0 | 1 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.24 | 40 | 0 | 24 | 300 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 453 | 1 | 0 | 0 | 280 | 0 | 280 | 51 | 0 | 210 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 76 | 0 | 3 | 0 | 300 | 0 | 206 | 0 | 30 | 0 | 0 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 30 | 3 | 70 | 0 | 1.15 | 0 | 3911.89 | 685 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 835 | 0 | 10 | 0 | 1016.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 3 | 0 | 0 | 1.41 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0.16 | 0 | 61 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 0.01 | 0 | 0 | 55 | 220 | 0 | 300 | 609 | 0 | 4652.55 | 8564.44 | 98.85
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 40 | 0 | 12 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 566 | 9 | 0 | 0 | 300 | 0 | 330 | 51 | 0 | 208 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 84 | 0 | 27 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 2.2 | 16 | 0 | 79 | 30 | 0 | 15 | 0 | 0 | 58 | 19 | 63 | 1 | 12.1 | 0 | 4298.97 | 779 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.02 | 945 | 0 | 10 | 0 | 1024.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.58 | 24 | 0 | 0 | 12.98 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 1.51 | 0 | 61 | 0 | 9 | 0 | 0 | 0 | 0 | 0.6 | 47 | 0.12 | 0 | 0 | 55 | 220 | 0 | 350 | 750 | 0 | 5158.99 | 9457.96 | 98.85
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.02 | 40 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 230 | 0 | 280 | 51 | 0 | 197 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 84 | 0 | 47 | 0 | 305 | 0 | 207 | 0 | 30 | 0 | 7 | 16 | 0 | 79 | 30 | 0 | 15 | 0 | 0 | 56 | 19 | 32 | 1 | 28.09 | 0 | 4235.11 | 873 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 967 | 0 | 10 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.28 | 52 | 0 | 0 | 32.72 | 0 | 0 | 190 | 0 | 0 | 0 | 350 | 0 | 1.85 | 0 | 59 | 0 | 18 | 0 | 0 | 0 | 0 | 3.2 | 100 | 0.18 | 0 | 0 | 55 | 180 | 0 | 350 | 920 | 0 | 5481.23 | 9716.34 | 98.85
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 250 | 0 | 0 | 23 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 40 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 575 | 16 | 0 | 0 | 230 | 0 | 250 | 51 | 0 | 219 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 96 | 0 | 59 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 9 | 16 | 0 | 79 | 30 | 0 | 15 | 0 | 0 | 56 | 19 | 32 | 2 | 36.46 | 0 | 4126.18 | 873 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 907 | 2 | 10 | 0 | 937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.68 | 74 | 0 | 0 | 46.77 | 0 | 0 | 165 | 0 | 0 | 0 | 347 | 0 | 4.15 | 0 | 57 | 0 | 24 | 0 | 0 | 0 | 0 | 4.6 | 137 | 0.4 | 0 | 0 | 55 | 180 | 0 | 300 | 944 | 0 | 5389.6 | 9515.78 | 98.85
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 250 | 0 | 0 | 27 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 40 | 0 | 5 | 354 | 0 | 0 | 13 | 0 | 0 | 224 | 0 | 0 | 0 | 580 | 19 | 0 | 0 | 230 | 0 | 250 | 51 | 0 | 199 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 108 | 0 | 66 | 0 | 310 | 0 | 207 | 0 | 30 | 0 | 10 | 16 | 0 | 79 | 30 | 0 | 15 | 0 | 0 | 60 | 19 | 32 | 2 | 43.14 | 0 | 4122.27 | 874 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 906 | 24 | 10 | 0 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.78 | 86 | 0 | 0 | 53.77 | 0 | 0 | 161 | 0 | 0 | 0 | 414 | 0 | 4.96 | 0 | 57 | 0 | 29 | 0 | 0 | 0 | 0 | 5.4 | 147 | 0.46 | 0 | 0 | 55 | 180 | 0 | 300 | 944 | 0 | 5518.37 | 9640.64 | 98.85
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 0 | 5 | 0 | 60 | 0 | 55 | 32 | 0 | 0 | 0 | 408 | 0 | 0 | 300 | 0 | 0 | 29 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 40 | 0 | 7 | 354 | 0 | 0 | 37 | 0 | 0 | 221 | 0 | 0 | 0 | 585 | 19 | 8 | 0 | 230 | 0 | 250 | 51 | 0 | 210 | 0 | 0 | 103 | 12 | 0 | 11 | 0 | 110 | 0 | 67 | 0 | 315 | 0 | 207 | 0 | 30 | 0 | 11 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 60 | 19 | 32 | 2 | 43.81 | 0 | 4486.09 | 874 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 941 | 57 | 10 | 0 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.01 | 89 | 0 | 0 | 54.46 | 0 | 0 | 168 | 0 | 0 | 0 | 414 | 0 | 5.12 | 0 | 58 | 0 | 31 | 0 | 0 | 0 | 0 | 3.7 | 144 | 0.44 | 0 | 0 | 55 | 220 | 0 | 300 | 950 | 0 | 5643.73 | 10129.82 | 98.85
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 29 | 0 | 17 | 0 | 145 | 0 | 55 | 67 | 0 | 0 | 0 | 420 | 0 | 0 | 300 | 0 | 0 | 28 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 3.01 | 40 | 0 | 9 | 354 | 0 | 0 | 17 | 0 | 54 | 218 | 0 | 0 | 0 | 580 | 18 | 42 | 0 | 230 | 0 | 250 | 51 | 0 | 203 | 0 | 0 | 104 | 68 | 0 | 11 | 0 | 108 | 0 | 64 | 0 | 320 | 0 | 207 | 10 | 30 | 0 | 10 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 65 | 19 | 29 | 2 | 37.88 | 0 | 4804.89 | 874 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1032 | 107 | 10 | 0 | 1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.98 | 88 | 0 | 0 | 52.64 | 0 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 4.77 | 0 | 58 | 0 | 24 | 0 | 0 | 0 | 0 | 3.6 | 88 | 0.45 | 0 | 0 | 55 | 220 | 0 | 300 | 950 | 0 | 5810.44 | 10615.33 | 98.85
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 31.4 | 0 | 17 | 0 | 145 | 0 | 55 | 66 | 0 | 0 | 0 | 389 | 0 | 0 | 300 | 0 | 0 | 24 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24 | 2.45 | 40 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 67 | 218 | 0 | 0 | 0 | 582 | 15 | 70 | 0 | 230 | 0 | 250 | 51 | 0 | 198 | 0 | 0 | 105 | 66 | 0 | 11 | 0 | 108 | 0 | 53 | 0 | 300 | 0 | 207 | 20 | 30 | 0 | 8 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 69 | 19 | 30 | 2 | 35.63 | 0 | 4740.48 | 873 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 968 | 107 | 10 | 0 | 970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.76 | 71 | 0 | 0 | 42.52 | 0 | 0 | 158 | 0 | 0 | 0 | 353 | 0 | 3.74 | 0 | 58 | 0 | 24 | 0 | 0 | 0 | 0 | 3 | 115 | 0.37 | 0 | 0 | 55 | 180 | 0 | 300 | 900 | 0 | 5490.39 | 10230.87 | 98.85
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 17 | 0 | 30 | 0 | 35 | 101 | 0 | 0 | 0 | 367 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 12 | 1.54 | 40 | 0 | 5 | 354 | 0 | 0 | 25 | 0 | 17 | 222 | 0 | 0 | 0 | 580 | 12 | 20 | 0 | 230 | 0 | 250 | 51 | 0 | 195 | 0 | 0 | 104 | 17 | 0 | 19 | 0 | 112 | 0 | 38 | 0 | 300 | 0 | 207 | 20 | 30 | 0 | 4 | 16 | 0 | 79 | 30 | 0 | 15 | 0 | 0 | 45 | 8 | 32 | 1 | 24.04 | 0 | 4358.58 | 874 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 885 | 106 | 10 | 0 | 1008.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.94 | 45 | 0 | 0 | 25.27 | 0 | 0 | 156 | 0 | 0 | 0 | 349 | 0 | 2.57 | 0 | 58 | 0 | 17 | 0 | 0 | 0 | 0 | 2 | 90 | 0.24 | 0 | 0 | 55 | 220 | 0 | 300 | 800 | 0 | 5260.79 | 9619.37 | 98.84
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 17 | 0 | 30 | 0 | 35 | 104 | 0 | 0 | 0 | 380 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 12 | 0.75 | 40 | 0 | 6 | 354 | 0 | 0 | 26 | 0 | 17 | 222 | 0 | 0 | 0 | 580 | 6 | 10 | 0 | 230 | 0 | 250 | 51 | 0 | 200 | 0 | 0 | 104 | 17 | 0 | 20 | 0 | 104 | 0 | 17 | 0 | 310 | 0 | 207 | 20 | 30 | 0 | 2 | 16 | 0 | 82 | 30 | 0 | 15 | 0 | 0 | 45 | 8 | 35 | 0 | 7.53 | 0 | 4371.28 | 873 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 815 | 105 | 10 | 0 | 1023.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.73 | 21 | 0 | 0 | 10.09 | 0 | 0 | 163 | 0 | 0 | 0 | 414 | 0 | 0.56 | 0 | 58 | 0 | 7 | 0 | 0 | 0 | 0 | 0.8 | 32 | 0.11 | 0 | 0 | 55 | 220 | 0 | 300 | 842 | 0 | 5164.01 | 9535.29 | 98.84
17:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 25 | 0 | 46 | 0 | 145 | 0 | 35 | 152 | 0 | 0 | 0 | 388 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 25.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 25 | 0.02 | 40 | 0 | 7 | 354 | 0 | 0 | 26 | 0 | 50 | 223 | 0 | 0 | 0 | 580 | 0 | 45 | 0 | 230 | 0 | 250 | 51 | 0 | 194 | 0 | 0 | 105 | 50 | 0 | 20 | 0 | 106 | 0 | 1 | 0 | 300 | 0 | 207 | 20 | 30 | 0 | 0 | 16 | 0 | 83 | 30 | 0 | 15 | 0 | 0 | 59 | 19 | 35 | 0 | 0.36 | 7 | 4659.88 | 873 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 910 | 106 | 10 | 0 | 1017.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 1 | 0 | 0 | 0.7 | 0 | 0 | 159 | 0 | 0 | 0 | 346 | 0 | 0.07 | 0 | 58 | 35 | 1 | 30 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 0 | 55 | 180 | 0 | 300 | 850 | 0 | 5117.67 | 9777.55 | 98.84
18:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 31.5 | 0 | 105 | 0 | 145 | 0 | 35 | 155 | 0 | 0 | 0 | 433 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 25.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 22 | 354 | 0 | 0 | 28 | 0 | 64 | 226 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 300 | 0 | 330 | 51 | 0 | 190 | 0 | 0 | 108 | 100 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 310 | 0 | 207 | 20 | 30 | 0 | 0 | 16 | 0 | 84 | 30 | 0 | 15 | 0 | 0 | 65 | 19 | 35 | 0 | 0 | 12 | 5123 | 873 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 108 | 10 | 0 | 1399.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 513 | 941 | 0 | 6114.44 | 11237.44 | 98.84
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 29.8 | 0 | 105 | 0 | 60 | 0 | 35 | 151 | 0 | 0 | 0 | 492 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 25.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 24 | 354 | 0 | 0 | 33 | 0 | 17 | 226 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 260 | 0 | 260 | 51 | 0 | 185 | 0 | 0 | 106 | 17 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 305 | 0 | 207 | 20 | 30 | 0 | 0 | 23 | 0 | 84 | 30 | 0 | 15 | 0 | 0 | 69 | 19 | 35 | 0 | 0 | 0 | 4773.3 | 874 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1065 | 108 | 10 | 0 | 1426.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 450 | 1041 | 0 | 6148.37 | 10921.67 | 98.84
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 15.6 | 0 | 105 | 0 | 15 | 0 | 35 | 158 | 0 | 0 | 0 | 529 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 23.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 22 | 354 | 0 | 0 | 0 | 0 | 17 | 227 | 0 | 0 | 0 | 591 | 0 | 0 | 0 | 260 | 0 | 260 | 51 | 0 | 198 | 0 | 0 | 109 | 17 | 0 | 20 | 0 | 106 | 0 | 0 | 0 | 320 | 0 | 207 | 20 | 30 | 0 | 0 | 23 | 0 | 84 | 30 | 0 | 15 | 0 | 0 | 69 | 19 | 35 | 0 | 0 | 0 | 4763.1 | 873 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 15 | 10 | 0 | 1329.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 58 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 453 | 1075 | 0 | 5943.86 | 10706.96
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 16.5 | 0 | 105 | 0 | 15 | 0 | 35 | 156 | 0 | 0 | 0 | 514 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 22 | 354 | 0 | 0 | 0 | 0 | 17 | 226 | 0 | 0 | 0 | 581 | 0 | 0 | 0 | 260 | 0 | 260 | 51 | 0 | 192 | 0 | 0 | 109 | 17 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 207 | 20 | 30 | 0 | 0 | 23 | 0 | 84 | 30 | 0 | 15 | 0 | 0 | 69 | 19 | 35 | 0 | 0 | 0 | 4706.5 | 874 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 0 | 10 | 0 | 1325.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 58 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 450 | 1070 | 0 | 5932.5 | 10639 | 98.84
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 16.4 | 0 | 98 | 0 | 15 | 0 | 17 | 156 | 0 | 0 | 0 | 445 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 33 | 354 | 0 | 0 | 0 | 0 | 17 | 226 | 0 | 0 | 0 | 582 | 0 | 0 | 0 | 260 | 0 | 260 | 51 | 0 | 190 | 0 | 0 | 108 | 17 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 207 | 20 | 30 | 0 | 0 | 21 | 0 | 85 | 30 | 0 | 15 | 0 | 0 | 59 | 19 | 35 | 0 | 0 | 0 | 4583.4 | 874 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 10 | 0 | 1334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 400 | 1070 | 0 | 5906 | 10489.4 | 98.83
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 17 | 108 | 0 | 0 | 0 | 395 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 187 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 207 | 20 | 30 | 0 | 0 | 21 | 0 | 85 | 30 | 0 | 15 | 0 | 0 | 59 | 19 | 35 | 0 | 0 | 0 | 4256 | 874 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146 | 0 | 10 | 0 | 1207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 400 | 1068 | 0 | 5799 | 10055 | 98.83
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 230 | 0 | 230 | 51 | 0 | 192 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 305 | 0 | 208 | 20 | 30 | 0 | 0 | 21 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 59 | 19 | 36 | 0 | 0 | 0 | 4094 | 873 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 10 | 0 | 1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 300 | 1068 | 0 | 5494 | 9588 | 98.83
Total KWH | 0 | 80640 | 0 | 0 | 0 | 0 | 0 | 0 | 8456400 | 0 | 0 | 219240 | 0 | 629280 | 0 | 785345 | 0 | 582034 | 1260000 | 0 | 0 | 0 | 9630311 | 0 | 51075 | 7311912 | 0 | 0 | 183957 | 0 | 411000 | 525600 | 0 | 0 | 0 | 0 | 0 | 0 | 86800 | 0 | 0 | 0 | 0 | 215040 | 19559 | 964000 | 0 | 461280 | 8312727.27 | 0 | 0 | 241440 | 0 | 430727 | 5546996 | 0 | 0 | 0 | 12703635 | 117720 | 347927 | 0 | 6070700 | 0 | 6348000 | 1176040 | 0 | 4932000 | 0 | 0 | 2433232 | 465120 | 0 | 372920 | 0 | 2247360 | 0 | 445573 | 0 | 7504000 | 0 | 5029000 | 224000 | 718440 | 0 | 65060 | 428856 | 0 | 1872000 | 692448 | 0 | 354000 | 0 | 0 | 1012800 | 312000 | 1032960 | 12400 | 267410 | 32400 | 103623364.27 | 19142545 | 5177664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459360 | 22669090 | 854400 | 240000 | 0 | 24762545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310352 | 560580 | 0 | 0 | 333008 | 0 | 0 | 4460755 | 0 | 0 | 0 | 9623200 | 0 | 29400 | 0 | 1364945 | 164400 | 182170 | 111849 | 0 | 0 | 0 | 27606.36 | 953280 | 2994 | 0 | 0 | 1657000 | 5436070 | 0 | 7827481 | 15512727.27 | 0 | 121863421.63 | 225486785.9

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10129.82 | MW | 12:00 Hr. | Energy Generated |  |  | 225.4868 |  | MKWHr.
| Day Peak Demand |  |  | 10129.82 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11237.44 | MW | 18:00 Hr. | Energy Demand |  |  | 225.4868 |  | MKWHr.
| Evening Peak Demand |  |  | 11237.44 | MW | 18:00 Hr. | Maximum Temperature |  |  | 28.8 |  | °C
| Minimum Generation of the Day |  |  | 7628.22 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 698.68 |  | MMCFD
| Maximum Generation of the Day |  |  | 11237.44 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.5646 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.3352 | 0 | 3.6076 | 0 | 0 | 0.18396 | 0 | 0 | 30.1268 | Gas | 98.1268 | Gas | 343075684.53
| Chattogram Zone |  |  | 6.0083 | 21.0164 | 0.88721 | 0 | 0.964 | 0.13728 | 0 | 0.0868 | 29.0999 | Coal | 68.3906 | Coal | 439679310.294
| Cumilla Zone |  |  | 21.3329 | 0 | 0.81305 | 0 | 0 | 0.44557 | 2.2474 | 0 | 24.8389 | HFO | 7.7957 | HFO | 131261313.65
| Mymensingh Zone |  |  | 1.033 | 0 | 1.3572 | 0 | 0 | 0.27981 | 0 | 0 | 2.67 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 16.8227 | 0 | 0 | 0 | 0 | 0.06506 | 0 | 0 | 16.8878 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 5.4177 | 22.6691 | 0.8544 | 0 | 0 | 0.45936 | 19.1425 | 0 | 48.5431 | Solar | 3.9704 | Solar | 62381123.2856
| Barishal Zone |  |  | 7.0931 | 23.3402 | 0 | 0 | 0 | 0.002994 | 0 | 0 | 30.4363 | Import | 46.1525 | Import | 276967815.8
| Rajshahi Zone |  |  | 14.084 | 0 | 0 | 0 | 0 | 1.2333 | 24.7625 | 0 | 40.0798 | Wind | 0.0868 | Wind | 1276828
| Rangpur Zone |  |  | 0 | 1.3649 | 0.27625 | 0 | 0 | 1.1631 | 0 | 0 | 2.8043
| Total |  |  | 98.1268 | 68.3906 | 7.7957 | 0 | 0.964 | 3.9704 | 46.1525 | 0.0868 | 225.4868
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 343075684.53 |  | Hydro | 96400
|  |  |  | Coal | 439679310.294 |  | Solar | 62381123.2856
|  |  |  | HFO | 131261313.65 |  | Import | 276967815.8
|  |  |  | HSD | 0 |  | Wind | 1276828
[5 empty] | Total: | 125,47,38,475 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.1425 | Peak Hr Flow | 873.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52112272.74 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.7625 | Peak Hr Flow | 1399.44 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2652 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2474 | Peak Hr Flow | 112.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2732 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.1525 | Peak Hr Flow | 2384.44 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4149
|  |  |  | Chattogram |  | 0 |  | 1224
|  |  |  | Cumilla |  | 0 |  | 913
|  |  |  | Mymensingh |  | 0 |  | 854
|  |  |  | Sylhet |  | 0 |  | 408
|  |  |  | Khulna |  | 0 |  | 1266
|  |  |  | Barishal |  | 0 |  | 307
|  |  |  | Rajshahi |  | 0 |  | 997
|  |  |  | Rangpur |  | 0 |  | 764
|  |  |  | Total |  | 0 |  | 10882
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:06 | Mirsorai 230/33kV S/S TR-1, 718T HT is restored.
| 08:09 | 16:38 | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Annual maintenance work
| 08:10 | 16:36 | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Annual maintenance work
| 08:10 | 09:09 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to S/D Taken by PBS for redhot
maintenance
| 08:10 | 16:32 | Hathazari-Kaptai 132kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Daed
Line chake
| 08:11 | 09:08 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to S/D Taken by PBS for redhot
maintenance
| 08:13 | 16:09 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to A/M
| 08:17 | 11:48 | Halishahar-Julda 132kV Ckt-1 Tripped from Halishahar 132/33kV end showing Distance relay
relays Due to General trip,zone-1,trip,B-phase,SOTF and from Juldah 132/33kV end showing
Siemens relays.
| 08:18 | 16:37 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) LT Scheduled S/D Due to Annual
Maintenance
| 08:18 | 16:36 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Scheduled S/D Due to Annual
Maintenance
| 08:22 | 09:37 | BIPTC S/S 10CF15 Tripped showing 87.1 Differential Relay relays Due to A Dead Bird was
stuck onto the filter
| 08:27 | 16:04 | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Annual
maintenance. and from Natore 132/33kV end Due to Annual maintenance work
| 08:27 | 16:28 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D Due to Annual Maintenance
| 08:27 | 16:27 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D Due to Annual Maintenance
| 08:28 | 14:57 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For ANNUAL maintenance
| 08:28 | 14:57 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For annual maintenance
| 08:30 | 19:48 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Annual
maintenance
| 08:34 | 16:45 | Rahanpur 132/33kV S/S TR-1 404T LT Scheduled S/D Due to Annual Maintenance
| 08:35 | 18:01 | Chowmuhani 132/33kV S/S TR1-415T LT Scheduled S/D Due to Yearly Schedule Maintenance
| 08:35 | 18:01 | Chowmuhani 132/33kV S/S TR1-415T HT Scheduled S/D Due to Yearly Schedule Maintenance
| 08:36 | 13:54 | Sirajganj 132/33kV S/S T3-(435) LT Scheduled S/D Due to annual maintenance
| 08:36 | 13:54 | Sirajganj 132/33kV S/S T3-(435) HT Scheduled S/D Due to annual maintenance
| 08:37 | 16:46 | Rahanpur 132/33kV S/S TR-1 404T HT Scheduled S/D Due to Annual maintenance
| 08:40 | 13:53 | Shahmirpur-Sikalbaha 132kV Ckt-2 Scheduled S/D from Shahmirpur 132/33kV end Due to Annual
Bay Maintenance at Shahmirpur End
| 08:42 | 16:17 | Bakulia-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance
| 08:43 | 15:44 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Dead line Check
| 08:46 |  | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end Due to Annual
maintenance
| 08:50 | 17:30 | Mirpur 132/33kV S/S Main Bus Scheduled S/D
| 08:57 | 14:15 | Narshingdi 132/33kV S/S 132 kV Main Bus-2 Scheduled S/D Due to Annual maintenance
| 09:03 | 17:35 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Maintenance work
| 09:04 | 17:30 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Maintenance work
| 09:05 |  | Fenchuganj- Fenchuganj-Khusiara 16 230kV Ckt-1 Scheduled S/D from Fenchuganj
230/132/33kV end.
| 09:05 | 16:12 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to AM
| 09:06 | 15:16 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance
|  | 09:07 | Mirsorai 230/33kV S/S TR-2, 728T LT is restored.
| 09:07 | 15:15 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance
|  | 09:07 | Mirsorai 230/33kV S/S TR-1, 718T LT is restored.
|  | 09:14 | Mirsorai 230/33kV S/S TR-2, 728T HT is restored.
| 09:17 | 09:37 | BIPTC S/S 10CF15 Scheduled S/D Due to Corrective Maintenance
| 09:20 | 15:20 | Mirsorai 230/33kV S/S TR-1, 718T HT Scheduled S/D Due to Annnual maintenance
| 09:30 |  | UttaraNew 132/33kV S/S GT-02 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 5.0MW load
interrup.
| 09:34 | 12:47 | Barapukuria 230/132/33kV S/S 132 KV Bus B Project Work S/D Due to Bus loop change of
Rangpur ckt_01
| 09:40 | 12:01 | Jashore 132/33kV S/S Cap. Bank-2 Scheduled S/D Due to Annual Maintenance
| 09:40 | 16:46 | Tongi 230/132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance
| 09:40 | 16:47 | Tongi 230/132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance Work
| 09:40 | 12:01 | Jashore 132/33kV S/S Cap. Bank-1 Scheduled S/D Due to Annual Maintenance
| 09:45 | 15:20 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D
| 09:49 | 15:08 | BIPTC S/S 10CF24 Scheduled S/D Due to Annual Maintenance
| 09:59 | 13:32 | Faridpur 132/33kV S/S Bus-B Scheduled S/D
| 09:59 | 13:32 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D
| 10:01 | 15:35 | Ghatail 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
| 10:03 | 15:33 | Ghatail 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
| 10:10 | 12:43 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Forced S/D Due to Safety and
clearance purpose
| 10:11 | 12:44 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Forced S/D Due to Safety and
clearance purpose
|  | 10:57 | Rajshahi-Rajshahi(New) 132kV Ckt-1 is restored.
| 11:02 | 20:26 | Rajendrapur 132/33kV S/S 132 kV BUS-1 Project Work S/D Due to Extention Bay Busber
Protection work.
| 12:00 |  | Day Peak Generation is 10127 MW.
|  | 13:43 | Maniknagar 132/33kV S/S Motijheel Ckt-2 is restored.
|  | 16:57 | Khulna (C) S/S Tr-2 415 T HT is restored.
|  | 16:58 | Khulna (C) S/S Tr-2 415 T LT is restored.
| 18:00 |  | Evening peak generation 11236 MW
| 19:52 |  | Kachua-Chowmuhoni 230 kV ckt-1 was switched ON for the first time
| 19:58 |  | Kachua-Chowmuhoni 230 kV ckt-3 was switched ON for the first time
|  | 20:22 | Bhulta 400/230kV S/S 400kV Bus-1 is restored.
| 21:12 |  | 250/350 MVA, 230/132 kV TR-2 transformer was charged from the high voltage side at
Chowmuhoni GIS grid substation for the first time
| 05:00 |  | Minimum Generation: 7467 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 8456400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7311912 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 31.5 | 219240 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 582034 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 51075 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25.5 | 411000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 525600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 785345 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 105 | 629280 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 80640 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 155 | 1260000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 183957 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 433 | 9630311 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1675 | 30126794
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117720 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 28 | 241440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5546996 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 64 | 430727 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 461280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19559 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 215040 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12703635 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 86800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 8312727.27 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1374 | 29099924.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4932000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 330 | 6348000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 300 | 6070700 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1176040 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 347927 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2433232 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 465120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 112 | 2247360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 372920 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 445573 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1231 | 24838872
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 35 | 1032960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 312000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 65 | 1012800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 267410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 32400 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 131 | 2669970
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 65060 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 20 | 224000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 718440 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 692448 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1872000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 354000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 428856 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7504000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5029000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 712 | 16887804
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 10 | 240000 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 873 | 19142545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 180 | 5177664 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 108 | 854400 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 459360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1112 | 22669090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2283 | 48543059
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 513 | 7827481 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 55 | 1657000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 941 | 15512727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5436070 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2994 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1729 | 30436272.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 310352 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 179 | 4460755 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 398 | 9623200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1399.44 | 24762545 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 333008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 560580 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1976.44 | 40079840
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1364945 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 111849 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27606.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 164400 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 182170 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 953280 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 126 | 2804250.36
Eastern Grid Total |  |  |  |  | 17395.105 | 5123 | 103623364.27
Western Grid Total |  |  |  |  | 10984.003 | 6114.44 | 121863421.63
National Grid Total |  |  |  |  | 28379.108 | 11237.44 | 225486785.9
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7547.67 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3334 | MW
i) Dhaka area |  |  | 4148.67 |  | MW | i) Khulna area |  |  |  | 1266 | MW
ii) Chattogram area |  |  | 1224 |  | MW | ii) Barishal area |  |  |  | 307 | MW
iii) Cumilla area |  |  | 913 |  | MW | iii) Rajshahi area |  |  |  | 997 | MW
iv) Mymensingh area |  |  | 854 |  | MW | iv) Rangpur area |  |  |  | 764 | MW
v) Sylhet area |  |  | 408 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10881.67 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 54 | 13:00 | 133 | Niamatpur | 48 | 08:00
2 | AKSML | 108 | 02:00 | 68 | Ishurdi | 51 | 18:00 | 134 | Noapara | 39 | 13:00
3 | Aftabnagar | 28 | 13:00 | 69 | Jaldhaka | 50 | 18:00 | 135 | PHP | 9 | 17:00
4 | Agargaon | 90 | 13:00 | 70 | Jamalpur | 89 | 18:00 | 136 | Pabna | 75 | 18:00
5 | Agrabad | 46 | 18:00 | 71 | Jashore | 105 | 13:00 | 137 | Palashbari | 84 | 18:00
6 | Amnura | 26 | 08:00 | 72 | Jhenaidah | 97 | 18:00 | 138 | Panchagarh | 47 | 18:00
7 | Ashuganj | 58 | 13:00 | 73 | Joydebpur | 101 | 12:00 | 139 | Patiya | 6 | 18:00
8 | BSRM | 196 | 16:00 | 74 | Joypurhat | 40 | 18:00 | 140 | Patuakhali | 47.5 | 21:00
9 | Bagerhat | 64 | 18:00 | 75 | Juldah | 13 | 16:00 | 141 | Payra | 24 | 18:00
10 | Bajitpur | 57 | 18:00 | 76 | KSRM | 26 | 16:00 | 142 | Postogola | 42 | 13:00
11 | Bakulia | 66 | 18:00 | 77 | Kabirpur | 188 | 16:00 | 143 | Purbachal | 27 | 13:00
12 | Banani | 48.8 | 13:00 | 78 | Kachua | 54 | 18:00 | 144 | Purbasadipur | 105 | 09:00
13 | Bangabhaban | 15 | 13:00 | 79 | Kallyanpur | 78 | 18:00 | 145 | Rahanpur | 22 | 11:00
14 | Barapukuria | 50 | 18:00 | 80 | Kalurghat | 34 | 12:00 | 146 | Rahim | 41 | 13:00
15 | Barguna | 10 | 18:00 | 81 | Kamrangirchar | 65 | 13:00 | 147 | Rajbari | 57 | 18:00
16 | Barishal | 91 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 99 | 18:00
17 | Barishal-230 | 64 | 18:00 | 83 | Kasba | 22 | 20:00 | 149 | Rajshahi | 77 | 13:00
18 | Baroaulia | 55 | 13:00 | 84 | Kazla | 88 | 13:00 | 150 | Rajshahi-230 | 56 | 13:00
19 | Baroirhat | 55 | 18:00 | 85 | Keranigonj | 53 | 13:00 | 151 | Ramganj | 66 | 18:00
20 | Bashundhara | 148 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 29 | 18:00
21 | BashundharaCement | 7 | 01:00 | 87 | Khulna | 62 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 177 | 18:00 | 154 | Rangpur | 98 | 18:00
23 | Benapole | 38 | 08:00 | 89 | Kishoreganj | 83 | 18:30 | 155 | Ruppur | 2.8 | 09:00
24 | Bhaluka | 124 | 18:00 | 90 | Kodda | 254 | 17:00 | 156 | SSM | 3 | 01:00
25 | Bhandaria | 38 | 19:30 | 91 | Kulaura | 28 | 18:00 | 157 | Saidpur | 92 | 18:00
26 | Bhangura | 22 | 08:00 | 92 | Kurigram | 48 | 08:00 | 158 | Satkhira | 88 | 18:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | Kushtia | 114 | 18:00 | 159 | Satmasjid | 82 | 13:00
28 | Bhulta | 178 | 11:00 | 94 | Laksam | 29 | 20:00 | 160 | Savar | 144 | 16:00
29 | Bog-Sherpur | 54 | 18:00 | 95 | Lakshmipur | 24 | 20:00 | 161 | SevenRings | 2.94 | 23:00
30 | Bogura | 114 | 18:30 | 96 | Lalbag | 54 | 20:00 | 162 | ShahCement | 30 | 04:00
31 | Borhanuddin | 62 | 22:00 | 97 | Lalmonirhat | 41 | 18:30 | 163 | Shahjadpur | 58 | 18:00
32 | Brahmanbaria | 80 | 13:00 | 98 | MI_Cement | 11.7 | 01:00 | 164 | Shahjibazar | 83 | 18:30
33 | Cantonment | 78 | 13:00 | 99 | Madanganj | 27 | 18:00 | 165 | Shahmirpur | 47 | 17:00
34 | Chandina | 8 | 12:00 | 100 | Madaripur | 68 | 19:00 | 166 | Shariatpur | 54 | 21:00
35 | Chandpur | 50 | 19:30 | 101 | Madartek | 57 | 13:00 | 167 | Sherpur | 108 | 18:30
36 | Chandraghona | 26 | 18:30 | 102 | Madunaghat | 41 | 18:00 | 168 | Shikalbaha | 22 | 13:00
37 | Chapai | 48 | 11:00 | 103 | Magura | 47 | 18:00 | 169 | Shitalakhya | 64.6 | 12:00
38 | Charsaidpur | 44 | 08:00 | 104 | Mahasthangarh | 52 | 18:00 | 170 | Sholosohor | 36 | 12:00
39 | Chauddagram | 50 | 13:00 | 105 | Maijdee | 28 | 18:00 | 171 | Shyampur | 122 | 02:00
40 | Chhatak | 27 | 18:00 | 106 | Manikganj | 93 | 18:00 | 172 | Siddhirganj | 96 | 13:00
41 | Chowmuhani | 100 | 13:00 | 107 | Maniknagar | 52 | 13:00 | 173 | Sirajganj | 84 | 19:00
42 | Chuadanga | 71 | 13:00 | 108 | Matarbari | 35 | 18:00 | 174 | Sonargaon | 140 | 09:00
43 | Coxsbazar | 107 | 18:00 | 109 | Matuail | 56 | 10:00 | 175 | Sreemongol | 57 | 18:30
44 | Cumilla(N) | 102 | 18:00 | 110 | Metrorail_Motijheel | 15 | 20:00 | 176 | Sreepur | 82 | 19:30
45 | Cumilla(S) | 112 | 12:00 | 111 | Metrorail_Uttara | 8 | 10:00 | 177 | Srinagar | 31.4 | 19:30
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 76 | 11:00 | 178 | Sunamganj | 40 | 18:00
47 | Daudkandi | 94 | 12:00 | 113 | Mirpur | 121 | 13:00 | 179 | Sylhet | 39 | 18:00
48 | DhakaUniversity | 62 | 13:00 | 114 | Mirsorai | 33 | 15:00 | 180 | Sylhet-132 | 75 | 13:00
49 | Dhamrai | 100 | 17:00 | 115 | Mirzapur | 39 | 18:00 | 181 | TK | 15 | 18:00
50 | Dhanmondi | 83 | 13:00 | 116 | Mithapukur | 54 | 18:00 | 182 | Tangail | 120 | 19:00
51 | Dohazari | 74 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 23 | 08:00
52 | Faridpur | 111 | 18:00 | 118 | Mogbazar | 65.4 | 14:00 | 184 | Tasnim | 16 | 00:00
53 | Fatullah | 93 | 17:00 | 119 | Mongla | 39 | 09:00 | 185 | Thakurgaon | 81 | 18:00
54 | Fenchuganj | 28 | 17:00 | 120 | Motijheel | 28 | 13:00 | 186 | Tongi | 101 | 13:00
55 | Feni | 67 | 13:00 | 121 | Muktagacha | 27 | 18:30 | 187 | Ullahpara | 25 | 18:00
56 | GPH | 98 | 03:00 | 122 | Munshiganj | 73 | 13:00 | 188 | Ullon | 57 | 14:00
57 | Ghatail | 58 | 08:00 | 123 | Muradnagar | 24 | 18:30 | 189 | Uttara | 60 | 14:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 132 | 18:00 | 190 | UttaraNew | 14 | 14:00
59 | Ghorashal-230 | 78 | 18:30 | 125 | Naogaon | 91 | 18:30 | 191 | Zigatola | 54 | 12:00
60 | Goalpara | 30 | 12:00 | 126 | Narail | 41 | 18:00
61 | Gollamari | 66 | 18:30 | 127 | Narinda | 58 | 13:00
62 | Gopalganj | 77 | 18:00 | 128 | Narshingdi | 134 | 19:30
63 | Gulshan | 78 | 13:00 | 129 | Natore | 97 | 18:00
64 | Halishahar | 51.5 | 14:00 | 130 | Nawabganj | 28.6 | 21:00
65 | HaripurSBU | 85 | 01:00 | 131 | Netrakona | 110 | 18:00
66 | Hasnabad | 76 | 18:00 | 132 | New | 72.6 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9264.42 | 0 |  | 9264.42
1:00 | 8687.15 | 0 |  | 8687.15
2:00 | 8292.96 | 0 |  | 8292.96
3:00 | 7994.08 | 0 |  | 7994.08
4:00 | 7628.22 | 0 |  | 7628.22
5:00 | 7670.42 | 0 |  | 7670.42
6:00 | 7936.49 | 0 |  | 7936.49
7:00 | 8564.44 | 0 |  | 8564.44
8:00 | 9457.96 | 0 |  | 9457.96
9:00 | 9716.34 | 0 |  | 9716.34
10:00 | 9515.78 | 0 |  | 9515.78
11:00 | 9640.64 | 0 |  | 9640.64
12:00 | 10129.82 | 0 |  | 10129.82
13:00 | 10615.33 | 0 |  | 10615.33
14:00 | 10230.87 | 0 |  | 10230.87
15:00 | 9619.37 | 0 |  | 9619.37
16:00 | 9535.29 | 0 |  | 9535.29
17:00 | 9777.55 | 0 |  | 9777.55
18:00 | 11237.44 | 0 |  | 11237.44
19:00 | 10921.67 | 0 |  | 10921.67
19:30 | 10706.96 | 0 |  | 10706.96
20:00 | 10639 | 0 |  | 10639
21:00 | 10489.4 | 0 |  | 10489.4
22:00 | 10055 | 0 |  | 10055
23:00 | 9588 | 0 |  | 9588
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 3984 | 5280.42 | 9264.42 | DAILY GENERATION CURVE
00:30 | 3963.5 | 5012.285 | 8975.785
01:00 | 3943 | 4744.15 | 8687.15 | 15-12-2025
01:30 | 3913.5 | 4576.555 | 8490.055
02:00 | 3884 | 4408.96 | 8292.96
02:30 | 3817.25 | 4326.27 | 8143.52
03:00 | 3750.5 | 4243.58 | 7994.08
03:30 | 3630.5 | 4180.65 | 7811.15
04:00 | 3510.5 | 4117.72 | 7628.22
04:30 | 3485 | 4164.32 | 7649.32
05:00 | 3459.5 | 4210.92 | 7670.42
05:30 | 3547 | 4256.455 | 7803.455
06:00 | 3634.5 | 4301.99 | 7936.49
06:30 | 3773.195 | 4477.27 | 8250.465
07:00 | 3911.89 | 4652.55 | 8564.44
07:30 | 4105.43 | 4905.77 | 9011.2
08:00 | 4298.97 | 5158.99 | 9457.96
08:30 | 4267.04 | 5320.11 | 9587.15
09:00 | 4235.11 | 5481.23 | 9716.34
09:30 | 4180.645 | 5435.415 | 9616.06
10:00 | 4126.18 | 5389.6 | 9515.78
10:30 | 4124.225 | 5453.985 | 9578.21
11:00 | 4122.27 | 5518.37 | 9640.64
11:30 | 4304.18 | 5581.05 | 9885.23
12:00 | 4486.09 | 5643.73 | 10129.82
12:30 | 4645.49 | 5727.085 | 10372.575
13:00 | 4804.89 | 5810.44 | 10615.33
13:30 | 4772.685 | 5650.415 | 10423.1
14:00 | 4740.48 | 5490.39 | 10230.87
14:30 | 4549.53 | 5375.59 | 9925.12
15:00 | 4358.58 | 5260.79 | 9619.37
15:30 | 4364.93 | 5212.4 | 9577.33
16:00 | 4371.28 | 5164.01 | 9535.29
16:30 | 4515.58 | 5140.84 | 9656.42
17:00 | 4659.88 | 5117.67 | 9777.55
17:30 | 4891.44 | 5616.055 | 10507.495
18:00 | 5123 | 6114.44 | 11237.44
18:30 | 4948.15 | 6131.405 | 11079.555
19:00 | 4773.3 | 6148.37 | 10921.67
19:30 | 4763.1 | 5943.86 | 10706.96
20:00 | 4706.5 | 5932.5 | 10639
20:30 | 4644.95 | 5919.25 | 10564.2 |  | Executive Engineer
21:00 | 4583.4 | 5906 | 10489.4 |  | Network Operation Division
21:30 | 4419.7 | 5852.5 | 10272.2
22:00 | 4256 | 5799 | 10055
22:30 | 4175 | 5646.5 | 9821.5
23:00 | 4094 | 5494 | 9588

## En-Curve
QF-LDC-12
Date | 15-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2959 | 1146 | 780 | 0 | 90 | 1119.42 | 40 | 3110 | 0 | 0 | 16 | 0 | 0 | 4 | 0 | DAILY ENERGY CURVE
00:30 | 2931.5 | 1148 | 772.5 | 0 | 87 | 989.785 | 40 | 2989 | 0 | 0 | 16 | 0 | 0 | 2 | 0 | 15-12-2025
01:00 | 2904 | 1150 | 765 | 0 | 84 | 860.15 | 40 | 2868 | 0 | 0 | 16 | 0 | 0 | 0 | 0
01:30 | 2911 | 1160 | 725 | 0 | 84 | 844.555 | 40 | 2711.5 | 0 | 0 | 12 | 0 | 0 | 2 | 0 | Energy Generated | 225.4868 |  | MKWHr
02:00 | 2918 | 1170 | 685 | 0 | 84 | 828.96 | 40 | 2555 | 0 | 0 | 8 | 0 | 0 | 4 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2887.5 | 1161.25 | 685 | 0 | 80 | 829.77 | 40 | 2449.5 | 0 | 0 | 4 | 0 | 0 | 6.5 | 0 | Total Energy Requirement | 225.4868 |  | MKWHr
03:00 | 2857 | 1152.5 | 685 | 0 | 76 | 830.58 | 40 | 2344 | 0 | 0 | 0 | 0 | 0 | 9 | 0
03:30 | 2832.5 | 1093 | 638 | 0 | 77 | 836.15 | 40 | 2282 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0
04:00 | 2808 | 1033.5 | 591 | 0 | 78 | 841.72 | 40 | 2220 | 0 | 0 | 0 | 0 | 0 | 16 | 0
04:30 | 2840 | 1028.5 | 590.5 | 0 | 78 | 848.82 | 40 | 2207.5 | 0 | 0 | 0 | 0 | 0 | 16 | 0
05:00 | 2872 | 1023.5 | 590 | 0 | 78 | 855.92 | 40 | 2195 | 0 | 0 | 0 | 0 | 0 | 16 | 0
05:30 | 2918 | 1038.5 | 613.5 | 0 | 78 | 843.955 | 40 | 2259 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0
06:00 | 2964 | 1053.5 | 637 | 0 | 78 | 831.99 | 40 | 2323 | 0 | 0 | 0 | 0 | 0 | 9 | 0
06:30 | 2981 | 1091 | 661 | 0 | 77 | 924.175 | 40 | 2440.5 | 12.79 | 0 | 16.5 | 0 | 0 | 6.5 | 0
07:00 | 2998 | 1128.5 | 685 | 0 | 76 | 1016.36 | 40 | 2558 | 25.58 | 0 | 33 | 0 | 0 | 4 | 0
07:30 | 3046 | 1137.25 | 732 | 0 | 80 | 1020.27 | 40 | 2792 | 106.68 | 0 | 55 | 0 | 0 | 2 | 0
08:00 | 3094 | 1146 | 779 | 0 | 84 | 1024.18 | 40 | 3026 | 187.78 | 0 | 77 | 0 | 0 | 0 | 0
08:30 | 2974.5 | 1125.5 | 826 | 0 | 84 | 1022.59 | 40 | 3125.5 | 285.56 | 0 | 103 | 0 | 0 | 0.5 | 0
09:00 | 2855 | 1105 | 873 | 0 | 84 | 1021 | 40 | 3225 | 383.34 | 0 | 129 | 0 | 0 | 1 | 0
09:30 | 2792 | 1067.5 | 873 | 0 | 90 | 979 | 40 | 3181 | 462.56 | 0 | 130.5 | 0 | 0 | 0.5 | 0
10:00 | 2729 | 1030 | 873 | 0 | 96 | 937 | 40 | 3137 | 541.78 | 0 | 132 | 0 | 0 | 0 | 0
10:30 | 2749.5 | 1010 | 873.5 | 0 | 102 | 933.5 | 40 | 3139 | 579.21 | 0 | 151.5 | 0 | 0 | 0 | 0
11:00 | 2770 | 990 | 874 | 0 | 108 | 930 | 40 | 3141 | 616.64 | 0 | 171 | 0 | 0 | 0 | 0
11:30 | 2817 | 1061 | 874 | 0 | 109 | 931 | 40 | 3164.5 | 622.23 | 0 | 266.5 | 0 | 0 | 0 | 0
12:00 | 2864 | 1132 | 874 | 0 | 110 | 932 | 40 | 3188 | 627.82 | 0 | 362 | 0 | 0 | 0 | 0
12:30 | 2865 | 1150.5 | 874 | 0 | 109 | 982.5 | 40 | 3231 | 585.075 | 0 | 535.5 | 0 | 0 | 0 | 0
13:00 | 2866 | 1169 | 874 | 0 | 108 | 1033 | 40 | 3274 | 542.33 | 0 | 709 | 0 | 0 | 0 | 0
13:30 | 2813 | 1124 | 873.5 | 0 | 108 | 1001.5 | 40 | 3218 | 520.4 | 0 | 722.7 | 0 | 0 | 2 | 0
14:00 | 2760 | 1079 | 873 | 0 | 108 | 970 | 40 | 3162 | 498.47 | 0 | 736.4 | 0 | 0 | 4 | 0
14:30 | 2741.5 | 1089.5 | 873.5 | 0 | 110 | 989.385 | 40 | 3069.5 | 422.035 | 0 | 584.7 | 0 | 0 | 5 | 0
15:00 | 2723 | 1100 | 874 | 0 | 112 | 1008.77 | 40 | 2977 | 345.6 | 0 | 433 | 0 | 0 | 6 | 0
15:30 | 2781 | 1116 | 873.5 | 0 | 108 | 1016.245 | 40 | 2963 | 242.585 | 0 | 429.5 | 0 | 0 | 7.5 | 0
16:00 | 2839 | 1132 | 873 | 0 | 104 | 1023.72 | 40 | 2949 | 139.57 | 0 | 426 | 0 | 0 | 9 | 0
16:30 | 2766.5 | 1111.75 | 873 | 0 | 105 | 1020.425 | 40 | 3000.5 | 74.745 | 17 | 640.5 | 0 | 0 | 7 | 0
17:00 | 2694 | 1091.5 | 873 | 0 | 106 | 1017.13 | 40 | 3052 | 9.92 | 34 | 855 | 0 | 0 | 5 | 0
17:30 | 2840 | 1147 | 873 | 0 | 109 | 1208.285 | 40 | 3320.5 | 4.96 | 34 | 926.75 | 0 | 0 | 4 | 0
18:00 | 2986 | 1202.5 | 873 | 0 | 112 | 1399.44 | 40 | 3589 | 0 | 34 | 998.5 | 0 | 0 | 3 | 0
18:30 | 2923 | 1234 | 873.5 | 0 | 106 | 1412.905 | 40 | 3584 | 0 | 17 | 886.65 | 0 | 0 | 2.5 | 0
19:00 | 2860 | 1265.5 | 874 | 0 | 100 | 1426.37 | 40 | 3579 | 0 | 0 | 774.8 | 0 | 0 | 2 | 0
19:30 | 2931 | 1314.5 | 873 | 0 | 106 | 1329.86 | 40 | 3566 | 0 | 0 | 542.6 | 0 | 0 | 4 | 0
20:00 | 2906 | 1291 | 874 | 0 | 104 | 1325.5 | 40 | 3571 | 0 | 0 | 526.5 | 0 | 0 | 1 | 0
20:30 | 2900.5 | 1259 | 874 | 0 | 104 | 1329.75 | 40 | 3573.5 | 0 | 0 | 482.95 | 0 | 0 | 0.5 | 0
21:00 | 2895 | 1227 | 874 | 0 | 104 | 1334 | 40 | 3576 | 0 | 0 | 439.4 | 0 | 0 | 0 | 0
21:30 | 2851.5 | 1198 | 874 | 0 | 98 | 1270.5 | 40 | 3591 | 0 | 0 | 349.2 | 0 | 0 | 0 | 0
22:00 | 2808 | 1169 | 874 | 0 | 92 | 1207 | 40 | 3606 | 0 | 0 | 259 | 0 | 0 | 0 | 0
22:30 | 2813 | 1169.5 | 873.5 | 0 | 93 | 1107.5 | 40 | 3548 | 0 | 0 | 177 | 0 | 0 | 0 | 0
23:00 | 2818 | 1170 | 873 | 0 | 94 | 1008 | 40 | 3490 | 0 | 0 | 95 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 408 | 03:00 | 385 | 12:00 | Meghnaghat | 409 | 03:00 | 386 | 12:00
Ashuganj | 412 | 3:00 | 390 | 12:00 | Payra | 418 | 05:00 | 410 | 12:00
Bhulta | 408 | 03:00 | 384 | 12:00 | Rahanpur | 419 | 05:00 | 402 | 18:00
Bibiana | 404 | 02:00 | 393 | 12:00 | Rampal | 410 | 03:00 | 397 | 11:00
BIPTC | 407 | 03:00 | 390 | 18:00
Bogura | 413 | 05:00 | 391 | 18:00
Gopalganj | 412 | 03:00 | 395 | 12:00
Kaliakoir | 403 | 03:00 | 377 | 11:00
Korerhat | 411 | 03:00 | 395 | 11:00
Madunaghat | 405 | 03:00 | 395 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 03:00 | 223 | 12:00 | Kachua | 239 | 02:00 | 231 | 10:00
AKSML | 235 | 03:00 | 227 | 11:00 | Kaliakoir | 238 | 03:00 | 220 | 11:00
Aminbazar | 238 | 02:00 | 224 | 11:00 | Keranigonj | 238 | 03:00 | 222 | 12:00
Ashuganj | 240 | 03:00 | 230 | 12:00 | Khulna(S) | 237 | 03:00 | 230 | 10:00
Ashuganj-400 | 240 | 03:00 | 230 | 12:00 | Korerhat | 238 | 06:00 | 228 | 11:00
Baghabari | 239 | 04:00 | 229 | 18:00 | Madunaghat | 234 | 03:00 | 227 | 11:00
Barapukuria | 231 | 03:00 | 218 | 18:00 | Madunaghat-400 | 235 | 04:00 | 228 | 11:00
Barapukuria-230 | 231 | 03:00 | 218 | 18:00 | Maniknagar | 238 | 03:00 | 222 | 11:00
Barishal | 244 | 03:00 | 236 | 12:00 | Meghnaghat | 243 | 05:00 | 230 | 12:00
Bheramara | 236 | 03:00 | 224 | 12:00 | Meghnaghat-400 | 240 | 05:00 | 225 | 12:00
Bhulta | 238 | 03:00 | 223 | 12:00 | Mirsorai | 237 | 02:00 | 227 | 13:00
Bibiana | 241 | 03:00 | 230 | 12:00 | Rajshahi | 237 | 03:00 | 224 | 18:00
BIPTC | 238 | 03:00 | 224 | 13:00 | Rampal | 236 | 04:00 | 228 | 11:00
Bogura | 242 | 04:00 | 229 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 241 | 03:00 | 228 | 18:30 | Rampura | 238 | 03:00 | 222 | 12:00
Borhanuddin | 245 | 02:00 | 241 | 10:00 | Shikalbaha | 233 | 02:00 | 226 | 11:00
BSRM | 237 | 03:00 | 228 | 12:00 | Shyampur | 239 | 05:00 | 223 | 12:00
Cumilla(N) | 236 | 05:00 | 226 | 12:00 | Siddhirganj | 237 | 03:00 | 225 | 10:00
Faridpur | 245 | 12:00 | 230 | 18:00 | Sirajgonj | 246 | 03:00 | 237 | 18:00
Fenchuganj | 240 | 06:00 | 232 | 12:00 | Sreepur | 237 | 03:00 | 228 | 12:00
Feni | 238 | 03:00 | 226 | 12:00 | Tongi | 234 | 04:00 | 218 | 11:00
Ghorashal | 242 | 04:00 | 230 | 13:00
Ghorashal-230 | 228 | 03:00 | 215 | 12:00
Gopalganj | 244 | 03:00 | 234 | 12:00
GPH | 237 | 03:00 | 228 | 11:00
Haripur | 239 | 04:00 | 224 | 12:00
Hasnabad | 237 | 01:00 | 222 | 11:00
Hathazari | 233 | 03:00 | 225 | 13:00
Ishurdi | 240 | 03:00 | 227 | 18:00
Jhenaidah | 237 | 03:00 | 224 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 124 | 12:00 | Lalbag | 136 | 03:00 | 125 | 12:00
Agargaon | 137 | 03:00 | 127 | 12:00 | Lalmonirhat | 131 | 03:00 | 122 | 08:00
Agrabad | 135 | 01:00 | 131 | 10:00 | Madanganj | 138 | 04:00 | 134 | 10:00
AKS | 135 | 01:00 | 130 | 07:00 | Madaripur | 140 | 04:00 | 135 | 12:00
Aminbazar | 137 | 02:00 | 129 | 11:00 | Madartek | 134 | 05:00 | 124 | 11:00
Amnura | 139 | 03:00 | 130 | 13:00 | Madunaghat | 136 | 03:00 | 133 | 10:00
Ashuganj | 143 | 07:00 | 139 | 12:00 | Magura | 137 | 04:00 | 126 | 13:00
Bagerhat | 138 | 04:00 | 123 | 19:30 | Mahasthangarh | 136 | 03:00 | 128 | 08:00
Bajitpur | 138 | 06:00 | 131 | 12:00 | Maijdee | 135 | 03:00 | 128 | 11:00
Bakulia | 136 | 03:00 | 132 | 10:00 | Manikganj | 132 | 02:00 | 120 | 11:00
Banani | 134 | 03:00 | 123 | 11:00 | Maniknagar | 138 | 04:00 | 127 | 12:00
Bangabhaban | 139 | 04:00 | 127 | 11:00 | Matarbari | 128 | 05:00 | 122 | 12:00
Barapukuria | 136 | 01:00 | 126 | 13:00 | Matuail | 140 | 04:00 | 132 | 11:00
Barguna | 136 | 00:00 | 134 | 02:00 | Metrorail_Motijheel | 138 | 04:00 | 127 | 12:00
Barishal | 141 | 05:00 | 135 | 12:00 | Metrorail_Uttara | 137 | 02:00 | 127 | 11:00
Barishal-230 | 141 | 02:00 | 135 | 12:00 | Millgate | 135 | 03:00 | 121 | 11:00
Baroaulia | 137 | 04:00 | 131 | 11:00 | Mirpur | 136 | 05:00 | 128 | 11:00
Baroirhat | 135 | 05:00 | 130 | 11:00 | Mirzapur | 137 | 05:00 | 128 | 12:00
Bashundhara | 134 | 02:00 | 124 | 12:00 | Mithapukur | 134 | 03:00 | 125 | 08:00
BashundharaCement | 138 | 04:00 | 134 | 14:00 | MI_Cement | 138.1 | 04:00 | 126 | 12:00
Beanibazar | 139 | 05:00 | 133 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 134 | 02:00 | 119 | 13:00 | Mogbazar | 138 | 01:00 | 125 | 12:00
Bhaluka | 138 | 06:00 | 130 | 18:00 | Mongla | 134 | 05:00 | 125 | 19:30
Bhandaria | 135 | 20:00 | 126 | 16:00 | Motijheel | 139 | 04:00 | 127 | 11:00
Bhangura | 141 | 04:00 | 133 | 12:00 | Muktagacha | 131 | 02:00 | 127 | 18:00
Bheramara | 141 | 03:00 | 135 | 13:00 | Munshiganj | 138 | 02:00 | 130 | 11:00
Bheramara(GK) | 140 | 02:00 | 135 | 18:00 | Muradnagar | 139 | 03:00 | 130 | 12:00
Bhulta | 133 | 07:00 | 126 | 11:00 | Mymensingh | 134 | 04:00 | 125 | 18:00
Bog-Sherpur | 138 | 03:00 | 130 | 18:00 | Naogaon | 134 | 04:00 | 127 | 08:00
Bogura | 137 | 05:00 | 124 | 11:00 | Narail | 137 | 04:00 | 125 | 13:00
Bogura-230 | 138 | 03:00 | 130 | 18:00 | Narinda | 138 | 04:00 | 127 | 12:00
Brahmanbaria | 139 | 05:00 | 134 | 12:00 | Narshingdi | 137 | 07:00 | 127 | 12:00
Cantonment | 137 | 02:00 | 127 | 11:00 | Natore | 136 | 00:00 | 131 | 12:00
Chandina | 140 | 03:00 | 133 | 12:00 | Nawabganj | 136 | 04:00 | 125 | 12:00
Chandpur | 138 | 04:00 | 134 | 11:00 | Netrakona | 132 | 01:00 | 120 | 18:00
Chandraghona | 137 | 02:00 | 133 | 11:00 | New | 138 | 17:00 | 122 | 11:00
Chapai | 140 | 05:00 | 133 | 18:00 | Niamatpur | 139 | 03:00 | 132 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 140 | 05:00 | 132 | 11:00 | Noapara | 134 | 03:00 | 120 | 13:00
Chauddagram | 138 | 02:00 | 131 | 11:00 | Pabna | 140 | 02:00 | 133 | 12:00
Chhatak | 138 | 03:00 | 130 | 11:00 | Palashbari | 134 | 04:00 | 123 | 18:00
Chowmuhani | 133 | 01:00 | 128 | 11:00 | Panchagarh | 137 | 17:00 | 124 | 18:00
Chuadanga | 136 | 04:00 | 125 | 13:00 | Patiya | 137 | 03:00 | 131 | 12:00
Coxsbazar | 127 | 04:00 | 120 | 12:00 | Patuakhali | 135 | 15:00 | 132 | 19:00
Cumilla(N) | 138 | 01:00 | 133 | 16:00 | Payra | 137 | 02:00 | 134 | 12:00
Cumilla(S) | 138 | 06:00 | 125 | 12:00 | PHP | 136 | 04:00 | 129 | 12:00
Daganbhuiyan | 136 | 03:00 | 129 | 12:00 | Postogola | 138 | 01:00 | 128 | 11:00
Daudkandi | 137 | 03:00 | 129 | 12:00 | Purbachal | 135 | 03:00 | 124 | 12:00
DhakaUniversity | 134 | 02:00 | 124 | 12:00 | Purbasadipur | 132 | 04:00 | 123 | 18:00
Dhamrai | 138 | 03:00 | 129 | 11:00 | Rahanpur | 140 | 03:00 | 135 | 18:30
Dhanmondi | 141 | 03:00 | 132 | 12:00 | Rahanpur-400 | 141 | 03:00 | 135 | 18:00
Dohazari | 133 | 04:00 | 128 | 18:00 | Rahim | 140 | 04:00 | 132 | 12:00
Faridpur | 140 | 03:00 | 134 | 12:00 | Rajbari | 140 | 03:00 | 133 | 13:00
Fatullah | 138 | 02:00 | 126 | 12:00 | Rajendrapur | 140 | 05:00 | 131 | 18:00
Fenchuganj | 143 | 05:00 | 139 | 12:00 | Rajshahi | 138 | 02:00 | 130 | 13:00
Feni | 134 | 02:00 | 128 | 10:00 | Rajshahi-230 | 136 | 03:00 | 130 | 08:00
Feni-230 | 136 | 03:00 | 130 | 11:00 | Ramganj | 135 | 01:00 | 130 | 11:00
Ghatail | 131 | 05:00 | 125 | 16:00 | Rampur | 136 | 03:00 | 130 | 12:00
Ghorashal | 137 | 06:00 | 126 | 11:00 | Rampura | 135 | 04:00 | 124 | 12:00
Goalpara | 137 | 03:00 | 129 | 19:30 | Rangamati | 138 | 04:00 | 132 | 10:00
Gollamari | 137 | 01:00 | 129 | 19:30 | Rangpur | 134 | 04:00 | 125 | 11:00
Gopalganj | 139 | 03:00 | 132 | 19:30 | Ruppur | 140 | 03:00 | 134 | 18:00
Gopalganj-400 | 141 | 03:00 | 135 | 12:00 | Saidpur | 134 | 03:00 | 123 | 18:00
Gulshan | 134 | 03:00 | 124 | 12:00 | Satkhira | 136 | 04:00 | 125 | 19:30
Halishahar | 137 | 03:00 | 131 | 10:00 | Satmasjid | 137 | 05:00 | 127 | 12:00
Haripur | 140 | 02:00 | 132 | 12:00 | Savar | 136 | 18:30 | 128 | 11:00
HaripurSBU | 140 | 02:00 | 132 | 12:00 | SevenRings | 138 | 02:00 | 126 | 13:00
Hasnabad | 136 | 02:00 | 128 | 11:00 | ShahCement | 140 | 05:00 | 132 | 11:00
Hathazari | 137 | 03:00 | 133 | 11:00 | Shahjadpur | 140 | 00:00 | 136 | 10:00
Ishurdi | 142 | 03:00 | 135 | 18:00 | Shahjibazar | 141 | 01:00 | 134 | 19:00
Jaldhaka | 132 | 04:00 | 123 | 08:00 | Shahmirpur | 137 | 03:00 | 132 | 11:00
Jamalpur | 130 | 10:00 | 121 | 01:00 | Shariatpur | 141 | 03:00 | 135 | 11:00
Jashore | 133 | 03:00 | 120 | 13:00 | Sherpur | 127 | 10:00 | 119 | 00:00
Jhenaidah | 138 | 03:00 | 121 | 18:00 | Shikalbaha | 126 | 06:00 | 121 | 11:00
Jhenaidah-230 | 138 | 03:00 | 128 | 13:00 | Shikalbaha-230 | 137 | 02:00 | 134 | 04:00
Joydebpur | 136 | 03:00 | 124 | 13:00 | Shitalakhya | 138 | 04:00 | 126 | 12:00
Joypurhat | 134 | 02:00 | 126 | 07:00 | Sholosohor | 137 | 03:00 | 132 | 11:00
Juldah | 135 | 00:00 | 132 | 12:00 | Shyampur | 137 | 03:00 | 129 | 12:00
Kabirpur | 136 | 18:00 | 119 | 11:00 | Shyampur-230 | 138 | 03:00 | 129 | 12:00
Kachua | 140 | 02:00 | 135 | 10:00 | Siddhirganj | 139 | 01:00 | 132 | 11:00
Kaliakoir | 142 | 03:00 | 130 | 12:00 | Sirajganj | 138 | 04:00 | 130 | 18:00
Kallyanpur | 138 | 07:00 | 129 | 10:00 | Sonargaon | 138 | 05:00 | 132 | 10:00
Kalurghat | 138 | 03:00 | 132 | 12:00 | Sreemongol | 141 | 02:00 | 135 | 18:30
Kamrangirchar | 136 | 03:00 | 125 | 11:00 | Sreepur | 140 | 05:00 | 133 | 11:00
Kaptai | 136 | 03:00 | 130 | 12:00 | Srinagar | 136 | 03:00 | 126 | 12:00
Kasba | 138 | 02:00 | 130 | 11:00 | SSM | 140 | 04:00 | 135 | 12:00
Kazla | 138 | 04:00 | 127 | 12:00 | Sunamganj | 137 | 05:00 | 130 | 18:00
Keranigonj | 136 | 03:00 | 126 | 12:00 | Sylhet | 139 | 02:00 | 133 | 13:00
Khagrachori | 137 | 03:00 | 132 | 11:00 | Sylhet-132 | 140 | 03:00 | 134 | 12:00
Khulna | 136 | 04:00 | 127 | 20:00 | Tangail | 133 | 04:00 | 125 | 12:00
Khulna(S) | 138 | 02:00 | 129 | 19:30 | Taraganj | 132 | 05:00 | 121 | 08:00
Khulshi | 134 | 04:00 | 129 | 12:00 | Tasnim | 138 | 05:00 | 132 | 09:00
Kishoreganj | 136 | 05:00 | 128 | 18:00 | Thakurgaon | 137 | 17:00 | 123 | 08:00
Kodda | 136 | 03:00 | 125 | 11:00 | TK | 136 | 00:00 | 133 | 11:00
KSRM | 136 | 01:00 | 130 | 10:00 | Tongi | 135 | 04:00 | 125 | 11:00
Kulaura | 143 | 05:00 | 137 | 12:00 | Ullahpara | 139 | 02:00 | 132 | 12:00
Kurigram | 130 | 06:00 | 120 | 18:00 | Ullon | 134 | 03:00 | 124 | 13:00
Kushtia | 138 | 05:00 | 127 | 18:00 | Uttara | 135 | 03:00 | 121 | 11:00
Laksam | 140 | 03:00 | 135 | 10:00 | UttaraNew | 137 | 02:00 | 127 | 11:00
Lakshmipur | 135 | 03:00 | 128 | 11:00 | Zigatola | 137 | 04:00 | 126 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division