## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-12-2025 | during | 17-12-2025 | during | 17-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 377 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 334 | 328 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 10 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 8 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | ST Under maint.& gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 335 | 80 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1087 | 817 | 5779.35 | 5749.35 | 1992.49 | 1971.49
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 197 | 227 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 36 | 26 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.06 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 400 | 575 | 612 | 612 | 582 | 582 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 3 | 0 | 4 | 0 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 277 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 971.06 | 1225 | 2525 | 2526.72 | 2017.78 | 2019.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 208 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 200 | 200 | 200 | 200 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 290 | 300 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 240 | 270 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 18 | 28 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 106 | 108 | 163 | 163 | 112 | 112 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 86 | 108 | 160 | 160 | 112 | 112 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1007 | 1042 | 2637.21 | 2572.21 | 2324.51 | 2259.51
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-12-2025 | during | 17-12-2025 | during | 17-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 104 | 69 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 56 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.62 | 0 | 45.15 | 0 | 45.15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 164.62 | 144 | 361.25 | 314 | 313.75 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 83 | 83 | 83 | 83
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 95 | 95 | 95 | 95 | 95 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 315 | 341 | 341 | 0 | 0 | Under Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 207 | 207 | 205 | 205 | 205 | 205 | GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 710 | 812 | 839 | 839 | 498 | 498
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 712 | 759 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 221 | 250 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 76 | 0 | 76 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 795 | 973 | 0 | 0 | 1000 | 1000 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1807 | 1982 | 2354 | 2278 | 2433.1 | 2357.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 250 | 400 | 0 | 0 | 500 | 500 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 55 | 55 | 55 | 55 | 55 | 55 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 564 | 860 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 0 | 0 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | Standby
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1089.47 | 1535 | 1401.32 | 1401.32 | 1988.32 | 1988.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 28.93 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 174 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 382 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.16 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 827.09 | 1128 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.41 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1615.59 | 1684 | 2837.87 | 2672.87 | 2576.49 | 2411.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 57 | 58 | 58 | 58 | 58 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 146 | 0 | 139.17 | 0 | 139.17 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 233.5 | 57 | 480.37 | 306 | 460.37 | 286
System Total |  |  |  |  | 28823.2 | 28379.108 | 8685.24 | 9298 | 19215.37 | 18659.47 | 14604.81 | 14057.9
Forecast Scenario (17-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8900 |  | 0 |  | 8900
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 8000 |  | 0 |  | 8000
|  |  |  | 3:00 | 7800 |  | 0 |  | 7800
|  |  |  | 4:00 | 7500 |  | 0 |  | 7500
|  |  |  | 5:00 | 7400 |  | 0 |  | 7400
|  |  |  | 6:00 | 7800 |  | 0 |  | 7800
|  |  |  | 7:00 | 8300 |  | 0 |  | 8300
|  |  |  | 8:00 | 9300 |  | 0 |  | 9300
|  |  |  | 9:00 | 9710 |  | 0 |  | 9710
|  |  |  | 10:00 | 9510 |  | 0 |  | 9510
|  |  |  | 11:00 | 9640 |  | 0 |  | 9640
|  |  |  | 12:00 | 10130 |  | 0 |  | 10130
|  |  |  | 13:00 | 10610 |  | 0 |  | 10610
|  |  |  | 14:00 | 10230 |  | 0 |  | 10230
|  |  |  | 15:00 | 9610 |  | 0 |  | 9610
|  |  |  | 16:00 | 9530 |  | 0 |  | 9530
|  |  |  | 17:00 | 9770 |  | 0 |  | 9770
|  |  |  | 18:00 | 11230 |  | 0 |  | 11230
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 10920 |  | 0 |  | 10920
|  |  |  | 19:30 | 10700 |  | 0 |  | 10700
|  |  |  | 20:00 | 10630 |  | 0 |  | 10630
|  |  |  | 21:00 | 10480 |  | 0 |  | 10480
|  |  |  | 22:00 | 10050 |  | 0 |  | 10050
|  |  |  | 23:00 | 9580 |  | 0 |  | 9580
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 10130.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11230.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11230.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 225.13 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:15 hrs on 17-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-12-2025 | [28 empty] | Date: | 16-12-2025 | [28 empty] | Date: | 16-12-2025 | [28 empty] | Date: | 16-12-2025 | [28 empty] | Date: | 16-12-2025 | [17 empty] | Date: | 16-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 354 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 584 | 0 | 0 | 0 | 280 | 0 | 230 | 51 | 0 | 190 | 0 | 0 | 110 | 0 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 315 | 0 | 207 | 30 | 30 | 0 | 0 | 20 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 24 | 19 | 36 | 0 | 0 | 0 | 4103.5 | 779 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1034 | 0 | 10 | 0 | 975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 300 | 1025 | 0 | 5189 | 9292.5 | 98.83
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 354 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 506 | 0 | 0 | 0 | 280 | 0 | 230 | 51 | 0 | 200 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 207 | 30 | 30 | 0 | 0 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 8 | 8 | 36 | 0 | 0 | 0 | 3869.5 | 726 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 937 | 0 | 6 | 0 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 900 | 0 | 4751 | 8620.5 | 98.82
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 354 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 491 | 0 | 0 | 0 | 280 | 0 | 230 | 51 | 0 | 206 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 300 | 0 | 207 | 30 | 30 | 0 | 0 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 8 | 8 | 51 | 0 | 0 | 0 | 3854.5 | 600 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 879 | 0 | 6 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 800 | 0 | 4393 | 8247.5 | 98.82
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 354 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 280 | 0 | 230 | 51 | 0 | 189 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 305 | 0 | 207 | 30 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 0 | 0 | 0 | 0 | 0 | 8 | 51 | 0 | 0 | 0 | 3663.5 | 607 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 6 | 0 | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 670 | 0 | 4231 | 7894.5 | 98.82
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 354 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 280 | 0 | 230 | 5 | 0 | 201 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 300 | 0 | 207 | 30 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 8 | 51 | 0 | 0 | 0 | 3504.5 | 607 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 0 | 6 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 600 | 0 | 4109 | 7613.5 | 98.82
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 275 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 280 | 0 | 230 | 5 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 300 | 0 | 207 | 30 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 8 | 51 | 0 | 0 | 0 | 3389.5 | 615 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 6 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 600 | 0 | 4078 | 7467.5 | 98.81
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 275 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 428 | 0 | 0 | 0 | 240 | 0 | 230 | 5 | 0 | 197 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 290 | 0 | 207 | 30 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 8 | 51 | 0 | 0 | 0 | 3384.5 | 616 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 6 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 600 | 0 | 4161 | 7545.5 | 98.81
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 40 | 0 | 37 | 275 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 445 | 2 | 0 | 0 | 285 | 0 | 230 | 5 | 0 | 209 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 70 | 0 | 3 | 0 | 300 | 0 | 205 | 30 | 30 | 0 | 0 | 16 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 10 | 19 | 51 | 0 | 0.91 | 0 | 3488.57 | 615 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 772 | 0 | 6 | 0 | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 3 | 0 | 0 | 1.48 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0.16 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 4 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 590 | 0 | 4171.17 | 7659.74 | 98.81
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 40 | 0 | 34 | 275 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 425 | 8 | 0 | 0 | 350 | 0 | 230 | 20 | 0 | 195 | 0 | 0 | 110 | 0 | 0 | 18 | 0 | 76 | 0 | 19 | 0 | 300 | 0 | 205 | 30 | 30 | 0 | 3 | 16 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 24 | 19 | 88 | 1 | 9.79 | 0 | 3929.25 | 665 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 802 | 0 | 6 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8 | 23 | 0 | 0 | 11.85 | 0 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 1.42 | 0 | 58 | 0 | 7 | 0 | 0 | 0 | 0 | 1.3 | 34 | 0.06 | 0 | 0 | 55 | 220 | 0 | 250 | 600 | 0 | 4380.43 | 8309.68 | 98.81
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 40 | 0 | 5 | 275 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 420 | 13 | 0 | 0 | 290 | 0 | 230 | 51 | 0 | 181 | 0 | 0 | 110 | 0 | 0 | 16 | 0 | 78 | 0 | 36 | 0 | 300 | 0 | 205 | 30 | 30 | 0 | 6 | 17 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 8 | 8 | 110 | 1 | 24.86 | 0 | 3835.74 | 665 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 769 | 0 | 6 | 0 | 831.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.89 | 55 | 0 | 0 | 32.19 | 0 | 0 | 165 | 0 | 0 | 0 | 334 | 0 | 2.91 | 0 | 57 | 0 | 16 | 0 | 0 | 0 | 0 | 3.1 | 96 | 0.08 | 0 | 0 | 55 | 180 | 0 | 250 | 560 | 0 | 4340.84 | 8176.58 | 98.8
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 23 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58 | 40 | 0 | 5 | 277 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 350 | 17 | 0 | 0 | 220 | 0 | 220 | 5 | 0 | 198 | 0 | 0 | 110 | 0 | 0 | 16 | 0 | 80 | 0 | 50 | 0 | 300 | 0 | 205 | 30 | 30 | 0 | 8 | 17 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 8 | 0 | 107 | 2 | 32.92 | 0 | 3479.5 | 665 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.34 | 760 | 0 | 6 | 0 | 833.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.49 | 79 | 0 | 0 | 42.82 | 0 | 0 | 164 | 0 | 0 | 0 | 364 | 0 | 3.96 | 0 | 58 | 0 | 23 | 0 | 0 | 0 | 0 | 4.4 | 133 | 0.16 | 0 | 0 | 55 | 180 | 0 | 250 | 500 | 0 | 4423.96 | 7903.46 | 98.8
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 27 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.99 | 40 | 0 | 10 | 277 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 325 | 18 | 0 | 0 | 220 | 0 | 220 | 5 | 0 | 207 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 86 | 0 | 55 | 0 | 310 | 0 | 206 | 18 | 20 | 0 | 10 | 17 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 8 | 0 | 106 | 2 | 41.47 | 0 | 3439.46 | 665 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 780 | 0 | 12 | 0 | 837.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.84 | 89 | 0 | 0 | 50.92 | 0 | 0 | 175 | 0 | 0 | 0 | 387 | 0 | 4.47 | 0 | 53 | 0 | 28 | 0 | 0 | 0 | 0 | 5.2 | 146 | 0.4 | 0 | 0 | 55 | 180 | 0 | 250 | 516 | 0 | 4551.85 | 7991.31 | 98.8
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 334 | 0 | 0 | 29 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.06 | 40 | 0 | 36 | 277 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 400 | 18 | 0 | 0 | 240 | 0 | 290 | 18 | 0 | 200 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 86 | 0 | 56 | 0 | 310 | 0 | 207 | 30 | 30 | 0 | 4 | 17 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 8 | 8 | 104 | 2 | 42.62 | 0 | 3939.68 | 712 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 795 | 0 | 4 | 0 | 827.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.93 | 97 | 0 | 0 | 50.41 | 0 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 4.16 | 0 | 52 | 0 | 30 | 0 | 0 | 0 | 0 | 5.5 | 146 | 0.47 | 0 | 0 | 55 | 220 | 0 | 250 | 564 | 0 | 4745.56 | 8685.24 | 98.8
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 331 | 0 | 0 | 27 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 40 | 0 | 39 | 354 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 440 | 19 | 0 | 0 | 320 | 0 | 330 | 51 | 0 | 206 | 0 | 0 | 106 | 0 | 0 | 16 | 0 | 104 | 0 | 49 | 0 | 310 | 0 | 207 | 30 | 30 | 0 | 5 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 24 | 19 | 104 | 2 | 39.87 | 0 | 4353.59 | 712 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 831 | 0 | 4 | 0 | 882.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.66 | 88 | 0 | 0 | 29.77 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 2.91 | 0 | 56 | 0 | 27 | 0 | 0 | 0 | 0 | 5.1 | 141 | 0.45 | 0 | 0 | 55 | 220 | 0 | 350 | 650 | 0 | 4992.95 | 9346.54 | 98.79
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 300 | 0 | 0 | 22 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 40 | 0 | 39 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 460 | 15 | 0 | 0 | 260 | 14 | 240 | 51 | 0 | 194 | 0 | 0 | 104 | 0 | 0 | 16 | 0 | 106 | 0 | 27 | 0 | 305 | 0 | 208 | 30 | 30 | 0 | 8 | 17 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 16 | 19 | 105 | 2 | 31.78 | 0 | 4111.08 | 712 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.04 | 829 | 0 | 9 | 0 | 851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.94 | 77 | 0 | 0 | 30.97 | 0 | 0 | 181 | 0 | 0 | 0 | 349 | 0 | 3.22 | 0 | 55 | 0 | 22 | 0 | 0 | 0 | 0 | 4.4 | 138 | 0.37 | 0 | 0 | 55 | 220 | 0 | 250 | 750 | 0 | 4875.94 | 8987.02 | 98.79
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 15 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 40 | 0 | 39 | 354 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 385 | 11 | 0 | 0 | 240 | 13 | 240 | 5 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 90 | 0 | 25 | 0 | 305 | 0 | 208 | 30 | 30 | 0 | 4 | 17 | 0 | 11 | 30 | 0 | 0 | 0 | 0 | 16 | 19 | 105 | 1 | 19.54 | 0 | 3626.84 | 712 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.89 | 751 | 0 | 8 | 0 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.62 | 51 | 0 | 0 | 22.35 | 0 | 0 | 140 | 0 | 0 | 0 | 355 | 0 | 1.97 | 0 | 56 | 0 | 16 | 0 | 0 | 0 | 0 | 2.9 | 97 | 0.22 | 0 | 0 | 55 | 180 | 0 | 250 | 612 | 0 | 4465.95 | 8092.79 | 98.79
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 300 | 0 | 0 | 7 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.52 | 40 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 310 | 5 | 0 | 0 | 240 | 0 | 240 | 5 | 0 | 205 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 96 | 0 | 10 | 0 | 320 | 0 | 207 | 30 | 30 | 0 | 2 | 17 | 0 | 11 | 20 | 0 | 0 | 0 | 0 | 16 | 19 | 104 | 0 | 8.02 | 0 | 3488.54 | 712 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 775 | 0 | 0 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.25 | 23 | 0 | 0 | 8.09 | 0 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 0.56 | 0 | 56 | 0 | 6 | 0 | 0 | 0 | 0 | 1.2 | 36 | 0.08 | 0 | 0 | 55 | 180 | 0 | 250 | 597 | 0 | 4262.18 | 7750.72 | 98.79
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.01 | 40 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 480 | 0 | 0 | 0 | 240 | 0 | 240 | 5 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 96 | 0 | 1 | 0 | 315 | 0 | 207 | 30 | 30 | 0 | 0 | 8 | 0 | 11 | 20 | 0 | 0 | 45 | 0 | 16 | 19 | 69 | 0 | 0.56 | 0 | 3432.57 | 712 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 847 | 0 | 0 | 0 | 975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 2 | 0 | 0 | 0.69 | 0 | 0 | 163 | 0 | 0 | 0 | 353 | 0 | 0.08 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.01 | 0 | 0 | 55 | 180 | 0 | 300 | 652 | 0 | 4502.72 | 7935.29 | 98.78
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 270 | 0 | 300 | 28 | 0 | 208 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 0 | 315 | 0 | 207 | 30 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 95 | 0 | 56 | 19 | 69 | 0 | 0 | 0 | 4040 | 759 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 973 | 0 | 0 | 0 | 1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 400 | 860 | 0 | 5258 | 9298 | 98.78
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 270 | 0 | 330 | 51 | 0 | 193 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 103 | 0 | 0 | 0 | 305 | 0 | 207 | 30 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 95 | 0 | 56 | 8 | 107 | 0 | 0 | 0 | 3971 | 852 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 942 | 0 | 3 | 0 | 1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 300 | 950 | 0 | 5283 | 9254 | 98.78
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 270 | 0 | 330 | 51 | 0 | 197 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 300 | 0 | 207 | 30 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 95 | 0 | 45 | 8 | 108 | 0 | 0 | 0 | 3992 | 852 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 0 | 2 | 0 | 1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 300 | 980 | 0 | 5228 | 9220
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 270 | 0 | 330 | 51 | 0 | 198 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 207 | 30 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 95 | 0 | 35 | 8 | 109 | 0 | 0 | 0 | 3989 | 852 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 0 | 8 | 0 | 1035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 300 | 900 | 0 | 5163 | 9152 | 98.78
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 350 | 0 | 330 | 51 | 0 | 200 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 207 | 30 | 30 | 0 | 0 | 13 | 0 | 83 | 30 | 0 | 0 | 95 | 0 | 35 | 8 | 114 | 0 | 0 | 0 | 4079 | 852 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 889 | 0 | 0 | 0 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 300 | 900 | 0 | 5062 | 9141 | 98.77
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 350 | 0 | 330 | 51 | 0 | 189 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 207 | 30 | 30 | 0 | 0 | 13 | 0 | 83 | 30 | 0 | 0 | 95 | 0 | 35 | 8 | 167 | 0 | 0 | 0 | 4082.5 | 852 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 0 | 2 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 300 | 900 | 0 | 4926 | 9008.5 | 98.77
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 489 | 0 | 0 | 0 | 300 | 0 | 280 | 51 | 0 | 201 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 305 | 0 | 206 | 30 | 30 | 0 | 0 | 22 | 0 | 42 | 30 | 0 | 0 | 95 | 0 | 16 | 0 | 167 | 0 | 0 | 0 | 3852.5 | 852 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 17 | 0 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 300 | 700 | 0 | 4641 | 8493.5 | 98.77
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8445600 | 0 | 0 | 0 | 0 | 17424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5496772 | 0 | 0 | 7204858 | 0 | 0 | 175519 | 0 | 268800 | 451440 | 0 | 0 | 0 | 0 | 0 | 0 | 4800 | 0 | 0 | 0 | 0 | 0 | 18363 | 976000 | 0 | 753600 | 7825454.55 | 0 | 0 | 0 | 0 | 0 | 4611405 | 0 | 0 | 0 | 10859999 | 114345 | 0 | 0 | 6852800 | 11400 | 6416000 | 835752 | 0 | 4909000 | 0 | 0 | 2044573 | 0 | 0 | 405210 | 0 | 2166720 | 0 | 332455 | 0 | 7449500 | 0 | 5035000 | 704000 | 711120 | 0 | 52221 | 408744 | 0 | 1122240 | 671520 | 0 | 0 | 655670 | 0 | 492000 | 249600 | 2086080 | 11350 | 249970 | 0 | 91097304.55 | 17498181 | 5297472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459360 | 19759997 | 0 | 96182 | 0 | 21218181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288644 | 597110 | 0 | 0 | 267000 | 0 | 0 | 4591527 | 0 | 0 | 0 | 9241818 | 0 | 24600 | 0 | 1314764 | 0 | 177079 | 0 | 0 | 0 | 0 | 33262.8 | 990720 | 2359 | 0 | 0 | 1321000 | 5199639 | 0 | 6802978 | 17735272.73 | 0 | 112917146.53 | 204014451.08

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 8685.24 | MW | 12:00 Hr. | Energy Generated |  |  | 204.0145 |  | MKWHr.
| Day Peak Demand |  |  | 8685.24 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9298 | MW | 18:00 Hr. | Energy Demand |  |  | 204.0145 |  | MKWHr.
| Evening Peak Demand |  |  | 9298 | MW | 18:00 Hr. | Maximum Temperature |  |  | 27.2 |  | °C
| Minimum Generation of the Day |  |  | 7467.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 667.45 |  | MMCFD
| Maximum Generation of the Day |  |  | 9346.54 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.1819 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 21.8675 | 0 | 0.017424 | 0 | 0 | 0.17552 | 0 | 0 | 22.0604 | Gas | 93.2987 | Gas | 326401200.23
| Chattogram Zone |  |  | 5.365 | 18.6855 | 0 | 0 | 0.976 | 0.13271 | 0 | 0.0048 | 25.164 | Coal | 64.2985 | Coal | 412614497.5614
| Cumilla Zone |  |  | 21.4747 | 0 | 0 | 0 | 0 | 0.33246 | 2.1667 | 0 | 23.9739 | HFO | 0.75902 | HFO | 13153894.56
| Mymensingh Zone |  |  | 2.0861 | 0 | 0.7416 | 0 | 0 | 0.26132 | 0 | 0 | 3.089 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 16.7578 | 0 | 0 | 0 | 0 | 0.052221 | 0 | 0 | 16.81 | Hydro | 0.976 | Hydro | 97600
| Khulna Zone |  |  | 5.3937 | 19.76 | 0 | 0 | 0 | 0.45936 | 17.4982 | 0 | 43.1112 | Solar | 3.7944 | Solar | 60591448.838
| Barishal Zone |  |  | 6.5206 | 24.5383 | 0 | 0 | 0 | 0.002359 | 0 | 0 | 31.0612 | Import | 40.8831 | Import | 244251501.72
| Rajshahi Zone |  |  | 13.8333 | 0 | 0 | 0 | 0 | 1.1774 | 21.2182 | 0 | 36.2289 | Wind | 0.0048 | Wind | 70608
| Rangpur Zone |  |  | 0 | 1.3148 | 0 | 0 | 0 | 1.2011 | 0 | 0 | 2.5158
| Total |  |  | 93.2987 | 64.2985 | 0.75902 | 0 | 0.976 | 3.7944 | 40.8831 | 0.0048 | 204.0145
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 326401200.23 |  | Hydro | 97600
|  |  |  | Coal | 412614497.5614 |  | Solar | 60591448.838
|  |  |  | HFO | 13153894.56 |  | Import | 244251501.72
|  |  |  | HSD | 0 |  | Wind | 70608
[5 empty] | Total: | 105,71,80,750 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.4982 | Peak Hr Flow | 759.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35727490.92 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.2182 | Peak Hr Flow | 1128.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2059 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.1667 | Peak Hr Flow | 108.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2383 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.8831 | Peak Hr Flow | 1995.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 2986
|  |  |  | Chattogram |  | 0 |  | 779
|  |  |  | Cumilla |  | 0 |  | 863
|  |  |  | Mymensingh |  | 0 |  | 824
|  |  |  | Sylhet |  | 0 |  | 376
|  |  |  | Khulna |  | 0 |  | 1170
|  |  |  | Barishal |  | 0 |  | 295
|  |  |  | Rajshahi |  | 0 |  | 963
|  |  |  | Rangpur |  | 0 |  | 700
|  |  |  | Total |  | 0 |  | 8956
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:50 |  | Matarbari- Bashkhali 400kV ckt-2 was shut down.
| 12:00 |  | Day Peak Generation: 8682 MW.
| 14:49 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 15:14 |  | Ashuganj 450 MW CCPP(North) Tripped with remarks:- GT
| 15:14 |  | Ashuganj 450 MW CCPP(North) Shutdown
| 15:53 |  | Summit Meghnaghat CCPP-2 ST tripped due to problem with the diverter damper.
|  | 15:55 | Niamatpur 132/33kV S/S Transformer-3(426T) HT is restored.
|  | 16:15 | Niamatpur 132/33kV S/S Transformer-3(426T) LT is restored.
| 18:00 |  | Evening Peak Generation is 9298 MW.
| 18:02 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- GT
| 01:20 |  | Summit Bibiyana-2 CCPP was shutdown due to maintenance purpose
| 02:35 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- Plant
| 02:35 |  | Ashuganj (South) 360 MW CCPP tripped due to tripping of a low-voltage transformer
| 05:00 |  | Minimum generation 6766 MW
| 06:35 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 07:19 |  | Hasnabad-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual Maintenance and from Hasnabad 230/132kV end Due to annual maintenance
| 07:26 |  | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Barishal 230/132kV end Due to Annual maintenance work
| 07:30 |  | Saidpur 132/33kV S/S TR-5 (434T) LT Project Work S/D Due to Project work
| 07:31 |  | Saidpur 132/33kV S/S TR-5 (434T) HT Project Work S/D Due to Project work
| 07:44 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 07:47 |  | Saidpur 132/33kV S/S BUS B Project Work S/D Due to Project work
| 08:00 |  | Kachua 230/132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 377 | 8445600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7204858 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 268800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 451440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 8 | 17424 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 175519 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 80 | 5496772 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 817 | 22060413
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114345 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 976000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 4611405 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 26 | 753600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18363 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 575 | 10859999 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 4800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 7825454.55 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1225 | 25163966.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 208 | 4909000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 11400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 300 | 6416000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 270 | 6852800 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 28 | 835752 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2044573 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 108 | 2166720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 405210 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 332455 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1042 | 23973910
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 69 | 2086080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 249600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 492000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 249970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 144 | 3089000
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 52221 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 704000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 711120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 671520 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1122240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 95 | 655670 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 408744 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7449500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5035000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 812 | 16810015
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 0 | 96182 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 759 | 17498181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 5297472 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 459360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 973 | 19759997 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1982 | 43111192
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 400 | 6802978 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 55 | 1321000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 860 | 17735272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5199639 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Plant shutdown as per NLDC requirement.
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2359 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1535 | 31061248.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 288644 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4591527 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 382 | 9241818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1128 | 21218181 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 267000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 597110 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1684 | 36228880
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1314764 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33262.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 177079 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 990720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 57 | 2515825.8
Eastern Grid Total |  |  |  |  | 17395.105 | 4040 | 91097304.55
Western Grid Total |  |  |  |  | 10984.003 | 5258 | 112917146.53
National Grid Total |  |  |  |  | 28379.108 | 9298 | 204014451.08
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 5827.6 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3128.2 | MW
i) Dhaka area |  |  | 2985.6 |  | MW | i) Khulna area |  |  |  | 1170 | MW
ii) Chattogram area |  |  | 779 |  | MW | ii) Barishal area |  |  |  | 294.8 | MW
iii) Cumilla area |  |  | 863 |  | MW | iii) Rajshahi area |  |  |  | 963.4 | MW
iv) Mymensingh area |  |  | 824 |  | MW | iv) Rangpur area |  |  |  | 700 | MW
v) Sylhet area |  |  | 376 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 8955.8 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 51 | 18:00 | 133 | Niamatpur | 48 | 08:00
2 | AKSML | 109 | 23:00 | 68 | Ishurdi | 43 | 18:00 | 134 | Noapara | 32 | 18:00
3 | Aftabnagar | 24 | 11:00 | 69 | Jaldhaka | 48 | 18:00 | 135 | PHP | 8 | 06:00
4 | Agargaon | 80 | 13:00 | 70 | Jamalpur | 91 | 18:00 | 136 | Pabna | 70 | 18:00
5 | Agrabad | 40 | 18:00 | 71 | Jashore | 105 | 13:00 | 137 | Palashbari | 82 | 18:00
6 | Amnura | 27 | 13:00 | 72 | Jhenaidah | 94 | 18:00 | 138 | Panchagarh | 46 | 18:00
7 | Ashuganj | 85 | 12:00 | 73 | Joydebpur | 71 | 13:00 | 139 | Patiya | 6 | 18:30
8 | BSRM | 182 | 02:00 | 74 | Joypurhat | 38 | 13:00 | 140 | Patuakhali | 45.7 | 21:00
9 | Bagerhat | 62 | 18:00 | 75 | Juldah | 11 | 00:00 | 141 | Payra | 24 | 21:00
10 | Bajitpur | 56 | 18:00 | 76 | KSRM | 8 | 00:00 | 142 | Postogola | 35 | 13:00
11 | Bakulia | 57 | 13:00 | 77 | Kabirpur | 125 | 00:00 | 143 | Purbachal | 25 | 13:00
12 | Banani | 34 | 13:00 | 78 | Kachua | 54 | 18:00 | 144 | Purbasadipur | 109 | 13:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 69 | 12:00 | 145 | Rahanpur | 22 | 08:00
14 | Barapukuria | 43 | 12:00 | 80 | Kalurghat | 22 | 00:00 | 146 | Rahim | 27 | 01:00
15 | Barguna | 10 | 18:00 | 81 | Kamrangirchar | 48 | 01:00 | 147 | Rajbari | 57 | 18:00
16 | Barishal | 78 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 78 | 00:00
17 | Barishal-230 | 62 | 20:00 | 83 | Kasba | 23 | 13:00 | 149 | Rajshahi | 76 | 13:00
18 | Baroaulia | 42 | 21:00 | 84 | Kazla | 73 | 13:00 | 150 | Rajshahi-230 | 60 | 13:00
19 | Baroirhat | 47 | 18:00 | 85 | Keranigonj | 49 | 13:00 | 151 | Ramganj | 68 | 13:00
20 | Bashundhara | 134 | 13:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 25 | 00:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 44 | 13:00 | 153 | Rangamati | 12 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 130 | 00:00 | 154 | Rangpur | 94 | 18:00
23 | Benapole | 38 | 08:00 | 89 | Kishoreganj | 84 | 19:30 | 155 | Ruppur | 2.2 | 15:00
24 | Bhaluka | 104 | 00:00 | 90 | Kodda | 186 | 00:00 | 156 | SSM | 2 | 00:00
25 | Bhandaria | 38 | 21:00 | 91 | Kulaura | 27 | 18:00 | 157 | Saidpur | 69 | 18:00
26 | Bhangura | 24 | 18:00 | 92 | Kurigram | 46 | 08:00 | 158 | Satkhira | 84 | 18:00
27 | Bheramara(GK) | 37 | 18:30 | 93 | Kushtia | 95 | 13:00 | 159 | Satmasjid | 73 | 13:00
28 | Bhulta | 163 | 00:00 | 94 | Laksam | 13 | 20:00 | 160 | Savar | 102 | 00:00
29 | Bog-Sherpur | 54 | 18:00 | 95 | Lakshmipur | 23 | 18:00 | 161 | SevenRings | 5.3 | 15:00
30 | Bogura | 104 | 12:00 | 96 | Lalbag | 50 | 00:00 | 162 | ShahCement | 31 | 00:00
31 | Borhanuddin | 63 | 20:00 | 97 | Lalmonirhat | 42 | 18:00 | 163 | Shahjadpur | 54 | 12:00
32 | Brahmanbaria | 80 | 18:00 | 98 | MI_Cement | 9.6 | 00:00 | 164 | Shahjibazar | 71 | 21:00
33 | Cantonment | 76 | 13:00 | 99 | Madanganj | 22 | 12:00 | 165 | Shahmirpur | 38 | 01:00
34 | Chandina | 6 | 06:00 | 100 | Madaripur | 70 | 13:00 | 166 | Shariatpur | 54 | 21:00
35 | Chandpur | 50 | 19:30 | 101 | Madartek | 58 | 13:00 | 167 | Sherpur | 104 | 18:00
36 | Chandraghona | 25 | 18:00 | 102 | Madunaghat | 37 | 13:00 | 168 | Shikalbaha | 19.5 | 11:00
37 | Chapai | 53 | 12:00 | 103 | Magura | 45 | 16:00 | 169 | Shitalakhya | 53.3 | 13:00
38 | Charsaidpur | 41 | 00:00 | 104 | Mahasthangarh | 54 | 08:00 | 170 | Sholosohor | 26 | 21:00
39 | Chauddagram | 49 | 13:00 | 105 | Maijdee | 28 | 21:00 | 171 | Shyampur | 128 | 11:00
40 | Chhatak | 24 | 19:30 | 106 | Manikganj | 79 | 00:00 | 172 | Siddhirganj | 70 | 00:00
41 | Chowmuhani | 99 | 18:00 | 107 | Maniknagar | 48 | 13:00 | 173 | Sirajganj | 80 | 18:30
42 | Chuadanga | 71 | 13:00 | 108 | Matarbari | 35 | 18:00 | 174 | Sonargaon | 119 | 00:00
43 | Coxsbazar | 103 | 18:00 | 109 | Matuail | 50 | 00:00 | 175 | Sreemongol | 47 | 17:00
44 | Cumilla(N) | 97 | 13:00 | 110 | Metrorail_Motijheel | 8 | 20:00 | 176 | Sreepur | 71 | 00:00
45 | Cumilla(S) | 112 | 19:30 | 111 | Metrorail_Uttara | 7 | 18:00 | 177 | Srinagar | 32.28 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 48 | 00:00 | 178 | Sunamganj | 38 | 19:30
47 | Daudkandi | 80 | 18:00 | 113 | Mirpur | 100 | 13:00 | 179 | Sylhet | 38 | 18:00
48 | DhakaUniversity | 30 | 13:00 | 114 | Mirsorai | 37 | 10:00 | 180 | Sylhet-132 | 73 | 21:00
49 | Dhamrai | 80 | 00:00 | 115 | Mirzapur | 30 | 00:00 | 181 | TK | 15 | 13:00
50 | Dhanmondi | 55 | 13:00 | 116 | Mithapukur | 47 | 08:00 | 182 | Tangail | 118 | 08:00
51 | Dohazari | 62 | 18:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 13 | 18:00
52 | Faridpur | 101 | 18:30 | 118 | Mogbazar | 53.8 | 14:00 | 184 | Tasnim | 24 | 00:00
53 | Fatullah | 79 | 00:00 | 119 | Mongla | 32 | 00:00 | 185 | Thakurgaon | 76 | 18:00
54 | Fenchuganj | 23 | 13:00 | 120 | Motijheel | 22 | 13:00 | 186 | Tongi | 85 | 00:00
55 | Feni | 71 | 13:00 | 121 | Muktagacha | 27 | 13:00 | 187 | Ullahpara | 25 | 18:00
56 | GPH | 21 | 02:00 | 122 | Munshiganj | 72 | 13:00 | 188 | Ullon | 52 | 13:00
57 | Ghatail | 60 | 08:00 | 123 | Muradnagar | 24 | 19:30 | 189 | Uttara | 54 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 132 | 18:00 | 190 | UttaraNew | 11 | 13:00
59 | Ghorashal-230 | 75 | 00:00 | 125 | Naogaon | 83 | 18:00 | 191 | Zigatola | 50 | 13:00
60 | Goalpara | 27 | 13:00 | 126 | Narail | 39 | 18:30
61 | Gollamari | 64 | 13:00 | 127 | Narinda | 38 | 13:00
62 | Gopalganj | 74 | 18:00 | 128 | Narshingdi | 130 | 19:30
63 | Gulshan | 56 | 13:00 | 129 | Natore | 97 | 18:00
64 | Halishahar | 32 | 18:00 | 130 | Nawabganj | 37.8 | 13:00
65 | HaripurSBU | 85 | 04:00 | 131 | Netrakona | 99 | 08:00
66 | Hasnabad | 65 | 13:00 | 132 | New | 52 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9292.5 | 0 |  | 9292.5
1:00 | 8620.5 | 0 |  | 8620.5
2:00 | 8247.5 | 0 |  | 8247.5
3:00 | 7894.5 | 0 |  | 7894.5
4:00 | 7613.5 | 0 |  | 7613.5
5:00 | 7467.5 | 0 |  | 7467.5
6:00 | 7545.5 | 0 |  | 7545.5
7:00 | 7659.74 | 0 |  | 7659.74
8:00 | 8309.68 | 0 |  | 8309.68
9:00 | 8176.58 | 0 |  | 8176.58
10:00 | 7903.46 | 0 |  | 7903.46
11:00 | 7991.31 | 0 |  | 7991.31
12:00 | 8685.24 | 0 |  | 8685.24
13:00 | 9346.54 | 0 |  | 9346.54
14:00 | 8987.02 | 0 |  | 8987.02
15:00 | 8092.79 | 0 |  | 8092.79
16:00 | 7750.72 | 0 |  | 7750.72
17:00 | 7935.29 | 0 |  | 7935.29
18:00 | 9298 | 0 |  | 9298
19:00 | 9254 | 0 |  | 9254
19:30 | 9220 | 0 |  | 9220
20:00 | 9152 | 0 |  | 9152
21:00 | 9141 | 0 |  | 9141
22:00 | 9008.5 | 0 |  | 9008.5
23:00 | 8493.5 | 0 |  | 8493.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4103.5 | 5189 | 9292.5 | DAILY GENERATION CURVE
00:30 | 3986.5 | 4970 | 8956.5
01:00 | 3869.5 | 4751 | 8620.5 | 16-12-2025
01:30 | 3862 | 4572 | 8434
02:00 | 3854.5 | 4393 | 8247.5
02:30 | 3759 | 4312 | 8071
03:00 | 3663.5 | 4231 | 7894.5
03:30 | 3584 | 4170 | 7754
04:00 | 3504.5 | 4109 | 7613.5
04:30 | 3447 | 4093.5 | 7540.5
05:00 | 3389.5 | 4078 | 7467.5
05:30 | 3387 | 4119.5 | 7506.5
06:00 | 3384.5 | 4161 | 7545.5
06:30 | 3436.535 | 4166.085 | 7602.62
07:00 | 3488.57 | 4171.17 | 7659.74
07:30 | 3708.91 | 4275.8 | 7984.71
08:00 | 3929.25 | 4380.43 | 8309.68
08:30 | 3882.495 | 4360.635 | 8243.13
09:00 | 3835.74 | 4340.84 | 8176.58
09:30 | 3657.62 | 4382.4 | 8040.02
10:00 | 3479.5 | 4423.96 | 7903.46
10:30 | 3459.48 | 4487.905 | 7947.385
11:00 | 3439.46 | 4551.85 | 7991.31
11:30 | 3689.57 | 4648.705 | 8338.275
12:00 | 3939.68 | 4745.56 | 8685.24
12:30 | 4146.635 | 4869.255 | 9015.89
13:00 | 4353.59 | 4992.95 | 9346.54
13:30 | 4232.335 | 4934.445 | 9166.78
14:00 | 4111.08 | 4875.94 | 8987.02
14:30 | 3868.96 | 4670.945 | 8539.905
15:00 | 3626.84 | 4465.95 | 8092.79
15:30 | 3557.69 | 4364.065 | 7921.755
16:00 | 3488.54 | 4262.18 | 7750.72
16:30 | 3460.555 | 4382.45 | 7843.005
17:00 | 3432.57 | 4502.72 | 7935.29
17:30 | 3736.285 | 4880.36 | 8616.645
18:00 | 4040 | 5258 | 9298
18:30 | 4005.5 | 5270.5 | 9276
19:00 | 3971 | 5283 | 9254
19:30 | 3992 | 5228 | 9220
20:00 | 3989 | 5163 | 9152
20:30 | 4034 | 5112.5 | 9146.5 |  | Executive Engineer
21:00 | 4079 | 5062 | 9141 |  | Network Operation Division
21:30 | 4080.75 | 4994 | 9074.75
22:00 | 4082.5 | 4926 | 9008.5
22:30 | 3967.5 | 4783.5 | 8751
23:00 | 3852.5 | 4641 | 8493.5

## En-Curve
QF-LDC-12
Date | 16-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2885 | 1118.5 | 779 | 0 | 96 | 975 | 40 | 3356 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2821 | 1092.5 | 752.5 | 0 | 93 | 947.5 | 40 | 3180.5 | 0 | 0 | 29.5 | 0 | 0 | 0 | 0 | 16-12-2025
01:00 | 2757 | 1066.5 | 726 | 0 | 90 | 920 | 40 | 3005 | 0 | 0 | 16 | 0 | 0 | 0 | 0
01:30 | 2774.5 | 1058 | 663 | 0 | 88 | 877 | 40 | 2917.5 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | Energy Generated | 204.0145 |  | MKWHr
02:00 | 2792 | 1049.5 | 600 | 0 | 86 | 834 | 40 | 2830 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2751 | 1056.5 | 603.5 | 0 | 84 | 838 | 40 | 2686 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | Total Energy Requirement | 204.0145 |  | MKWHr
03:00 | 2710 | 1063.5 | 607 | 0 | 82 | 842 | 40 | 2542 | 0 | 0 | 8 | 0 | 0 | 0 | 0
03:30 | 2697 | 979.5 | 607 | 0 | 78 | 838 | 40 | 2506.5 | 0 | 0 | 8 | 0 | 0 | 0 | 0
04:00 | 2684 | 895.5 | 607 | 0 | 74 | 834 | 40 | 2471 | 0 | 0 | 8 | 0 | 0 | 0 | 0
04:30 | 2661.5 | 890 | 611 | 0 | 74 | 832 | 40 | 2424 | 0 | 0 | 8 | 0 | 0 | 0 | 0
05:00 | 2639 | 884.5 | 615 | 0 | 74 | 830 | 40 | 2377 | 0 | 0 | 8 | 0 | 0 | 0 | 0
05:30 | 2661.5 | 889.5 | 615.5 | 0 | 77 | 830.5 | 40 | 2384.5 | 0 | 0 | 8 | 0 | 0 | 0 | 0
06:00 | 2684 | 894.5 | 616 | 0 | 80 | 831 | 40 | 2392 | 0 | 0 | 8 | 0 | 0 | 0 | 0
06:30 | 2716.5 | 899 | 615.5 | 0 | 75 | 836.5 | 40 | 2391.5 | 10.12 | 0 | 18.5 | 0 | 0 | 0 | 0
07:00 | 2749 | 903.5 | 615 | 0 | 70 | 842 | 40 | 2391 | 20.24 | 0 | 29 | 0 | 0 | 0 | 0
07:30 | 2879.5 | 986 | 640 | 0 | 73 | 840 | 40 | 2400.5 | 89.71 | 0 | 36 | 0 | 0 | 0 | 0
08:00 | 3010 | 1068.5 | 665 | 0 | 76 | 838 | 40 | 2410 | 159.18 | 0 | 43 | 0 | 0 | 0 | 0
08:30 | 2918 | 1040.25 | 665 | 0 | 77 | 834.835 | 40 | 2370.5 | 268.045 | 0 | 29.5 | 0 | 0 | 0 | 0
09:00 | 2826 | 1012 | 665 | 0 | 78 | 831.67 | 40 | 2331 | 376.91 | 0 | 16 | 0 | 0 | 0 | 0
09:30 | 2763.5 | 933.5 | 665 | 0 | 79 | 832.73 | 40 | 2263 | 451.29 | 0 | 12 | 0 | 0 | 0 | 0
10:00 | 2701 | 855 | 665 | 0 | 80 | 833.79 | 40 | 2195 | 525.67 | 0 | 8 | 0 | 0 | 0 | 0
10:30 | 2687.5 | 868.5 | 665 | 0 | 83 | 835.405 | 40 | 2198 | 561.98 | 0 | 8 | 0 | 0 | 0 | 0
11:00 | 2674 | 882 | 665 | 0 | 86 | 837.02 | 40 | 2201 | 598.29 | 0 | 8 | 0 | 0 | 0 | 0
11:30 | 2847.5 | 967.5 | 688.5 | 0 | 86 | 832.055 | 40 | 2269.5 | 595.22 | 0 | 12 | 0 | 0 | 0 | 0
12:00 | 3021 | 1053 | 712 | 0 | 86 | 827.09 | 40 | 2338 | 592.15 | 0 | 16 | 0 | 0 | 0 | 0
12:30 | 3101.5 | 1109 | 712 | 0 | 95 | 854.575 | 40 | 2509.5 | 564.815 | 0 | 29.5 | 0 | 0 | 0 | 0
13:00 | 3182 | 1165 | 712 | 0 | 104 | 882.06 | 40 | 2681 | 537.48 | 0 | 43 | 0 | 0 | 0 | 0
13:30 | 3048 | 1157.5 | 712 | 0 | 105 | 866.53 | 40 | 2689.5 | 509.25 | 0 | 39 | 0 | 0 | 0 | 0
14:00 | 2914 | 1150 | 712 | 0 | 106 | 851 | 40 | 2698 | 481.02 | 0 | 35 | 0 | 0 | 0 | 0
14:30 | 2821.5 | 1027.5 | 712 | 0 | 98 | 846 | 40 | 2553 | 406.905 | 0 | 35 | 0 | 0 | 0 | 0
15:00 | 2729 | 905 | 712 | 0 | 90 | 841 | 40 | 2408 | 332.79 | 0 | 35 | 0 | 0 | 0 | 0
15:30 | 2723.5 | 898 | 712 | 0 | 93 | 838.5 | 40 | 2348 | 233.255 | 0 | 35 | 0 | 0 | 0.5 | 0
16:00 | 2718 | 891 | 712 | 0 | 96 | 836 | 40 | 2288 | 133.72 | 0 | 35 | 0 | 0 | 1 | 0
16:30 | 2745 | 774 | 712 | 0 | 96 | 905.5 | 40 | 2462 | 72.505 | 0 | 35 | 0 | 0 | 1 | 0
17:00 | 2772 | 657 | 712 | 0 | 96 | 975 | 40 | 2636 | 11.29 | 0 | 35 | 0 | 0 | 1 | 0
17:30 | 2956 | 737.5 | 735.5 | 0 | 102 | 1051.5 | 40 | 2927.5 | 5.645 | 0 | 59 | 0 | 0 | 2 | 0
18:00 | 3140 | 818 | 759 | 0 | 108 | 1128 | 40 | 3219 | 0 | 0 | 83 | 0 | 0 | 3 | 0
18:30 | 3165 | 790 | 805.5 | 0 | 105.5 | 1101 | 40 | 3193.5 | 0 | 0 | 73.5 | 0 | 0 | 2 | 0
19:00 | 3190 | 762 | 852 | 0 | 103 | 1074 | 40 | 3168 | 0 | 0 | 64 | 0 | 0 | 1 | 0
19:30 | 3216 | 763 | 852 | 0 | 112 | 1032 | 40 | 3150 | 0 | 0 | 53 | 0 | 0 | 2 | 0
20:00 | 3229 | 774 | 852 | 0 | 108 | 1035 | 40 | 3070 | 0 | 0 | 43 | 0 | 0 | 1 | 0
20:30 | 3282.5 | 769.5 | 852 | 0 | 106 | 980.5 | 40 | 3072.5 | 0 | 0 | 43 | 0 | 0 | 0.5 | 0
21:00 | 3336 | 765 | 852 | 0 | 104 | 926 | 40 | 3075 | 0 | 0 | 43 | 0 | 0 | 0 | 0
21:30 | 3335.5 | 762.75 | 852 | 0 | 100 | 878.5 | 40 | 3063 | 0 | 0 | 43 | 0 | 0 | 0 | 0
22:00 | 3335 | 760.5 | 852 | 0 | 96 | 831 | 40 | 3051 | 0 | 0 | 43 | 0 | 0 | 0 | 0
22:30 | 3290 | 744.5 | 852 | 0 | 96 | 839 | 40 | 2860 | 0 | 0 | 29.5 | 0 | 0 | 0 | 0
23:00 | 3245 | 728.5 | 852 | 0 | 96 | 847 | 40 | 2669 | 0 | 0 | 16 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 409 | 06:00 | 397 | 18:30 | Meghnaghat | 410 | 06:00 | 398 | 18:00
Ashuganj | 413 | 8:00 | 403 | 13:00 | Payra | 418 | 06:00 | 412 | 18:30
Bhulta | 409 | 05:00 | 399 | 13:00 | Rahanpur | 418 | 03:00 | 406 | 18:00
Bibiana | 406 | 06:00 | 398 | 13:00 | Rampal | 411 | 05:00 | 401 | 18:30
BIPTC | 407 | 02:00 | 391 | 13:00
Bogura | 413 | 05:00 | 397 | 18:00
Gopalganj | 412 | 05:00 | 402 | 18:00
Kaliakoir | 405 | 06:00 | 393 | 13:00
Korerhat | 413 | 06:00 | 402 | 18:00
Madunaghat | 408 | 06:00 | 400 | 19:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 03:00 | 232 | 13:00 | Kachua | 236 | 00:00 | 234 | 12:00
AKSML | 237 | 06:00 | 232 | 18:00 | Kaliakoir | 239 | 06:00 | 232 | 13:00
Aminbazar | 240 | 05:00 | 232 | 00:00 | Keranigonj | 239 | 06:00 | 231 | 13:00
Ashuganj | 241 | 05:00 | 236 | 12:00 | Khulna(S) | 238 | 16:00 | 232 | 18:30
Ashuganj-400 | 241 | 8:00 | 236 | 12:00 | Korerhat | 239 | 04:00 | 234 | 00:00
Baghabari | 241 | 05:00 | 233 | 18:00 | Madunaghat | 236 | 04:00 | 231 | 00:00
Barapukuria | 231 | 04:00 | 218 | 18:00 | Madunaghat-400 | 237 | 07:00 | 232 | 00:00
Barapukuria-230 | 231 | 4:00 | 217 | 18:30 | Maniknagar | 238 | 04:00 | 232 | 13:00
Barishal | 245 | 06:00 | 239 | 13:00 | Meghnaghat | 246 | 08:00 | 238 | 00:00
Bheramara | 235 | 03:00 | 227 | 13:00 | Meghnaghat-400 | 241 | 06:00 | 233 | 00:00
Bhulta | 239 | 05:00 | 233 | 13:00 | Mirsorai | 239 | 03:00 | 235 | 00:00
Bibiana | 242 | 03:00 | 233 | 13:00 | Rajshahi | 237 | 05:00 | 227 | 13:00
BIPTC | 237 | 00:00 | 227 | 13:00 | Rampal | 237 | 15:00 | 230 | 18:30
Bogura | 242 | 03:00 | 232 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 241 | 04:00 | 231 | 18:00 | Rampura | 239 | 06:00 | 232 | 13:00
Borhanuddin | 245 | 03:00 | 241 | 18:00 | Shikalbaha | 235 | 07:00 | 230 | 00:00
BSRM | 239 | 03:00 | 235 | 00:00 | Shyampur | 239 | 06:00 | 232 | 13:00
Cumilla(N) | 239 | 03:00 | 233 | 13:00 | Siddhirganj | 240 | 06:00 | 234 | 13:00
Faridpur | 244 | 04:00 | 238 | 13:00 | Sirajgonj | 245 | 06:00 | 240 | 18:00
Fenchuganj | 240 | 02:00 | 234 | 13:00 | Sreepur | 238 | 05:00 | 232 | 13:00
Feni | 239 | 05:00 | 233 | 13:00 | Tongi | 236 | 09:00 | 227 | 00:00
Ghorashal | 242 | 04:00 | 235 | 00:00
Ghorashal-230 | 230 | 05:00 | 222 | 13:00
Gopalganj | 244 | 03:00 | 238 | 18:00
GPH | 237 | 03:00 | 233 | 13:00
Haripur | 239 | 03:00 | 234 | 00:00
Hasnabad | 239 | 08:00 | 232 | 00:00
Hathazari | 236 | 09:00 | 228 | 00:00
Ishurdi | 238 | 00:00 | 231 | 13:00
Jhenaidah | 236 | 03:00 | 227 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 131 | 11:00 | Lalbag | 136 | 04:00 | 131 | 13:00
Agargaon | 137 | 03:00 | 132 | 13:00 | Lalmonirhat | 133 | 05:00 | 122 | 18:00
Agrabad | 137 | 01:00 | 134 | 00:00 | Madanganj | 138 | 10:00 | 133 | 01:00
AKS | 135 | 01:00 | 130 | 00:00 | Madaripur | 140 | 05:00 | 136 | 12:00
Aminbazar | 138 | 05:00 | 133 | 00:00 | Madartek | 134 | 04:00 | 130 | 13:00
Amnura | 139 | 05:00 | 131 | 13:00 | Madunaghat | 138 | 05:00 | 135 | 00:00
Ashuganj | 144 | 03:00 | 140 | 11:00 | Magura | 136 | 03:00 | 127 | 13:00
Bagerhat | 138 | 05:00 | 126 | 18:00 | Mahasthangarh | 136 | 02:00 | 129 | 18:00
Bajitpur | 137 | 00:00 | 133 | 12:00 | Maijdee | 135 | 03:00 | 131 | 13:00
Bakulia | 138 | 04:00 | 134 | 00:00 | Manikganj | 134 | 05:00 | 128 | 00:00
Banani | 135 | 04:00 | 130 | 13:00 | Maniknagar | 138 | 05:00 | 133 | 13:00
Bangabhaban | 138 | 05:00 | 133 | 13:00 | Matarbari | 129 | 08:00 | 121 | 18:00
Barapukuria | 136 | 06:00 | 127 | 18:00 | Matuail | 142 | 07:00 | 138 | 00:00
Barguna | 137 | 05:00 | 135 | 00:00 | Metrorail_Motijheel | 138 | 05:00 | 133 | 13:00
Barishal | 140 | 02:00 | 137 | 13:00 | Metrorail_Uttara | 140 | 02:00 | 132 | 13:00
Barishal-230 | 141 | 05:00 | 137 | 13:00 | Millgate | 136 | 05:00 | 130 | 00:00
Baroaulia | 137 | 02:00 | 134 | 00:00 | Mirpur | 138 | 05:00 | 133 | 00:00
Baroirhat | 136 | 02:00 | 133 | 13:00 | Mirzapur | 137 | 05:00 | 131 | 18:00
Bashundhara | 135 | 03:00 | 131 | 12:00 | Mithapukur | 135 | 04:00 | 125 | 18:00
BashundharaCement | 138 | 10:00 | 133 | 01:00 | MI_Cement | 139 | 06:00 | 133 | 13:00
Beanibazar | 140 | 04:00 | 133 | 13:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 134 | 04:00 | 122 | 13:00 | Mogbazar | 137 | 03:00 | 132 | 13:00
Bhaluka | 137 | 05:00 | 133 | 13:00 | Mongla | 133 | 04:00 | 128 | 13:00
Bhandaria | 140 | 06:00 | 130 | 18:00 | Motijheel | 138 | 05:00 | 133 | 13:00
Bhangura | 141 | 04:00 | 134 | 13:00 | Muktagacha | 133 | 22:00 | 123 | 18:00
Bheramara | 141 | 05:00 | 137 | 13:00 | Munshiganj | 139 | 04:00 | 136 | 00:00
Bheramara(GK) | 140 | 03:00 | 136 | 13:00 | Muradnagar | 140 | 06:00 | 135 | 13:00
Bhulta | 133 | 08:00 | 130 | 00:00 | Mymensingh | 134 | 05:00 | 121 | 18:00
Bog-Sherpur | 138 | 03:00 | 131 | 18:00 | Naogaon | 134 | 01:00 | 127 | 13:00
Bogura | 138 | 06:00 | 132 | 18:00 | Narail | 136 | 03:00 | 127 | 13:00
Bogura-230 | 138 | 03:00 | 131 | 18:00 | Narinda | 138 | 5:00 | 133 | 13:00
Brahmanbaria | 138 | 01:00 | 135 | 11:00 | Narshingdi | 138 | 04:00 | 134 | 00:00
Cantonment | 138 | 06:00 | 132 | 13:00 | Natore | 137 | 04:00 | 132 | 13:00
Chandina | 141 | 05:00 | 137 | 13:00 | Nawabganj | 137 | 06:00 | 132 | 00:00
Chandpur | 139 | 06:00 | 130 | 03:00 | Netrakona | 131 | 21:00 | 124 | 13:00
Chandraghona | 139 | 06:00 | 136 | 11:00 | New | 138 | 11:00 | 131 | 18:00
Chapai | 139 | 01:00 | 135 | 13:00 | Niamatpur | 139 | 04:00 | 135 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 141 | 06:00 | 137 | 00:00 | Noapara | 135 | 04:00 | 122 | 13:00
Chauddagram | 138 | 03:00 | 134 | 13:00 | Pabna | 139 | 00:00 | 134 | 18:00
Chhatak | 139 | 03:00 | 131 | 13:00 | Palashbari | 134 | 04:00 | 124 | 18:00
Chowmuhani | 135 | 03:00 | 130 | 13:00 | Panchagarh | 135 | 03:00 | 123 | 08:00
Chuadanga | 137 | 05:00 | 127 | 13:00 | Patiya | 137 | 03:00 | 133 | 18:30
Coxsbazar | 128 | 04:00 | 121 | 18:00 | Patuakhali | 135 | 01:00 | 133 | 18:00
Cumilla(N) | 140 | 03:00 | 137 | 13:00 | Payra | 137 | 03:00 | 135 | 18:00
Cumilla(S) | 140 | 08:00 | 126 | 13:00 | PHP | 136 | 02:00 | 133 | 13:00
Daganbhuiyan | 136 | 03:00 | 133 | 18:00 | Postogola | 139 | 05:00 | 135 | 00:00
Daudkandi | 138 | 04:00 | 134 | 13:00 | Purbachal | 135 | 03:00 | 130 | 13:00
DhakaUniversity | 136 | 04:00 | 131 | 13:00 | Purbasadipur | 132 | 04:00 | 123 | 18:00
Dhamrai | 140 | 05:00 | 135 | 00:00 | Rahanpur | 140 | 01:00 | 129 | 22:00
Dhanmondi | 142 | 06:00 | 139 | 00:00 | Rahanpur-400 | 141 | 03:00 | 136 | 18:00
Dohazari | 135 | 05:00 | 130 | 13:00 | Rahim | 140 | 02:00 | 134 | 09:00
Faridpur | 140 | 04:00 | 135 | 18:00 | Rajbari | 140 | 03:00 | 136 | 13:00
Fatullah | 138 | 06:00 | 133 | 00:00 | Rajendrapur | 140 | 05:00 | 135 | 13:00
Fenchuganj | 145 | 07:00 | 139 | 13:00 | Rajshahi | 138 | 06:00 | 132 | 13:00
Feni | 135 | 05:00 | 133 | 00:00 | Rajshahi-230 | 137 | 03:00 | 131 | 13:00
Feni-230 | 137 | 06:00 | 133 | 13:00 | Ramganj | 136 | 04:00 | 132 | 13:00
Ghatail | 132 | 22:00 | 124 | 18:00 | Rampur | 137 | 04:00 | 134 | 18:00
Ghorashal | 138 | 06:00 | 135 | 00:00 | Rampura | 135 | 05:00 | 130 | 13:00
Goalpara | 133 | 03:00 | 130 | 12:00 | Rangamati | 138 | 05:00 | 135 | 00:00
Gollamari | 135 | 06:00 | 130 | 13:00 | Rangpur | 135 | 05:00 | 125 | 18:00
Gopalganj | 138 | 06:00 | 133 | 18:00 | Ruppur | 140 | 00:00 | 136 | 18:00
Gopalganj-400 | 141 | 03:00 | 137 | 18:00 | Saidpur | 133 | 04:00 | 122 | 18:00
Gulshan | 135 | 06:00 | 130 | 13:00 | Satkhira | 132 | 01:00 | 127 | 13:00
Halishahar | 138 | 03:00 | 135 | 00:00 | Satmasjid | 137 | 05:00 | 132 | 00:00
Haripur | 141 | 03:00 | 138 | 00:00 | Savar | 137 | 06:00 | 132 | 13:00
HaripurSBU | 141 | 03:00 | 138 | 00:00 | SevenRings | 139 | 17:00 | 134 | 13:00
Hasnabad | 140 | 05:00 | 135 | 00:00 | ShahCement | 141 | 06:00 | 137 | 00:00
Hathazari | 138 | 07:00 | 134 | 20:00 | Shahjadpur | 141 | 02:00 | 138 | 07:00
Ishurdi | 142 | 05:00 | 137 | 13:00 | Shahjibazar | 141 | 01:00 | 135 | 17:00
Jaldhaka | 132 | 05:00 | 120 | 18:00 | Shahmirpur | 138 | 05:00 | 135 | 00:00
Jamalpur | 128 | 07:00 | 117 | 17:00 | Shariatpur | 141 | 05:00 | 136 | 13:00
Jashore | 134 | 04:00 | 122 | 13:00 | Sherpur | 125 | 19:00 | 115 | 01:00
Jhenaidah | 138 | 04:00 | 123 | 13:00 | Shikalbaha | 127 | 05:00 | 123 | 18:00
Jhenaidah-230 | 138 | 05:00 | 130 | 13:00 | Shikalbaha-230 | 139 | 07:00 | 134 | 00:00
Joydebpur | 136 | 22:00 | 131 | 13:00 | Shitalakhya | 139 | 06:00 | 136 | 20:00
Joypurhat | 134 | 03:00 | 126 | 13:00 | Sholosohor | 138 | 08:00 | 135 | 00:00
Juldah | 138 | 04:00 | 135 | 00:00 | Shyampur | 136 | 00:00 | 134 | 01:00
Kabirpur | 140 | 05:00 | 128 | 00:00 | Shyampur-230 | 138 | 03:00 | 134 | 13:00
Kachua | 141 | 06:00 | 137 | 12:00 | Siddhirganj | 141 | 04:00 | 138 | 00:00
Kaliakoir | 142 | 06:00 | 137 | 18:00 | Sirajganj | 138 | 03:00 | 132 | 18:00
Kallyanpur | 138 | 08:00 | 134 | 00:00 | Sonargaon | 140 | 07:00 | 135 | 02:00
Kalurghat | 138 | 05:00 | 135 | 13:00 | Sreemongol | 141 | 01:00 | 136 | 16:00
Kamrangirchar | 136 | 03:00 | 131 | 00:00 | Sreepur | 140 | 05:00 | 136 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 06:00 | 131 | 13:00
Kasba | 140 | 05:00 | 128 | 02:00 | SSM | 140 | 01:00 | 136 | 00:00
Kazla | 138 | 06:00 | 133 | 00:00 | Sunamganj | 138 | 02:00 | 132 | 13:00
Keranigonj | 137 | 06:00 | 131 | 13:00 | Sylhet | 140 | 05:00 | 134 | 12:00
Khagrachori | 138 | 05:00 | 134 | 13:00 | Sylhet-132 | 140 | 03:00 | 136 | 11:00
Khulna | 133 | 03:00 | 128 | 18:30 | Tangail | 132 | 03:00 | 127 | 17:00
Khulna(S) | 134 | 03:00 | 130 | 13:00 | Taraganj | 133 | 04:00 | 125 | 18:30
Khulshi | 137 | 05:00 | 133 | 00:00 | Tasnim | 140 | 05:00 | 136 | 00:00
Kishoreganj | 135 | 05:00 | 130 | 13:00 | Thakurgaon | 134 | 04:00 | 121 | 08:00
Kodda | 136 | 05:00 | 131 | 00:00 | TK | 137 | 04:00 | 134 | 00:00
KSRM | 138 | 09:00 | 134 | 19:30 | Tongi | 137 | 07:00 | 131 | 00:00
Kulaura | 142 | 04:00 | 138 | 13:00 | Ullahpara | 139 | 04:00 | 133 | 18:00
Kurigram | 132 | 04:00 | 118 | 18:00 | Ullon | 135 | 05:00 | 130 | 13:00
Kushtia | 137 | 02:00 | 130 | 13:00 | Uttara | 135 | 03:00 | 130 | 13:00
Laksam | 140 | 04:00 | 137 | 00:00 | UttaraNew | 137 | 04:00 | 132 | 13:00
Lakshmipur | 135 | 03:00 | 131 | 18:00 | Zigatola | 137 | 06:00 | 131 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division