## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-12-2025 | during | 18-12-2025 | during | 18-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 376 | 329 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 334 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 43 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 28.5 | 20.2 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 16 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 94 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 155 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 420 | 420 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 505 | 550 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1335.5 | 1618.2 | 5779.35 | 5749.35 | 3203.49 | 3182.49
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 3 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 226 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 64 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 33 | 33 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 10 | 17 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.1 | 0 | 3.28 | 0 | 3.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 2 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 355 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1226.1 | 1369 | 2558 | 2557.72 | 2047.78 | 2047.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 199 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 140 | 0 | 200 | 200 | 200 | 200 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 80 | 65 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 0 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 93 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 104 | 108 | 163 | 163 | 112 | 112 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 118 | 122 | 160 | 160 | 134 | 134 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 47 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1313 | 1003 | 2637.21 | 2572.21 | 2198.21 | 2133.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-12-2025 | during | 18-12-2025 | during | 18-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 158 | 163 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 57 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.52 | 0 | 45.15 | 0 | 45.15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 211.52 | 239 | 361.15 | 314 | 313.65 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 96 | 95 | 95 | 95 | 95 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 206 | 207 | 205 | 205 | 205 | 205 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 468 | 481 | 518 | 518 | 498 | 498
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 24 | 17 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 894 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 330 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 66 | 0 | 74 | 0 | 74 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 789 | 1122 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2023 | 2371 | 2352 | 2278 | 1591.1 | 1517.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 280 | 502 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 55 | 0 | 55 | 55 | 55 | 55 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 732 | 1070 | 1085.32 | 1085.32 | 1025.32 | 1025.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant shutdown as per NLDC requirement.
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.43 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1287.43 | 1792 | 1928.32 | 1928.32 | 1428.32 | 1428.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 47.89 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 203 | 193 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 400 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.12 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 894 | 1421.81 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.44 | 0 | 61 | 1 | 61 | 1 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 92 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1708.45 | 2014.81 | 2869.87 | 2704.87 | 2554.49 | 2389.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 59 | 57 | 57 | 57 | 57 | 57 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 60 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.5 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 143 | 0 | 143.48 | 0 | 143.48 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 237.5 | 167 | 497.68 | 319 | 463.68 | 285
System Total |  |  |  |  | 28823.2 | 28379.108 | 9810.5 | 11055.01 | 19501.58 | 18941.47 | 14298.72 | 13747.61
Forecast Scenario (18-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9260 |  | 0 |  | 9260
|  |  |  | 1:00 | 8680 |  | 0 |  | 8680
|  |  |  | 2:00 | 8290 |  | 0 |  | 8290
|  |  |  | 3:00 | 7990 |  | 0 |  | 7990
|  |  |  | 4:00 | 7620 |  | 0 |  | 7620
|  |  |  | 5:00 | 7670 |  | 0 |  | 7670
|  |  |  | 6:00 | 7930 |  | 0 |  | 7930
|  |  |  | 7:00 | 8560 |  | 0 |  | 8560
|  |  |  | 8:00 | 9450 |  | 0 |  | 9450
|  |  |  | 9:00 | 9710 |  | 0 |  | 9710
|  |  |  | 10:00 | 9510 |  | 0 |  | 9510
|  |  |  | 11:00 | 9640 |  | 0 |  | 9640
|  |  |  | 12:00 | 10130 |  | 0 |  | 10130
|  |  |  | 13:00 | 10610 |  | 0 |  | 10610
|  |  |  | 14:00 | 10230 |  | 0 |  | 10230
|  |  |  | 15:00 | 9610 |  | 0 |  | 9610
|  |  |  | 16:00 | 9530 |  | 0 |  | 9530
|  |  |  | 17:00 | 9770 |  | 0 |  | 9770
|  |  |  | 18:00 | 11230 |  | 0 |  | 11230
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 10920 |  | 0 |  | 10920
|  |  |  | 19:30 | 10700 |  | 0 |  | 10700
|  |  |  | 20:00 | 10630 |  | 0 |  | 10630
|  |  |  | 21:00 | 10480 |  | 0 |  | 10480
|  |  |  | 22:00 | 10050 |  | 0 |  | 10050
|  |  |  | 23:00 | 9580 |  | 0 |  | 9580
Probable Maximum Temperature: |  |  | 27.10°C
Probable Maximum Demand at Day Peak: |  |  | 10130.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11230.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11230.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.08 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:01 hrs on 18-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-12-2025 | [28 empty] | Date: | 17-12-2025 | [28 empty] | Date: | 17-12-2025 | [28 empty] | Date: | 17-12-2025 | [28 empty] | Date: | 17-12-2025 | [17 empty] | Date: | 17-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 300 | 0 | 280 | 51 | 0 | 191 | 0 | 0 | 110 | 0 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 206 | 30 | 30 | 0 | 0 | 22 | 0 | 42 | 30 | 0 | 0 | 94 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 3765.5 | 805 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 18 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 250 | 600 | 0 | 4399 | 8164.5 | 98.77
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 304 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 300 | 0 | 280 | 5 | 0 | 191 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 150 | 0 | 207 | 30 | 30 | 0 | 0 | 16 | 0 | 11 | 20 | 0 | 0 | 94 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 3374.5 | 788 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 17 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 560 | 0 | 4277 | 7651.5 | 98.76
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 304 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 250 | 0 | 240 | 5 | 0 | 196 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 204 | 30 | 30 | 0 | 0 | 8 | 0 | 5 | 20 | 0 | 0 | 94 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 3014.5 | 711 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 17 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 560 | 0 | 4233 | 7247.5 | 98.76
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 305 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 199 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 204 | 30 | 30 | 0 | 0 | 8 | 0 | 5 | 20 | 0 | 0 | 94 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 2695.5 | 711 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 17 | 0 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 555 | 0 | 4223 | 6918.5 | 98.76
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 305 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 197 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 8 | 0 | 5 | 20 | 0 | 0 | 94 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 2705.5 | 617 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 17 | 0 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 560 | 0 | 4133 | 6838.5 | 98.76
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 305 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 8 | 0 | 5 | 20 | 0 | 0 | 95 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 2647.5 | 616 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 17 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 180 | 0 | 250 | 560 | 0 | 4119 | 6766.5 | 98.75
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 305 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 420 | 0 | 0 | 11 | 345 | 0 | 0 | 11 | 0 | 205 | 10 | 0 | 111 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 8 | 0 | 41 | 20 | 0 | 0 | 95 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 3054.5 | 654 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 17 | 0 | 850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 220 | 0 | 250 | 560 | 0 | 4267 | 7321.5 | 98.75
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.17 | 40 | 0 | 26 | 355 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 490 | 1 | 0 | 16 | 350 | 0 | 0 | 51 | 0 | 207 | 10 | 0 | 111 | 0 | 0 | 11 | 0 | 84 | 0 | 3 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 17 | 0 | 42 | 20 | 0 | 0 | 95 | 0 | 0 | 0 | 169 | 0 | 0.78 | 0 | 3356.95 | 700 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 850 | 0 | 17 | 0 | 866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 3 | 0 | 0 | 1.26 | 0 | 0 | 177 | 0 | 0 | 0 | 382 | 0 | 0.12 | 0 | 60 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 4 | 0.01 | 0 | 0 | 55 | 220 | 0 | 300 | 656 | 0 | 4546.59 | 7903.54 | 98.75
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 335 | 0 | 0 | 7 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 9 | 355 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 585 | 5 | 0 | 53 | 360 | 0 | 0 | 51 | 3 | 207 | 20 | 0 | 110 | 0 | 0 | 17 | 0 | 92 | 0 | 17 | 0 | 0 | 0 | 205 | 30 | 30 | 0 | 1 | 17 | 0 | 83 | 30 | 0 | 0 | 95 | 0 | 25 | 0 | 168 | 1 | 11.32 | 0 | 3729.32 | 795 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 950 | 0 | 17 | 0 | 941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.79 | 22 | 0 | 0 | 11.87 | 0 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 1.33 | 0 | 58 | 0 | 8 | 0 | 0 | 0 | 0 | 1.2 | 40 | 0.1 | 0 | 0 | 55 | 220 | 0 | 350 | 844 | 0 | 5191.29 | 8920.61 | 98.75
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 330 | 0 | 0 | 15 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.75 | 40 | 0 | 5 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 575 | 11 | 0 | 66 | 335 | 0 | 0 | 51 | 11 | 194 | 39 | 0 | 109 | 0 | 0 | 18 | 0 | 106 | 0 | 31 | 0 | 0 | 0 | 205 | 30 | 30 | 0 | 7 | 17 | 0 | 83 | 30 | 0 | 0 | 96 | 0 | 25 | 0 | 165 | 1 | 25.44 | 0 | 3813.69 | 889 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 977 | 0 | 17 | 0 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.43 | 52 | 0 | 0 | 32.49 | 0 | 0 | 193 | 0 | 0 | 0 | 401 | 0 | 3.02 | 0 | 59 | 0 | 17 | 0 | 0 | 0 | 0 | 3.1 | 97 | 0.24 | 0 | 0 | 55 | 220 | 0 | 350 | 890 | 0 | 5496.28 | 9309.97 | 98.74
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 335 | 0 | 0 | 21 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 40 | 0 | 7 | 354 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 500 | 15 | 0 | 80 | 330 | 53 | 0 | 51 | 22 | 192 | 39 | 0 | 108 | 0 | 0 | 0 | 0 | 112 | 0 | 48 | 0 | 0 | 0 | 205 | 30 | 30 | 0 | 9 | 17 | 0 | 81 | 30 | 0 | 0 | 96 | 0 | 8 | 0 | 165 | 2 | 36.27 | 0 | 3827.3 | 890 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 877 | 0 | 28 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.38 | 73 | 0 | 0 | 47 | 0 | 0 | 191 | 0 | 0 | 0 | 405 | 0 | 4.29 | 0 | 58 | 0 | 23 | 0 | 0 | 0 | 0 | 4.5 | 139 | 0.36 | 0 | 0 | 55 | 220 | 0 | 350 | 750 | 0 | 5281.53 | 9108.83 | 98.74
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 335 | 0 | 0 | 25 | 0 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2.99 | 40 | 0 | 10 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 500 | 17 | 0 | 81 | 345 | 53 | 45 | 51 | 30 | 198 | 39 | 0 | 105 | 0 | 0 | 19 | 0 | 118 | 0 | 59 | 0 | 0 | 0 | 206 | 30 | 30 | 0 | 10 | 12 | 0 | 83 | 30 | 0 | 0 | 96 | 0 | 8 | 0 | 161 | 2 | 42.31 | 0 | 4089.8 | 890 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 759 | 0 | 20 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.69 | 88 | 0 | 0 | 53.18 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 4.83 | 0 | 59 | 0 | 28 | 0 | 0 | 0 | 0 | 5.2 | 146 | 0.44 | 0 | 0 | 55 | 220 | 0 | 280 | 700 | 0 | 5118.34 | 9208.14 | 98.74
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 334 | 0 | 0 | 27 | 0 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.1 | 40 | 0 | 10 | 354 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 580 | 17 | 0 | 93 | 393 | 140 | 80 | 51 | 30 | 199 | 39 | 0 | 104 | 0 | 0 | 19 | 0 | 118 | 0 | 47 | 0 | 0 | 0 | 206 | 30 | 30 | 0 | 11 | 12 | 0 | 83 | 0 | 0 | 0 | 96 | 0 | 8 | 0 | 158 | 2 | 43.52 | 0 | 4554.12 | 894 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 789 | 0 | 24 | 0 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.89 | 92 | 0 | 0 | 52.44 | 0 | 0 | 203 | 0 | 0 | 0 | 414 | 0 | 5.12 | 0 | 59 | 0 | 30 | 0 | 0 | 0 | 0 | 5.5 | 143 | 0.43 | 0 | 0 | 55 | 220 | 0 | 280 | 732 | 0 | 5256.38 | 9810.5 | 98.73
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 55 | 30 | 0 | 0 | 0 | 565 | 0 | 0 | 335 | 0 | 0 | 26 | 0 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 13 | 354 | 0 | 0 | 3 | 0 | 10 | 222 | 0 | 0 | 0 | 612 | 16 | 10 | 46 | 245 | 173 | 33 | 51 | 0 | 142 | 0 | 0 | 104 | 21 | 0 | 19 | 0 | 134 | 0 | 36 | 0 | 0 | 0 | 206 | 30 | 30 | 0 | 10 | 17 | 0 | 83 | 0 | 0 | 0 | 96 | 0 | 54 | 19 | 159 | 2 | 30.7 | 0 | 4539.2 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 953 | 0 | 20 | 0 | 1019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.63 | 97 | 0 | 0 | 47.54 | 0 | 0 | 208 | 0 | 0 | 0 | 402 | 0 | 1.05 | 0 | 57 | 0 | 26 | 0 | 0 | 0 | 0 | 5.3 | 136 | 0.42 | 0 | 0 | 55 | 220 | 0 | 400 | 905 | 0 | 5807.94 | 10347.14 | 98.73
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 27 | 0 | 6 | 0 | 15 | 0 | 55 | 17 | 0 | 0 | 0 | 455 | 0 | 0 | 270 | 0 | 0 | 22 | 0 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 15 | 354 | 0 | 0 | 21 | 0 | 22 | 222 | 0 | 0 | 0 | 612 | 13 | 12 | 0 | 215 | 173 | 33 | 51 | 0 | 140 | 0 | 0 | 104 | 17 | 0 | 19 | 0 | 132 | 0 | 50 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 9 | 17 | 0 | 83 | 0 | 0 | 0 | 96 | 0 | 16 | 8 | 158 | 1 | 35 | 0 | 4211.5 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 979 | 0 | 18 | 0 | 1033.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.85 | 78 | 0 | 0 | 39.09 | 0 | 0 | 172 | 0 | 0 | 0 | 347 | 0 | 1.55 | 0 | 57 | 0 | 22 | 0 | 0 | 0 | 0 | 4.4 | 133 | 0.33 | 0 | 0 | 55 | 180 | 0 | 400 | 900 | 0 | 5651.15 | 9862.65 | 98.73
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 55 | 17 | 0 | 0 | 0 | 465 | 0 | 0 | 332 | 0 | 0 | 15 | 0 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.33 | 40 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 612 | 5 | 0 | 0 | 215 | 173 | 33 | 51 | 0 | 140 | 0 | 0 | 104 | 0 | 0 | 19 | 0 | 116 | 0 | 33 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 5 | 17 | 0 | 80 | 0 | 0 | 0 | 96 | 0 | 16 | 8 | 158 | 1 | 24.88 | 0 | 4094.71 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 994 | 0 | 17 | 0 | 874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.19 | 50 | 0 | 0 | 24.44 | 0 | 0 | 174 | 0 | 0 | 0 | 365 | 0 | 2.59 | 0 | 57 | 0 | 17 | 0 | 0 | 0 | 0 | 3 | 91 | 0.2 | 0 | 0 | 55 | 180 | 0 | 300 | 890 | 0 | 5298.42 | 9393.13 | 98.73
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 330 | 0 | 0 | 6 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.62 | 40 | 0 | 11 | 354 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 612 | 4 | 0 | 0 | 215 | 173 | 18 | 51 | 0 | 140 | 0 | 0 | 105 | 0 | 0 | 19 | 0 | 112 | 0 | 14 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 2 | 17 | 0 | 80 | 0 | 0 | 0 | 96 | 0 | 19 | 18 | 158 | 0 | 8.93 | 0 | 4115.55 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1009 | 0 | 17 | 0 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.77 | 19 | 0 | 0 | 9.35 | 0 | 0 | 178 | 0 | 0 | 0 | 380 | 0 | 0.59 | 0 | 57 | 0 | 7 | 0 | 0 | 0 | 0 | 1.4 | 37 | 0.73 | 0 | 0 | 0 | 220 | 0 | 300 | 902 | 0 | 5176.84 | 9292.39 | 98.72
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 21.4 | 0 | 44 | 0 | 120 | 0 | 35 | 147 | 0 | 0 | 0 | 495 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 25 | 0.02 | 40 | 0 | 16 | 355 | 0 | 0 | 9 | 0 | 26 | 225 | 0 | 0 | 0 | 612 | 0 | 38 | 0 | 215 | 173 | 18 | 51 | 0 | 140 | 0 | 0 | 106 | 41 | 0 | 19 | 0 | 122 | 0 | 1 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 96 | 0 | 57 | 18 | 162 | 0 | 0.38 | 0 | 4560.3 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1050 | 0 | 17 | 0 | 953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 1 | 0 | 0 | 0.74 | 0 | 0 | 175 | 0 | 0 | 0 | 328 | 0 | 0.08 | 0 | 57 | 35 | 1 | 30 | 0 | 0 | 0 | 0.1 | 3 | 0 | 0 | 0 | 0 | 220 | 0 | 300 | 1004 | 0 | 5328.74 | 9889.04 | 98.72
18:00 | 0 | 17 | 5 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 65 | 0 | 95 | 0 | 55 | 153 | 0 | 0 | 0 | 515 | 0 | 17 | 333 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 20 | 354 | 0 | 0 | 19 | 0 | 66 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 250 | 0 | 60 | 51 | 0 | 204 | 0 | 0 | 106 | 51 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 205 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 96 | 0 | 57 | 19 | 162 | 0 | 0 | 0 | 4627 | 901 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 17 | 0 | 1283.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 57 | 35 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 500 | 1071 | 0 | 6157.47 | 10784.47 | 98.72
19:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 94 | 0 | 45 | 0 | 35 | 155 | 0 | 0 | 0 | 550 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 20.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 17 | 355 | 0 | 0 | 3 | 0 | 64 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 393 | 0 | 65 | 51 | 0 | 193 | 0 | 0 | 108 | 51 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 18 | 96 | 0 | 57 | 19 | 163 | 0 | 0 | 0 | 4710.2 | 902 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 17 | 0 | 1421.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 57 | 50 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 502 | 1070 | 0 | 6344.81 | 11055.01 | 98.72
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 116 | 0 | 45 | 0 | 35 | 146 | 0 | 0 | 0 | 550 | 0 | 17 | 331 | 0 | 0 | 0 | 0 | 20.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 40 | 0 | 19 | 354 | 0 | 0 | 0 | 0 | 62 | 227 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 393 | 0 | 100 | 51 | 0 | 195 | 0 | 0 | 108 | 49 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 18 | 96 | 0 | 57 | 19 | 164 | 0 | 0 | 0 | 4717.2 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 17 | 0 | 1420.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 57 | 50 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 400 | 1060 | 0 | 6111.46 | 10828.66 | 98.72
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 35 | 147 | 0 | 0 | 0 | 545 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 19 | 354 | 0 | 0 | 0 | 0 | 34 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 393 | 0 | 130 | 51 | 0 | 198 | 0 | 0 | 108 | 49 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 18 | 96 | 0 | 57 | 19 | 163 | 0 | 0 | 0 | 4625.5 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 12 | 0 | 1420.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 58 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 400 | 1060 | 0 | 6073.72 | 10699.22 | 98.71
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 550 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 22 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 393 | 0 | 180 | 51 | 0 | 199 | 0 | 0 | 109 | 50 | 0 | 14 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 207 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 57 | 19 | 155 | 0 | 0 | 0 | 4562.5 | 900 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1117 | 0 | 2 | 0 | 1332.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 400 | 1068 | 0 | 5956.12 | 10518.62 | 98.71
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 393 | 0 | 180 | 51 | 0 | 190 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 204 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 16 | 19 | 150 | 0 | 0 | 0 | 4208.5 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074 | 0 | 6 | 0 | 1323.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 319 | 1064 | 0 | 5819.17 | 10027.67 | 98.71
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 340 | 0 | 150 | 51 | 0 | 195 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 204 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 16 | 19 | 149 | 0 | 0 | 0 | 4105.5 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 2 | 0 | 1222.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 284 | 999 | 0 | 5476.49 | 9581.99 | 98.71
Total KWH | 0 | 36480 | 15360 | 0 | 0 | 0 | 0 | 0 | 8593200 | 0 | 0 | 78840 | 0 | 390240 | 0 | 357545 | 0 | 500176 | 849600 | 0 | 0 | 0 | 7495642 | 0 | 49962 | 7843003 | 0 | 0 | 164099 | 0 | 419400 | 527400 | 0 | 0 | 0 | 0 | 0 | 0 | 46560 | 0 | 0 | 0 | 0 | 253440 | 13563 | 968000 | 0 | 403200 | 8276363.64 | 0 | 0 | 95040 | 0 | 316981 | 5289600 | 0 | 0 | 0 | 12267271 | 105300 | 160581 | 451636 | 7536000 | 1157500 | 1846000 | 1015856 | 104640 | 4625000 | 191952 | 0 | 2346866 | 420000 | 0 | 401960 | 0 | 2473920 | 0 | 356500 | 0 | 116790 | 0 | 5043000 | 717000 | 719880 | 0 | 6428 | 350112 | 0 | 1454400 | 0 | 0 | 136000 | 2294950 | 0 | 530400 | 187200 | 3733440 | 11200 | 267410 | 0 | 94012886.64 | 20031272 | 6538464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393120 | 22305460 | 0 | 368000 | 0 | 23989091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281876 | 577340 | 0 | 0 | 302256 | 0 | 0 | 4675455 | 0 | 0 | 0 | 9261890 | 0 | 27000 | 0 | 1344872 | 193668 | 180989 | 147801 | 0 | 0 | 0 | 33491.88 | 977760 | 2647 | 0 | 0 | 849000 | 5325257 | 0 | 7868319 | 20477090.91 | 0 | 126152119.79 | 220165006.43

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9810.5 | MW | 12:00 Hr. | Energy Generated |  |  | 220.165 |  | MKWHr.
| Day Peak Demand |  |  | 9810.5 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11055.01 | MW | 19:00 Hr. | Energy Demand |  |  | 220.165 |  | MKWHr.
| Evening Peak Demand |  |  | 11055.01 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.1 |  | °C
| Minimum Generation of the Day |  |  | 6766.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 720.07 |  | MMCFD
| Maximum Generation of the Day |  |  | 11055.01 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.4407 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.8786 | 0 | 2.2782 | 0 | 0 | 0.1641 | 0 | 0 | 27.3209 | Gas | 91.8325 | Gas | 318763905
| Chattogram Zone |  |  | 5.6928 | 20.5436 | 0.66546 | 0 | 0.968 | 0.11886 | 0 | 0.04656 | 28.0353 | Coal | 72.5394 | Coal | 465696852.6401
| Cumilla Zone |  |  | 19.6774 | 0 | 0.58058 | 0 | 0 | 0.3565 | 2.4739 | 0 | 23.0884 | HFO | 4.5833 | HFO | 75574295.92
| Mymensingh Zone |  |  | 3.7334 | 0 | 0.7176 | 0 | 0 | 0.27861 | 0 | 0 | 4.7297 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 10.8321 | 0 | 0 | 0 | 0 | 0.006428 | 0 | 0 | 10.8386 | Hydro | 0.968 | Hydro | 96800
| Khulna Zone |  |  | 6.9065 | 22.3055 | 0 | 0 | 0 | 0.39312 | 20.0313 | 0 | 49.6363 | Solar | 3.701 | Solar | 59605637.8148
| Barishal Zone |  |  | 6.1743 | 28.3454 | 0 | 0 | 0 | 0.002647 | 0 | 0 | 34.5223 | Import | 46.4943 | Import | 277436487.41
| Rajshahi Zone |  |  | 13.9373 | 0 | 0 | 0 | 0 | 1.1885 | 23.9891 | 0 | 39.1149 | Wind | 0.04656 | Wind | 684897.6
| Rangpur Zone |  |  | 0 | 1.3449 | 0.34147 | 0 | 0 | 1.1922 | 0 | 0 | 2.8786
| Total |  |  | 91.8325 | 72.5394 | 4.5833 | 0 | 0.968 | 3.701 | 46.4943 | 0.04656 | 220.165
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 318763905 |  | Hydro | 96800
|  |  |  | Coal | 465696852.6401 |  | Solar | 59605637.8148
|  |  |  | HFO | 75574295.92 |  | Import | 277436487.41
|  |  |  | HSD | 0 |  | Wind | 684897.6
[5 empty] | Total: | 119,78,58,876 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.0313 | Peak Hr Flow | 902.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44946036.37 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.9891 | Peak Hr Flow | 1421.81 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2913 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4739 | Peak Hr Flow | 122.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2913 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.4943 | Peak Hr Flow | 2445.81 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4018
|  |  |  | Chattogram |  | 0 |  | 1172
|  |  |  | Cumilla |  | 0 |  | 937
|  |  |  | Mymensingh |  | 0 |  | 840
|  |  |  | Sylhet |  | 0 |  | 388
|  |  |  | Khulna |  | 0 |  | 1214
|  |  |  | Barishal |  | 0 |  | 311
|  |  |  | Rajshahi |  | 0 |  | 978
|  |  |  | Rangpur |  | 0 |  | 709
|  |  |  | Total |  | 0 |  | 10567
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 17:48 | Kachua 230/132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance
| 08:01 | 17:48 | Kachua 230/132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance
| 08:04 | 17:18 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to Yearly maintenance. | [7 empty] | 3.0MW load
interrup.
| 08:04 | 17:18 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to Yearly maintenance. | [7 empty] | 3.0MW load
interrup.
| 08:09 | 17:56 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) LT Scheduled S/D Due to Annual
Maintenance
| 08:10 | 17:55 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Scheduled S/D Due to Annual
Maintenance
| 08:15 | 17:19 | Bhulta 400/230kV S/S 400kV Bus-2 Scheduled S/D
| 08:19 | 16:19 | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to For 33 kv yearly maintainence work.
| 08:20 | 16:19 | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to For 33 kv yearly maintenance Work.
| 08:21 | 15:44 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to Annual
maintenance and from Khulna(S) 230/132kV end Due to Annual maintenance Work
| 08:24 | 17:49 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance.
| 08:25 | 14:26 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to Annual Maintenance Work
| 08:26 | 15:35 | Shahmirpur 132/33kV S/S 406T HT Scheduled S/D Due to Annual Maintenance
| 08:26 | 15:36 | Shahmirpur 132/33kV S/S 406T LT Scheduled S/D Due to Annual Maintenacne
| 08:26 | 15:07 | Bakulia-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance
| 08:27 | 11:46 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D Due to Annual Maintenance.
| 08:28 | 11:46 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D Due to Annual Maintenance.
| 08:31 | 15:40 | Mahasthangar-Palashbari 132kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due to
Annual Maintenance work.
| 08:32 | 16:51 | Rahanpur 132/33kV S/S TR-1 404T LT Scheduled S/D Due to Annual Maintenance.
| 08:35 | 16:35 | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to
Annual Maintenance and from Shahjibazar 132/33kV end Due to Shutdown for annual
maitenance
| 08:35 | 16:51 | Rahanpur 132/33kV S/S TR-1 404T HT Scheduled S/D Due to Annual Maintenance.
| 08:41 | 15:39 | Mahasthangar-Palashbari 132kV Ckt-1 Scheduled S/D from Palashbari 132/33kV end Due to
Annual maintenance
| 08:42 | 17:03 | Bhulta-Rampura 230 kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance and from Bhulta 400/230kVend.
| 08:48 | 15:46 | Sirajganj 132/33kV S/S T3-(435) LT Scheduled S/D Due to Annual Maintenance
| 08:48 | 15:45 | Sirajganj 132/33kV S/S T3-(435) HT Scheduled S/D Due to annual maintenance
| 09:01 | 14:26 | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to Annual Maintenance Work
| 09:07 | 13:33 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to Annual maintenance
| 09:09 | 16:58 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 LT Scheduled S/D Due to Annual
Maintenance(testing).
| 09:09 | 16:58 | Cumilla(N) 230/132/33kV S/S 230KV ATR-01 HT Scheduled S/D
| 09:18 | 13:25 | Jashore 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintance
| 09:18 | 13:25 | Jashore 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintance
| 09:24 |  | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual maintenance work.
| 09:24 | 15:29 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maintenance at Bibiyana substation end.
| 09:25 | 13:26 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to Annual maintenance
|  | 09:30 | Saidpur 132/33kV S/S BUS B is restored.
| 09:31 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 09:33 | 16:32 | Bogura 400/230kV S/S ATR-01 LT Scheduled S/D Due to Annual Maintenance.
| 09:34 | 16:32 | Bogura 400/230kV S/S ATR-01 HT Scheduled S/D Due to Annual Maintenance.
| 09:36 | 16:57 | BIPTC S/S 10CF25 Scheduled S/D Due to Annual Maintenance
| 09:38 |  | Brahmanbaria 132/33kV S/S 403T LT Project Work S/D
| 09:38 |  | Brahmanbaria 132/33kV S/S 403T HT Project Work S/D
| 09:39 |  | Hathazari-Kaptai 132kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
Maintenance (Deadline checking)
| 09:43 | 17:12 | Bhulta-Narsingdi 132 kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to For
annual maintenance work.
| 09:44 |  | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to Am
| 09:45 | 17:11 | Haripur-Narsingdi 132kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to For
annul maintenance purpose.
| 09:49 | 16:18 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D
| 09:49 | 16:17 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D
| 10:11 | 23:51 | BIPTC S/S Baharampur-1 Scheduled S/D Due to Shutdown is taken from Baharampur end.
| 10:16 | 15:43 | Ghatail 132/33kV S/S T-2 LT Scheduled S/D Due to annual maintenance
| 10:17 | 15:42 | Ghatail 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance
| 10:45 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 10:58 | 15:13 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Annual
maintenance.
|  | 11:05 | Saidpur 132/33kV S/S TR-5 (434T) HT is restored.
|  | 11:07 | Saidpur 132/33kV S/S TR-5 (434T) LT is restored.
| 11:49 | 13:30 | Bhaluka 132/33kV S/S Bus A Scheduled S/D Due to Annual maintenance
| 11:59 | 17:15 | Kaliakoir 400/230/132kV S/S 230kV Bus 2 Scheduled S/D Due to Annual Maintenance
| 12:00 |  | Day Peak Generation: 9807 MW.
| 12:10 | 14:12 | Saidpur 132/33kV S/S TR-01 HT Scheduled S/D Due to Project work.
| 12:15 | 13:55 | Saidpur 132/33kV S/S BUS A Scheduled S/D Due to Project Work.
| 14:41 | 16:35 | Bogura 230/132kV S/S T-03 LT Forced S/D
| 14:41 | 16:34 | Bogura 230/132kV S/S T-03 HT Forced S/D
| 15:15 | 16:35 | Saidpur 132/33kV S/S BUS B Scheduled S/D Due to Project work.
| 15:20 | 16:30 | Saidpur 132/33kV S/S TR-5 (434T) HT Scheduled S/D Due to Project work.
| 15:21 | 16:31 | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to Project work.
| 15:28 |  | Bhola 225MW CCPP tripped.
|  | 15:43 | Ghatail 132/33kV S/S T-2 LT is restored.
|  | 15:47 | Hasnabad-Keraniganj 230kV Ckt-2 is restored.
|  | 15:47 | Hasnabad-Keraniganj 230kV Ckt-2 is restored.
| 16:00 |  | P Sadipur 230/132kv T1 & T2 - S/D.
| 16:08 |  | Bp - P Sadipur 230kv Ckt 1 & 2 S/D.
| 16:34 |  | BP P/P 230KV Bus 2 S/D.
|  | 16:40 | Barishal(N)-Madaripur 132 kV Ckt-1 is restored.
| 17:38 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 18:53 |  | Meghnaghat 230/132kV S/S Meghnaghat-ST (MPL) Scheduled S/D Due to DUE TO RADE HOT AT DS
FINGER OF DS 839S, SHUTDOWN OF BUS 2 SIDE CB 838B. NO POWER INTERRUPTION WILL HAPPEN FOR
THIS BREAKER SHITUDOWN.
| 19:00 |  | Evening Peak Generation: 11054 MW.
| 05:00 |  | Minimum Generation is 7537 MW.
| 07:38 |  | Mahasthangar-Palashbari 132kV Ckt-1 Scheduled S/D from Palashbari 132/33kV end Due to
Annual Maintenance
| 07:41 |  | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Siddhirganj 132/33kV end Due to Relay
installation and from Haripur 230/132kV end Due to Shutdown taken by Siddhirganj S/S.
| 07:49 |  | Shyampur 230/132kV S/S Auto TR-1 HT Tripped showing Differential trip R,Y phase relays
Due to Differential trip R,Y phase
| 07:51 |  | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8593200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7843003 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 78840 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 500176 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 49962 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.2 | 419400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 15360 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 357545 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 94 | 390240 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 36480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 155 | 849600 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 164099 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 550 | 7495642 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1618.2 | 27320947
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 105300 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 3 | 95040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 968000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5289600 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 64 | 316981 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 403200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13563 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 253440 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12267271 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 46560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 355 | 8276363.64 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1369 | 28035318.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 193 | 4625000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 1157500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 65 | 1846000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 7536000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 191952 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 104640 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 451636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1015856 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 160581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2346866 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 420000 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 122 | 2473920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 401960 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 356500 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1003 | 23088411
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 163 | 3733440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 187200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 530400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 267410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 239 | 4729650
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 6428 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719880 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1454400 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2294950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 136000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 350112 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 116790 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 207 | 5043000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Plant shutdown due to maintenance work
Sylhet Area Total |  |  |  |  | 2325 | 481 | 10838560
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 17 | 368000 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 20031272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 330 | 6538464 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 393120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1122 | 22305460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2371 | 49636316
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 502 | 7868319 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 849000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1070 | 20477090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5325257 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Plant shutdown as per NLDC requirement.
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2647 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1792 | 34522313.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 281876 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4675455 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 400 | 9261890 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1421.81 | 23989091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 302256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 577340 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2014.81 | 39114908
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1344872 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 60 | 147801 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33491.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 193668 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 180989 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 977760 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 167 | 2878581.88
Eastern Grid Total |  |  |  |  | 17395.105 | 4710.2 | 94012886.64
Western Grid Total |  |  |  |  | 10984.003 | 6344.81 | 126152119.79
National Grid Total |  |  |  |  | 28379.108 | 11055.01 | 220165006.43
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-12-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7355.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3212 | MW
i) Dhaka area |  |  | 4018.11 |  | MW | i) Khulna area |  |  |  | 1214 | MW
ii) Chattogram area |  |  | 1172.2 |  | MW | ii) Barishal area |  |  |  | 311 | MW
iii) Cumilla area |  |  | 937 |  | MW | iii) Rajshahi area |  |  |  | 978 | MW
iv) Mymensingh area |  |  | 840 |  | MW | iv) Rangpur area |  |  |  | 709 | MW
v) Sylhet area |  |  | 388 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10567.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 57 | 13:00 | 133 | Niamatpur | 50 | 08:00
2 | AKSML | 148 | 02:00 | 68 | Ishurdi | 50 | 18:00 | 134 | Noapara | 37 | 18:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jaldhaka | 59 | 18:00 | 135 | PHP | 8 | 11:00
4 | Agargaon | 87 | 13:00 | 70 | Jamalpur | 88 | 18:30 | 136 | Pabna | 72 | 18:30
5 | Agrabad | 44 | 18:00 | 71 | Jashore | 103 | 13:00 | 137 | Palashbari | 86 | 18:00
6 | Amnura | 26 | 08:00 | 72 | Jhenaidah | 95 | 18:00 | 138 | Panchagarh | 46 | 18:30
7 | Ashuganj | 57 | 12:00 | 73 | Joydebpur | 96 | 18:00 | 139 | Patiya | 6.4 | 18:00
8 | BSRM | 190 | 06:00 | 74 | Joypurhat | 41 | 18:30 | 140 | Patuakhali | 47.5 | 21:00
9 | Bagerhat | 64 | 18:00 | 75 | Juldah | 12 | 08:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 63 | 19:00 | 76 | KSRM | 11 | 07:00 | 142 | Postogola | 38 | 13:00
11 | Bakulia | 65 | 13:00 | 77 | Kabirpur | 176 | 12:00 | 143 | Purbachal | 26 | 13:00
12 | Banani | 46.8 | 13:00 | 78 | Kachua | 65 | 18:00 | 144 | Purbasadipur | 112 | 13:00
13 | Bangabhaban | 14 | 10:00 | 79 | Kallyanpur | 75 | 12:00 | 145 | Rahanpur | 22 | 08:00
14 | Barapukuria | 49 | 12:00 | 80 | Kalurghat | 30 | 10:00 | 146 | Rahim | 25 | 13:00
15 | Barguna | 10 | 18:30 | 81 | Kamrangirchar | 60 | 13:00 | 147 | Rajbari | 60 | 18:00
16 | Barishal | 86 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 101 | 18:00
17 | Barishal-230 | 64 | 18:00 | 83 | Kasba | 22 | 14:00 | 149 | Rajshahi | 79 | 13:00
18 | Baroaulia | 54 | 12:00 | 84 | Kazla | 81 | 18:30 | 150 | Rajshahi-230 | 60 | 13:00
19 | Baroirhat | 49 | 13:00 | 85 | Keranigonj | 64 | 12:00 | 151 | Ramganj | 66 | 18:00
20 | Bashundhara | 138 | 13:00 | 86 | Khagrachori | 22 | 18:00 | 152 | Rampur | 27 | 14:00
21 | BashundharaCement | 2 | 23:00 | 87 | Khulna | 52 | 13:00 | 153 | Rangamati | 12 | 18:00
22 | Beanibazar | 48 | 20:00 | 88 | Khulshi | 172 | 18:30 | 154 | Rangpur | 108 | 18:00
23 | Benapole | 38 | 08:00 | 89 | Kishoreganj | 84 | 20:00 | 155 | Ruppur | 3 | 10:00
24 | Bhaluka | 121 | 18:00 | 90 | Kodda | 252 | 16:00 | 156 | SSM | 8 | 23:00
25 | Bhandaria | 36 | 20:00 | 91 | Kulaura | 31 | 18:00 | 157 | Saidpur | 83 | 18:30
26 | Bhangura | 23 | 13:00 | 92 | Kurigram | 54 | 16:00 | 158 | Satkhira | 86 | 18:30
27 | Bheramara(GK) | 42 | 18:00 | 93 | Kushtia | 114 | 18:00 | 159 | Satmasjid | 75 | 14:00
28 | Bhulta | 184 | 19:00 | 94 | Laksam | 21 | 20:00 | 160 | Savar | 155 | 18:00
29 | Bog-Sherpur | 56 | 09:00 | 95 | Lakshmipur | 24 | 19:30 | 161 | SevenRings | 11.28 | 16:00
30 | Bogura | 110 | 18:30 | 96 | Lalbag | 45 | 21:00 | 162 | ShahCement | 31 | 23:00
31 | Borhanuddin | 63 | 21:00 | 97 | Lalmonirhat | 45 | 18:00 | 163 | Shahjadpur | 58 | 18:00
32 | Brahmanbaria | 86 | 19:00 | 98 | MI_Cement | 16.4 | 23:00 | 164 | Shahjibazar | 81 | 18:30
33 | Cantonment | 74 | 13:00 | 99 | Madanganj | 26 | 13:00 | 165 | Shahmirpur | 41 | 16:00
34 | Chandina | 8 | 21:00 | 100 | Madaripur | 70 | 13:00 | 166 | Shariatpur | 54 | 20:00
35 | Chandpur | 56 | 13:00 | 101 | Madartek | 55 | 14:00 | 167 | Sherpur | 112 | 18:00
36 | Chandraghona | 25 | 19:00 | 102 | Madunaghat | 38 | 13:00 | 168 | Shikalbaha | 15.5 | 08:00
37 | Chapai | 45 | 13:00 | 103 | Magura | 46 | 18:00 | 169 | Shitalakhya | 62 | 12:00
38 | Charsaidpur | 26 | 16:00 | 104 | Mahasthangarh | 54 | 08:00 | 170 | Sholosohor | 33 | 12:00
39 | Chauddagram | 46 | 18:30 | 105 | Maijdee | 29 | 21:00 | 171 | Shyampur | 132 | 13:00
40 | Chhatak | 22 | 22:00 | 106 | Manikganj | 84 | 18:00 | 172 | Siddhirganj | 95 | 18:00
41 | Chowmuhani | 98 | 18:00 | 107 | Maniknagar | 51 | 13:00 | 173 | Sirajganj | 82 | 18:30
42 | Chuadanga | 73 | 13:00 | 108 | Matarbari | 37 | 18:00 | 174 | Sonargaon | 134 | 19:00
43 | Coxsbazar | 101 | 18:00 | 109 | Matuail | 58 | 13:00 | 175 | Sreemongol | 55 | 18:30
44 | Cumilla(N) | 90 | 13:00 | 110 | Metrorail_Motijheel | 24 | 19:00 | 176 | Sreepur | 90 | 18:30
45 | Cumilla(S) | 133 | 13:00 | 111 | Metrorail_Uttara | 6 | 15:00 | 177 | Srinagar | 30.14 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Millgate | 68 | 12:00 | 178 | Sunamganj | 41 | 18:00
47 | Daudkandi | 114 | 20:00 | 113 | Mirpur | 106.5 | 13:00 | 179 | Sylhet | 31 | 00:00
48 | DhakaUniversity | 60 | 13:00 | 114 | Mirsorai | 34 | 16:00 | 180 | Sylhet-132 | 104 | 18:00
49 | Dhamrai | 92 | 17:00 | 115 | Mirzapur | 37 | 18:00 | 181 | TK | 17 | 18:00
50 | Dhanmondi | 80 | 13:00 | 116 | Mithapukur | 46 | 18:00 | 182 | Tangail | 120 | 18:00
51 | Dohazari | 64 | 20:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 15 | 18:00
52 | Faridpur | 111 | 18:30 | 118 | Mogbazar | 64.7 | 13:00 | 184 | Tasnim | 29 | 12:00
53 | Fatullah | 75 | 12:00 | 119 | Mongla | 37 | 18:00 | 185 | Thakurgaon | 84 | 18:30
54 | Fenchuganj | 24 | 14:00 | 120 | Motijheel | 30 | 18:00 | 186 | Tongi | 88 | 10:00
55 | Feni | 88 | 17:00 | 121 | Muktagacha | 27 | 13:00 | 187 | Ullahpara | 26 | 18:30
56 | GPH | 86 | 16:00 | 122 | Munshiganj | 70 | 21:00 | 188 | Ullon | 51 | 14:00
57 | Ghatail | 60 | 18:00 | 123 | Muradnagar | 26 | 18:30 | 189 | Uttara | 56 | 13:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 133 | 18:30 | 190 | UttaraNew | 14 | 13:00
59 | Ghorashal-230 | 73 | 19:30 | 125 | Naogaon | 88 | 13:00 | 191 | Zigatola | 54 | 13:00
60 | Goalpara | 27 | 13:00 | 126 | Narail | 42 | 18:00
61 | Gollamari | 68 | 13:00 | 127 | Narinda | 56 | 13:00
62 | Gopalganj | 76 | 18:00 | 128 | Narshingdi | 143 | 18:30
63 | Gulshan | 80 | 13:00 | 129 | Natore | 98 | 18:00
64 | Halishahar | 47 | 10:00 | 130 | Nawabganj | 36.2 | 13:00
65 | HaripurSBU | 110 | 09:00 | 131 | Netrakona | 99 | 08:00
66 | Hasnabad | 66 | 12:00 | 132 | New | 69 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8164.5 | 0 |  | 8164.5
1:00 | 7651.5 | 0 |  | 7651.5
2:00 | 7247.5 | 0 |  | 7247.5
3:00 | 6918.5 | 0 |  | 6918.5
4:00 | 6838.5 | 0 |  | 6838.5
5:00 | 6766.5 | 0 |  | 6766.5
6:00 | 7321.5 | 0 |  | 7321.5
7:00 | 7903.54 | 0 |  | 7903.54
8:00 | 8920.61 | 0 |  | 8920.61
9:00 | 9309.97 | 0 |  | 9309.97
10:00 | 9108.83 | 0 |  | 9108.83
11:00 | 9208.14 | 0 |  | 9208.14
12:00 | 9810.5 | 0 |  | 9810.5
13:00 | 10347.14 | 0 |  | 10347.14
14:00 | 9862.65 | 0 |  | 9862.65
15:00 | 9393.13 | 0 |  | 9393.13
16:00 | 9292.39 | 0 |  | 9292.39
17:00 | 9889.04 | 0 |  | 9889.04
18:00 | 10784.47 | 0 |  | 10784.47
19:00 | 11055.01 | 0 |  | 11055.01
19:30 | 10828.66 | 0 |  | 10828.66
20:00 | 10699.22 | 0 |  | 10699.22
21:00 | 10518.62 | 0 |  | 10518.62
22:00 | 10027.67 | 0 |  | 10027.67
23:00 | 9581.99 | 0 |  | 9581.99
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 3765.5 | 4399 | 8164.5 | DAILY GENERATION CURVE
00:30 | 3570 | 4338 | 7908
01:00 | 3374.5 | 4277 | 7651.5 | 17-12-2025
01:30 | 3194.5 | 4255 | 7449.5
02:00 | 3014.5 | 4233 | 7247.5
02:30 | 2855 | 4228 | 7083
03:00 | 2695.5 | 4223 | 6918.5
03:30 | 2700.5 | 4178 | 6878.5
04:00 | 2705.5 | 4133 | 6838.5
04:30 | 2676.5 | 4126 | 6802.5
05:00 | 2647.5 | 4119 | 6766.5
05:30 | 2851 | 4193 | 7044
06:00 | 3054.5 | 4267 | 7321.5
06:30 | 3205.725 | 4406.795 | 7612.52
07:00 | 3356.95 | 4546.59 | 7903.54
07:30 | 3543.135 | 4868.94 | 8412.075
08:00 | 3729.32 | 5191.29 | 8920.61
08:30 | 3771.505 | 5343.785 | 9115.29
09:00 | 3813.69 | 5496.28 | 9309.97
09:30 | 3820.495 | 5388.905 | 9209.4
10:00 | 3827.3 | 5281.53 | 9108.83
10:30 | 3958.55 | 5199.935 | 9158.485
11:00 | 4089.8 | 5118.34 | 9208.14
11:30 | 4321.96 | 5187.36 | 9509.32
12:00 | 4554.12 | 5256.38 | 9810.5
12:30 | 4546.66 | 5532.16 | 10078.82
13:00 | 4539.2 | 5807.94 | 10347.14
13:30 | 4375.35 | 5729.545 | 10104.895
14:00 | 4211.5 | 5651.15 | 9862.65
14:30 | 4153.105 | 5474.785 | 9627.89
15:00 | 4094.71 | 5298.42 | 9393.13
15:30 | 4105.13 | 5237.63 | 9342.76
16:00 | 4115.55 | 5176.84 | 9292.39
16:30 | 4337.925 | 5252.79 | 9590.715
17:00 | 4560.3 | 5328.74 | 9889.04
17:30 | 4593.65 | 5743.105 | 10336.755
18:00 | 4627 | 6157.47 | 10784.47
18:30 | 4668.6 | 6251.14 | 10919.74
19:00 | 4710.2 | 6344.81 | 11055.01
19:30 | 4717.2 | 6111.46 | 10828.66
20:00 | 4625.5 | 6073.72 | 10699.22
20:30 | 4594 | 6014.92 | 10608.92 |  | Executive Engineer
21:00 | 4562.5 | 5956.12 | 10518.62 |  | Network Operation Division
21:30 | 4385.5 | 5887.645 | 10273.145
22:00 | 4208.5 | 5819.17 | 10027.67
22:30 | 4157 | 5647.83 | 9804.83
23:00 | 4105.5 | 5476.49 | 9581.99

## En-Curve
QF-LDC-12
Date | 17-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3218 | 733.5 | 805 | 0 | 94 | 837 | 40 | 2437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3201 | 587.5 | 796.5 | 0 | 91 | 836.5 | 40 | 2354.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 17-12-2025
01:00 | 3184 | 441.5 | 788 | 0 | 88 | 836 | 40 | 2272 | 0 | 0 | 0 | 0 | 0 | 2 | 0
01:30 | 3136 | 344 | 749.5 | 0 | 85 | 836 | 40 | 2257 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Energy Generated | 220.165 |  | MKWHr
02:00 | 3088 | 246.5 | 711 | 0 | 82 | 836 | 40 | 2242 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2920.5 | 246.5 | 711 | 0 | 83 | 840 | 40 | 2240 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Total Energy Requirement | 220.165 |  | MKWHr
03:00 | 2753 | 246.5 | 711 | 0 | 84 | 844 | 40 | 2238 | 0 | 0 | 0 | 0 | 0 | 2 | 0
03:30 | 2758.5 | 246.5 | 664 | 0 | 83 | 837 | 40 | 2245.5 | 0 | 0 | 0 | 0 | 0 | 4 | 0
04:00 | 2764 | 246.5 | 617 | 0 | 82 | 830 | 40 | 2253 | 0 | 0 | 0 | 0 | 0 | 6 | 0
04:30 | 2733.5 | 246.5 | 616.5 | 0 | 81 | 828.5 | 40 | 2249.5 | 0 | 0 | 0 | 0 | 0 | 7 | 0
05:00 | 2703 | 246.5 | 616 | 0 | 80 | 827 | 40 | 2246 | 0 | 0 | 0 | 0 | 0 | 8 | 0
05:30 | 2825.5 | 305 | 635 | 0 | 83 | 838.5 | 40 | 2312 | 0 | 0 | 0 | 0 | 0 | 5 | 0
06:00 | 2948 | 363.5 | 654 | 0 | 86 | 850 | 40 | 2378 | 0 | 0 | 0 | 0 | 0 | 2 | 0
06:30 | 2979 | 417.25 | 677 | 0 | 85 | 858 | 40 | 2544.5 | 9.77 | 0 | 0 | 0 | 0 | 2 | 0
07:00 | 3010 | 471 | 700 | 0 | 84 | 866 | 40 | 2711 | 19.54 | 0 | 0 | 0 | 0 | 2 | 0
07:30 | 3060 | 543.5 | 747.5 | 0 | 88 | 903.5 | 40 | 2926.5 | 87.075 | 0 | 14.5 | 0 | 0 | 1.5 | 0
08:00 | 3110 | 616 | 795 | 0 | 92 | 941 | 40 | 3142 | 154.61 | 0 | 29 | 0 | 0 | 1 | 0
08:30 | 3100 | 632.75 | 842 | 0 | 99 | 933 | 40 | 3173.5 | 258.54 | 0 | 35.5 | 0 | 0 | 1 | 0
09:00 | 3090 | 649.5 | 889 | 0 | 106 | 925 | 40 | 3205 | 362.47 | 0 | 42 | 0 | 0 | 1 | 0
09:30 | 3105 | 670.5 | 889.5 | 0 | 109 | 874 | 40 | 3047 | 440.4 | 0 | 33.5 | 0 | 0 | 0.5 | 0
10:00 | 3120 | 691.5 | 890 | 0 | 112 | 823 | 40 | 2889 | 518.33 | 0 | 25 | 0 | 0 | 0 | 0
10:30 | 3156.5 | 768.5 | 890 | 0 | 115 | 830.5 | 40 | 2770.5 | 556.985 | 0 | 26.5 | 0 | 0 | 4 | 0
11:00 | 3193 | 845.5 | 890 | 0 | 118 | 838 | 40 | 2652 | 595.64 | 0 | 28 | 0 | 0 | 8 | 0
11:30 | 3272.5 | 959.5 | 892 | 0 | 118 | 866 | 40 | 2723 | 594.32 | 0 | 39.5 | 0 | 0 | 4.5 | 0
12:00 | 3352 | 1073.5 | 894 | 0 | 118 | 894 | 40 | 2794 | 593 | 0 | 51 | 0 | 0 | 1 | 0
12:30 | 3223.5 | 1069 | 897.5 | 0 | 126 | 956.5 | 40 | 3037.5 | 565.82 | 0 | 162.5 | 0 | 0 | 0.5 | 0
13:00 | 3095 | 1064.5 | 901 | 0 | 134 | 1019 | 40 | 3281 | 538.64 | 0 | 274 | 0 | 0 | 0 | 0
13:30 | 2981 | 967.5 | 901 | 0 | 133 | 1026.465 | 40 | 3291.5 | 513.43 | 0 | 251 | 0 | 0 | 0 | 0
14:00 | 2867 | 870.5 | 901 | 0 | 132 | 1033.93 | 40 | 3302 | 488.22 | 0 | 228 | 0 | 0 | 0 | 0
14:30 | 2911.5 | 871 | 901.5 | 0 | 124 | 953.965 | 40 | 3254.5 | 407.425 | 0 | 164 | 0 | 0 | 0 | 0
15:00 | 2956 | 871.5 | 902 | 0 | 116 | 874 | 40 | 3207 | 326.63 | 0 | 100 | 0 | 0 | 0 | 0
15:30 | 2934.5 | 934.25 | 901.5 | 0 | 114 | 870.5 | 40 | 3220.5 | 229.01 | 0 | 96 | 0 | 0 | 2.5 | 0
16:00 | 2913 | 997 | 901 | 0 | 112 | 867 | 40 | 3234 | 131.39 | 0 | 92 | 0 | 0 | 5 | 0
16:30 | 2892.5 | 970.75 | 901 | 0 | 117 | 910 | 40 | 3306 | 71.265 | 8.5 | 369.2 | 0 | 0 | 4.5 | 0
17:00 | 2872 | 944.5 | 901 | 0 | 122 | 953 | 40 | 3378 | 11.14 | 17 | 646.4 | 0 | 0 | 4 | 0
17:30 | 2946.5 | 956.25 | 901 | 0 | 124 | 1118.235 | 40 | 3539.5 | 5.57 | 19.5 | 682.7 | 0 | 0 | 3.5 | 0
18:00 | 3021 | 968 | 901 | 0 | 126 | 1283.47 | 40 | 3701 | 0 | 22 | 719 | 0 | 0 | 3 | 0
18:30 | 3077 | 984.1 | 901.5 | 0 | 124 | 1352.64 | 40 | 3709.5 | 0 | 19 | 709.5 | 0 | 0 | 2.5 | 0
19:00 | 3133 | 1000.2 | 902 | 0 | 122 | 1421.81 | 40 | 3718 | 0 | 16 | 700 | 0 | 0 | 2 | 0
19:30 | 3103 | 1002.2 | 901 | 0 | 112 | 1420.46 | 40 | 3592 | 0 | 0 | 658 | 0 | 0 | 0 | 0
20:00 | 3138 | 992.5 | 901 | 0 | 104 | 1420.72 | 40 | 3597 | 0 | 0 | 506 | 0 | 0 | 0 | 0
20:30 | 3158.5 | 993.5 | 900.5 | 0 | 112 | 1376.42 | 40 | 3602.5 | 0 | 0 | 425 | 0 | 0 | 0.5 | 0
21:00 | 3179 | 994.5 | 900 | 0 | 120 | 1332.12 | 40 | 3608 | 0 | 0 | 344 | 0 | 0 | 1 | 0
21:30 | 3163 | 996 | 900.5 | 0 | 112 | 1327.645 | 40 | 3544 | 0 | 0 | 189.5 | 0 | 0 | 0.5 | 0
22:00 | 3147 | 997.5 | 901 | 0 | 104 | 1323.17 | 40 | 3480 | 0 | 0 | 35 | 0 | 0 | 0 | 0
22:30 | 3073.5 | 1000.5 | 901 | 0 | 104 | 1272.83 | 40 | 3377.5 | 0 | 0 | 35 | 0 | 0 | 0.5 | 0
23:00 | 3000 | 1003.5 | 901 | 0 | 104 | 1222.49 | 40 | 3275 | 0 | 0 | 35 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 407 | 04:00 | 389 | 12:00 | Meghnaghat | 406 | 04:00 | 392 | 10:00
Ashuganj | 412 | 1:00 | 397 | 11:00 | Payra | 417 | 02:00 | 410 | 18:00
Bhulta | 407 | 00:00 | 390 | 12:00 | Rahanpur | 419 | 04:00 | 403 | 18:30
Bibiana | 403 | 00:00 | 388 | 12:00 | Rampal | 411 | 01:00 | 398 | 13:00
BIPTC | 406 | 04:00 | 387 | 11:00
Bogura | 413 | 03:00 | 392 | 18:30
Gopalganj | 411 | 01:00 | 398 | 13:00
Kaliakoir | 403 | 01:00 | 378 | 12:00
Korerhat | 410 | 04:00 | 397 | 12:00
Madunaghat | 405 | 03:00 | 397 | 18:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 04:00 | 225 | 12:00 | Kachua | 238 | 02:00 | 230 | 12:00
AKSML | 236 | 02:00 | 227 | 12:00 | Kaliakoir | 239 | 04:00 | 223 | 12:00
Aminbazar | 238 | 03:00 | 226 | 12:00 | Keranigonj | 238 | 04:00 | 225 | 12:00
Ashuganj | 241 | 00:00 | 228 | 18:00 | Khulna(S) | 239 | 00:00 | 231 | 18:00
Ashuganj-400 | 241 | 00:00 | 228 | 18:00 | Korerhat | 238 | 04:00 | 230 | 12:00
Baghabari | 241 | 00:00 | 230 | 18:00 | Madunaghat | 235 | 03:00 | 227 | 12:00
Barapukuria | 232 | 05:00 | 220 | 08:00 | Madunaghat-400 | 235 | 03:00 | 229 | 13:00
Barapukuria-230 | 232 | 05:00 | 220 | 08:00 | Maniknagar | 237 | 00:00 | 227 | 12:00
Barishal | 244 | 03:00 | 237 | 18:00 | Meghnaghat | 243 | 04:00 | 232 | 12:00
Bheramara | 237 | 06:00 | 224 | 18:00 | Meghnaghat-400 | 239 | 01:00 | 229 | 12:00
Bhulta | 239 | 04:00 | 227 | 12:00 | Mirsorai | 239 | 05:00 | 230 | 12:00
Bibiana | 239 | 02:00 | 228 | 12:00 | Rajshahi | 239 | 05:00 | 224 | 18:00
BIPTC | 239 | 00:00 | 224 | 18:30 | Rampal | 238 | 03:00 | 228 | 06:00
Bogura | 242 | 04:00 | 230 | 18:30 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 241 | 03:00 | 229 | 18:30 | Rampura | 238 | 01:00 | 226 | 15:00
Borhanuddin | 245 | 02:00 | 241 | 12:00 | Shikalbaha | 233 | 00:00 | 227 | 12:00
BSRM | 238 | 02:00 | 229 | 15:00 | Shyampur | 238 | 01:00 | 227 | 12:00
Cumilla(N) | 238 | 01:00 | 229 | 15:00 | Siddhirganj | 239 | 03:00 | 230 | 10:00
Faridpur | 245 | 04:00 | 235 | 18:30 | Sirajgonj | 246 | 02:00 | 236 | 18:30
Fenchuganj | 238 | 00:00 | 231 | 10:00 | Sreepur | 239 | 01:00 | 224 | 18:30
Feni | 238 | 01:00 | 229 | 15:00 | Tongi | 235 | 04:00 | 220 | 11:00
Ghorashal | 240 | 00:00 | 230 | 15:00
Ghorashal-230 | 237 | 11:00 | 216 | 18:00
Gopalganj | 244 | 01:00 | 236 | 12:00
GPH | 236 | 01:00 | 228 | 16:00
Haripur | 239 | 01:00 | 228 | 15:00
Hasnabad | 238 | 03:00 | 227 | 11:00
Hathazari | 234 | 05:00 | 226 | 13:00
Ishurdi | 241 | 06:00 | 227 | 18:30
Jhenaidah | 238 | 03:00 | 224 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 01:00 | 126 | 12:00 | Lalbag | 136 | 03:00 | 126 | 12:00
Agargaon | 137 | 01:00 | 129 | 12:00 | Lalmonirhat | 130 | 02:00 | 121 | 07:00
Agrabad | 137 | 02:00 | 130 | 12:00 | Madanganj | 139 | 00:00 | 134 | 15:00
AKS | 135 | 01:00 | 129 | 12:00 | Madaripur | 139 | 03:00 | 136 | 11:00
Aminbazar | 138 | 03:00 | 130 | 12:00 | Madartek | 134 | 01:00 | 127 | 12:00
Amnura | 139 | 02:00 | 131 | 18:30 | Madunaghat | 138 | 02:00 | 133 | 12:00
Ashuganj | 142 | 00:00 | 136 | 18:00 | Magura | 137 | 05:00 | 126 | 18:00
Bagerhat | 134 | 02:00 | 125 | 18:00 | Mahasthangarh | 136 | 03:00 | 127 | 18:00
Bajitpur | 137 | 01:00 | 129 | 18:00 | Maijdee | 134 | 02:00 | 129 | 12:00
Bakulia | 136 | 01:00 | 131 | 12:00 | Manikganj | 131 | 00:00 | 122 | 12:00
Banani | 135 | 01:00 | 126 | 12:00 | Maniknagar | 138 | 00:00 | 129 | 13:00
Bangabhaban | 139 | 03:00 | 130 | 12:00 | Matarbari | 129 | 03:00 | 120 | 18:00
Barapukuria | 136 | 04:00 | 128 | 08:00 | Matuail | 141.3 | 04:00 | 133 | 13:00
Barguna | 137 | 00:00 | 134 | 13:00 | Metrorail_Motijheel | 138 | 01:00 | 129 | 13:00
Barishal | 141 | 00:00 | 135 | 18:00 | Metrorail_Uttara | 137 | 01:00 | 129 | 12:00
Barishal-230 | 141 | 02:00 | 136 | 12:00 | Millgate | 136 | 02:00 | 123 | 12:00
Baroaulia | 135 | 00:00 | 133 | 09:00 | Mirpur | 137 | 03:00 | 129 | 12:00
Baroirhat | 136 | 05:00 | 130 | 12:00 | Mirzapur | 139 | 04:00 | 128 | 12:00
Bashundhara | 136 | 05:00 | 127 | 11:00 | Mithapukur | 134 | 02:00 | 125 | 18:00
BashundharaCement | 139 | 00:00 | 134 | 15:00 | MI_Cement | 138 | 06:00 | 129 | 12:00
Beanibazar | 138 | 00:00 | 132 | 18:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 136 | 02:00 | 121 | 13:00 | Mogbazar | 137 | 02:00 | 127 | 13:00
Bhaluka | 136 | 00:00 | 129 | 18:00 | Mongla | 133 | 01:00 | 125 | 18:30
Bhandaria | 139 | 05:00 | 134 | 13:00 | Motijheel | 139 | 03:00 | 130 | 12:00
Bhangura | 140 | 01:00 | 132 | 18:00 | Muktagacha | 136 | 05:00 | 129 | 08:00
Bheramara | 141 | 02:00 | 135 | 18:00 | Munshiganj | 139 | 02:00 | 131 | 12:00
Bheramara(GK) | 141 | 03:00 | 135 | 18:00 | Muradnagar | 140 | 04:00 | 132 | 12:00
Bhulta | 130 | 00:00 | 128 | 12:00 | Mymensingh | 134 | 04:00 | 122 | 18:30
Bog-Sherpur | 138 | 04:00 | 130 | 18:30 | Naogaon | 134 | 04:00 | 126 | 13:00
Bogura | 137 | 00:00 | 131 | 13:00 | Narail | 138 | 04:00 | 127 | 13:00
Bogura-230 | 138 | 02:00 | 131 | 18:00 | Narinda | 138 | 00:00 | 129 | 13:00
Brahmanbaria | 138 | 00:00 | 128 | 18:30 | Narshingdi | 137 | 00:00 | 125 | 14:00
Cantonment | 137 | 01:00 | 128 | 12:00 | Natore | 138 | 06:00 | 131 | 18:30
Chandina | 140 | 00:00 | 134 | 12:00 | Nawabganj | 137 | 04:00 | 126 | 12:00
Chandpur | 138 | 03:00 | 134 | 12:00 | Netrakona | 132 | 02:00 | 120 | 18:00
Chandraghona | 138 | 05:00 | 133 | 12:00 | New | 135 | 00:00 | 125 | 12:00
Chapai | 139 | 03:00 | 134 | 13:00 | Niamatpur | 140 | 04:00 | 134 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 141 | 03:00 | 133 | 13:00 | Noapara | 136 | 04:00 | 122 | 13:00
Chauddagram | 138 | 04:00 | 131 | 12:00 | Pabna | 140 | 02:00 | 133 | 18:00
Chhatak | 138 | 00:00 | 129 | 18:00 | Palashbari | 133 | 03:00 | 124 | 18:00
Chowmuhani | 133 | 04:00 | 127 | 13:00 | Panchagarh | 137 | 19:30 | 123 | 08:00
Chuadanga | 140 | 04:00 | 125 | 18:00 | Patiya | 134 | 00:00 | 131 | 20:00
Coxsbazar | 128 | 02:00 | 121 | 18:00 | Patuakhali | 135 | 00:00 | 132 | 18:00
Cumilla(N) | 141 | 01:00 | 133 | 12:00 | Payra | 137 | 00:00 | 134 | 13:00
Cumilla(S) | 140 | 01:00 | 123 | 13:00 | PHP | 136 | 02:00 | 130 | 12:00
Daganbhuiyan | 136 | 03:00 | 131 | 12:00 | Postogola | 139 | 01:00 | 130 | 12:00
Daudkandi | 139 | 02:00 | 130 | 12:00 | Purbachal | 135 | 01:00 | 126 | 13:00
DhakaUniversity | 136 | 02:00 | 127 | 12:00 | Purbasadipur | 132 | 06:00 | 124 | 16:00
Dhamrai | 139 | 04:00 | 130 | 12:00 | Rahanpur | 140 | 01:00 | 135 | 18:30
Dhanmondi | 141 | 00:00 | 135.5 | 12:00 | Rahanpur-400 | 141 | 04:00 | 135 | 18:30
Dohazari | 134 | 04:00 | 129 | 12:00 | Rahim | 141 | 02:00 | 134 | 12:00
Faridpur | 140 | 02:00 | 134 | 13:00 | Rajbari | 140 | 01:00 | 134 | 13:00
Fatullah | 139 | 05:00 | 129 | 12:00 | Rajendrapur | 139 | 00:00 | 129 | 18:00
Fenchuganj | 142 | 00:00 | 136 | 15:00 | Rajshahi | 138 | 01:00 | 130 | 18:00
Feni | 135 | 00:00 | 130 | 13:00 | Rajshahi-230 | 138 | 04:00 | 129 | 18:00
Feni-230 | 136 | 00:00 | 131 | 13:00 | Ramganj | 136 | 01:00 | 131 | 12:00
Ghatail | 135 | 03:00 | 127 | 08:00 | Rampur | 136 | 00:00 | 130 | 12:00
Ghorashal | 138 | 00:00 | 127 | 18:00 | Rampura | 135 | 02:00 | 127 | 12:00
Goalpara | 136 | 04:00 | 129 | 13:00 | Rangamati | 137 | 01:00 | 133 | 12:00
Gollamari | 135 | 00:00 | 130 | 13:00 | Rangpur | 134 | 02:00 | 125 | 18:00
Gopalganj | 138 | 01:00 | 132 | 18:00 | Ruppur | 141 | 00:00 | 134 | 18:00
Gopalganj-400 | 141 | 01:00 | 130 | 17:00 | Saidpur | 133 | 02:00 | 121 | 18:00
Gulshan | 134 | 01:00 | 127 | 12:00 | Satkhira | 134 | 03:00 | 125 | 18:30
Halishahar | 137 | 01:00 | 131 | 16:00 | Satmasjid | 137 | 04:00 | 128 | 12:00
Haripur | 141 | 01:00 | 135 | 12:00 | Savar | 137 | 02:00 | 129 | 12:00
HaripurSBU | 140 | 01:00 | 127 | 12:00 | SevenRings | 138 | 02:00 | 126 | 13:00
Hasnabad | 139 | 02:00 | 129 | 12:00 | ShahCement | 141 | 03:00 | 133 | 13:00
Hathazari | 137 | 00:00 | 127 | 17:00 | Shahjadpur | 141 | 00:00 | 135 | 18:00
Ishurdi | 142 | 00:00 | 136 | 18:00 | Shahjibazar | 138 | 00:00 | 130 | 16:00
Jaldhaka | 131 | 04:00 | 120 | 18:00 | Shahmirpur | 137 | 04:00 | 132 | 12:00
Jamalpur | 130 | 13:00 | 118 | 08:00 | Shariatpur | 140 | 02:00 | 134 | 13:00
Jashore | 136 | 02:00 | 122 | 13:00 | Sherpur | 127 | 13:00 | 114 | 08:00
Jhenaidah | 138 | 00:00 | 120 | 18:00 | Shikalbaha | 126 | 02:00 | 121 | 12:00
Jhenaidah-230 | 139 | 05:00 | 128 | 18:30 | Shikalbaha-230 | 138 | 03:00 | 133 | 12:00
Joydebpur | 137 | 00:00 | 122 | 18:00 | Shitalakhya | 138 | 06:00 | 129 | 12:00
Joypurhat | 134 | 03:00 | 126 | 12:00 | Sholosohor | 137 | 00:00 | 133 | 12:00
Juldah | 137 | 01:00 | 132 | 16:00 | Shyampur | 136 | 00:00 | 130 | 10:00
Kabirpur | 140 | 03:00 | 122 | 12:00 | Shyampur-230 | 138 | 00:00 | 131 | 12:00
Kachua | 140 | 02:00 | 135 | 12:00 | Siddhirganj | 140 | 00:00 | 134 | 12:00
Kaliakoir | 142 | 04:00 | 131 | 12:00 | Sirajganj | 138 | 03:00 | 130 | 18:00
Kallyanpur | 138 | 01:00 | 129 | 12:00 | Sonargaon | 140 | 01:00 | 133 | 12:00
Kalurghat | 136 | 00:00 | 133 | 12:00 | Sreemongol | 139 | 00:00 | 131 | 18:00
Kamrangirchar | 137 | 06:00 | 126 | 12:00 | Sreepur | 141 | 01:00 | 130 | 18:30
Kaptai | 136 | 01:00 | 130 | 12:00 | Srinagar | 136 | 00:00 | 127 | 12:00
Kasba | 139 | 01:00 | 132 | 12:00 | SSM | 140 | 01:00 | 135 | 16:00
Kazla | 138 | 02:00 | 129 | 13:00 | Sunamganj | 137 | 02:00 | 128 | 18:00
Keranigonj | 136 | 01:00 | 127 | 12:00 | Sylhet | 138 | 00:00 | 132 | 18:00
Khagrachori | 137 | 01:00 | 132 | 12:00 | Sylhet-132 | 139 | 00:00 | 133 | 15:00
Khulna | 134 | 02:00 | 127 | 18:00 | Tangail | 134 | 01:00 | 126 | 12:00
Khulna(S) | 135 | 00:00 | 130 | 13:00 | Taraganj | 132 | 05:00 | 123 | 18:00
Khulshi | 135 | 01:00 | 129 | 12:00 | Tasnim | 140 | 01:00 | 133 | 13:00
Kishoreganj | 135 | 00:00 | 127 | 18:00 | Thakurgaon | 134 | 04:00 | 122 | 08:00
Kodda | 138 | 02:00 | 123 | 12:00 | TK | 138 | 04:00 | 133 | 12:00
KSRM | 137 | 01:00 | 132 | 12:00 | Tongi | 137 | 04:00 | 127 | 15:00
Kulaura | 141 | 00:00 | 135 | 15:00 | Ullahpara | 139 | 04:00 | 131 | 18:00
Kurigram | 131 | 04:00 | 118 | 18:00 | Ullon | 135 | 02:00 | 127 | 12:00
Kushtia | 138 | 02:00 | 128 | 18:00 | Uttara | 136 | 03:00 | 125 | 12:00
Laksam | 140 | 01:00 | 134 | 12:00 | UttaraNew | 137 | 01:00 | 129 | 12:00
Lakshmipur | 134 | 00:00 | 130 | 11:00 | Zigatola | 136 | 00:00 | 127 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division