## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-12-2025 | [28 empty] | Date: | 18-12-2025 | [28 empty] | Date: | 18-12-2025 | [28 empty] | Date: | 18-12-2025 | [28 empty] | Date: | 18-12-2025 | [17 empty] | Date: | 18-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 572 | 0 | 0 | 0 | 345 | 0 | 150 | 51 | 0 | 191 | 0 | 0 | 110 | 0 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 17 | 94 | 0 | 16 | 19 | 153 | 0 | 0 | 0 | 4125.5 | 805 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 902 | 0 | 2 | 0 | 1171.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 280 | 1000 | 0 | 5226.98 | 9352.48 | 98.7
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 577 | 0 | 0 | 0 | 340 | 0 | 150 | 51 | 0 | 193 | 0 | 0 | 110 | 0 | 0 | 16 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 16 | 0 | 157 | 0 | 0 | 0 | 4038.5 | 805 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 2 | 0 | 840.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 280 | 800 | 0 | 4596.54 | 8635.04 | 98.7
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 300 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 444 | 0 | 0 | 0 | 350 | 0 | 150 | 51 | 0 | 194 | 0 | 0 | 111 | 0 | 0 | 15 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 17 | 96 | 0 | 8 | 0 | 162 | 0 | 0 | 0 | 3779.5 | 712 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 2 | 0 | 835.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 280 | 600 | 0 | 4277.91 | 8057.41 | 98.7
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 300 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 370 | 0 | 150 | 5 | 0 | 205 | 0 | 0 | 111 | 0 | 0 | 15 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 17 | 96 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 3600.5 | 711 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 0 | 2 | 0 | 842.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 280 | 560 | 0 | 4233.13 | 7833.63 | 98.7
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 301 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 370 | 0 | 150 | 5 | 0 | 193 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 17 | 96 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 3538.5 | 617 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 2 | 0 | 839.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 280 | 560 | 0 | 4088.56 | 7627.06 | 98.69
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 300 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 300 | 0 | 150 | 5 | 0 | 200 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 17 | 96 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 3419.5 | 617 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 2 | 0 | 844.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 286 | 560 | 0 | 4118.58 | 7538.08 | 98.69
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 370 | 0 | 150 | 19 | 0 | 199 | 0 | 0 | 111 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 17 | 0 | 41 | 0 | 0 | 17 | 96 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 3751.5 | 666 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 0 | 2 | 0 | 842.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 286 | 575 | 0 | 4237.1 | 7988.6 | 98.69
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 40 | 0 | 38 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 500 | 2 | 0 | 0 | 393 | 0 | 150 | 51 | 0 | 199 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 88 | 0 | 3 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 1 | 17 | 0 | 42 | 0 | 0 | 17 | 96 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 3932.23 | 713 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | 838 | 0 | 2 | 0 | 934.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.31 | 2 | 0 | 0 | 1.27 | 0 | 0 | 179 | 0 | 0 | 0 | 352 | 0 | 0.12 | 0 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 4 | 0.01 | 0 | 0 | 0 | 220 | 0 | 280 | 645 | 0 | 4481.4 | 8413.63 | 98.69
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 295 | 0 | 0 | 9 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 40 | 0 | 16 | 354 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 562 | 8 | 0 | 0 | 393 | 0 | 150 | 51 | 0 | 205 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 86 | 0 | 28 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 3 | 0 | 0 | 81 | 0 | 0 | 17 | 96 | 0 | 25 | 19 | 150 | 1 | 0 | 0 | 4170.99 | 806 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3 | 958 | 0 | 2 | 0 | 940.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.54 | 24 | 0 | 0 | 13.09 | 0 | 0 | 183 | 0 | 0 | 0 | 389 | 0 | 1.58 | 0 | 57 | 0 | 9 | 0 | 0 | 0 | 0 | 1.3 | 47 | 0.1 | 0 | 0 | 0 | 220 | 0 | 280 | 838 | 0 | 5042.12 | 9213.11 | 98.69
09:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 328 | 0 | 0 | 19 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.98 | 40 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 578 | 13 | 0 | 0 | 370 | 0 | 150 | 51 | 0 | 197 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 100 | 0 | 47 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 7 | 17 | 0 | 81 | 0 | 0 | 17 | 96 | 0 | 56 | 19 | 144 | 1 | 0 | 0 | 4297.98 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 990 | 0 | 2 | 0 | 823.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.67 | 57 | 0 | 0 | 36.01 | 0 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 3.38 | 0 | 58 | 35 | 18 | 0 | 0 | 0 | 0 | 3.1 | 101 | 0.29 | 0 | 0 | 0 | 220 | 0 | 280 | 950 | 0 | 5401.41 | 9699.39 | 98.68
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 30 | 0 | 0 | 0 | 520 | 0 | 0 | 332 | 0 | 0 | 25 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 40 | 0 | 10 | 354 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 580 | 17 | 0 | 0 | 335 | 0 | 120 | 51 | 0 | 191 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 98 | 0 | 58 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 10 | 17 | 0 | 81 | 0 | 0 | 17 | 96 | 0 | 56 | 19 | 132 | 2 | 0 | 0 | 4267.72 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 847 | 0 | 2 | 0 | 843.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.23 | 79 | 0 | 0 | 49.72 | 0 | 0 | 180 | 0 | 0 | 0 | 377 | 0 | 4.53 | 0 | 61 | 0 | 24 | 0 | 0 | 0 | 0 | 4.6 | 141 | 0.43 | 0 | 0 | 0 | 220 | 0 | 309 | 800 | 0 | 5200.88 | 9468.6 | 98.68
11:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 33 | 0 | 0 | 0 | 470 | 0 | 0 | 280 | 0 | 0 | 29 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 40 | 0 | 8 | 354 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 580 | 18 | 0 | 0 | 393 | 0 | 100 | 51 | 0 | 194 | 0 | 0 | 103 | 0 | 0 | 17 | 0 | 112 | 0 | 66 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 11 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 56 | 19 | 120 | 2 | 0 | 0 | 4233.12 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 940 | 0 | 0 | 0 | 841.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.98 | 95 | 0 | 0 | 56.81 | 0 | 0 | 181 | 0 | 0 | 0 | 356 | 0 | 5.07 | 0 | 58 | 0 | 29 | 0 | 0 | 0 | 0 | 5.3 | 141 | 0.5 | 0 | 0 | 0 | 220 | 0 | 350 | 830 | 0 | 5385.4 | 9618.52 | 98.68
12:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17.5 | 0 | 0 | 0 | 135 | 0 | 54 | 32 | 0 | 0 | 0 | 460 | 0 | 0 | 280 | 0 | 0 | 27 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3.23 | 40 | 0 | 9 | 354 | 0 | 0 | 0 | 0 | 43 | 223 | 0 | 0 | 0 | 580 | 19 | 2 | 0 | 393 | 0 | 100 | 51 | 0 | 206 | 0 | 0 | 103 | 61 | 0 | 19 | 0 | 112 | 0 | 67 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 11 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 56 | 19 | 120 | 2 | 0 | 0 | 4538.73 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 1022 | 0 | 0 | 0 | 919.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.03 | 93 | 0 | 0 | 58.92 | 0 | 0 | 195 | 0 | 0 | 0 | 383 | 0 | 5.21 | 0 | 58 | 0 | 31 | 0 | 0 | 0 | 0 | 5.7 | 139 | 0.52 | 0 | 0 | 0 | 220 | 0 | 350 | 900 | 0 | 5663.73 | 10202.46 | 98.67
13:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 30.7 | 0 | 10 | 0 | 195 | 0 | 55 | 80 | 0 | 0 | 0 | 465 | 0 | 0 | 280 | 0 | 0 | 28 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 3.01 | 40 | 0 | 19 | 354 | 0 | 0 | 12 | 0 | 71 | 222 | 0 | 0 | 0 | 580 | 18 | 50 | 0 | 393 | 0 | 100 | 51 | 0 | 201 | 0 | 0 | 105 | 76 | 0 | 15 | 0 | 120 | 0 | 63 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 10 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 56 | 19 | 110 | 2 | 0 | 0 | 4793.71 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 1030 | 0 | 0 | 0 | 1074.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.03 | 90 | 0 | 0 | 57.32 | 0 | 0 | 205 | 0 | 0 | 0 | 367 | 0 | 5.21 | 0 | 59 | 0 | 28 | 0 | 0 | 0 | 0 | 5.4 | 138 | 0.52 | 0 | 0 | 0 | 220 | 0 | 350 | 960 | 0 | 5861.54 | 10655.25 | 98.67
14:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 27 | 0 | 17 | 0 | 195 | 0 | 55 | 54 | 0 | 0 | 0 | 435 | 0 | 0 | 280 | 0 | 0 | 23 | 0 | 21.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 2.48 | 40 | 0 | 12 | 354 | 0 | 0 | 19 | 0 | 68 | 222 | 0 | 0 | 0 | 580 | 15 | 24 | 0 | 393 | 0 | 100 | 51 | 0 | 197 | 0 | 0 | 101 | 85 | 0 | 17 | 0 | 120 | 0 | 54 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 9 | 17 | 0 | 83 | 0 | 0 | 17 | 96 | 0 | 59 | 19 | 110 | 2 | 0 | 0 | 4677.68 | 903 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 975 | 0 | 0 | 0 | 1079.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.75 | 78 | 0 | 0 | 46.44 | 0 | 0 | 193 | 0 | 0 | 0 | 349 | 0 | 4.34 | 0 | 56 | 0 | 23 | 0 | 0 | 0 | 0 | 4.5 | 134 | 0.52 | 0 | 0 | 0 | 220 | 0 | 280 | 900 | 0 | 5595.88 | 10273.56 | 98.67
15:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 15.8 | 0 | 17 | 0 | 145 | 0 | 0 | 65 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 15 | 0 | 29.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 25 | 1.7 | 40 | 0 | 8 | 354 | 0 | 0 | 26 | 0 | 64 | 221 | 0 | 0 | 0 | 580 | 12 | 12 | 0 | 393 | 0 | 130 | 51 | 0 | 191 | 0 | 0 | 103 | 83 | 0 | 17 | 0 | 108 | 0 | 40 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 5 | 17 | 0 | 83 | 0 | 0 | 15 | 96 | 0 | 59 | 19 | 110 | 1 | 0 | 0 | 4486.7 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 906 | 0 | 0 | 0 | 1070.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.19 | 50 | 0 | 0 | 26.84 | 0 | 0 | 178 | 0 | 0 | 0 | 340 | 0 | 2.96 | 0 | 59 | 0 | 17 | 0 | 0 | 0 | 0 | 3.1 | 90 | 0.52 | 0 | 0 | 0 | 220 | 0 | 280 | 900 | 0 | 5365.68 | 9852.38 | 98.67
16:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 17.3 | 0 | 17 | 0 | 145 | 0 | 0 | 66 | 0 | 0 | 0 | 350 | 0 | 0 | 330 | 0 | 0 | 7 | 0 | 29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0.81 | 40 | 0 | 8 | 354 | 0 | 0 | 19 | 0 | 34 | 222 | 0 | 0 | 0 | 576 | 6 | 12 | 0 | 393 | 0 | 130 | 51 | 0 | 203 | 0 | 0 | 104 | 51 | 0 | 17 | 0 | 112 | 0 | 20 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 2 | 17 | 0 | 85 | 0 | 0 | 15 | 96 | 0 | 59 | 19 | 110 | 0 | 10.34 | 0 | 4385.45 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 798 | 0 | 0 | 0 | 1070.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.97 | 22 | 0 | 0 | 10.16 | 0 | 0 | 192 | 0 | 0 | 0 | 414 | 0 | 0.68 | 0 | 59 | 0 | 7 | 0 | 0 | 0 | 0 | 1.3 | 35 | 0.07 | 0 | 0 | 0 | 220 | 0 | 280 | 851 | 0 | 5139.44 | 9524.89 | 98.67
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 16.6 | 7 | 39 | 0 | 195 | 0 | 0 | 81 | 0 | 0 | 0 | 445 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 28.5 | 22 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 24 | 25 | 0.02 | 40 | 7 | 16 | 354 | 0 | 0 | 19 | 0 | 42 | 223 | 0 | 0 | 0 | 540 | 0 | 31 | 0 | 350 | 0 | 130 | 51 | 0 | 190 | 0 | 2 | 104 | 49 | 0 | 17 | 0 | 114 | 0 | 1 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 17 | 0 | 85 | 0 | 0 | 15 | 96 | 0 | 59 | 19 | 110 | 0 | 0.48 | 0 | 4510.6 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.52 | 804 | 0 | 0 | 0 | 1227.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 1 | 0 | 0 | 0.72 | 0 | 0 | 185 | 0 | 0 | 0 | 343 | 0 | 0.09 | 0 | 58 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 3 | 0.01 | 0 | 0 | 0 | 220 | 0 | 350 | 880 | 0 | 5229.25 | 9739.85 | 98.66
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 26.7 | 35 | 111 | 0 | 280 | 0 | 50 | 112 | 0 | 0 | 0 | 450 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 24.5 | 22 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 36 | 25 | 0 | 40 | 33 | 15 | 354 | 0 | 0 | 32 | 0 | 71 | 227 | 0 | 0 | 0 | 590 | 0 | 40 | 0 | 340 | 0 | 90 | 51 | 0 | 193 | 0 | 16 | 107 | 69 | 0 | 20 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 17 | 0 | 83 | 0 | 0 | 15 | 96 | 0 | 59 | 19 | 111 | 0 | 0 | 7 | 5001.2 | 902 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1425.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 58 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 505 | 1004 | 0 | 6238.86 | 11240.06 | 98.66
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 45.3 | 0 | 111 | 0 | 293 | 0 | 55 | 115 | 0 | 0 | 0 | 435 | 0 | 17 | 300 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 25 | 0 | 40 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 90 | 226 | 0 | 0 | 0 | 602 | 0 | 12 | 0 | 393 | 0 | 90 | 51 | 0 | 183 | 0 | 0 | 107 | 111 | 8 | 13 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 83 | 0 | 0 | 15 | 96 | 0 | 60 | 19 | 111 | 0 | 0 | 0 | 4836.3 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 0 | 0 | 1451.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 58 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 220 | 0 | 413 | 1044 | 0 | 6113.7 | 10950 | 98.66
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 45.3 | 0 | 38 | 0 | 293 | 0 | 55 | 82 | 0 | 0 | 0 | 455 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 88 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 393 | 0 | 90 | 51 | 0 | 194 | 0 | 0 | 108 | 116 | 0 | 13 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 83 | 0 | 0 | 15 | 96 | 0 | 59 | 19 | 111 | 0 | 0 | 0 | 4756.8 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 1404.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 58 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 220 | 0 | 373 | 1050 | 0 | 6037.7 | 10794.5
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 46.6 | 0 | 52 | 0 | 293 | 0 | 55 | 89 | 0 | 0 | 0 | 445 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 19.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 13 | 350 | 0 | 0 | 0 | 0 | 88 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 275 | 79 | 90 | 51 | 0 | 194 | 0 | 0 | 109 | 110 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 21 | 0 | 83 | 0 | 0 | 15 | 96 | 0 | 60 | 19 | 112 | 0 | 0 | 0 | 4727.8 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 1361.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 58 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 220 | 0 | 304 | 1062 | 0 | 5913.78 | 10641.58 | 98.65
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 47.8 | 0 | 0 | 0 | 293 | 0 | 55 | 48 | 0 | 0 | 0 | 455 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 87 | 226 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 220 | 212 | 30 | 51 | 0 | 140 | 0 | 0 | 109 | 114 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 21 | 0 | 86 | 0 | 0 | 15 | 96 | 0 | 60 | 19 | 112 | 0 | 0 | 0 | 4574.8 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 0 | 0 | 1330.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 220 | 0 | 304 | 1065 | 0 | 5911.64 | 10486.44 | 98.65
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 48.8 | 0 | 0 | 0 | 195 | 0 | 55 | 17 | 0 | 0 | 0 | 430 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 34 | 350 | 0 | 0 | 0 | 0 | 88 | 226 | 0 | 0 | 0 | 578 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 132 | 0 | 0 | 109 | 116 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 21 | 0 | 86 | 0 | 0 | 15 | 96 | 0 | 60 | 19 | 111 | 0 | 0 | 0 | 4443.8 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 220 | 0 | 305 | 1070 | 0 | 5799 | 10242.8 | 98.65
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 350 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 235 | 254 | 0 | 51 | 0 | 132 | 0 | 0 | 109 | 17 | 0 | 13 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 21 | 0 | 86 | 0 | 0 | 15 | 96 | 0 | 16 | 19 | 117 | 0 | 0 | 0 | 3829 | 902 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 220 | 0 | 304 | 1054 | 0 | 5721 | 9550 | 98.65
Total KWH | 0 | 30720 | 166080 | 0 | 0 | 0 | 0 | 0 | 8503200 | 0 | 0 | 357120 | 58680 | 413424 | 0 | 2336967 | 0 | 491137 | 888480 | 0 | 0 | 0 | 11125827 | 0 | 24870 | 6988867 | 0 | 0 | 183596 | 0 | 475200 | 510840 | 0 | 0 | 53945 | 0 | 0 | 0 | 5280 | 0 | 52980 | 0 | 43200 | 310080 | 20281 | 964000 | 60218 | 523200 | 8298181.82 | 0 | 0 | 200640 | 0 | 845563 | 5458468 | 0 | 0 | 0 | 12687271 | 126765 | 282691 | 0 | 8370000 | 952000 | 2756000 | 1113568 | 0 | 4700000 | 0 | 28800 | 2558398 | 1039200 | 12600 | 405880 | 0 | 2429760 | 0 | 449336 | 0 | 0 | 0 | 5156000 | 716000 | 722640 | 0 | 12719.3 | 428400 | 0 | 1560600 | 0 | 0 | 392000 | 2310210 | 0 | 943200 | 319200 | 3073920 | 12650 | 6340 | 11280 | 102968473.12 | 20144727 | 6469344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478800 | 22436360 | 0 | 16727 | 0 | 24958267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316428 | 601740 | 0 | 0 | 354736 | 0 | 0 | 4690645 | 0 | 0 | 0 | 9154836 | 0 | 33300 | 0 | 1374981 | 160451 | 189847 | 76809 | 0 | 0 | 0 | 34404.84 | 982080 | 3166 | 0 | 0 | 364000 | 5469843 | 0 | 7611638.8 | 21570909.09 | 0 | 127494039.73 | 230462512.85

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-12-2025 | during | 19-12-2025 | during | 19-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 352 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 300 | 0 | 0 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 26.7 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 54 | 50 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 29 | 24.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 0 | 52.19 | 52.19 | 52 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 135 | 280 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 111 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 32 | 112 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 460 | 450 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1434.5 | 1797.2 | 5429.15 | 5399.15 | 2484.49 | 2454.49
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 227 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 43 | 71 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 33 | 33 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 36 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 15 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.23 | 0 | 3.01 | 0 | 3.01 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 33 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 31 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 590 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 354 | 354 | 354 | 354 | 354 | 354 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1296.23 | 1478 | 2557.73 | 2559.72 | 2047.51 | 2049.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 206 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 250 | 250 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 100 | 90 | 318.81 | 318.81 | 220 | 220 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 340 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 2 | 40 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 103 | 107 | 163 | 163 | 112 | 112 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 61 | 69 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 112 | 120 | 160 | 160 | 120 | 120 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1114 | 1046 | 2687.21 | 2622.21 | 1835.4 | 1770.4
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-12-2025 | during | 19-12-2025 | during | 19-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 120 | 111 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 45.15 | 0 | 45.15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 7 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 197 | 196 | 361.25 | 314 | 313.75 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 96 | 96 | 95 | 95 | 95 | 95 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 15 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 213 | 213 | 210 | 210 | 210 | 210 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 497 | 484 | 521 | 521 | 521 | 521
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 336 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1022 | 1102 | 0 | 0 | 1000 | 1000 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2251 | 2340 | 2344 | 2272 | 2589.1 | 2517.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 350 | 505 | 0 | 0 | 350 | 350 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 0 | 55 | 55 | 55 | 55 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 900 | 1004 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 0 | 0 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant is on standby as per NLDC requirement
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1470.52 | 1729 | 1708.32 | 1707.32 | 1838.32 | 1837.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54.03 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 188 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 383 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.21 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 919.35 | 1425.86 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.92 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1708.51 | 2027.86 | 2837.87 | 2671.87 | 2774.49 | 2608.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 58 | 57 | 57 | 57 | 57 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 139 | 0 | 143.83 | 0 | 143.83 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 233.7 | 142 | 464.03 | 285 | 464.03 | 285
System Total |  |  |  |  | 28823.2 | 28379.108 | 10202.46 | 11240.06 | 18910.56 | 18352.27 | 14868.09 | 14309.8
Forecast Scenario (19-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9270 |  | 0 |  | 9270
|  |  |  | 1:00 | 8730 |  | 0 |  | 8730
|  |  |  | 2:00 | 8170 |  | 0 |  | 8170
|  |  |  | 3:00 | 7950 |  | 0 |  | 7950
|  |  |  | 4:00 | 7620 |  | 0 |  | 7620
|  |  |  | 5:00 | 7500 |  | 0 |  | 7500
|  |  |  | 6:00 | 7700 |  | 0 |  | 7700
|  |  |  | 7:00 | 7840 |  | 0 |  | 7840
|  |  |  | 8:00 | 8640 |  | 0 |  | 8640
|  |  |  | 9:00 | 8740 |  | 0 |  | 8740
|  |  |  | 10:00 | 8280 |  | 0 |  | 8280
|  |  |  | 11:00 | 8580 |  | 0 |  | 8580
|  |  |  | 12:00 | 9150 |  | 0 |  | 9150
|  |  |  | 13:00 | 10170 |  | 0 |  | 10170
|  |  |  | 14:00 | 8710 |  | 0 |  | 8710
|  |  |  | 15:00 | 7880 |  | 0 |  | 7880
|  |  |  | 16:00 | 7800 |  | 0 |  | 7800
|  |  |  | 17:00 | 8250 |  | 0 |  | 8250
|  |  |  | 18:00 | 9440 |  | 0 |  | 9440
|  |  |  | 18:30 | 9500 |  | 0 |  | 9500
|  |  |  | 19:00 | 9660 |  | 0 |  | 9660
|  |  |  | 19:30 | 9630 |  | 0 |  | 9630
|  |  |  | 20:00 | 9540 |  | 0 |  | 9540
|  |  |  | 21:00 | 9510 |  | 0 |  | 9510
|  |  |  | 22:00 | 9250 |  | 0 |  | 9250
|  |  |  | 23:00 | 8910 |  | 0 |  | 8910
Probable Maximum Temperature: |  |  | 28.00°C
Probable Maximum Demand at Day Peak: |  |  | 9150.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 9660.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9660.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 207.29 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 11:22 hrs on 19-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10202.46 | MW | 12:00 Hr. | Energy Generated |  |  | 230.4625 |  | MKWHr.
| Day Peak Demand |  |  | 10202.46 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11240.06 | MW | 18:00 Hr. | Energy Demand |  |  | 230.4625 |  | MKWHr.
| Evening Peak Demand |  |  | 11240.06 | MW | 18:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 7538.08 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 706.82 |  | MMCFD
| Maximum Generation of the Day |  |  | 11240.06 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.6437 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 27.6039 | 0 | 4.7675 | 0 | 0 | 0.1836 | 0 | 0 | 32.555 | Gas | 94.9666 | Gas | 330369082.43
| Chattogram Zone |  |  | 5.9817 | 20.9855 | 1.5666 | 0 | 0.964 | 0.14705 | 0 | 0.00528 | 29.6501 | Coal | 73.9793 | Coal | 474096198.1661
| Cumilla Zone |  |  | 20.8558 | 0 | 1.3633 | 0 | 0 | 0.44934 | 2.4298 | 0 | 25.0982 | HFO | 9.2083 | HFO | 152430552.32
| Mymensingh Zone |  |  | 3.0739 | 0 | 1.2737 | 0 | 0 | 0.01899 | 0 | 0 | 4.3666 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 11.2858 | 0 | 0 | 0 | 0 | 0.012719 | 0 | 0 | 11.2986 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 6.4861 | 22.4364 | 0 | 0 | 0 | 0.4788 | 20.1447 | 0 | 49.546 | Solar | 3.8062 | Solar | 59262051.0564
| Barishal Zone |  |  | 5.8338 | 29.1825 | 0 | 0 | 0 | 0.003166 | 0 | 0 | 35.0196 | Import | 47.5328 | Import | 284328478.24
| Rajshahi Zone |  |  | 13.8455 | 0 | 0 | 0 | 0 | 1.3062 | 24.9583 | 0 | 40.11 | Wind | 0.00528 | Wind | 77668.8
| Rangpur Zone |  |  | 0 | 1.375 | 0.23726 | 0 | 0 | 1.2063 | 0 | 0 | 2.8186
| Total |  |  | 94.9666 | 73.9793 | 9.2083 | 0 | 0.964 | 3.8062 | 47.5328 | 0.00528 | 230.4625
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 330369082.43 |  | Hydro | 96400
|  |  |  | Coal | 474096198.1661 |  | Solar | 59262051.0564
|  |  |  | HFO | 152430552.32 |  | Import | 284328478.24
|  |  |  | HSD | 0 |  | Wind | 77668.8
[5 empty] | Total: | 130,06,60,431 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.1447 | Peak Hr Flow | 902.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45429672.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.9583 | Peak Hr Flow | 1425.86 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2808 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4298 | Peak Hr Flow | 120.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2808 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.5328 | Peak Hr Flow | 2447.86 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4223
|  |  |  | Chattogram |  | 0 |  | 1177
|  |  |  | Cumilla |  | 0 |  | 956
|  |  |  | Mymensingh |  | 0 |  | 865
|  |  |  | Sylhet |  | 0 |  | 404
|  |  |  | Khulna |  | 0 |  | 1271
|  |  |  | Barishal |  | 0 |  | 312
|  |  |  | Rajshahi |  | 0 |  | 967
|  |  |  | Rangpur |  | 0 |  | 760
|  |  |  | Total |  | 0 |  | 10935
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 16:25 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to
annual maintenance work
| 08:06 | 16:39 | Shahmirpur 132/33kV S/S 416T LT Scheduled S/D Due to Annual Maintenance of Tr-02
| 08:07 | 16:38 | Shahmirpur 132/33kV S/S 416T HT Scheduled S/D Due to Annual maintenance of Tr-02
| 08:16 | 15:18 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to annual
maintenance
| 08:25 | 15:57 | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Scheduled S/D Due to Annual Maintenance
| 08:26 | 16:56 | Rahanpur 400/132kV S/S Rahanpur-Niamatpur 132 KV Line Ckt-01 Scheduled S/D
| 08:27 | 17:15 | Chandpur 132/33kV S/S 402T (T-01) HT Scheduled S/D Due to Maintenance
| 08:28 | 15:17 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end.
| 08:29 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to Between
Bogura Ckt-1 & Joypurhat ckt-2 T connect. Project work. and from Bogura 230/132kVend.
| 08:30 | 16:11 | Kurigram 132/33kV S/S Capacitor Bank Scheduled S/D Due to Annual Maintenance
|  | 08:32 | Shyampur 230/132kV S/S Auto TR-1 HT is restored.
| 08:32 | 11:08 | Shyampur 230/132kV S/S Aux TR-1 HT Forced S/D Due to Shutdown taken
| 08:33 |  | Joypurhat 132/33kV S/S Naogaon Ckt.-2 Scheduled S/D Due to Rearrange Line in naogaon
joypurhat 132KV line in tower no 01.
| 08:34 | 14:39 | Bakulia-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance
| 08:35 | 17:29 | Chowmuhani 132/33kV S/S TR2-425T HT Scheduled S/D Due to Yearly Schedule Maintenance
| 08:35 | 17:29 | Chowmuhani 132/33kV S/S TR2-425T LT Scheduled S/D Due to Yearly Schedule Maintenance
| 08:38 | 15:35 | Mahasthangar-Palashbari 132kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due to
Annual Maintenance work. and from Palashbari 132/33kV end Due to Annual Maintenance
| 08:45 | 16:04 | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to
Annual maintanence and from Shahjibazar 132/33kV end Due to Annual Maintenance
| 09:00 | 23:05 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Bay
annual maintenance .
| 09:01 | 16:28 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to Annual maintenance
| 09:02 | 16:25 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to Annual maintenace
| 09:10 | 16:51 | Rahanpur 132/33kV S/S TR-2 (414T) HT Scheduled S/D Due to Annual Maintenance
| 09:10 | 16:51 | Rahanpur 132/33kV S/S TR-2 (414T) LT Scheduled S/D Due to Annual Maintenance
| 09:18 | 14:40 | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 LT Scheduled S/D Due to Tandelta Test
| 09:18 | 14:40 | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 HT Scheduled S/D Due to Tandelta Test
| 09:18 | 16:11 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Deadline Checking work
| 09:23 | 11:08 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to annual maintenance (SPMD)
| 09:23 | 11:08 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to annual maintenance (SPMD)
| 09:24 | 15:47 | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance and from Bhulta 400/230kVend.
| 09:24 | 13:20 | BIPTC S/S 10CF26 Scheduled S/D Due to Annual Maintenance.
| 09:25 | 16:58 | Bogura 400/230kV S/S ATR-01 LT Scheduled S/D Due to Annual maintenance
| 09:26 | 16:58 | Bogura 400/230kV S/S ATR-01 HT Scheduled S/D Due to Annual maintenance
| 09:32 | 16:18 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D Due to Annual Maintenance
| 09:33 | 16:18 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintenance
| 09:35 | 15:00 | Mymensingh 132/33kV S/S Bus A Scheduled S/D
| 09:42 | 14:29 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Annual maintenance work
| 09:42 | 14:28 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to Annual maintenance work
| 09:46 | 14:00 | Jashore 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance
| 09:46 | 14:00 | Jashore 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance
| 09:50 | 15:48 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
Maintenance (Deadline check )
| 10:02 | 15:14 | Ghatail 132/33kV S/S T-2 LT Scheduled S/D Due to Due to annual maintenance work
| 10:03 | 15:13 | Ghatail 132/33kV S/S T-2 HT Scheduled S/D Due to Due to annual maintenance work
| 10:10 | 00:05 | BIPTC S/S Baharampur-2 Scheduled S/D Due to Shutdown is taken by baharampur end.
| 10:25 | 13:36 | Meghnaghat 230/132kV S/S Bus2 Scheduled S/D Due to Red hot maintenance
| 10:30 | 13:46 | Meghnaghat 400/230kV S/S 230kV BUS Section 02 Scheduled S/D Due to 230 kV Bus Section- 2
shutdown instructed by NLDC
| 11:09 | 12:50 | Chauddagram 132/33kV S/S 132 kv T-2 HT Scheduled S/D Due to annual namintenance (SPMD)
| 11:09 | 12:50 | Chauddagram 132/33kV S/S 132 kv T-2 LT Scheduled S/D Due to annual maintenance (SPMD)
| 11:33 | 12:57 | Juldah 132/33kV S/S 132/33 KV 406T T-1 HT Forced S/D Due to Working on 33 KV GIS | [7 empty] | 3.5MW load
interrup.
| 11:33 | 12:57 | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Forced S/D Due to Working on 33KV GIS | [7 empty] | 3.5MW load
interrup.
| 12:00 |  | Day Peak Generation: 10199 MW.
| 12:17 | 15:17 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to Annual maintenance
|  | 14:32 | Saidpur 132/33kV S/S TR-2 (404T) HT is restored.
|  | 14:38 | Saidpur 132/33kV S/S TR-2 (404T) LT is restored.
| 15:27 | 17:30 | Mymensingh 132/33kV S/S Bus B Scheduled S/D Due to None
|  | 15:55 | Mirpur 132/33kV S/S Reserve Bus is restored.
| 16:11 | 16:37 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Tripped showing 33 KV REF-615, 132 KV | [7 empty] | 30.0MW load
|  |  | RET-670 RET-650 relays Due to 33 KV pdb outgoing feeder tripped due to incommer 1& 2 | [7 empty] | interrup.
tripped.
|  | 16:27 | Barishal(N)-Madaripur 132 kV Ckt-1 is restored.
| 18:00 |  | Evening peak generation: 11240 MW
| 18:01 | 19:47 | Rampura-Ullon-2 132kV Ckt-1 Forced S/D from Rampura 230/132kV end Due to S/D taken by
NLDC for Emergency work in Ullon ss
|  | 18:45 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
|  | 19:05 | Ghorasal-Tongi 230kV Ckt-1 is restored.
|  | 19:07 | Ghorasal-Tongi 230kV Ckt-2 is restored.
| 19:31 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 19:47 |  | Kalurghat 132/33kV S/S TRFO-02(516T) HT Forced S/D Due to Pdb-33 kv -3 outgoing feeder,
Emergency s/d due to DS maintenance.
|  | 21:02 | Haripur-Siddirganj 132kV Ckt-1 is restored.
| 21:19 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- Plant
|  | 21:21 | Barapukuria-Rangpur 132 kV Ckt-1 is restored.
| 21:32 |  | Barapukuria-Rangpur 132 kV Ckt-2 Project Work S/D from Rangpur 132/33kV end Due to Re
conducting
| 03:28 |  | Siddhirganj 335 MW CCPP was shut down due to an air-inlet filter change.
| 03:53 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 03:53 |  | From NLDC: Ashuganj North CCPP GT shutdown due to maintenance purposes.
| 04:00 |  | Minimum Generation: 7651 MW.
| 05:14 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 07:11 |  | Keranigonj 230/132/33kV S/S ATR-1 LT Scheduled S/D Due to Annual Maintenance Work
| 07:11 |  | Keranigonj 230/132/33kV S/S ATR-1 HT Scheduled S/D Due to Annual Maintenance work
|  | 07:19 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 07:20 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
| 07:48 |  | Bheramara P/S-Ishurdi 132 kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to Annual
Maintenance Bridge Section and from Bheramara 230/132kV end Due to Anula Maintenance
| 07:48 |  | Bheramara P/S-Ishurdi 132 kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end Due to Annual
Maintenance Bridge Section and from Bheramara 230/132kV end Due to Anula Maintenance
| 07:50 |  | Jhenaidah 230/132kV S/S Transformer- 2 LT Scheduled S/D Due to Annual Maintenance.
| 07:51 |  | Jhenaidah 230/132kV S/S Transformer- 2 HT Scheduled S/D Due to Annual Maintenance.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 352 | 8503200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6988867 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 26.7 | 357120 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 50 | 491137 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 24870 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24.5 | 475200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 510840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 166080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 280 | 2336967 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 111 | 413424 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 30720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 112 | 888480 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 183596 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 58680 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 450 | 11125827 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1797.2 | 32555008
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126765 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 200640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5458468 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 71 | 845563 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 52980 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 43200 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 523200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 60218 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 310080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 31 | 53945 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 590 | 12687271 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 5280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 354 | 8298181.82 | U1 S/D 20/NOV/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4895.723 | 1478 | 29650072.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 193 | 4700000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 952000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 90 | 2756000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 340 | 8370000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1113568 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 282691 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 107 | 2558398 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 69 | 1039200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 120 | 2429760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 405880 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 12600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 28800 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 449336 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1046 | 25098233
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 111 | 3073920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 319200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 943200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 6340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 7 | 11280 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 196 | 4366590
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 12719.3 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 722640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1560600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2310210 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 428400 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Shutdown
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 213 | 5156000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 484 | 11298569.3
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 0 | 16727 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 20144727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 336 | 6469344 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 478800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1102 | 22436360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2340 | 49545958
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 505 | 7611638.8 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 364000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1004 | 21570909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5469843 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Plant shutdown as per NLDC requirement.
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3166 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1729 | 35019556.89
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 316428 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4690645 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9154836 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1425.86 | 24958267 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 354736 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 601740 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2027.86 | 40109952
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1374981 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 76809 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34404.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 160451 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189847 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 982080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 142 | 2818572.84
Eastern Grid Total |  |  |  |  | 17395.105 | 5001.2 | 102968473.12
Western Grid Total |  |  |  |  | 10984.003 | 6238.86 | 127494039.73
National Grid Total |  |  |  |  | 28379.108 | 11240.06 | 230462512.85
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7624.66 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3309.5 | MW
i) Dhaka area |  |  | 4222.66 |  | MW | i) Khulna area |  |  |  | 1270.9 | MW
ii) Chattogram area |  |  | 1177 |  | MW | ii) Barishal area |  |  |  | 311.6 | MW
iii) Cumilla area |  |  | 956 |  | MW | iii) Rajshahi area |  |  |  | 967 | MW
iv) Mymensingh area |  |  | 865 |  | MW | iv) Rangpur area |  |  |  | 760 | MW
v) Sylhet area |  |  | 404 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10934.16 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 58 | 13:00 | 133 | Niamatpur | 46 | 07:00
2 | AKSML | 103.9 | 15:00 | 68 | Ishurdi | 47 | 18:30 | 134 | Noapara | 40 | 18:00
3 | Aftabnagar | 26 | 16:00 | 69 | Jaldhaka | 57 | 18:00 | 135 | PHP | 8 | 00:00
4 | Agargaon | 85 | 13:00 | 70 | Jamalpur | 92 | 18:00 | 136 | Pabna | 74 | 18:00
5 | Agrabad | 44 | 18:00 | 71 | Jashore | 103 | 13:00 | 137 | Palashbari | 81 | 18:00
6 | Amnura | 26 | 08:00 | 72 | Jhenaidah | 95 | 18:00 | 138 | Panchagarh | 44 | 18:30
7 | Ashuganj | 54 | 00:00 | 73 | Joydebpur | 92 | 12:00 | 139 | Patiya | 7 | 18:00
8 | BSRM | 204 | 03:00 | 74 | Joypurhat | 43 | 12:00 | 140 | Patuakhali | 47.5 | 21:00
9 | Bagerhat | 62 | 19:30 | 75 | Juldah | 11 | 00:00 | 141 | Payra | 22 | 18:00
10 | Bajitpur | 58 | 18:00 | 76 | KSRM | 11 | 08:00 | 142 | Postogola | 39 | 13:00
11 | Bakulia | 74 | 18:00 | 77 | Kabirpur | 187 | 18:00 | 143 | Purbachal | 27 | 12:00
12 | Banani | 47 | 13:00 | 78 | Kachua | 56 | 20:00 | 144 | Purbasadipur | 108 | 18:00
13 | Bangabhaban | 14 | 11:00 | 79 | Kallyanpur | 78 | 13:00 | 145 | Rahanpur | 23 | 08:00
14 | Barapukuria | 49 | 18:00 | 80 | Kalurghat | 38 | 09:00 | 146 | Rahim | 32 | 14:00
15 | Barguna | 10 | 18:00 | 81 | Kamrangirchar | 64 | 13:00 | 147 | Rajbari | 58 | 18:30
16 | Barishal | 89 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 98 | 18:00
17 | Barishal-230 | 66 | 19:30 | 83 | Kasba | 22 | 18:00 | 149 | Rajshahi | 77 | 21:00
18 | Baroaulia | 61 | 13:00 | 84 | Kazla | 85 | 18:30 | 150 | Rajshahi-230 | 58 | 13:00
19 | Baroirhat | 40 | 13:00 | 85 | Keranigonj | 65 | 18:00 | 151 | Ramganj | 70 | 13:00
20 | Bashundhara | 144 | 13:00 | 86 | Khagrachori | 24 | 18:00 | 152 | Rampur | 28 | 14:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 51 | 13:00 | 153 | Rangamati | 13 | 18:00
22 | Beanibazar | 46 | 18:00 | 88 | Khulshi | 179 | 17:00 | 154 | Rangpur | 98 | 18:00
23 | Benapole | 40 | 08:00 | 89 | Kishoreganj | 84 | 18:30 | 155 | Ruppur | 3.2 | 15:00
24 | Bhaluka | 118 | 18:00 | 90 | Kodda | 262 | 18:00 | 156 | SSM | 13 | 07:00
25 | Bhandaria | 37 | 21:00 | 91 | Kulaura | 30 | 18:00 | 157 | Saidpur | 90 | 18:00
26 | Bhangura | 23 | 18:00 | 92 | Kurigram | 47 | 18:00 | 158 | Satkhira | 86 | 08:00
27 | Bheramara(GK) | 43 | 18:00 | 93 | Kushtia | 112 | 18:00 | 159 | Satmasjid | 77 | 14:00
28 | Bhulta | 192 | 15:00 | 94 | Laksam | 21 | 13:00 | 160 | Savar | 151 | 12:00
29 | Bog-Sherpur | 54 | 09:00 | 95 | Lakshmipur | 28 | 18:00 | 161 | SevenRings | 12.21 | 23:00
30 | Bogura | 109 | 19:00 | 96 | Lalbag | 55 | 13:00 | 162 | ShahCement | 35 | 04:00
31 | Borhanuddin | 66 | 21:00 | 97 | Lalmonirhat | 43 | 18:00 | 163 | Shahjadpur | 58 | 18:00
32 | Brahmanbaria | 88 | 18:00 | 98 | MI_Cement | 16.8 | 23:00 | 164 | Shahjibazar | 78 | 18:00
33 | Cantonment | 79 | 13:00 | 99 | Madanganj | 20 | 07:00 | 165 | Shahmirpur | 41 | 18:00
34 | Chandina | 10 | 19:30 | 100 | Madaripur | 68 | 20:00 | 166 | Shariatpur | 55 | 21:00
35 | Chandpur | 52 | 21:00 | 101 | Madartek | 54 | 13:00 | 167 | Sherpur | 112 | 18:00
36 | Chandraghona | 24 | 19:30 | 102 | Madunaghat | 39 | 18:00 | 168 | Shikalbaha | 27 | 13:00
37 | Chapai | 51 | 08:00 | 103 | Magura | 49 | 18:00 | 169 | Shitalakhya | 63.9 | 12:00
38 | Charsaidpur | 28 | 12:00 | 104 | Mahasthangarh | 54 | 08:00 | 170 | Sholosohor | 34 | 18:00
39 | Chauddagram | 49 | 13:00 | 105 | Maijdee | 28 | 21:00 | 171 | Shyampur | 134 | 10:00
40 | Chhatak | 24 | 22:00 | 106 | Manikganj | 95 | 18:00 | 172 | Siddhirganj | 92 | 15:00
41 | Chowmuhani | 106 | 18:00 | 107 | Maniknagar | 54 | 13:00 | 173 | Sirajganj | 70 | 08:00
42 | Chuadanga | 74 | 18:00 | 108 | Matarbari | 36 | 18:00 | 174 | Sonargaon | 140 | 18:30
43 | Coxsbazar | 107 | 18:00 | 109 | Matuail | 54 | 10:00 | 175 | Sreemongol | 57 | 18:00
44 | Cumilla(N) | 91 | 13:00 | 110 | Metrorail_Motijheel | 16 | 09:00 | 176 | Sreepur | 90 | 18:00
45 | Cumilla(S) | 120 | 14:00 | 111 | Metrorail_Uttara | 9 | 21:00 | 177 | Srinagar | 32.3 | 13:00
46 | Daganbhuiyan | 0 | 01:00 | 112 | Millgate | 78 | 12:00 | 178 | Sunamganj | 39 | 18:30
47 | Daudkandi | 108 | 20:00 | 113 | Mirpur | 106 | 14:00 | 179 | Sylhet | 37 | 19:30
48 | DhakaUniversity | 64 | 13:00 | 114 | Mirsorai | 43 | 15:00 | 180 | Sylhet-132 | 79 | 18:00
49 | Dhamrai | 100 | 18:00 | 115 | Mirzapur | 37 | 18:30 | 181 | TK | 17 | 18:30
50 | Dhanmondi | 85 | 13:00 | 116 | Mithapukur | 52 | 18:00 | 182 | Tangail | 114 | 08:00
51 | Dohazari | 62 | 18:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 15 | 18:00
52 | Faridpur | 111 | 18:00 | 118 | Mogbazar | 63.9 | 14:00 | 184 | Tasnim | 30 | 02:00
53 | Fatullah | 90 | 12:00 | 119 | Mongla | 47 | 18:00 | 185 | Thakurgaon | 78 | 18:00
54 | Fenchuganj | 26 | 18:00 | 120 | Motijheel | 31 | 13:00 | 186 | Tongi | 85 | 18:00
55 | Feni | 77 | 13:00 | 121 | Muktagacha | 28 | 18:00 | 187 | Ullahpara | 24 | 18:00
56 | GPH | 94 | 03:00 | 122 | Munshiganj | 73 | 22:00 | 188 | Ullon | 44 | 18:00
57 | Ghatail | 60 | 18:00 | 123 | Muradnagar | 24 | 19:00 | 189 | Uttara | 77 | 12:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 132 | 18:00 | 190 | UttaraNew | 10 | 13:00
59 | Ghorashal-230 | 80 | 18:00 | 125 | Naogaon | 84 | 13:00 | 191 | Zigatola | 54 | 12:00
60 | Goalpara | 30 | 13:00 | 126 | Narail | 39.5 | 18:30
61 | Gollamari | 70 | 13:00 | 127 | Narinda | 62 | 13:00
62 | Gopalganj | 75 | 18:30 | 128 | Narshingdi | 136 | 19:00
63 | Gulshan | 86 | 13:00 | 129 | Natore | 98 | 18:00
64 | Halishahar | 51 | 15:00 | 130 | Nawabganj | 28.6 | 13:00
65 | HaripurSBU | 86 | 08:00 | 131 | Netrakona | 101 | 18:00
66 | Hasnabad | 68 | 12:00 | 132 | New | 72 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9352.48 | 0 |  | 9352.48
1:00 | 8635.04 | 0 |  | 8635.04
2:00 | 8057.41 | 0 |  | 8057.41
3:00 | 7833.63 | 0 |  | 7833.63
4:00 | 7627.06 | 0 |  | 7627.06
5:00 | 7538.08 | 0 |  | 7538.08
6:00 | 7988.6 | 0 |  | 7988.6
7:00 | 8413.63 | 0 |  | 8413.63
8:00 | 9213.11 | 0 |  | 9213.11
9:00 | 9699.39 | 0 |  | 9699.39
10:00 | 9468.6 | 0 |  | 9468.6
11:00 | 9618.52 | 0 |  | 9618.52
12:00 | 10202.46 | 0 |  | 10202.46
13:00 | 10655.25 | 0 |  | 10655.25
14:00 | 10273.56 | 0 |  | 10273.56
15:00 | 9852.38 | 0 |  | 9852.38
16:00 | 9524.89 | 0 |  | 9524.89
17:00 | 9739.85 | 0 |  | 9739.85
18:00 | 11240.06 | 0 |  | 11240.06
19:00 | 10950 | 0 |  | 10950
19:30 | 10794.5 | 0 |  | 10794.5
20:00 | 10641.58 | 0 |  | 10641.58
21:00 | 10486.44 | 0 |  | 10486.44
22:00 | 10242.8 | 0 |  | 10242.8
23:00 | 9550 | 0 |  | 9550
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4125.5 | 5226.98 | 9352.48 | DAILY GENERATION CURVE
00:30 | 4082 | 4911.76 | 8993.76
01:00 | 4038.5 | 4596.54 | 8635.04 | 18-12-2025
01:30 | 3909 | 4437.225 | 8346.225
02:00 | 3779.5 | 4277.91 | 8057.41
02:30 | 3690 | 4255.52 | 7945.52
03:00 | 3600.5 | 4233.13 | 7833.63
03:30 | 3569.5 | 4160.845 | 7730.345
04:00 | 3538.5 | 4088.56 | 7627.06
04:30 | 3479 | 4103.57 | 7582.57
05:00 | 3419.5 | 4118.58 | 7538.08
05:30 | 3585.5 | 4177.84 | 7763.34
06:00 | 3751.5 | 4237.1 | 7988.6
06:30 | 3841.865 | 4359.25 | 8201.115
07:00 | 3932.23 | 4481.4 | 8413.63
07:30 | 4051.61 | 4761.76 | 8813.37
08:00 | 4170.99 | 5042.12 | 9213.11
08:30 | 4234.485 | 5221.765 | 9456.25
09:00 | 4297.98 | 5401.41 | 9699.39
09:30 | 4282.85 | 5301.145 | 9583.995
10:00 | 4267.72 | 5200.88 | 9468.6
10:30 | 4250.42 | 5293.14 | 9543.56
11:00 | 4233.12 | 5385.4 | 9618.52
11:30 | 4385.925 | 5524.565 | 9910.49
12:00 | 4538.73 | 5663.73 | 10202.46
12:30 | 4666.22 | 5762.635 | 10428.855
13:00 | 4793.71 | 5861.54 | 10655.25
13:30 | 4735.695 | 5728.71 | 10464.405
14:00 | 4677.68 | 5595.88 | 10273.56
14:30 | 4582.19 | 5480.78 | 10062.97
15:00 | 4486.7 | 5365.68 | 9852.38
15:30 | 4436.075 | 5252.56 | 9688.635
16:00 | 4385.45 | 5139.44 | 9524.89
16:30 | 4448.025 | 5184.345 | 9632.37
17:00 | 4510.6 | 5229.25 | 9739.85
17:30 | 4755.9 | 5734.055 | 10489.955
18:00 | 5001.2 | 6238.86 | 11240.06
18:30 | 4918.75 | 6176.28 | 11095.03
19:00 | 4836.3 | 6113.7 | 10950
19:30 | 4756.8 | 6037.7 | 10794.5
20:00 | 4727.8 | 5913.78 | 10641.58
20:30 | 4651.3 | 5912.71 | 10564.01 |  | Executive Engineer
21:00 | 4574.8 | 5911.64 | 10486.44 |  | Network Operation Division
21:30 | 4509.3 | 5855.32 | 10364.62
22:00 | 4443.8 | 5799 | 10242.8
22:30 | 4136.4 | 5760 | 9896.4
23:00 | 3829 | 5721 | 9550

## En-Curve
QF-LDC-12
Date | 18-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3017 | 1017.5 | 805 | 0 | 100 | 1171.98 | 40 | 3166 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3006.5 | 988 | 805 | 0 | 95 | 1006.26 | 40 | 3027.5 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | 18-12-2025
01:00 | 2996 | 958.5 | 805 | 0 | 90 | 840.54 | 40 | 2889 | 0 | 0 | 16 | 0 | 0 | 0 | 0
01:30 | 3005 | 917 | 758.5 | 0 | 89 | 838.225 | 40 | 2685.5 | 0 | 0 | 12 | 0 | 0 | 1 | 0 | Energy Generated | 230.4625 |  | MKWHr
02:00 | 3014 | 875.5 | 712 | 0 | 88 | 835.91 | 40 | 2482 | 0 | 0 | 8 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3022.5 | 838.5 | 711.5 | 0 | 84 | 839.02 | 40 | 2405 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | Total Energy Requirement | 230.4625 |  | MKWHr
03:00 | 3031 | 801.5 | 711 | 0 | 80 | 842.13 | 40 | 2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 3008 | 797 | 664 | 0 | 82 | 840.845 | 40 | 2298.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2985 | 792.5 | 617 | 0 | 84 | 839.56 | 40 | 2269 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2961.5 | 771 | 617 | 0 | 81 | 842.07 | 40 | 2270 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2938 | 749.5 | 617 | 0 | 78 | 844.58 | 40 | 2271 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2993 | 796 | 641.5 | 0 | 81 | 843.34 | 40 | 2368.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 3048 | 842.5 | 666 | 0 | 84 | 842.1 | 40 | 2466 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 3049 | 869.25 | 689.5 | 0 | 86 | 888.275 | 40 | 2569 | 10.09 | 0 | 0 | 0 | 0 | 0 | 0
07:00 | 3050 | 896 | 713 | 0 | 88 | 934.45 | 40 | 2672 | 20.18 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 3077.5 | 935 | 759.5 | 0 | 87 | 937.33 | 40 | 2860.5 | 94.54 | 0 | 22 | 0 | 0 | 0 | 0
08:00 | 3105 | 974 | 806 | 0 | 86 | 940.21 | 40 | 3049 | 168.9 | 0 | 44 | 0 | 0 | 0 | 0
08:30 | 3110.5 | 990 | 854 | 0 | 93 | 882.085 | 40 | 3129.5 | 277.165 | 1 | 79 | 0 | 0 | 0 | 0
09:00 | 3116 | 1006 | 902 | 0 | 100 | 823.96 | 40 | 3210 | 385.43 | 2 | 114 | 0 | 0 | 0 | 0
09:30 | 3050 | 988 | 902 | 0 | 99 | 833.665 | 40 | 3080.5 | 454.83 | 9 | 127 | 0 | 0 | 0 | 0
10:00 | 2984 | 970 | 902 | 0 | 98 | 843.37 | 40 | 2951 | 524.23 | 16 | 140 | 0 | 0 | 0 | 0
10:30 | 2960.5 | 943.5 | 902 | 0 | 105 | 842.555 | 40 | 3031.5 | 555.005 | 20.5 | 143 | 0 | 0 | 0 | 0
11:00 | 2937 | 917 | 902 | 0 | 112 | 841.74 | 40 | 3112 | 585.78 | 25 | 146 | 0 | 0 | 0 | 0
11:30 | 2964.5 | 913.5 | 902 | 0 | 112 | 880.545 | 40 | 3188 | 589.695 | 25 | 295.25 | 0 | 0 | 0 | 0
12:00 | 2992 | 910 | 902 | 0 | 112 | 919.35 | 40 | 3264 | 593.61 | 25 | 444.5 | 0 | 0 | 0 | 0
12:30 | 2985.5 | 911 | 902 | 0 | 116 | 996.705 | 40 | 3298.5 | 581.05 | 29.5 | 568.6 | 0 | 0 | 0 | 0
13:00 | 2979 | 912 | 902 | 0 | 120 | 1074.06 | 40 | 3333 | 568.49 | 34 | 692.7 | 0 | 0 | 0 | 0
13:30 | 2948.5 | 895.1 | 902.5 | 0 | 120 | 1076.695 | 40 | 3239 | 532.26 | 34 | 676.35 | 0 | 0 | 0 | 0
14:00 | 2918 | 878.2 | 903 | 0 | 120 | 1079.33 | 40 | 3145 | 496.03 | 34 | 660 | 0 | 0 | 0 | 0
14:30 | 2916.5 | 857.7 | 902.5 | 0 | 114 | 1074.7 | 40 | 3112 | 415.67 | 34 | 595.4 | 0 | 0 | 0.5 | 0
15:00 | 2915 | 837.2 | 902 | 0 | 108 | 1070.07 | 40 | 3079 | 335.31 | 34 | 530.8 | 0 | 0 | 1 | 0
15:30 | 2992.5 | 814.1 | 902 | 0 | 110 | 1070.165 | 40 | 2998.5 | 242.32 | 21 | 497.55 | 0 | 0 | 0.5 | 0
16:00 | 3070 | 791 | 902 | 0 | 112 | 1070.26 | 40 | 2918 | 149.33 | 8 | 464.3 | 0 | 0 | 0 | 0
16:30 | 2983 | 846.25 | 902 | 0 | 113 | 1149.08 | 40 | 2952 | 80.59 | 23.5 | 542.95 | 0 | 0 | 0 | 0
17:00 | 2896 | 901.5 | 902 | 0 | 114 | 1227.9 | 40 | 2986 | 11.85 | 39 | 621.6 | 0 | 0 | 0 | 0
17:30 | 2969 | 902 | 902 | 0 | 117 | 1326.88 | 40 | 3299.5 | 5.925 | 40 | 887.65 | 0 | 0 | 0 | 0
18:00 | 3042 | 902.5 | 902 | 0 | 120 | 1425.86 | 40 | 3613 | 0 | 41 | 1153.7 | 0 | 0 | 0 | 0
18:30 | 3001 | 883.25 | 901.5 | 0 | 113 | 1438.78 | 40 | 3593.5 | 0 | 24.5 | 1099.5 | 0 | 0 | 0 | 0
19:00 | 2960 | 864 | 901 | 0 | 106 | 1451.7 | 40 | 3574 | 0 | 8 | 1045.3 | 0 | 0 | 0 | 0
19:30 | 3023 | 884.5 | 902 | 0 | 108 | 1404.7 | 40 | 3551 | 0 | 0 | 881.3 | 0 | 0 | 0 | 0
20:00 | 2971 | 887.2 | 902 | 0 | 106 | 1361.78 | 40 | 3501 | 0 | 0 | 872.6 | 0 | 0 | 0 | 0
20:30 | 2970 | 887.1 | 902 | 0 | 106 | 1346.21 | 40 | 3502 | 0 | 0 | 810.7 | 0 | 0 | 0 | 0
21:00 | 2969 | 887 | 902 | 0 | 106 | 1330.64 | 40 | 3503 | 0 | 0 | 748.8 | 0 | 0 | 0 | 0
21:30 | 2972.5 | 890.5 | 902 | 0 | 106 | 1277.32 | 40 | 3490 | 0 | 0 | 686.3 | 0 | 0 | 0 | 0
22:00 | 2976 | 894 | 902 | 0 | 106 | 1224 | 40 | 3477 | 0 | 0 | 623.8 | 0 | 0 | 0 | 0
22:30 | 2967 | 878.5 | 902 | 0 | 106 | 1209.5 | 40 | 3455.5 | 0 | 0 | 337.9 | 0 | 0 | 0 | 0
23:00 | 2958 | 863 | 902 | 0 | 106 | 1195 | 40 | 3434 | 0 | 0 | 52 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 410 | 04:00 | 386 | 11:00 | Meghnaghat | 411 | 04:00 | 389 | 11:00
Ashuganj | 413 | 4:00 | 362 | 7:00 | Payra | 418 | 01:00 | 410 | 13:00
Bhulta | 409 | 04:00 | 387 | 11:00 | Rahanpur | 419 | 04:00 | 399 | 18:00
Bibiana | 403 | 02:00 | 390 | 11:00 | Rampal | 412 | 03:00 | 300 | 18:00
BIPTC | 408 | 03:00 | 388 | 10:00
Bogura | 414 | 05:00 | 383 | 18:00
Gopalganj | 413 | 04:00 | 395 | 13:00
Kaliakoir | 404 | 04:00 | 379 | 11:00
Korerhat | 412 | 03:00 | 396 | 12:00
Madunaghat | 409 | 05:00 | 394 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 224 | 12:00 | Kachua | 237 | 02:00 | 228 | 11:00
AKSML | 236 | 02:00 | 228 | 11:00 | Kaliakoir | 238 | 03:00 | 223 | 11:00
Aminbazar | 238 | 05:00 | 226 | 11:00 | Keranigonj | 239 | 04:00 | 223 | 12:00
Ashuganj | 240 | 05:00 | 229 | 11:00 | Khulna(S) | 240 | 03:00 | 229 | 18:00
Ashuganj-400 | 240 | 05:00 | 229 | 11:00 | Korerhat | 239 | 03:00 | 229 | 12:00
Baghabari | 240 | 00:00 | 230 | 18:00 | Madunaghat | 236 | 04:00 | 228 | 12:00
Barapukuria | 230 | 04:00 | 126 | 00:00 | Madunaghat-400 | 237 | 04:00 | 228 | 12:00
Barapukuria-230 | 230 | 04:00 | 126 | 00:00 | Maniknagar | 238 | 02:00 | 225 | 12:00
Barishal | 245 | 03:00 | 235 | 13:00 | Meghnaghat | 243 | 03:00 | 232 | 12:00
Bheramara | 238 | 06:00 | 221 | 18:00 | Meghnaghat-400 | 241 | 04:00 | 227 | 12:00
Bhulta | 240 | 04:00 | 225 | 12:00 | Mirsorai | 239 | 07:00 | 229 | 11:00
Bibiana | 237 | 01:00 | 229 | 12:00 | Rajshahi | 239 | 03:00 | 224 | 13:00
BIPTC | 241 | 06:00 | 223 | 18:00 | Rampal | 237 | 02:00 | 227 | 13:00
Bogura | 243 | 04:00 | 227 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 242 | 05:00 | 227 | 18:00 | Rampura | 239 | 04:00 | 224 | 12:00
Borhanuddin | 246 | 03:00 | 240 | 18:00 | Shikalbaha | 234 | 03:00 | 227 | 11:00
BSRM | 239 | 04:00 | 229 | 12:00 | Shyampur | 240 | 04:00 | 224 | 12:00
Cumilla(N) | 238 | 06:00 | 228 | 12:00 | Siddhirganj | 239 | 01:00 | 226 | 11:00
Faridpur | 245 | 04:00 | 235 | 12:00 | Sirajgonj | 246 | 03:00 | 235 | 18:00
Fenchuganj | 240 | 03:00 | 231 | 11:00 | Sreepur | 237 | 01:00 | 224 | 18:00
Feni | 239 | 04:00 | 229 | 12:00 | Tongi | 235 | 19:30 | 215 | 11:00
Ghorashal | 238 | 23:00 | 230 | 11:00
Ghorashal-230 | 234 | 06:00 | 213 | 18:00
Gopalganj | 245 | 04:00 | 235 | 12:00
GPH | 237 | 04:00 | 229 | 12:00
Haripur | 240 | 03:00 | 226 | 12:00
Hasnabad | 239 | 06:00 | 225 | 11:00
Hathazari | 234 | 05:00 | 224 | 11:00
Ishurdi | 242 | 06:00 | 225 | 18:00
Jhenaidah | 239 | 06:00 | 221 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 126 | 11:00 | Lalbag | 136 | 06:00 | 127 | 12:00
Agargaon | 138 | 04:00 | 128 | 11:00 | Lalmonirhat | 130 | 02:00 | 120 | 18:00
Agrabad | 136 | 01:00 | 131 | 11:00 | Madanganj | 139 | 01:00 | 134 | 22:00
AKS | 134 | 01:00 | 130 | 10:00 | Madaripur | 140 | 04:00 | 135 | 18:00
Aminbazar | 138 | 05:00 | 129 | 11:00 | Madartek | 135 | 04:00 | 126 | 12:00
Amnura | 139 | 06:00 | 129 | 13:00 | Madunaghat | 138 | 04:00 | 131 | 16:00
Ashuganj | 141 | 03:00 | 136 | 18:00 | Magura | 137 | 04:00 | 124 | 13:00
Bagerhat | 133 | 04:00 | 122 | 18:00 | Mahasthangarh | 136 | 02:00 | 126 | 18:00
Bajitpur | 137 | 05:00 | 130 | 18:30 | Maijdee | 135 | 04:00 | 129 | 12:00
Bakulia | 138 | 04:00 | 132 | 11:00 | Manikganj | 133 | 03:00 | 122 | 11:00
Banani | 136 | 03:00 | 126 | 11:00 | Maniknagar | 138 | 03:00 | 128 | 12:00
Bangabhaban | 138 | 03:00 | 128 | 12:00 | Matarbari | 128 | 02:00 | 122 | 18:00
Barapukuria | 135 | 04:00 | 124 | 08:00 | Matuail | 141 | 04:00 | 133 | 12:00
Barguna | 137 | 03:00 | 134 | 11:00 | Metrorail_Motijheel | 138 | 03:00 | 128 | 12:00
Barishal | 140 | 05:00 | 134 | 13:00 | Metrorail_Uttara | 138 | 02:00 | 128 | 11:00
Barishal-230 | 142 | 04:00 | 134 | 13:00 | Millgate | 135 | 02:00 | 121 | 11:00
Baroaulia | 135 | 00:00 | 132 | 12:00 | Mirpur | 137 | 03:00 | 128 | 11:00
Baroirhat | 135 | 00:00 | 131 | 11:00 | Mirzapur | 138 | 04:00 | 128 | 11:00
Bashundhara | 136 | 04:00 | 125 | 12:00 | Mithapukur | 134 | 04:00 | 122 | 18:00
BashundharaCement | 139 | 01:00 | 134 | 22:00 | MI_Cement | 138.4 | 06:00 | 126 | 12:00
Beanibazar | 136 | 03:00 | 131 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 135 | 04:00 | 118 | 13:00 | Mogbazar | 137 | 02:00 | 127 | 11:00
Bhaluka | 136 | 04:00 | 128 | 18:00 | Mongla | 132 | 05:00 | 122 | 18:00
Bhandaria | 138 | 04:00 | 133 | 13:00 | Motijheel | 138 | 03:00 | 128 | 12:00
Bhangura | 139 | 03:00 | 131 | 18:00 | Muktagacha | 132 | 22:00 | 126 | 18:00
Bheramara | 142 | 06:00 | 135 | 18:00 | Munshiganj | 139 | 02:00 | 131 | 11:00
Bheramara(GK) | 141 | 03:00 | 135 | 18:00 | Muradnagar | 140 | 04:00 | 132 | 11:00
Bhulta | 132 | 01:00 | 127 | 11:00 | Mymensingh | 132 | 06:00 | 120 | 18:00
Bog-Sherpur | 138 | 03:00 | 130 | 13:00 | Naogaon | 135 | 05:00 | 123 | 13:00
Bogura | 138 | 03:00 | 129 | 18:00 | Narail | 138 | 05:00 | 124 | 13:00
Bogura-230 | 138 | 02:00 | 129 | 18:00 | Narinda | 138 | 03:00 | 128 | 12:00
Brahmanbaria | 135 | 01:00 | 129 | 11:00 | Narshingdi | 139 | 06:00 | 126 | 11:00
Cantonment | 137 | 03:00 | 128 | 11:00 | Natore | 138 | 01:00 | 130 | 13:00
Chandina | 141 | 02:00 | 134 | 12:00 | Nawabganj | 137 | 04:00 | 126 | 12:00
Chandpur | 139 | 05:00 | 135 | 09:00 | Netrakona | 130 | 09:00 | 118 | 18:00
Chandraghona | 139 | 05:00 | 133 | 15:00 | New | 135 | 03:00 | 124 | 12:00
Chapai | 139 | 03:00 | 133 | 18:00 | Niamatpur | 140 | 03:00 | 132 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 141 | 04:00 | 133 | 12:00 | Noapara | 136 | 04:00 | 118 | 13:00
Chauddagram | 138 | 03:00 | 131 | 12:00 | Pabna | 141 | 06:00 | 132 | 18:00
Chhatak | 136 | 03:00 | 130 | 00:00 | Palashbari | 133 | 02:00 | 121 | 18:00
Chowmuhani | 134 | 02:00 | 130 | 00:00 | Panchagarh | 138 | 04:00 | 120 | 08:00
Chuadanga | 136 | 04:00 | 124 | 13:00 | Patiya | 138 | 04:00 | 132 | 11:00
Coxsbazar | 127 | 02:00 | 121 | 17:00 | Patuakhali | 136 | 04:00 | 132 | 11:00
Cumilla(N) | 140 | 05:00 | 133 | 13:00 | Payra | 138 | 04:00 | 134 | 12:00
Cumilla(S) | 141 | 04:00 | 124 | 12:00 | PHP | 136 | 02:00 | 130 | 12:00
Daganbhuiyan | 136 | 02:00 | 130 | 13:00 | Postogola | 138 | 01:00 | 129 | 12:00
Daudkandi | 137 | 04:00 | 129 | 13:00 | Purbachal | 136 | 03:00 | 125 | 12:00
DhakaUniversity | 136 | 03:00 | 126 | 11:00 | Purbasadipur | 131 | 03:00 | 122 | 18:00
Dhamrai | 137 | 03:00 | 130 | 12:00 | Rahanpur | 139 | 01:00 | 133 | 18:00
Dhanmondi | 142.5 | 04:00 | 134 | 12:00 | Rahanpur-400 | 141 | 02:00 | 134 | 18:00
Dohazari | 134 | 05:00 | 129 | 11:00 | Rahim | 140 | 01:00 | 133 | 13:00
Faridpur | 140 | 06:00 | 134 | 12:00 | Rajbari | 140 | 03:00 | 133 | 13:00
Fatullah | 138 | 01:00 | 126 | 12:00 | Rajendrapur | 138 | 03:00 | 129 | 18:00
Fenchuganj | 139 | 01:00 | 135 | 11:00 | Rajshahi | 138 | 01:00 | 130 | 13:00
Feni | 135 | 05:00 | 129 | 13:00 | Rajshahi-230 | 138 | 02:00 | 129 | 13:00
Feni-230 | 137 | 04:00 | 131 | 11:00 | Ramganj | 136 | 01:00 | 132 | 10:00
Ghatail | 133 | 04:00 | 125 | 18:00 | Rampur | 137 | 03:00 | 131 | 11:00
Ghorashal | 135 | 00:00 | 127 | 11:00 | Rampura | 135 | 02:00 | 126 | 12:00
Goalpara | 135 | 04:00 | 128 | 12:00 | Rangamati | 137 | 04:00 | 133 | 11:00
Gollamari | 135 | 04:00 | 128 | 12:00 | Rangpur | 133 | 05:00 | 122 | 13:00
Gopalganj | 139 | 04:00 | 131 | 12:00 | Ruppur | 142 | 02:00 | 134 | 18:00
Gopalganj-400 | 142 | 04:00 | 135 | 13:00 | Saidpur | 134 | 03:00 | 118 | 08:00
Gulshan | 135 | 04:00 | 125 | 12:00 | Satkhira | 133 | 04:00 | 124 | 18:00
Halishahar | 138 | 04:00 | 132 | 10:00 | Satmasjid | 137 | 03:00 | 127 | 13:00
Haripur | 141 | 02:00 | 134 | 12:00 | Savar | 137 | 18:30 | 128 | 12:00
HaripurSBU | 141 | 05:00 | 134 | 13:00 | SevenRings | 137 | 04:00 | 126 | 12:00
Hasnabad | 139 | 04:00 | 129 | 11:00 | ShahCement | 141 | 04:00 | 133 | 12:00
Hathazari | 137 | 03:00 | 133 | 11:00 | Shahjadpur | 141 | 01:00 | 135 | 12:00
Ishurdi | 143 | 06:00 | 135 | 18:00 | Shahjibazar | 136 | 01:00 | 131 | 11:00
Jaldhaka | 129 | 04:00 | 113 | 08:00 | Shahmirpur | 137 | 01:00 | 132 | 11:00
Jamalpur | 129 | 10:00 | 116 | 07:00 | Shariatpur | 141 | 02:00 | 134 | 12:00
Jashore | 136 | 05:00 | 119 | 13:00 | Sherpur | 126 | 10:00 | 113 | 07:00
Jhenaidah | 139 | 04:00 | 121 | 18:00 | Shikalbaha | 127 | 02:00 | 121 | 11:00
Jhenaidah-230 | 139 | 04:00 | 127 | 13:00 | Shikalbaha-230 | 138 | 02:00 | 133 | 11:00
Joydebpur | 134 | 04:00 | 123 | 12:00 | Shitalakhya | 138.4 | 06:00 | 126 | 12:00
Joypurhat | 135 | 03:00 | 121 | 13:00 | Sholosohor | 138 | 04:00 | 133 | 11:00
Juldah | 137 | 02:00 | 132 | 12:00 | Shyampur | 137 | 02:00 | 128 | 11:00
Kabirpur | 139 | 04:00 | 122 | 12:00 | Shyampur-230 | 139 | 04:00 | 129 | 11:00
Kachua | 140 | 02:00 | 135 | 11:00 | Siddhirganj | 141 | 05:00 | 133 | 11:00
Kaliakoir | 141 | 03:00 | 131 | 11:00 | Sirajganj | 138 | 03:00 | 130 | 18:00
Kallyanpur | 138 | 06:00 | 130 | 12:00 | Sonargaon | 139 | 04:00 | 132 | 11:00
Kalurghat | 137 | 02:00 | 133 | 11:00 | Sreemongol | 137 | 04:00 | 131 | 12:00
Kamrangirchar | 136 | 05:00 | 125 | 12:00 | Sreepur | 139 | 01:00 | 130 | 18:00
Kaptai | 138 | 1:00 | 132 | 11:00 | Srinagar | 137 | 06:00 | 126 | 12:00
Kasba | 139 | 03:00 | 131 | 13:00 | SSM | 140 | 19:00 | 136 | 11:00
Kazla | 138 | 04:00 | 128 | 12:00 | Sunamganj | 134 | 04:00 | 129 | 12:00
Keranigonj | 137 | 04:00 | 126 | 12:00 | Sylhet | 136 | 04:00 | 131 | 12:00
Khagrachori | 137 | 02:00 | 132 | 12:00 | Sylhet-132 | 135 | 01:00 | 133 | 11:00
Khulna | 135 | 04:00 | 126 | 18:00 | Tangail | 133 | 04:00 | 126 | 11:00
Khulna(S) | 135 | 01:00 | 128 | 13:00 | Taraganj | 132 | 03:00 | 121 | 18:00
Khulshi | 136 | 02:00 | 130 | 12:00 | Tasnim | 140 | 02:00 | 132 | 11:00
Kishoreganj | 134 | 04:00 | 125 | 18:00 | Thakurgaon | 135 | 04:00 | 116 | 08:00
Kodda | 134 | 01:00 | 122 | 11:00 | TK | 138 | 05:00 | 133 | 11:00
KSRM | 137 | 00:00 | 131 | 12:00 | Tongi | 135 | 01:00 | 124 | 11:00
Kulaura | 139 | 03:00 | 134 | 12:00 | Ullahpara | 140 | 04:00 | 131 | 18:00
Kurigram | 130 | 06:00 | 118 | 08:00 | Ullon | 137 | 14:00 | 125 | 12:00
Kushtia | 138 | 04:00 | 128 | 18:00 | Uttara | 135 | 04:00 | 122 | 12:00
Laksam | 140 | 05:00 | 134 | 04:00 | UttaraNew | 138 | 03:00 | 128 | 11:00
Lakshmipur | 135 | 04:00 | 130 | 10:00 | Zigatola | 137 | 04:00 | 126 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division