## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-12-2025 | during | 21-12-2025 | during | 21-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 348 | 318 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 40 | 104 | 208.13 | 208.13 | 130 | 130 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 10 | 39.3 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26.5 | 20.5 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 34 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 43 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 80 | 130 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 540 | 500 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1089.5 | 1407.8 | 5417.15 | 5399.15 | 2456.86 | 2492.86
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 14 | 0 | 14 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 24 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 225 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 4 | 61 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 37 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 17 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.34 | 0 | 2.01 | 0 | 2.01 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 21 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 580 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 565 | 685 | 720 | 780 | 720 | 520 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1437.34 | 1769 | 3563.73 | 3611.72 | 3005.51 | 2793.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 204 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 250 | 250 | 250 | 250 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 230 | 140 | 318.81 | 318.81 | 318.81 | 318.81 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 360 | 340 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 68 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 106 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 26 | 93 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 110 | 118 | 160 | 160 | 116 | 116 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 20 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1117 | 1139 | 2652.21 | 2622.21 | 2446.21 | 2416.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-12-2025 | during | 21-12-2025 | during | 21-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 70 | 64 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 0.7 | 0 | 0.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 35 | 57 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.37 | 0 | 27.1 | 0 | 27.1 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 2 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 161.37 | 142 | 341.8 | 314 | 294.3 | 266.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 25 | 82 | 95 | 95 | 95 | 95 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 211 | 213 | 210 | 210 | 210 | 210 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 420 | 474 | 503 | 503 | 503 | 503
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 806 | 806 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 55 | 0 | 35 | 0 | 35 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1055 | 1056 | 0 | 0 | 1148 | 1148 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2166 | 2112 | 2307 | 2272 | 2700.1 | 2665.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 350 | 502 | 0 | 0 | 500 | 500 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 68 | 68 | 70 | 70 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 896 | 1050 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1494.52 | 1840 | 1943.32 | 1943.32 | 2310.32 | 2310.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 39.98 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 176 | 171 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 367 | 342 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 28 | 28 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.77 | 0 | 2.8 | 0 | 2.8 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1036.45 | 1365 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | On test
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 37.74 | 0 | 25 | 0 | 25 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 67 | 0 | 55 | 0 | 55 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1727.94 | 1900 | 2996.67 | 2913.87 | 2471.29 | 2388.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 60 | 60 | 60 | 60 | 60 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 2.8 | 0 | 2.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 85.98 | 0 | 85.98 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 240 | 200 | 428.78 | 322 | 394.78 | 288
System Total |  |  |  |  | 28823.2 | 28379.108 | 9853.67 | 10983.8 | 20153.66 | 19901.27 | 16582.37 | 16123.98
Forecast Scenario (21-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8942 |  | 0 |  | 8942
|  |  |  | 1:00 | 8468 |  | 0 |  | 8468
|  |  |  | 2:00 | 8001 |  | 0 |  | 8001
|  |  |  | 3:00 | 7696 |  | 0 |  | 7696
|  |  |  | 4:00 | 7477 |  | 0 |  | 7477
|  |  |  | 5:00 | 7367 |  | 0 |  | 7367
|  |  |  | 6:00 | 7824 |  | 0 |  | 7824
|  |  |  | 7:00 | 8328 |  | 0 |  | 8328
|  |  |  | 8:00 | 9065 |  | 0 |  | 9065
|  |  |  | 9:00 | 9591 |  | 0 |  | 9591
|  |  |  | 10:00 | 9634 |  | 0 |  | 9634
|  |  |  | 11:00 | 9660 |  | 0 |  | 9660
|  |  |  | 12:00 | 10200 |  | 0 |  | 10200
|  |  |  | 13:00 | 10690 |  | 0 |  | 10690
|  |  |  | 14:00 | 10190 |  | 0 |  | 10190
|  |  |  | 15:00 | 9880 |  | 0 |  | 9880
|  |  |  | 16:00 | 9700 |  | 0 |  | 9700
|  |  |  | 17:00 | 10130 |  | 0 |  | 10130
|  |  |  | 18:00 | 11310 |  | 0 |  | 11310
|  |  |  | 18:30 | 11100 |  | 0 |  | 11100
|  |  |  | 19:00 | 11090 |  | 0 |  | 11090
|  |  |  | 19:30 | 10920 |  | 0 |  | 10920
|  |  |  | 20:00 | 10850 |  | 0 |  | 10850
|  |  |  | 21:00 | 10580 |  | 0 |  | 10580
|  |  |  | 22:00 | 10170 |  | 0 |  | 10170
|  |  |  | 23:00 | 9710 |  | 0 |  | 9710
Probable Maximum Temperature: |  |  | 29.20°C
Probable Maximum Demand at Day Peak: |  |  | 10200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11310.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11310.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 226.95184 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:07 hrs on 21-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-12-2025 | [28 empty] | Date: | 20-12-2025 | [28 empty] | Date: | 20-12-2025 | [28 empty] | Date: | 20-12-2025 | [28 empty] | Date: | 20-12-2025 | [17 empty] | Date: | 20-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 335 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 577 | 0 | 0 | 0 | 310 | 0 | 100 | 51 | 0 | 196 | 0 | 0 | 110 | 0 | 0 | 13 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 0 | 0 | 15 | 96 | 0 | 8 | 8 | 118 | 0 | 0 | 0 | 3670 | 806 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866 | 0 | 2 | 0 | 865.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 220 | 0 | 250 | 950 | 0 | 4909.91 | 8579.91 | 98.6
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 300 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 535 | 0 | 0 | 0 | 230 | 113 | 30 | 51 | 0 | 160 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 80 | 0 | 0 | 15 | 96 | 0 | 8 | 8 | 118 | 0 | 0 | 0 | 3473 | 759 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 2 | 0 | 837.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 220 | 0 | 250 | 850 | 0 | 4610.62 | 8083.62 | 98.59
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 220 | 39 | 30 | 51 | 0 | 130 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 15 | 96 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 3203 | 665 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 2 | 0 | 841.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 220 | 0 | 250 | 800 | 0 | 4464.06 | 7667.06 | 98.59
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 292 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 220 | 193 | 0 | 5 | 0 | 130 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 15 | 96 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 3169 | 599 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 2 | 0 | 840.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 220 | 0 | 250 | 660 | 0 | 4259.5 | 7428.5 | 98.59
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 293 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 220 | 260 | 0 | 5 | 0 | 130 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 15 | 96 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 3172 | 525 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 2 | 0 | 831.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 180 | 0 | 250 | 600 | 0 | 4069.06 | 7241.06 | 98.59
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 293 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 220 | 164 | 0 | 5 | 0 | 160 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 15 | 96 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 3028 | 525 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 2 | 0 | 833.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 0 | 50 | 180 | 0 | 250 | 550 | 0 | 4026.38 | 7054.38 | 98.59
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 309 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 393 | 0 | 0 | 15 | 0 | 199 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 0 | 17 | 0 | 80 | 0 | 0 | 15 | 96 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 3422 | 525 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 0 | 2 | 0 | 831.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 220 | 0 | 250 | 570 | 0 | 4160.42 | 7582.42 | 98.59
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 40 | 0 | 42 | 422 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 560 | 2 | 0 | 0 | 363 | 0 | 0 | 51 | 0 | 205 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 76 | 0 | 3 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 1 | 17 | 0 | 80 | 0 | 0 | 15 | 96 | 0 | 2 | 3 | 116 | 0 | 1.04 | 0 | 3699.16 | 525 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 862 | 0 | 2 | 0 | 933.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0 | 0.22 | 0 | 0 | 197 | 0 | 0 | 0 | 400 | 0 | 0.02 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.05 | 0 | 0 | 68 | 220 | 0 | 300 | 610 | 0 | 4429.65 | 8128.81 | 98.59
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 91 | 0 | 3 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 513 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 585 | 8 | 0 | 0 | 375 | 0 | 0 | 51 | 0 | 218 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 86 | 0 | 17 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 2 | 17 | 0 | 80 | 0 | 0 | 15 | 96 | 0 | 24 | 19 | 112 | 0 | 9.46 | 0 | 3965.46 | 618 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 920 | 0 | 2 | 0 | 931.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 2 | 0 | 0 | 2.45 | 0 | 0 | 206 | 0 | 0 | 0 | 414 | 0 | 0.25 | 0 | 62 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 14 | 0.09 | 0 | 0 | 68 | 220 | 0 | 407 | 791 | 0 | 4922.21 | 8887.67 | 98.58
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 60 | 0 | 8 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.98 | 40 | 0 | 9 | 513 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 580 | 14 | 0 | 0 | 334 | 0 | 77 | 51 | 0 | 194 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 90 | 0 | 44 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 3 | 17 | 0 | 80 | 0 | 0 | 18 | 96 | 0 | 24 | 19 | 72 | 0 | 17.93 | 0 | 3990.91 | 692 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1065 | 0 | 0 | 0 | 1034.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 9 | 0 | 0 | 11.49 | 0 | 0 | 208 | 0 | 0 | 0 | 366 | 0 | 1.46 | 0 | 60 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 23 | 0.24 | 0 | 0 | 70 | 220 | 0 | 450 | 968 | 0 | 5457.04 | 9447.95 | 98.58
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 495 | 0 | 0 | 0 | 40 | 0 | 12 | 0 | 24.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 40 | 0 | 9 | 513 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 580 | 17 | 0 | 0 | 290 | 0 | 170 | 51 | 0 | 189 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 98 | 0 | 53 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 7 | 17 | 0 | 80 | 0 | 0 | 18 | 96 | 0 | 24 | 19 | 72 | 0 | 29.27 | 0 | 3978.38 | 712 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 1082 | 0 | 0 | 0 | 1036.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.92 | 25 | 0 | 0 | 19.38 | 0 | 0 | 192 | 0 | 0 | 0 | 336 | 0 | 1.37 | 0 | 60 | 0 | 7 | 0 | 0 | 0 | 0 | 2.7 | 50 | 0.25 | 0 | 0 | 68 | 180 | 0 | 350 | 932 | 0 | 5354.12 | 9332.5 | 98.58
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 40 | 0 | 22 | 0 | 25.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | 40 | 0 | 9 | 513 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 580 | 18 | 0 | 0 | 305 | 0 | 230 | 51 | 0 | 194 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 100 | 0 | 62 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 8 | 17 | 0 | 80 | 0 | 0 | 18 | 40 | 0 | 35 | 19 | 72 | 1 | 36.02 | 0 | 3964.96 | 806 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 1052 | 0 | 0 | 0 | 1020.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2 | 34 | 0 | 0 | 30.4 | 0 | 0 | 178 | 0 | 0 | 0 | 349 | 0 | 3.66 | 0 | 62 | 0 | 17 | 0 | 0 | 0 | 0 | 4.8 | 125 | 0.4 | 0 | 0 | 68 | 180 | 0 | 350 | 900 | 0 | 5489.11 | 9454.07 | 98.58
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 540 | 0 | 0 | 0 | 40 | 0 | 23 | 0 | 26.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.34 | 40 | 0 | 12 | 565 | 0 | 0 | 0 | 0 | 4 | 224 | 0 | 0 | 0 | 580 | 9 | 0 | 0 | 360 | 0 | 230 | 51 | 0 | 204 | 0 | 0 | 105 | 26 | 0 | 11 | 0 | 110 | 0 | 20 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 9 | 17 | 0 | 80 | 0 | 0 | 18 | 25 | 0 | 35 | 19 | 70 | 1 | 36.37 | 0 | 4225.21 | 806 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1055 | 0 | 0 | 0 | 1036.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.98 | 67 | 0 | 0 | 37.74 | 0 | 0 | 176 | 0 | 0 | 0 | 367 | 0 | 3.77 | 0 | 62 | 0 | 28 | 0 | 0 | 0 | 0 | 5 | 145 | 0.52 | 0 | 0 | 68 | 180 | 0 | 350 | 896 | 0 | 5628.46 | 9853.67 | 98.57
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 30.8 | 0 | 10 | 0 | 60 | 0 | 14 | 102 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 40 | 0 | 22 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 3.14 | 40 | 0 | 13 | 626 | 0 | 0 | 0 | 0 | 50 | 223 | 0 | 0 | 0 | 580 | 19 | 20 | 0 | 305 | 0 | 180 | 51 | 0 | 195 | 0 | 0 | 104 | 72 | 0 | 11 | 0 | 118 | 0 | 30 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 8 | 17 | 0 | 80 | 0 | 0 | 18 | 25 | 0 | 35 | 19 | 63 | 2 | 33.89 | 0 | 4472.33 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 1070 | 0 | 0 | 0 | 1033.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.92 | 54 | 0 | 0 | 38.4 | 0 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 2.94 | 0 | 62 | 0 | 26 | 0 | 0 | 0 | 0 | 4.9 | 141 | 0.43 | 0 | 0 | 68 | 220 | 0 | 350 | 900 | 0 | 5815.28 | 10287.61 | 98.57
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 33.7 | 0 | 0 | 0 | 60 | 0 | 17 | 97 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 40 | 0 | 20 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 2.62 | 40 | 0 | 15 | 635 | 0 | 0 | 0 | 0 | 49 | 222 | 0 | 0 | 0 | 580 | 16 | 20 | 0 | 275 | 0 | 180 | 51 | 0 | 194 | 0 | 0 | 103 | 79 | 0 | 14 | 0 | 108 | 0 | 24 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 7 | 17 | 0 | 80 | 0 | 0 | 18 | 82 | 0 | 35 | 19 | 63 | 1 | 27.93 | 0 | 4406.25 | 740 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 1050 | 0 | 0 | 0 | 1040.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.53 | 44 | 0 | 0 | 31.49 | 0 | 0 | 173 | 0 | 0 | 0 | 387 | 0 | 2.63 | 0 | 61 | 0 | 21 | 0 | 0 | 0 | 0 | 4 | 115 | 0.16 | 0 | 0 | 68 | 180 | 0 | 300 | 894 | 0 | 5428.82 | 9835.07 | 98.57
15:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 31.4 | 0 | 19 | 0 | 30 | 0 | 17 | 70 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 41 | 0 | 11 | 0 | 28.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 1.72 | 40 | 0 | 10 | 657 | 0 | 0 | 0 | 0 | 34 | 223 | 0 | 0 | 0 | 540 | 12 | 20 | 0 | 275 | 0 | 140 | 51 | 0 | 197 | 0 | 0 | 104 | 51 | 0 | 14 | 0 | 108 | 0 | 19 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 4 | 17 | 0 | 80 | 0 | 0 | 18 | 82 | 0 | 35 | 19 | 62 | 1 | 18.87 | 0 | 4255.49 | 712 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1018 | 0 | 0 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.45 | 16 | 0 | 0 | 17.7 | 0 | 0 | 175 | 0 | 0 | 0 | 362 | 0 | 1.51 | 0 | 61 | 0 | 14 | 0 | 0 | 0 | 0 | 2.7 | 74 | 0.19 | 0 | 0 | 68 | 220 | 0 | 300 | 940 | 0 | 5353.55 | 9609.04 | 98.57
16:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 31.4 | 0 | 44 | 0 | 30 | 0 | 17 | 65 | 0 | 0 | 0 | 445 | 0 | 0 | 0 | 41 | 0 | 4 | 0 | 28.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0.8 | 40 | 0 | 10 | 720 | 0 | 0 | 0 | 0 | 31 | 223 | 0 | 0 | 0 | 524 | 6 | 20 | 0 | 285 | 0 | 140 | 51 | 0 | 199 | 0 | 0 | 105 | 48 | 0 | 14 | 0 | 108 | 0 | 10 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 2 | 17 | 0 | 42 | 0 | 0 | 18 | 82 | 0 | 35 | 19 | 63 | 0 | 7.56 | 0 | 4196.26 | 712 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 999 | 0 | 0 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.18 | 10 | 0 | 0 | 6.45 | 0 | 0 | 174 | 0 | 0 | 0 | 370 | 0 | 0.57 | 0 | 60 | 0 | 6 | 0 | 0 | 0 | 0 | 1.1 | 30 | 0.08 | 0 | 0 | 68 | 200 | 0 | 300 | 950 | 0 | 5310.38 | 9506.64 | 98.56
17:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 32.1 | 0 | 43 | 0 | 48 | 0 | 17 | 95 | 0 | 0 | 0 | 490 | 0 | 13 | 0 | 41 | 0 | 1 | 0 | 28.5 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 25 | 0 | 40 | 4 | 15 | 690 | 0 | 0 | 4 | 0 | 30 | 223 | 0 | 0 | 0 | 520 | 0 | 31 | 0 | 325 | 0 | 140 | 51 | 0 | 190 | 0 | 11 | 106 | 53 | 0 | 10 | 0 | 104 | 0 | 1 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 18 | 82 | 0 | 40 | 19 | 64 | 0 | 0.37 | 0 | 4384.97 | 712 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1005 | 0 | 0 | 0 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0 | 18 | 0 | 0.75 | 0 | 0 | 197 | 0 | 0 | 0 | 343 | 0 | 0.07 | 0 | 59 | 35 | 0 | 34 | 0 | 0 | 0 | 0.1 | 2 | 0.01 | 0 | 0 | 60 | 200 | 0 | 350 | 966 | 0 | 5438.79 | 9823.76 | 98.56
18:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 39.3 | 0 | 43 | 0 | 145 | 0 | 35 | 130 | 0 | 0 | 0 | 500 | 0 | 17 | 0 | 104 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 24 | 0 | 37 | 25 | 0 | 40 | 21 | 17 | 685 | 0 | 0 | 24 | 0 | 61 | 225 | 0 | 0 | 0 | 580 | 0 | 68 | 0 | 340 | 0 | 140 | 51 | 0 | 190 | 0 | 16 | 106 | 93 | 0 | 17 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 0 | 0 | 18 | 82 | 0 | 57 | 19 | 64 | 0 | 0 | 2 | 4931.8 | 806 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 0 | 0 | 0 | 1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 60 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 502 | 1050 | 0 | 6052 | 10983.8 | 98.56
19:00 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 28.2 | 0 | 43 | 0 | 80 | 0 | 35 | 101 | 0 | 0 | 0 | 540 | 0 | 17 | 0 | 102 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 25 | 714 | 0 | 0 | 0 | 0 | 34 | 226 | 0 | 0 | 0 | 694 | 0 | 12 | 0 | 305 | 0 | 140 | 51 | 0 | 199 | 0 | 0 | 108 | 68 | 0 | 17 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 0 | 0 | 17 | 82 | 0 | 57 | 19 | 64 | 0 | 0 | 0 | 4725.7 | 900 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 4 | 0 | 1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 60 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 450 | 1020 | 0 | 6020 | 10745.7 | 98.56
19:30 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 28.2 | 0 | 54 | 0 | 80 | 0 | 35 | 102 | 0 | 0 | 0 | 550 | 0 | 17 | 0 | 102 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 19 | 720 | 0 | 0 | 0 | 0 | 32 | 226 | 0 | 0 | 0 | 707 | 0 | 12 | 0 | 305 | 0 | 140 | 51 | 0 | 191 | 0 | 0 | 108 | 64 | 0 | 17 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 0 | 0 | 17 | 82 | 0 | 57 | 19 | 64 | 0 | 0 | 0 | 4780.7 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 4 | 0 | 1261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 60 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 400 | 1020 | 0 | 5887 | 10667.7
20:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 32.4 | 0 | 58 | 0 | 30 | 0 | 17 | 99 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 23 | 720 | 0 | 0 | 0 | 0 | 16 | 226 | 0 | 0 | 0 | 700 | 0 | 10 | 0 | 305 | 0 | 140 | 51 | 0 | 199 | 0 | 0 | 108 | 65 | 0 | 17 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 0 | 0 | 17 | 82 | 0 | 57 | 0 | 64 | 0 | 0 | 0 | 4650.9 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 4 | 0 | 1273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 400 | 1020 | 0 | 5895 | 10545.9 | 98.55
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 23.4 | 0 | 60 | 0 | 15 | 0 | 17 | 52 | 0 | 0 | 0 | 552 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 23 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 766 | 0 | 0 | 0 | 305 | 0 | 140 | 51 | 0 | 187 | 0 | 0 | 109 | 17 | 0 | 17 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 0 | 0 | 18 | 82 | 0 | 57 | 0 | 65 | 0 | 0 | 0 | 4531.9 | 901 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 4 | 0 | 1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 60 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 400 | 1020 | 0 | 5937 | 10468.9 | 98.55
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 867 | 0 | 0 | 0 | 310 | 0 | 140 | 51 | 0 | 190 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 30 | 0 | 18 | 82 | 0 | 45 | 0 | 64 | 0 | 0 | 0 | 4434 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 0 | 4 | 0 | 1177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 300 | 950 | 0 | 5587 | 10021 | 98.55
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 715 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 866 | 0 | 0 | 0 | 310 | 0 | 140 | 51 | 0 | 196 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 30 | 0 | 18 | 82 | 0 | 24 | 0 | 77 | 0 | 0 | 0 | 4380 | 875 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 875 | 0 | 4 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 190 | 0 | 300 | 800 | 0 | 4990 | 9370 | 98.55
Total KWH | 0 | 39360 | 139680 | 0 | 0 | 0 | 0 | 0 | 8409600 | 0 | 0 | 291240 | 0 | 363168 | 0 | 558022 | 0 | 207904 | 1002240 | 0 | 0 | 0 | 12413359 | 0 | 54286 | 0 | 1552000 | 0 | 131645 | 0 | 426600 | 514800 | 0 | 0 | 0 | 55200 | 0 | 0 | 12480 | 0 | 52520 | 0 | 63360 | 200640 | 19680 | 972000 | 55199 | 401760 | 13032727.27 | 0 | 0 | 41280 | 0 | 374690 | 5349793 | 0 | 0 | 0 | 14045453 | 129060 | 274327 | 0 | 7287500 | 821200 | 2594000 | 1108768 | 0 | 4602000 | 0 | 46080 | 2491368 | 644160 | 0 | 313600 | 0 | 2261760 | 0 | 292309 | 0 | 0 | 0 | 5186000 | 716000 | 714240 | 0 | 50720 | 443060 | 0 | 1454400 | 82848 | 0 | 413000 | 1971200 | 0 | 697200 | 242400 | 1953600 | 6000 | 222030 | 11040 | 97810556.27 | 17610909 | 6486912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342720 | 22981820 | 0 | 50182 | 0 | 24777396 | 0 | 0 | 0 | 0 | 18912 | 0 | 0 | 0 | 0 | 167724 | 276132 | 41424 | 0 | 188240 | 0 | 0 | 4588673 | 0 | 0 | 0 | 8965818 | 0 | 17520 | 0 | 1405090 | 155123 | 127019 | 206265 | 0 | 0 | 0 | 26705.4 | 712080 | 2118 | 0 | 0 | 1597000 | 5325319 | 0 | 8114125 | 21248000 | 0 | 125433226.4 | 223243782.67

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9853.67 | MW | 12:00 Hr. | Energy Generated |  |  | 223.2438 |  | MKWHr.
| Day Peak Demand |  |  | 9853.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10983.8 | MW | 18:00 Hr. | Energy Demand |  |  | 223.2438 |  | MKWHr.
| Evening Peak Demand |  |  | 10983.8 | MW | 18:00 Hr. | Maximum Temperature |  |  | 27.5 |  | °C
| Minimum Generation of the Day |  |  | 7054.38 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 677.32 |  | MMCFD
| Maximum Generation of the Day |  |  | 10983.8 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.6437 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.3164 | 0 | 2.6559 | 0 | 0 | 0.13165 | 0 | 0 | 26.1039 | Gas | 88.2346 | Gas | 310215953.1
| Chattogram Zone |  |  | 5.7516 | 27.0782 | 0.84289 | 0 | 0.972 | 0.14874 | 0 | 0.01248 | 34.8058 | Coal | 80.8272 | Coal | 544634373.8931
| Cumilla Zone |  |  | 19.2184 | 0 | 0.96457 | 0 | 0 | 0.29231 | 2.2618 | 0 | 22.7371 | HFO | 5.8357 | HFO | 95679196.58
| Mymensingh Zone |  |  | 1.9536 | 0 | 0.95064 | 0 | 0 | 0.22803 | 0 | 0 | 3.1323 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 10.9807 | 0 | 0 | 0 | 0 | 0.05072 | 0 | 0 | 11.0315 | Hydro | 0.972 | Hydro | 97200
| Khulna Zone |  |  | 6.5371 | 22.9818 | 0 | 0 | 0 | 0.34272 | 17.6109 | 0 | 47.4725 | Solar | 2.7117 | Solar | 43359871.25
| Barishal Zone |  |  | 6.9223 | 29.3621 | 0 | 0 | 0 | 0.002118 | 0 | 0 | 36.2866 | Import | 44.6501 | Import | 265750741.56
| Rajshahi Zone |  |  | 13.5545 | 0 | 0.060336 | 0 | 0 | 0.64962 | 24.7774 | 0 | 39.0418 | Wind | 0.01248 | Wind | 183580.8
| Rangpur Zone |  |  | 0 | 1.4051 | 0.36139 | 0 | 0 | 0.8658 | 0 | 0 | 2.6323
| Total |  |  | 88.2346 | 80.8272 | 5.8357 | 0 | 0.972 | 2.7117 | 44.6501 | 0.01248 | 223.2438
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 310215953.1 |  | Hydro | 97200
|  |  |  | Coal | 544634373.8931 |  | Solar | 43359871.25
|  |  |  | HFO | 95679196.58 |  | Import | 265750741.56
|  |  |  | HSD | 0 |  | Wind | 183580.8
[5 empty] | Total: | 125,99,20,917 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.6109 | Peak Hr Flow | 806.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52177872.74 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.7774 | Peak Hr Flow | 1365.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2666 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2618 | Peak Hr Flow | 118.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2818 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.6501 | Peak Hr Flow | 2289.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4038
|  |  |  | Chattogram |  | 0 |  | 1229
|  |  |  | Cumilla |  | 0 |  | 909
|  |  |  | Mymensingh |  | 0 |  | 860
|  |  |  | Sylhet |  | 0 |  | 389
|  |  |  | Khulna |  | 0 |  | 1236
|  |  |  | Barishal |  | 0 |  | 310
|  |  |  | Rajshahi |  | 0 |  | 959
|  |  |  | Rangpur |  | 0 |  | 759
|  |  |  | Total |  | 0 |  | 10689
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 | 16:14 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to
annual maintenance work and from Madaripur 132/33kV end Due to Annual Maintenance
| 08:11 | 16:14 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to
annual maintenance work and from Madaripur 132/33kV end Due to Annual Maintenance
| 08:11 | 16:14 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to
annual maintenance work and from Madaripur 132/33kV end Due to Annual Maintenance
| 08:15 | 16:28 | Ishurdi-Pabna 132kV ckt Scheduled S/D from Pabna 132/33kV end Due to Annual Maintenance.
and from Ishurdi 132/33kVend.
| 08:22 |  | Barapukuria-Rangpur 132 kV Ckt-2 Project Work S/D from Barapukuria 230/132/33kV end Due
to Reconductoring work for capacity upgradation and from Rangpur 132/33kV end Due to
Conductor Re-Conducting
| 08:22 | 17:43 | C.nawabganj-Rajshahi 132 kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to Annual
Maintenance. and from Rajshahi 230/132/33kV end Due to Annual Maintenance.
| 08:30 | 09:45 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance.
| 08:36 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 08:41 | 16:16 | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to
Annual Maintanance works. and from Shahjibazar 132/33kV end Due to Shutdown for annual
maitenance.
| 08:43 | 15:38 | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance
| 08:50 | 15:51 | Kodda 132/33kV S/S Bus-2 Scheduled S/D Due to Annual maintenance
| 08:54 | 18:26 | Chowmuhani 132/33kV S/S TR3-435T LT Scheduled S/D Due to Annual Maintenance
| 08:55 | 18:26 | Chowmuhani 132/33kV S/S TR3-435T HT Scheduled S/D Due to Annual Maintenance
| 08:56 | 16:58 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Scheduled S/D Due to Annual Maintenance
| 08:56 | 16:58 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT Scheduled S/D Due to Annual maintenance
| 09:06 | 09:48 | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to 132kV Bus 2 annual maintenance
| 09:06 | 14:54 | Sirajganj 132/33kV S/S T4-(445) LT Scheduled S/D Due to Annual Maintenance
| 09:06 | 14:54 | Sirajganj 132/33kV S/S T4-(445) HT Scheduled S/D Due to Annual Maintenance
| 09:11 | 16:51 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to Annual maintenance.
| 09:12 | 16:51 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to Annual maintenance.
| 09:21 |  | Ashuganj-Ghorasal 132kV Ckt-2 Scheduled S/D from Ashuganj 230/132/33kV end Due to
Shutdown by PGB OFCN
| 09:24 | 14:31 | Jashore 132/33kV S/S T-3 LT Scheduled S/D Due to Annual Maintenance
| 09:24 | 14:30 | Jashore 132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintenance
| 09:29 | 11:15 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D Due to Tandelta Test
| 09:29 | 11:15 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D Due to Tandelta Test
| 09:42 |  | KSRM 132/33kV S/S Transformer-02 HT Scheduled S/D Due to 33 kV Bus-02 Emergency
Maintenance
| 09:48 | 10:35 | Kodda 132/33kV S/S RPCL 100 MW PS Scheduled S/D Due to 132kV Bus 2 Annual maintenance
| 09:59 | 15:08 | Haripur 230/132kV S/S 132kV Main Bus Sec-1 Scheduled S/D Due to Annual Maintenance
| 09:59 | 15:53 | Mahasthangar-Palashbari 132kV Ckt-1 Forced S/D from Palashbari 132/33kV end. and from
Mahasthangarh 132/33kV end Due to Annual maintenance
| 10:04 | 17:54 | Chowmuhani 132/33kV S/S HFPL line Project Work S/D Due to Bypass conductor installment in
the area of medical.
| 10:06 | 22:24 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Loop
changing work
| 10:16 | 15:34 | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to Bus DS maintenance
| 10:20 | 16:55 | Sonargaon 132/33kV S/S BUS A Forced S/D Due to Bashundhara line DS Maintenance
| 10:29 | 15:09 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Deadline checking by Savar Grid S/S
| 10:35 | 11:58 | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Kodda 132/33kV end Due to 132kV bus 2
maintenance
| 10:35 | 11:58 | Kodda-Rajendrapur 132kV Ckt-2 Scheduled S/D from Kodda 132/33kV end Due to 132kV bus 2
maintenance
| 11:26 | 15:06 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Scheduled S/D Due to Tandelta test
| 11:26 | 15:06 | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Scheduled S/D Due to Tandelta test
|  | 11:54 | Keranigonj 230/132/33kV S/S ATR-1 HT is restored.
|  | 11:55 | Keranigonj 230/132/33kV S/S ATR-1 LT is restored.
|  | 11:55 | Keranigonj 230/132/33kV S/S ATR-1 LT is restored.
| 12:00 |  | Day peak generation 9849 MW
| 12:20 | 12:58 | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to Annual maintenance
| 12:21 | 12:54 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to A/M
| 12:55 | 13:15 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to A/M
| 12:55 | 13:15 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to A/M
| 13:18 | 13:27 | Kabirpur -Kodda 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing Backup protection | [7 empty] | 140.0MW load
|  |  | realy poerated relays Due to Over current | [7 empty] | interrup. Kabirpur
132/33kV end
| 14:35 | 14:58 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to A/M
| 14:35 | 14:58 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to AM
| 18:08 |  | SS Power Bashkhali Unit-1 was synchronized
|  | 18:14 | Aminbazar-Meghnaghat 400kV Ckt-1 is restored.
| 19:06 |  | Around 65 MW interruption occurred from 19:06 hrs. to 19:29 hrs. under Ullon grid s/s
(DPDC) due to tripping of Rampura-Ullon ckt-1 and Ullon-Dhanmondi ckt-1 showing distance
(zone-1, Blue phase) relay caused by 132 kV circuit breaker blast at Ullon end. Now Ullon
is taking load through Rampura-Ullon ckt-2.
| 19:08 | 20:43 | Rampura-Ullon-2 132kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance
protection 21.Z1 (BN) relays Due to No
| 19:37 |  | Moghbazar-Rampura 132kV Ckt-1 Forced S/D from Rampura 230/132kV end Due to S/D Taken by
NLDC
|  | 21:00 | Jhenaidah 230/132kV S/S Transformer- 2 HT is restored.
|  | 21:03 | Jhenaidah 230/132kV S/S Transformer- 2 LT is restored.
| 21:36 |  | Khulna(C )-Noapara 132kV Ckt-1 Forced S/D from Khulna (C) end Due to ALDC
recommendation.
| 21:36 |  | Khulna(C )-Noapara 132kV Ckt-2 Forced S/D from Khulna (C) end Due to ALDC
recommendation.
| 03:57 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 03:57 |  | Ashuganj North CCPP GT was sync.
| 05:58 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
| 05:59 |  | Ashuganj (South) 360 MW CCPP was shutdown.
| 06:15 |  | Siddhirganj 335 MW CCPP GT was sync.
| 07:13 |  | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual maintenance. | [7 empty] | 10.0MW load
interrup.
| 07:14 |  | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual maintenance. | [7 empty] | 10.0MW load
interrup.
| 07:35 |  | Bashundhara-Rampura 132 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance.
| 07:48 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Tripped showing BUCHHOLZ
Relay relays Due to TR SELF PROTECTION TRIP, OLTC 1/2/3 BUCHHOLZ TRIP
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 318 | 8409600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 104 | 1552000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 39.3 | 291240 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 207904 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 54286 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 426600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 514800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 139680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 558022 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 43 | 363168 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 39360 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 130 | 1002240 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 131645 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 500 | 12413359 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1407.8 | 26103904
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 129060 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 41280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 972000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 225 | 5349793 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 61 | 374690 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 52520 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 63360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 401760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 55200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 21 | 55199 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 200640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 14045453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 12480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 685 | 13032727.27 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 1769 | 34805842.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4602000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 821200 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 140 | 2594000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 340 | 7287500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1108768 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 68 | 274327 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 106 | 2491368 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 93 | 644160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 118 | 2261760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 313600 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 46080 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 292309 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1139 | 22737072
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 64 | 1953600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 242400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 697200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 222030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 2 | 11040 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 142 | 3132270
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 50720 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 714240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 82848 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1454400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 82 | 1971200 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 413000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 443060 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 213 | 5186000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 474 | 11031468
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 0 | 50182 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 806 | 17610909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6486912 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 342720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1056 | 22981820 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2112 | 47472543
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 502 | 8114125 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 68 | 1597000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1050 | 21248000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5325319 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2118 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1840 | 36286562
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 167724 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 171 | 4588673 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 342 | 8965818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 41424 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 18912 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 17520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1365 | 24777396 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 188240 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 276132 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1900 | 39041839
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 60 | 1405090 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 206265 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 26705.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 155123 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 127019 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 712080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 200 | 2632282.4
Eastern Grid Total |  |  |  |  | 17395.105 | 4931.8 | 97810556.27
Western Grid Total |  |  |  |  | 10984.003 | 6052 | 125433226.4
National Grid Total |  |  |  |  | 28379.108 | 10983.8 | 223243782.67
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7425.07 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3264.7 | MW
i) Dhaka area |  |  | 4038.07 |  | MW | i) Khulna area |  |  |  | 1236.5 | MW
ii) Chattogram area |  |  | 1229 |  | MW | ii) Barishal area |  |  |  | 310 | MW
iii) Cumilla area |  |  | 909 |  | MW | iii) Rajshahi area |  |  |  | 959.2 | MW
iv) Mymensingh area |  |  | 860 |  | MW | iv) Rangpur area |  |  |  | 759 | MW
v) Sylhet area |  |  | 389 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10689.77 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 73 | 19:30 | 133 | Netrakona | 102 | 18:00
2 | AKSML | 115.7 | 07:00 | 68 | Hathazari | 58 | 14:00 | 134 | New | 72 | 12:00
3 | Aftabnagar | 26 | 14:00 | 69 | Hatirjheel | 0 | 23:00 | 135 | Niamatpur | 46 | 09:00
4 | Agargaon | 85 | 13:00 | 70 | Ishurdi | 48 | 18:30 | 136 | Noapara | 39 | 18:30
5 | Agrabad | 42 | 18:30 | 71 | Jaldhaka | 54 | 18:00 | 137 | PHP | 8 | 19:00
6 | Amnura | 26 | 09:00 | 72 | Jamalpur | 88 | 19:00 | 138 | Pabna | 71 | 18:00
7 | Ashuganj | 57 | 12:00 | 73 | Jashore | 106 | 13:00 | 139 | Palashbari | 75 | 18:00
8 | BSRM | 203 | 04:00 | 74 | Jhenaidah | 95 | 18:00 | 140 | Panchagarh | 50 | 18:00
9 | Bagerhat | 58 | 18:00 | 75 | Joydebpur | 91 | 12:00 | 141 | Patiya | 6.3 | 20:00
10 | Bajitpur | 54 | 18:00 | 76 | Joypurhat | 42 | 09:00 | 142 | Patuakhali | 46 | 21:00
11 | Bakerganj | 0 | 20:00 | 77 | Juldah | 10 | 00:00 | 143 | Payra | 22 | 18:00
12 | Bakulia | 64 | 18:00 | 78 | KSRM | 15 | 18:00 | 144 | Postogola | 40 | 13:00
13 | Banani | 38 | 13:00 | 79 | Kabirpur | 183 | 16:00 | 145 | Purbachal | 26 | 13:00
14 | Bangabhaban | 6 | 10:00 | 80 | Kachua | 55 | 19:30 | 146 | Purbasadipur | 108 | 12:00
15 | Barapukuria | 48 | 18:00 | 81 | Kallyanpur | 75 | 13:00 | 147 | Rahanpur | 23 | 18:00
16 | Barguna | 10 | 18:00 | 82 | Kalurghat | 32 | 15:00 | 148 | Rahim | 45 | 12:00
17 | Barishal | 83 | 13:00 | 83 | Kamrangirchar | 61 | 12:00 | 149 | Rajbari | 59 | 18:00
18 | Barishal-230 | 74 | 21:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 97 | 18:00
19 | Baroaulia | 52 | 13:00 | 85 | Kasba | 26 | 19:00 | 151 | Rajshahi | 74 | 13:00
20 | Baroirhat | 50 | 13:00 | 86 | Kazla | 82 | 12:00 | 152 | Rajshahi-230 | 62 | 13:00
21 | Bashundhara | 143 | 13:00 | 87 | Keranigonj | 54 | 13:00 | 153 | Ramganj | 66 | 18:00
22 | BashundharaCement | 12 | 15:00 | 88 | Khagrachori | 26 | 18:00 | 154 | Rampur | 28 | 18:00
23 | Beanibazar | 44 | 18:00 | 89 | Khulna | 52 | 13:00 | 155 | Rangamati | 14 | 18:00
24 | Benapole | 34 | 08:00 | 90 | Khulshi | 171 | 12:00 | 156 | Rangpur | 102 | 18:00
25 | Bhaluka | 121 | 18:30 | 91 | Kishoreganj | 85 | 19:00 | 157 | Ruppur | 1.4 | 00:00
26 | Bhandaria | 36 | 22:00 | 92 | Kodda | 251 | 10:00 | 158 | SSM | 1 | 23:00
27 | Bhangura | 22 | 08:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 90 | 18:00
28 | Bheramara(GK) | 42 | 18:00 | 94 | Kurigram | 48 | 18:00 | 160 | Satkhira | 93 | 18:00
29 | Bhulta | 172 | 19:00 | 95 | Kushtia | 115 | 18:00 | 161 | Satmasjid | 75 | 13:00
30 | Bog-Sherpur | 52 | 09:00 | 96 | Laksam | 24 | 13:00 | 162 | Savar | 158 | 12:00
31 | Bogura | 108 | 18:00 | 97 | Lakshmipur | 24 | 20:00 | 163 | SevenRings | 12.21 | 19:00
32 | Borhanuddin | 63 | 20:00 | 98 | Lalbag | 52 | 12:00 | 164 | ShahCement | 31 | 04:00
33 | Brahmanbaria | 86 | 19:30 | 99 | Lalmonirhat | 43 | 18:00 | 165 | Shahjadpur | 52 | 18:00
34 | Cantonment | 63 | 13:00 | 100 | MI_Cement | 12.4 | 23:00 | 166 | Shahjibazar | 81 | 18:00
35 | Chandina | 8 | 13:00 | 101 | Madanganj | 27 | 21:00 | 167 | Shahmirpur | 42 | 18:00
36 | Chandpur | 54 | 13:00 | 102 | Madaripur | 68 | 13:00 | 168 | Shariatpur | 54 | 19:30
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 54 | 12:00 | 169 | Sherpur | 106 | 18:00
38 | Chapai | 52 | 13:00 | 104 | Madunaghat | 39 | 18:00 | 170 | Shikalbaha | 14.5 | 23:00
39 | Charsaidpur | 41 | 12:00 | 105 | Magura | 54 | 18:00 | 171 | Shitalakhya | 62.1 | 12:00
40 | Chauddagram | 48 | 13:00 | 106 | Mahasthangarh | 46 | 09:00 | 172 | Sholosohor | 32 | 12:00
41 | Chhatak | 18 | 12:00 | 107 | Maijdee | 28 | 21:00 | 173 | Shyampur | 138 | 11:00
42 | Chowmuhani | 101 | 19:30 | 108 | Manikganj | 88 | 20:00 | 174 | Siddhirganj | 94 | 12:00
43 | Chuadanga | 68 | 13:00 | 109 | Maniknagar | 52 | 13:00 | 175 | Sirajganj | 74 | 18:00
44 | Coxsbazar | 102 | 18:00 | 110 | Matarbari | 36 | 18:00 | 176 | Sonargaon | 135 | 10:00
45 | Cumilla(N) | 79 | 18:00 | 111 | Matuail | 55 | 13:00 | 177 | Sreemongol | 55 | 17:00
46 | Cumilla(S) | 117 | 13:00 | 112 | Metrorail_Motijheel | 24 | 13:00 | 178 | Sreepur | 93 | 12:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 9 | 17:00 | 179 | Srinagar | 30 | 19:30
48 | Daudkandi | 102 | 19:00 | 114 | Millgate | 74 | 12:00 | 180 | Sunamganj | 38 | 19:00
49 | DhakaUniversity | 52 | 13:00 | 115 | Mirpur | 115 | 12:00 | 181 | Sylhet | 44 | 17:00
50 | Dhamrai | 96 | 09:00 | 116 | Mirsorai | 8 | 18:00 | 182 | Sylhet-132 | 72 | 20:00
51 | Dhanmondi | 78 | 13:00 | 117 | Mirzapur | 37 | 18:00 | 183 | TK | 17 | 19:30
52 | Dohazari | 63 | 18:00 | 118 | Mithapukur | 52 | 18:00 | 184 | Tangail | 116 | 07:00
53 | Faridpur | 104 | 18:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:00
54 | Fatullah | 87 | 15:00 | 120 | Mogbazar | 55.5 | 20:00 | 186 | Tasnim | 12 | 15:00
55 | Fenchuganj | 23 | 18:30 | 121 | Mongla | 25 | 18:30 | 187 | Thakurgaon | 79 | 18:00
56 | Feni | 70 | 18:00 | 122 | Motijheel | 25 | 12:00 | 188 | Tongi | 100 | 11:00
57 | GPH | 94 | 14:00 | 123 | Muktagacha | 27 | 18:00 | 189 | Ullahpara | 25 | 18:00
58 | Ghatail | 60 | 18:00 | 124 | Munshiganj | 71 | 19:00 | 190 | Ullon | 46 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 24 | 19:30 | 191 | Uttara | 59 | 18:30
60 | Ghorashal-230 | 82 | 18:00 | 126 | Mymensingh | 131 | 18:00 | 192 | UttaraNew | 26 | 13:00
61 | Goalpara | 30 | 18:00 | 127 | Naogaon | 83 | 13:00 | 193 | Zigatola | 56 | 13:00
62 | Gollamari | 68 | 13:00 | 128 | Narail | 40 | 18:30
63 | Gopalganj | 75 | 18:00 | 129 | Narinda | 56 | 13:00
64 | Gulshan | 68 | 13:00 | 130 | Narshingdi | 137 | 19:00
65 | Halishahar | 51 | 15:00 | 131 | Natore | 95 | 18:00
66 | HaripurSBU | 87 | 23:00 | 132 | Nawabganj | 31.4 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8579.91 | 0 |  | 8579.91
1:00 | 8083.62 | 0 |  | 8083.62
2:00 | 7667.06 | 0 |  | 7667.06
3:00 | 7428.5 | 0 |  | 7428.5
4:00 | 7241.06 | 0 |  | 7241.06
5:00 | 7054.38 | 0 |  | 7054.38
6:00 | 7582.42 | 0 |  | 7582.42
7:00 | 8128.81 | 0 |  | 8128.81
8:00 | 8887.67 | 0 |  | 8887.67
9:00 | 9447.95 | 0 |  | 9447.95
10:00 | 9332.5 | 0 |  | 9332.5
11:00 | 9454.07 | 0 |  | 9454.07
12:00 | 9853.67 | 0 |  | 9853.67
13:00 | 10287.61 | 0 |  | 10287.61
14:00 | 9835.07 | 0 |  | 9835.07
15:00 | 9609.04 | 0 |  | 9609.04
16:00 | 9506.64 | 0 |  | 9506.64
17:00 | 9823.76 | 0 |  | 9823.76
18:00 | 10983.8 | 0 |  | 10983.8
19:00 | 10745.7 | 0 |  | 10745.7
19:30 | 10667.7 | 0 |  | 10667.7
20:00 | 10545.9 | 0 |  | 10545.9
21:00 | 10468.9 | 0 |  | 10468.9
22:00 | 10021 | 0 |  | 10021
23:00 | 9370 | 0 |  | 9370
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 3670 | 4909.91 | 8579.91 | DAILY GENERATION CURVE
00:30 | 3571.5 | 4760.265 | 8331.765
01:00 | 3473 | 4610.62 | 8083.62 | 20-12-2025
01:30 | 3338 | 4537.34 | 7875.34
02:00 | 3203 | 4464.06 | 7667.06
02:30 | 3186 | 4361.78 | 7547.78
03:00 | 3169 | 4259.5 | 7428.5
03:30 | 3170.5 | 4164.28 | 7334.78
04:00 | 3172 | 4069.06 | 7241.06
04:30 | 3100 | 4047.72 | 7147.72
05:00 | 3028 | 4026.38 | 7054.38
05:30 | 3225 | 4093.4 | 7318.4
06:00 | 3422 | 4160.42 | 7582.42
06:30 | 3560.58 | 4295.035 | 7855.615
07:00 | 3699.16 | 4429.65 | 8128.81
07:30 | 3832.31 | 4675.93 | 8508.24
08:00 | 3965.46 | 4922.21 | 8887.67
08:30 | 3978.185 | 5189.625 | 9167.81
09:00 | 3990.91 | 5457.04 | 9447.95
09:30 | 3984.645 | 5405.58 | 9390.225
10:00 | 3978.38 | 5354.12 | 9332.5
10:30 | 3971.67 | 5421.615 | 9393.285
11:00 | 3964.96 | 5489.11 | 9454.07
11:30 | 4095.085 | 5558.785 | 9653.87
12:00 | 4225.21 | 5628.46 | 9853.67
12:30 | 4348.77 | 5721.87 | 10070.64
13:00 | 4472.33 | 5815.28 | 10287.61
13:30 | 4439.29 | 5622.05 | 10061.34
14:00 | 4406.25 | 5428.82 | 9835.07
14:30 | 4330.87 | 5391.185 | 9722.055
15:00 | 4255.49 | 5353.55 | 9609.04
15:30 | 4225.875 | 5331.965 | 9557.84
16:00 | 4196.26 | 5310.38 | 9506.64
16:30 | 4290.615 | 5374.585 | 9665.2
17:00 | 4384.97 | 5438.79 | 9823.76
17:30 | 4658.385 | 5745.395 | 10403.78
18:00 | 4931.8 | 6052 | 10983.8
18:30 | 4828.75 | 6036 | 10864.75
19:00 | 4725.7 | 6020 | 10745.7
19:30 | 4780.7 | 5887 | 10667.7
20:00 | 4650.9 | 5895 | 10545.9
20:30 | 4591.4 | 5916 | 10507.4 |  | Executive Engineer
21:00 | 4531.9 | 5937 | 10468.9 |  | Network Operation Division
21:30 | 4482.95 | 5762 | 10244.95
22:00 | 4434 | 5587 | 10021
22:30 | 4407 | 5288.5 | 9695.5
23:00 | 4380 | 4990 | 9370

## En-Curve
QF-LDC-12
Date | 20-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2721 | 1005 | 806 | 0 | 90 | 865.91 | 40 | 3036 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2664 | 982 | 782.5 | 0 | 89 | 851.765 | 40 | 2906.5 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 20-12-2025
01:00 | 2607 | 959 | 759 | 0 | 88 | 837.62 | 40 | 2777 | 0 | 0 | 16 | 0 | 0 | 0 | 0
01:30 | 2561.5 | 905 | 712 | 0 | 81 | 839.34 | 40 | 2728.5 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | Energy Generated | 223.2438 |  | MKWHr
02:00 | 2516 | 851 | 665 | 0 | 74 | 841.06 | 40 | 2680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2578 | 810.5 | 632 | 0 | 73 | 840.78 | 40 | 2573.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 223.2438 |  | MKWHr
03:00 | 2640 | 770 | 599 | 0 | 72 | 840.5 | 40 | 2467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2667.5 | 737.5 | 562 | 0 | 71 | 835.78 | 40 | 2421 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2695 | 705 | 525 | 0 | 70 | 831.06 | 40 | 2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2632.5 | 719.5 | 525 | 0 | 71 | 832.175 | 40 | 2327.5 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2570 | 734 | 525 | 0 | 72 | 833.29 | 40 | 2280 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2648 | 847.5 | 525 | 0 | 73 | 832.355 | 40 | 2352.5 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2726 | 961 | 525 | 0 | 74 | 831.42 | 40 | 2425 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2720 | 986.5 | 525 | 0 | 75 | 882.26 | 40 | 2619 | 5.355 | 0 | 2.5 | 0 | 0 | 0 | 0
07:00 | 2714 | 1012 | 525 | 0 | 76 | 933.1 | 40 | 2813 | 10.71 | 0 | 5 | 0 | 0 | 0 | 0
07:30 | 2772 | 1000 | 571.5 | 0 | 81 | 932.395 | 40 | 3045.5 | 41.845 | 0 | 24 | 0 | 0 | 0 | 0
08:00 | 2830 | 988 | 618 | 0 | 86 | 931.69 | 40 | 3278 | 72.98 | 0 | 43 | 0 | 0 | 0 | 0
08:30 | 2780 | 994 | 655 | 0 | 88 | 983.3 | 40 | 3457 | 117.51 | 0 | 53 | 0 | 0 | 0 | 0
09:00 | 2730 | 1000 | 692 | 0 | 90 | 1034.91 | 40 | 3636 | 162.04 | 0 | 63 | 0 | 0 | 0 | 0
09:30 | 2700 | 944.7 | 702 | 0 | 94 | 1035.705 | 40 | 3576.5 | 219.32 | 0 | 78 | 0 | 0 | 0 | 0
10:00 | 2670 | 889.4 | 712 | 0 | 98 | 1036.5 | 40 | 3517 | 276.6 | 0 | 93 | 0 | 0 | 0 | 0
10:30 | 2674 | 855.1 | 759 | 0 | 99 | 1028.575 | 40 | 3487 | 350.11 | 0 | 100.5 | 0 | 0 | 0 | 0
11:00 | 2678 | 820.8 | 806 | 0 | 100 | 1020.65 | 40 | 3457 | 423.62 | 0 | 108 | 0 | 0 | 0 | 0
11:30 | 2717 | 880.15 | 806 | 0 | 105 | 1028.55 | 40 | 3482.5 | 453.67 | 0 | 141 | 0 | 0 | 0 | 0
12:00 | 2756 | 939.5 | 806 | 0 | 110 | 1036.45 | 40 | 3508 | 483.72 | 0 | 174 | 0 | 0 | 0 | 0
12:30 | 2728 | 967 | 853.5 | 0 | 114 | 1035.07 | 40 | 3548 | 483.67 | 0 | 299.4 | 0 | 0 | 2 | 0
13:00 | 2700 | 994.5 | 901 | 0 | 118 | 1033.69 | 40 | 3588 | 483.62 | 0 | 424.8 | 0 | 0 | 4 | 0
13:30 | 2681.5 | 946.75 | 820.5 | 0 | 113 | 1036.85 | 40 | 3554 | 433.99 | 0 | 429.75 | 0 | 0 | 5 | 0
14:00 | 2663 | 899 | 740 | 0 | 108 | 1040.01 | 40 | 3520 | 384.36 | 0 | 434.7 | 0 | 0 | 6 | 0
14:30 | 2633.5 | 920.75 | 726 | 0 | 108 | 1053.505 | 40 | 3518 | 316.25 | 8.5 | 393.05 | 0 | 0 | 4.5 | 0
15:00 | 2604 | 942.5 | 712 | 0 | 108 | 1067 | 40 | 3516 | 248.14 | 17 | 351.4 | 0 | 0 | 3 | 0
15:30 | 2613.5 | 882.5 | 712 | 0 | 108 | 1107.5 | 40 | 3534.5 | 178.94 | 21 | 358.4 | 0 | 0 | 1.5 | 0
16:00 | 2623 | 822.5 | 712 | 0 | 108 | 1148 | 40 | 3553 | 109.74 | 25 | 365.4 | 0 | 0 | 0 | 0
16:30 | 2636.5 | 849 | 712 | 0 | 106 | 1176 | 40 | 3571.5 | 58.95 | 46 | 469.25 | 0 | 0 | 0 | 0
17:00 | 2650 | 875.5 | 712 | 0 | 104 | 1204 | 40 | 3590 | 8.16 | 67 | 573.1 | 0 | 0 | 0 | 0
17:30 | 2670.5 | 912 | 759 | 0 | 111 | 1284.5 | 40 | 3761.5 | 4.08 | 73.5 | 787.7 | 0 | 0 | 0 | 0
18:00 | 2691 | 948.5 | 806 | 0 | 118 | 1365 | 40 | 3933 | 0 | 80 | 1002.3 | 0 | 0 | 0 | 0
18:30 | 2708 | 972.5 | 853 | 0 | 113 | 1345.5 | 40 | 3988 | 0 | 49 | 795.75 | 0 | 0 | 0 | 0
19:00 | 2725 | 996.5 | 900 | 0 | 108 | 1326 | 40 | 4043 | 0 | 18 | 589.2 | 0 | 0 | 0 | 0
19:30 | 2694 | 1000.5 | 901 | 0 | 110 | 1261 | 40 | 4016 | 0 | 50 | 595.2 | 0 | 0 | 0 | 0
20:00 | 2727 | 1004.5 | 901 | 0 | 110 | 1273 | 40 | 4013 | 0 | 33 | 444.4 | 0 | 0 | 0 | 0
20:30 | 2743.5 | 1005.5 | 901 | 0 | 107 | 1271 | 40 | 4050.5 | 0 | 16.5 | 372.4 | 0 | 0 | 0 | 0
21:00 | 2760 | 1006.5 | 901 | 0 | 104 | 1269 | 40 | 4088 | 0 | 0 | 300.4 | 0 | 0 | 0 | 0
21:30 | 2778 | 1004.25 | 888 | 0 | 104 | 1223 | 40 | 4035 | 0 | 0 | 172.7 | 0 | 0 | 0 | 0
22:00 | 2796 | 1002 | 875 | 0 | 104 | 1177 | 40 | 3982 | 0 | 0 | 45 | 0 | 0 | 0 | 0
22:30 | 2778.5 | 970 | 875 | 0 | 102 | 1095.5 | 40 | 3800 | 0 | 0 | 34.5 | 0 | 0 | 0 | 0
23:00 | 2761 | 938 | 875 | 0 | 100 | 1014 | 40 | 3618 | 0 | 0 | 24 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 409 | 04:00 | 384 | 12:00 | Meghnaghat | 413 | 05:00 | 388 | 12:00
Ashuganj | 413 | 6:00 | 388 | 12:00 | Payra | 418 | 04:00 | 410 | 12:00
Bhulta | 414 | 04:00 | 384 | 12:00 | Rahanpur | 419 | 04:00 | 404 | 18:30
Bibiana | 404 | 03:00 | 386 | 12:00 | Rampal | 411 | 03:00 | 397 | 21:00
BIPTC | 408 | 03:00 | 390 | 13:00
Bogura | 414 | 04:00 | 394 | 19:00
Gopalganj | 413 | 04:00 | 393 | 13:00
Kaliakoir | 403 | 04:00 | 377 | 11:00
Korerhat | 413 | 06:00 | 397 | 11:00
Madunaghat | 407 | 05:00 | 396 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 222 | 12:00 | Kachua | 238 | 04:00 | 232 | 11:00
AKSML | 239 | 06:00 | 228 | 11:00 | Kaliakoir | 240 | 04:00 | 221 | 11:00
Aminbazar | 240 | 03:00 | 222 | 12:00 | Keranigonj | 240 | 04:00 | 221 | 12:00
Ashuganj | 237 | 02:00 | 227 | 13:00 | Khulna(S) | 239 | 05:00 | 227 | 13:00
Ashuganj-400 | 237 | 6:00 | 226 | 12:00 | Korerhat | 239 | 03:00 | 230 | 11:00
Baghabari | 242 | 03:00 | 232 | 13:00 | Madunaghat | 236 | 05:00 | 228 | 12:00
Barapukuria | 230 | 05:00 | 217 | 09:00 | Madunaghat-400 | 236 | 04:00 | 229 | 12:00
Barapukuria-230 | 230 | 5:00 | 216 | 10:00 | Maniknagar | 240 | 04:00 | 222 | 12:00
Barishal | 245 | 05:00 | 236 | 12:00 | Meghnaghat | 244 | 02:00 | 230 | 12:00
Bheramara | 239 | 04:00 | 226 | 13:00 | Meghnaghat-400 | 241 | 03:00 | 225 | 12:00
Bhulta | 241 | 03:00 | 223 | 12:00 | Mirsorai | 239 | 05:00 | 229 | 12:00
Bibiana | 241 | 03:00 | 227 | 12:00 | Rajshahi | 240 | 04:00 | 227 | 19:00
BIPTC | 241 | 06:00 | 226 | 13:00 | Rampal | 237 | 04:00 | 227 | 13:00
Bogura | 242 | 04:00 | 231 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 241 | 03:00 | 230 | 19:00 | Rampura | 241 | 04:00 | 221 | 13:00
Borhanuddin | 246 | 06:00 | 240 | 12:00 | Shikalbaha | 234 | 02:00 | 227 | 19:30
BSRM | 239 | 05:00 | 228 | 12:00 | Shyampur | 240 | 03:00 | 223 | 12:00
Cumilla(N) | 239 | 05:00 | 228 | 13:00 | Siddhirganj | 242 | 04:00 | 226 | 11:00
Faridpur | 245 | 04:00 | 235 | 12:00 | Sirajgonj | 246 | 04:00 | 238 | 13:00
Fenchuganj | 240 | 03:00 | 230 | 12:00 | Sreepur | 236 | 04:00 | 226 | 13:00
Feni | 239 | 03:00 | 228 | 12:00 | Tongi | 236 | 01:00 | 215 | 11:00
Ghorashal | 240 | 00:00 | 235 | 10:00
Ghorashal-230 | 233 | 04:00 | 214 | 13:00
Gopalganj | 245 | 05:00 | 233 | 13:00
GPH | 237 | 03:00 | 229 | 12:00
Haripur | 241 | 03:00 | 224 | 12:00
Hasnabad | 238 | 01:00 | 222 | 11:00
Hathazari | 236 | 05:00 | 227 | 12:00
Ishurdi | 242 | 04:00 | 229 | 13:00
Jhenaidah | 240 | 04:00 | 227 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 126 | 12:00 | Laksam | 140 | 03:00 | 135 | 12:00 | 138 | 03:00 | 125 | 12:00
Agargaon | 138 | 04:00 | 127 | 12:00 | Lakshmipur | 134 | 03:00 | 129 | 11:00 | 138 | 03:00 | 125 | 12:00
Agrabad | 136 | 00:00 | 131 | 11:00 | Lalbag | 137 | 02:00 | 124 | 13:00
AKS | 135 | 03:00 | 129 | 12:00 | Lalmonirhat | 131 | 17:00 | 121 | 07:00
Aminbazar | 137 | 03:00 | 127 | 12:00 | Madanganj | 140 | 05:00 | 134 | 19:00
Amnura | 139 | 05:00 | 131 | 13:00 | Madaripur | 138 | 05:00 | 135 | 12:00
Ashuganj | 141 | 03:00 | 136 | 13:00 | Madartek | 136 | 04:00 | 126 | 12:00
Bagerhat | 131 | 03:00 | 122 | 18:00 | Madunaghat | 138 | 03:00 | 133 | 13:00
Bajitpur | 137 | 03:00 | 130 | 18:00 | Magura | 138 | 03:00 | 130 | 11:00
Bakerganj | 135 | 22:00 | 133 | 18:00 | Mahasthangarh | 137 | 04:00 | 128 | 09:00
Bakulia | 136 | 02:00 | 131 | 11:00 | Maijdee | 134 | 02:00 | 129 | 11:00
Banani | 137 | 02:00 | 124 | 13:00 | Manikganj | 132 | 00:00 | 119 | 11:00
Bangabhaban | 138 | 04:00 | 126 | 13:00 | Maniknagar | 139 | 03:00 | 127 | 12:00
Barapukuria | 139 | 05:00 | 129 | 08:00 | Matarbari | 130 | 03:00 | 122 | 20:00
Barguna | 137 | 02:00 | 134 | 12:00 | Matuail | 142 | 05:00 | 133 | 12:00
Barishal | 140 | 04:00 | 134 | 12:00 | Metrorail_Motijheel | 139 | 03:00 | 127 | 12:00
Barishal-230 | 141 | 03:00 | 135 | 12:00 | Metrorail_Uttara | 138 | 04:00 | 125 | 12:00
Baroaulia | 135 | 00:00 | 131 | 12:00 | Millgate | 135 | 02:00 | 119 | 12:00
Baroirhat | 137 | 03:00 | 130 | 12:00 | Mirpur | 138 | 03:00 | 126 | 12:00
Bashundhara | 137 | 03:00 | 125 | 12:00 | Mirzapur | 138 | 04:00 | 127 | 12:00
BashundharaCement | 140 | 05:00 | 134 | 19:00 | Mithapukur | 136 | 05:00 | 125 | 09:00
Beanibazar | 136 | 03:00 | 129 | 13:00 | MI_Cement | 139 | 04:00 | 125 | 12:00
Benapole | 130 | 23:00 | 116 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 136 | 05:00 | 129 | 13:00 | Mogbazar | 140 | 04:00 | 126 | 12:00
Bhandaria | 138 | 01:00 | 134 | 13:00 | Mongla | 133 | 04:00 | 123 | 18:00
Bhangura | 141 | 03:00 | 133 | 13:00 | Motijheel | 138 | 04:00 | 126 | 13:00
Bheramara | 142 | 04:00 | 137 | 08:00 | Muktagacha | 132 | 02:00 | 126 | 18:00
Bheramara(GK) | 141 | 03:00 | 137 | 08:00 | Munshiganj | 139 | 00:00 | 133 | 11:00
Bhulta | 132 | 03:00 | 124 | 14:00 | Muradnagar | 140 | 04:00 | 132 | 12:00
Bog-Sherpur | 138 | 03:00 | 131 | 09:00 | Mymensingh | 132 | 11:00 | 124 | 18:00
Bogura | 138 | 06:00 | 131 | 09:00 | Naogaon | 135 | 06:00 | 127 | 09:00
Bogura-230 | 138 | 02:00 | 132 | 09:00 | Narail | 140 | 04:00 | 129 | 13:00
Brahmanbaria | 137 | 06:00 | 128 | 12:00 | Narinda | 139 | 3:00 | 127 | 12:00
Cantonment | 138 | 03:00 | 127 | 12:00 | Narshingdi | 139 | 03:00 | 124 | 12:00
Chandina | 141 | 03:00 | 133 | 12:00 | Natore | 137 | 00:00 | 132 | 13:00
Chandpur | 139 | 03:00 | 135 | 10:00 | Nawabganj | 138 | 04:00 | 125 | 11:00
Chandraghona | 138 | 04:00 | 134 | 12:00 | Netrakona | 129 | 03:00 | 120 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 05:00 | 134 | 09:00 | New | 136 | 06:00 | 120 | 11:00
Charsaidpur | 141 | 03:00 | 132 | 12:00 | Niamatpur | 140 | 03:00 | 134 | 18:00
Chauddagram | 138 | 02:00 | 132 | 11:00 | Noapara | 132 | 05:00 | 122 | 13:00
Chhatak | 135 | 00:00 | 130 | 10:00 | Pabna | 141 | 04:00 | 128 | 12:00
Chowmuhani | 133 | 04:00 | 127 | 12:00 | Palashbari | 134 | 03:00 | 123 | 09:00
Chuadanga | 139 | 04:00 | 128 | 13:00 | Panchagarh | 140 | 17:00 | 124 | 09:00
Coxsbazar | 129 | 02:00 | 122 | 14:00 | Patiya | 136 | 00:00 | 131 | 07:00
Cumilla(N) | 141 | 05:00 | 133 | 12:00 | Patuakhali | 136 | 03:00 | 132 | 18:00
Cumilla(S) | 140 | 02:00 | 124 | 12:00 | Payra | 138 | 06:00 | 135 | 09:00
Daganbhuiyan | 137 | 05:00 | 130 | 12:00 | PHP | 137 | 04:00 | 130 | 12:00
Daudkandi | 138 | 05:00 | 130 | 16:00 | Postogola | 140 | 03:00 | 127 | 12:00
DhakaUniversity | 137 | 03:00 | 125 | 12:00 | Purbachal | 137 | 04:00 | 125 | 12:00
Dhamrai | 139 | 04:00 | 128 | 12:00 | Purbasadipur | 133 | 04:00 | 120 | 08:00
Dhanmondi | 143 | 04:00 | 134 | 12:00 | Rahanpur | 140 | 04:00 | 135 | 18:00
Dohazari | 135 | 05:00 | 129 | 11:00 | Rahanpur-400 | 141 | 04:00 | 136 | 09:00
Faridpur | 140 | 03:00 | 133 | 12:00 | Rahim | 140 | 01:00 | 133 | 11:00
Fatullah | 140 | 04:00 | 126 | 12:00 | Rajbari | 140 | 03:00 | 133 | 12:00
Fenchuganj | 140 | 03:00 | 134 | 12:00 | Rajendrapur | 137 | 03:00 | 130 | 12:00
Feni | 135 | 02:00 | 130 | 10:00 | Rajshahi | 139 | 02:00 | 132 | 13:00
Feni-230 | 137 | 03:00 | 130 | 12:00 | Rajshahi-230 | 139 | 05:00 | 131 | 19:00
Ghatail | 133 | 04:00 | 126 | 18:00 | Ramganj | 135 | 00:00 | 131 | 22:00
Ghorashal | 136 | 01:00 | 126 | 13:00 | Rampur | 136 | 01:00 | 1 | 04:00
Goalpara | 134 | 03:00 | 126 | 13:00 | Rampura | 136 | 03:00 | 124 | 13:00
Gollamari | 134 | 05:00 | 126 | 13:00 | Rangamati | 138 | 03:00 | 133 | 12:00
Gopalganj | 137 | 03:00 | 131 | 13:00 | Rangpur | 135 | 04:00 | 126 | 08:00
Gopalganj-400 | 141 | 02:00 | 135 | 12:00 | Ruppur | 141 | 05:00 | 136 | 13:00
Gulshan | 135 | 05:00 | 125 | 12:00 | Saidpur | 134 | 17:00 | 122 | 08:00
Halishahar | 138 | 06:00 | 132 | 11:00 | Satkhira | 132 | 03:00 | 122 | 18:00
Haripur | 141 | 01:00 | 134 | 11:00 | Satmasjid | 138 | 04:00 | 126 | 12:00
HaripurSBU | 142 | 03:00 | 134 | 11:00 | Savar | 135 | 03:00 | 126 | 12:00
Hasnabad | 139 | 04:00 | 128 | 12:00 | SevenRings | 137 | 03:00 | 126 | 12:00
Hathazari | 139 | 05:00 | 134 | 10:00 | ShahCement | 141 | 03:00 | 132 | 12:00
Hatirjheel | 0 | 23:00 | N/A | N/A | Shahjadpur | 142 | 00:00 | 135 | 12:00
Ishurdi | 143 | 02:00 | 137 | 13:00 | Shahjibazar | 139 | 05:00 | 130 | 12:00
Jaldhaka | 133 | 05:00 | 121 | 09:00 | Shahmirpur | 136 | 00:00 | 132 | 11:00
Jamalpur | 129 | 11:00 | 122 | 00:00 | Shariatpur | 141 | 04:00 | 134 | 12:00
Jashore | 133 | 02:00 | 118 | 13:00 | Sherpur | 127 | 11:00 | 118 | 23:00
Jhenaidah | 140 | 02:00 | 125 | 08:00 | Shikalbaha | 126 | 00:00 | 121 | 12:00
Jhenaidah-230 | 141 | 04:00 | 131 | 13:00 | Shikalbaha-230 | 138 | 02:00 | 134 | 11:00
Joydebpur | 134 | 01:00 | 123 | 12:00 | Shitalakhya | 139 | 04:00 | 125 | 12:00
Joypurhat | 134 | 02:00 | 126 | 08:00 | Sholosohor | 138 | 03:00 | 133 | 11:00
Juldah | 137 | 05:00 | 132 | 11:00 | Shyampur | 138 | 02:00 | 133 | 11:00
Kabirpur | 137 | 03:00 | 118 | 11:00 | Shyampur-230 | 139 | 03:00 | 128 | 12:00
Kachua | 141 | 04:00 | 135 | 11:00 | Siddhirganj | 142 | 03:00 | 133 | 12:00
Kaliakoir | 142 | 04:00 | 132 | 11:00 | Sirajganj | 138 | 02:00 | 130 | 09:00
Kallyanpur | 137 | 04:00 | 127 | 12:00 | Sonargaon | 138 | 09:00 | 132 | 10:00
Kalurghat | 138 | 02:00 | 133 | 11:00 | Sreemongol | 139 | 07:00 | 132 | 12:00
Kamrangirchar | 138 | 02:00 | 124 | 13:00 | Sreepur | 138 | 02:00 | 132 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 138 | 06:00 | 125 | 11:00
Kasba | 139 | 01:00 | 130 | 13:00 | SSM | 139 | 18:00 | 136 | 09:00
Kazla | 136 | 04:00 | 127 | 12:00 | Sunamganj | 134 | 01:00 | 129 | 12:00
Keranigonj | 138 | 04:00 | 125 | 13:00 | Sylhet | 136 | 03:00 | 130 | 13:00
Khagrachori | 138 | 03:00 | 132 | 12:00 | Sylhet-132 | 136 | 01:00 | 133 | 09:00
Khulna | 132 | 06:00 | 124 | 18:30 | Tangail | 133 | 04:00 | 124 | 16:00
Khulna(S) | 134 | 03:00 | 127 | 13:00 | Taraganj | 134 | 06:00 | 123 | 08:00
Khulshi | 136 | 04:00 | 130 | 12:00 | Tasnim | 141 | 03:00 | 132 | 10:00
Kishoreganj | 134 | 03:00 | 127 | 18:00 | Thakurgaon | 139 | 17:00 | 120 | 09:00
Kodda | 135 | 01:00 | 122 | 11:00 | TK | 137 | 03:00 | 132 | 12:00
KSRM | 139 | 03:00 | 132 | 12:00 | Tongi | 137 | 01:00 | 124 | 11:00
Kulaura | 140 | 03:00 | 133 | 13:00 | Ullahpara | 139 | 04:00 | 132 | 18:30
Kurigram | 132 | 05:00 | 118 | 08:00 | Ullon | 136 | 03:00 | 125 | 12:00
Kushtia | 139 | 05:00 | 130 | 13:00 | Uttara | 136 | 03:00 | 121 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division