## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-12-2025 | during | 22-12-2025 | during | 22-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 336 | 342 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 130 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 34.3 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 54 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.5 | 23 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 95 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 101 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 17 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 480 | 335 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1061.5 | 1552.3 | 5781.35 | 5749.35 | 2512.06 | 2487.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 12 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 224 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 68 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 20 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.23 | 0 | 3.33 | 0 | 3.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 851 | 856 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 780 | 780 | 780 | 780 | 780 | 780 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1927.23 | 2092 | 3618.05 | 3615.72 | 3090.83 | 3088.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 190 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 170 | 16 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 109 | 108 | 163 | 163 | 130 | 130 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 46 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 116 | 112 | 160 | 160 | 118 | 118 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 24.5 | 24.5 | 15 | 15 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 962 | 983 | 2790.56 | 2725.56 | 1928.55 | 1863.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-12-2025 | during | 22-12-2025 | during | 22-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 56 | 34 | 157.5 | 157.5 | 120 | 120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.16 | 0 | 0 | 0 | 0 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 139.16 | 129 | 315.7 | 314 | 230.7 | 229
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 16 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 82 | 82 | 0 | 0 | 85 | 85 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 15 | 17 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 211 | 211 | 210 | 210 | 215 | 215 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 506 | 487 | 428 | 428 | 518 | 518
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 888 | 901 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 240 | 205 | 410 | 410 | 265 | 265 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 65 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 996 | 592 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2189 | 1702 | 2332 | 2272 | 1432.1 | 1372.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 250 | 503 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 108 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 888 | 1080 | 1085.32 | 1085.32 | 1025.32 | 1025.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant is on standby as per NLDC requirement
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.37 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1473.37 | 1911 | 2003.32 | 2003.32 | 1503.32 | 1503.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 32.15 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 173 | 182 | 220 | 220 | 198 | 198 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 347 | 400 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 26 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.73 | 0 | 4.6 | 0 | 4.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1034.49 | 1382 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 24.37 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 20 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1633.74 | 1990 | 3079.47 | 2913.87 | 2554.09 | 2388.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 64 | 60 | 63 | 63 | 63 | 63 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.8 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 142 | 0 | 146.88 | 0 | 146.88 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 239.8 | 200 | 487.08 | 305 | 473.08 | 291
System Total |  |  |  |  | 28823.2 | 28379.108 | 10131.8 | 11046.3 | 20835.53 | 20326.82 | 14242.73 | 13741.02
Forecast Scenario (22-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9210 |  | 0 |  | 9210
|  |  |  | 1:00 | 8490 |  | 0 |  | 8490
|  |  |  | 2:00 | 8110 |  | 0 |  | 8110
|  |  |  | 3:00 | 7760 |  | 0 |  | 7760
|  |  |  | 4:00 | 7540 |  | 0 |  | 7540
|  |  |  | 5:00 | 7490 |  | 0 |  | 7490
|  |  |  | 6:00 | 7950 |  | 0 |  | 7950
|  |  |  | 7:00 | 8540 |  | 0 |  | 8540
|  |  |  | 8:00 | 9450 |  | 0 |  | 9450
|  |  |  | 9:00 | 9610 |  | 0 |  | 9610
|  |  |  | 10:00 | 9410 |  | 0 |  | 9410
|  |  |  | 11:00 | 9660 |  | 0 |  | 9660
|  |  |  | 12:00 | 10205 |  | 0 |  | 10205
|  |  |  | 13:00 | 10690 |  | 0 |  | 10690
|  |  |  | 14:00 | 10190 |  | 0 |  | 10190
|  |  |  | 15:00 | 9880 |  | 0 |  | 9880
|  |  |  | 16:00 | 9700 |  | 0 |  | 9700
|  |  |  | 17:00 | 10130 |  | 0 |  | 10130
|  |  |  | 18:00 | 11310 |  | 0 |  | 11310
|  |  |  | 18:30 | 11150 |  | 0 |  | 11150
|  |  |  | 19:00 | 11090 |  | 0 |  | 11090
|  |  |  | 19:30 | 10920 |  | 0 |  | 10920
|  |  |  | 20:00 | 10850 |  | 0 |  | 10850
|  |  |  | 21:00 | 10580 |  | 0 |  | 10580
|  |  |  | 22:00 | 10170 |  | 0 |  | 10170
|  |  |  | 23:00 | 9710 |  | 0 |  | 9710
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 10205.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11310.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11310.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.725 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:08 hrs on 22-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-12-2025 | [28 empty] | Date: | 21-12-2025 | [28 empty] | Date: | 21-12-2025 | [28 empty] | Date: | 21-12-2025 | [28 empty] | Date: | 21-12-2025 | [17 empty] | Date: | 21-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 720 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 310 | 0 | 140 | 51 | 0 | 194 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 21 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 24 | 0 | 75 | 0 | 0 | 0 | 4329 | 780 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 783 | 0 | 4 | 0 | 978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 300 | 600 | 0 | 4613 | 8942 | 98.54
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 600 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 310 | 0 | 140 | 51 | 0 | 198 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 4125 | 746 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 4 | 0 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 250 | 565 | 0 | 4343 | 8468 | 98.54
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 580 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 703 | 0 | 0 | 0 | 310 | 0 | 140 | 5 | 0 | 203 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 0 | 0 | 42 | 20 | 0 | 15 | 82 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 3908 | 498 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769 | 0 | 4 | 0 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 250 | 565 | 0 | 4093 | 8001 | 98.54
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 580 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 260 | 0 | 140 | 5 | 0 | 193 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 213 | 30 | 30 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 15 | 82 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 3634 | 497 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 4 | 0 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 180 | 0 | 250 | 560 | 0 | 4062 | 7696 | 98.54
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 580 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 250 | 15 | 99 | 5 | 0 | 202 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 15 | 82 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 3568 | 357 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 4 | 0 | 839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 180 | 0 | 250 | 560 | 0 | 3909 | 7477 | 98.54
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 580 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 215 | 76 | 70 | 5 | 0 | 173 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 15 | 82 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 3429 | 357 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 4 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 180 | 0 | 250 | 560 | 0 | 3938 | 7367 | 98.53
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 582 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 665 | 0 | 0 | 0 | 215 | 114 | 0 | 5 | 0 | 162 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 0 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 3772 | 451 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 0 | 4 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 250 | 560 | 0 | 4052 | 7824 | 98.53
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 140 | 41 | 0 | 1 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 583 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 781 | 2 | 0 | 0 | 215 | 264 | 0 | 5 | 0 | 161 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 88 | 0 | 3 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 0 | 0 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 2 | 0 | 77 | 0 | 0.67 | 0 | 4141.67 | 593 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 767 | 0 | 4 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0.45 | 0 | 0 | 192 | 0 | 0 | 0 | 375 | 0 | 0.06 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 68 | 220 | 0 | 250 | 570 | 0 | 4187.87 | 8329.54 | 98.53
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 218 | 0 | 0 | 3 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 7 | 580 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 851 | 9 | 0 | 0 | 215 | 264 | 0 | 32 | 0 | 142 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 96 | 0 | 21 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 2 | 0 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 45 | 0 | 61 | 0 | 7.43 | 0 | 4267.43 | 792 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 870 | 0 | 4 | 0 | 928.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.35 | 4 | 0 | 0 | 3.28 | 0 | 0 | 181 | 0 | 0 | 0 | 398 | 0 | 0.38 | 0 | 64 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 10 | 0.1 | 0 | 0 | 68 | 220 | 0 | 250 | 740 | 0 | 4799.54 | 9066.97 | 98.52
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.97 | 40 | 0 | 10 | 720 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 871 | 14 | 0 | 0 | 215 | 200 | 0 | 51 | 0 | 172 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 94 | 0 | 41 | 0 | 0 | 0 | 212 | 30 | 30 | 0 | 6 | 17 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 45 | 0 | 61 | 0 | 18.68 | 0 | 4317.65 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 952 | 0 | 0 | 0 | 1023.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.85 | 6 | 0 | 0 | 5.79 | 0 | 0 | 202 | 0 | 0 | 0 | 353 | 0 | 0.6 | 0 | 63 | 0 | 5 | 0 | 0 | 0 | 0 | 0.9 | 32 | 0.21 | 0 | 0 | 68 | 220 | 0 | 300 | 888 | 0 | 5278.57 | 9596.22 | 98.52
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 518 | 0 | 0 | 2 | 0 | 0 | 10 | 0 | 22.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 40 | 0 | 9 | 720 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 795 | 17 | 0 | 0 | 215 | 170 | 0 | 51 | 0 | 208 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 98 | 0 | 55 | 0 | 0 | 0 | 215 | 30 | 30 | 0 | 8 | 17 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 45 | 0 | 61 | 0 | 26.42 | 0 | 4328.66 | 888 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 982 | 0 | 0 | 0 | 1031.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.84 | 11 | 0 | 0 | 7.08 | 0 | 0 | 175 | 0 | 0 | 0 | 338 | 0 | 0.73 | 0 | 64 | 0 | 8 | 0 | 0 | 0 | 0 | 1.7 | 56 | 0.34 | 0 | 0 | 68 | 180 | 0 | 250 | 890 | 0 | 5235.46 | 9564.12 | 98.52
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 490 | 0 | 0 | 1 | 0 | 0 | 11 | 0 | 22.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.15 | 40 | 0 | 7 | 780 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 570 | 19 | 0 | 0 | 235 | 170 | 0 | 51 | 0 | 190 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 98 | 0 | 60 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 10 | 17 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 45 | 0 | 59 | 1 | 34.82 | 0 | 4164.47 | 887 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 1008 | 0 | 0 | 0 | 1036.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.06 | 24 | 0 | 0 | 12.3 | 0 | 0 | 177 | 0 | 0 | 0 | 350 | 0 | 2.12 | 0 | 64 | 0 | 24 | 0 | 0 | 0 | 0 | 4 | 143 | 0.42 | 0 | 0 | 70 | 180 | 0 | 250 | 890 | 0 | 5464.82 | 9629.29 | 98.52
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 480 | 0 | 0 | 130 | 0 | 0 | 17 | 0 | 22.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.23 | 40 | 0 | 12 | 780 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 851 | 19 | 0 | 0 | 250 | 170 | 0 | 51 | 0 | 190 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 116 | 0 | 65 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 11 | 17 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 45 | 0 | 56 | 1 | 37.16 | 0 | 4595.89 | 888 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 996 | 0 | 0 | 0 | 1034.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.15 | 20 | 0 | 0 | 24.37 | 0 | 0 | 173 | 0 | 0 | 0 | 347 | 0 | 2.73 | 0 | 64 | 0 | 29 | 0 | 0 | 0 | 0 | 4.8 | 142 | 0.37 | 0 | 0 | 115 | 220 | 0 | 250 | 888 | 0 | 5535.91 | 10131.8 | 98.51
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 72 | 0 | 0 | 0 | 550 | 0 | 0 | 250 | 0 | 0 | 22 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 20 | 780 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 864 | 18 | 0 | 0 | 250 | 170 | 0 | 51 | 0 | 180 | 0 | 0 | 107 | 0 | 0 | 12 | 0 | 122 | 0 | 62 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 10 | 17 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 45 | 0 | 29 | 2 | 34.99 | 0 | 4874.49 | 887 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 759 | 0 | 0 | 0 | 1117.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.78 | 32 | 0 | 0 | 40.12 | 0 | 0 | 193 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 63 | 0 | 27 | 0 | 0 | 0 | 0 | 5 | 123 | 0.41 | 0 | 0 | 118 | 220 | 0 | 450 | 950 | 0 | 5643.82 | 10518.31 | 98.51
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 12 | 0 | 0 | 0 | 60 | 0 | 0 | 72 | 0 | 0 | 0 | 440 | 0 | 0 | 250 | 0 | 0 | 17 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2.48 | 40 | 0 | 14 | 780 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 869 | 16 | 0 | 0 | 250 | 60 | 0 | 51 | 0 | 200 | 0 | 0 | 105 | 21 | 0 | 11 | 0 | 120 | 0 | 51 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 9 | 17 | 0 | 80 | 30 | 0 | 15 | 82 | 0 | 56 | 2 | 31 | 1 | 27.24 | 0 | 4684.72 | 901 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 586 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.14 | 28 | 0 | 0 | 32.39 | 0 | 0 | 189 | 0 | 0 | 0 | 270 | 0 | 2.26 | 0 | 62 | 0 | 22 | 0 | 0 | 0 | 0 | 4.2 | 115 | 0.32 | 0 | 0 | 108 | 180 | 0 | 500 | 950 | 0 | 5390.31 | 10075.03 | 98.51
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 72 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 12 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 40 | 0 | 10 | 780 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 860 | 12 | 0 | 0 | 250 | 23 | 0 | 51 | 0 | 198 | 0 | 0 | 104 | 0 | 0 | 11 | 0 | 110 | 0 | 35 | 0 | 0 | 0 | 211 | 30 | 30 | 0 | 5 | 17 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 56 | 19 | 31 | 1 | 18.73 | 0 | 4624.44 | 901 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 588 | 0 | 0 | 0 | 1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.34 | 29 | 0 | 0 | 19.52 | 0 | 0 | 175 | 0 | 0 | 0 | 355 | 0 | 1.85 | 0 | 63 | 0 | 14 | 0 | 0 | 0 | 0 | 2.7 | 75 | 0.22 | 0 | 0 | 108 | 180 | 0 | 400 | 850 | 0 | 5063.63 | 9688.07 | 98.51
16:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 12 | 0 | 145 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 40 | 0 | 10 | 780 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 862 | 6 | 0 | 0 | 250 | 21 | 0 | 51 | 0 | 191 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 100 | 0 | 13 | 0 | 0 | 0 | 211 | 12 | 30 | 0 | 2 | 17 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 58 | 19 | 31 | 0 | 6.73 | 1 | 4532.47 | 901 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 590 | 0 | 0 | 0 | 1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.33 | 14 | 0 | 0 | 6.86 | 0 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 0.61 | 0 | 59 | 0 | 5 | 0 | 0 | 0 | 0 | 1.1 | 30 | 0.09 | 0 | 0 | 108 | 220 | 0 | 350 | 867 | 0 | 5010.99 | 9543.46 | 98.5
17:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 15 | 0 | 60 | 0 | 145 | 0 | 7 | 25 | 0 | 0 | 0 | 370 | 0 | 42 | 280 | 0 | 0 | 1 | 0 | 24 | 22 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.03 | 40 | 3 | 16 | 780 | 0 | 0 | 2 | 0 | 19 | 223 | 0 | 0 | 0 | 855 | 0 | 6 | 0 | 250 | 17 | 0 | 51 | 0 | 187 | 0 | 0 | 106 | 23 | 0 | 11 | 0 | 84 | 0 | 1 | 0 | 0 | 0 | 212 | 16 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 58 | 19 | 34 | 0 | 0.44 | 17 | 4653.47 | 901 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 590 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 2 | 0 | 0 | 0.64 | 0 | 0 | 172 | 0 | 0 | 0 | 339 | 0 | 0.06 | 0 | 60 | 35 | 0 | 34 | 0 | 0 | 0 | 0.1 | 2 | 0.01 | 0 | 0 | 108 | 180 | 0 | 450 | 960 | 0 | 5128.08 | 9781.55 | 98.5
18:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 34.3 | 0 | 95 | 0 | 195 | 0 | 54 | 101 | 0 | 0 | 0 | 335 | 0 | 55 | 280 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 40 | 15 | 20 | 780 | 0 | 0 | 12 | 0 | 68 | 224 | 0 | 0 | 0 | 856 | 0 | 50 | 0 | 393 | 16 | 0 | 51 | 0 | 190 | 0 | 0 | 108 | 46 | 0 | 17 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 211 | 16 | 30 | 0 | 0 | 21 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 59 | 18 | 34 | 0 | 0 | 18 | 5243.3 | 901 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 4 | 0 | 1382 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 60 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 220 | 0 | 503 | 1080 | 0 | 5803 | 11046.3 | 98.5
19:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 45.8 | 0 | 109 | 0 | 30 | 0 | 0 | 100 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 25 | 780 | 0 | 0 | 0 | 0 | 34 | 225 | 0 | 0 | 0 | 905 | 0 | 50 | 0 | 395 | 82 | 0 | 51 | 0 | 190 | 0 | 0 | 108 | 91 | 0 | 17 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 213 | 16 | 30 | 0 | 0 | 21 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 59 | 18 | 34 | 0 | 0 | 18 | 5113.8 | 901 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 0 | 4 | 0 | 1453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 60 | 70 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 220 | 0 | 503 | 1080 | 0 | 5809 | 10922.8 | 98.5
19:30 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 17 | 0 | 115 | 0 | 30 | 0 | 0 | 50 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 26 | 780 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 922 | 0 | 0 | 0 | 395 | 17 | 0 | 51 | 0 | 194 | 0 | 0 | 108 | 51 | 0 | 17 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 211 | 16 | 30 | 0 | 0 | 21 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 59 | 18 | 34 | 0 | 0 | 18 | 4873 | 901 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593 | 0 | 4 | 0 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 60 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 220 | 0 | 503 | 1080 | 0 | 5816 | 10689
20:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 28 | 780 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 395 | 16 | 0 | 51 | 0 | 193 | 0 | 0 | 109 | 51 | 0 | 17 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 211 | 16 | 30 | 0 | 0 | 21 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 59 | 18 | 34 | 0 | 0 | 18 | 4892 | 901 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 0 | 4 | 0 | 1460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 60 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 220 | 0 | 502 | 1080 | 0 | 5791 | 10683 | 98.49
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 780 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 395 | 16 | 0 | 51 | 0 | 188 | 0 | 0 | 109 | 0 | 0 | 17 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 211 | 41 | 30 | 0 | 0 | 12 | 0 | 80 | 30 | 0 | 17 | 82 | 0 | 59 | 18 | 34 | 0 | 0 | 0 | 4847 | 901 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 4 | 0 | 1318.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 62 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 220 | 0 | 502 | 1080 | 0 | 5624.26 | 10471.26 | 98.49
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 780 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 395 | 16 | 0 | 51 | 0 | 198 | 0 | 0 | 109 | 0 | 0 | 17 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 212 | 21 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 16 | 24 | 0 | 35 | 18 | 34 | 0 | 0 | 0 | 4719 | 901 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 0 | 4 | 0 | 1204.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 220 | 0 | 370 | 900 | 0 | 5102.81 | 9821.81 | 98.49
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 780 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1012 | 0 | 0 | 0 | 393 | 17 | 0 | 51 | 0 | 199 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 16 | 26 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 4514 | 901 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 0 | 4 | 0 | 1132.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 180 | 0 | 300 | 900 | 0 | 4902.7 | 9416.7 | 98.49
Total KWH | 0 | 0 | 76320 | 0 | 0 | 0 | 0 | 0 | 8380800 | 0 | 0 | 127800 | 0 | 557136 | 0 | 768033 | 0 | 81910 | 665280 | 0 | 0 | 0 | 10736723 | 0 | 96816 | 3708020 | 551000 | 0 | 90274 | 0 | 432000 | 528840 | 0 | 0 | 0 | 33622 | 0 | 0 | 0 | 0 | 0 | 0 | 20160 | 171840 | 20164 | 972000 | 36000 | 458400 | 17047272.73 | 0 | 0 | 19680 | 0 | 158072 | 5173010 | 0 | 0 | 0 | 19990907 | 132570 | 140509 | 0 | 6963500 | 2066300 | 752000 | 1016360 | 0 | 4690000 | 0 | 0 | 2390498 | 293280 | 0 | 306320 | 0 | 2367360 | 0 | 405636 | 0 | 0 | 0 | 5156000 | 687000 | 721680 | 0 | 61870 | 280560 | 0 | 1624320 | 679872 | 0 | 379000 | 1826870 | 0 | 858000 | 151200 | 1169280 | 6600 | 214840 | 82080 | 106325584.73 | 18725090 | 5774976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326880 | 17359999 | 0 | 58545 | 0 | 25191170 | 0 | 0 | 0 | 0 | 42048 | 0 | 0 | 0 | 0 | 159976 | 162410 | 0 | 0 | 155248 | 0 | 0 | 4639209 | 0 | 0 | 0 | 8898909 | 0 | 10740 | 0 | 1455272 | 276275 | 133625 | 235488 | 0 | 0 | 0 | 26082.36 | 720000 | 2506 | 0 | 0 | 2193000 | 5285186 | 0 | 8256725 | 20708363.64 | 0 | 120797723 | 227123307.73

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10131.8 | MW | 12:00 Hr. | Energy Generated |  |  | 227.1233 |  | MKWHr.
| Day Peak Demand |  |  | 10131.8 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11046.3 | MW | 18:00 Hr. | Energy Demand |  |  | 227.1233 |  | MKWHr.
| Evening Peak Demand |  |  | 11046.3 | MW | 18:00 Hr. | Maximum Temperature |  |  | 28.3 |  | °C
| Minimum Generation of the Day |  |  | 7367 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 670.77 |  | MMCFD
| Maximum Generation of the Day |  |  | 11046.3 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.5925 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.3374 | 0 | 2.3733 | 0 | 0 | 0.090274 | 0 | 0 | 26.801 | Gas | 87.5282 | Gas | 307962842.58
| Chattogram Zone |  |  | 5.6314 | 37.0382 | 0.43937 | 0 | 0.972 | 0.15273 | 0 | 0 | 44.2337 | Coal | 84.8185 | Coal | 565824360.6081
| Cumilla Zone |  |  | 18.185 | 0 | 0.43379 | 0 | 0 | 0.40564 | 2.3674 | 0 | 21.3918 | HFO | 4.8915 | HFO | 80469248.1
| Mymensingh Zone |  |  | 1.1693 | 0 | 1.0913 | 0 | 0 | 0.22144 | 0 | 0 | 2.482 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 11.3553 | 0 | 0 | 0 | 0 | 0.06187 | 0 | 0 | 11.4172 | Hydro | 0.972 | Hydro | 97200
| Khulna Zone |  |  | 5.8335 | 17.36 | 0 | 0 | 0 | 0.32688 | 18.7251 | 0 | 42.2455 | Solar | 2.6294 | Solar | 41499474.752
| Barishal Zone |  |  | 7.4782 | 28.9651 | 0 | 0 | 0 | 0.002506 | 0 | 0 | 36.4458 | Import | 46.2836 | Import | 274325394.4
| Rajshahi Zone |  |  | 13.5381 | 0 | 0.042048 | 0 | 0 | 0.48837 | 25.1912 | 0 | 39.2597 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 1.4553 | 0.51176 | 0 | 0 | 0.87971 | 0 | 0 | 2.8467
| Total |  |  | 87.5282 | 84.8185 | 4.8915 | 0 | 0.972 | 2.6294 | 46.2836 | 0 | 227.1233
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 307962842.58 |  | Hydro | 97200
|  |  |  | Coal | 565824360.6081 |  | Solar | 41499474.752
|  |  |  | HFO | 80469248.1 |  | Import | 274325394.4
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 127,01,78,520 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.7251 | Peak Hr Flow | 901.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46756813.83 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.1912 | Peak Hr Flow | 1382.00 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2332 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3674 | Peak Hr Flow | 112.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2682 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.2836 | Peak Hr Flow | 2395.00 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4162
|  |  |  | Chattogram |  | 0 |  | 1144
|  |  |  | Cumilla |  | 0 |  | 938
|  |  |  | Mymensingh |  | 0 |  | 861
|  |  |  | Sylhet |  | 0 |  | 399
|  |  |  | Khulna |  | 0 |  | 1251
|  |  |  | Barishal |  | 0 |  | 309
|  |  |  | Rajshahi |  | 0 |  | 986
|  |  |  | Rangpur |  | 0 |  | 774
|  |  |  | Total |  | 0 |  | 10824
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 14:19 | Rampura 230/132kV S/S 132 kV Busbar-1 Scheduled S/D Due to Maintenance work for
Bashundhara-2 BUS-1 DS
| 08:23 |  | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to 132 TR-3 Change
| 08:24 |  | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to 132 TR-3 Change
| 08:24 | 15:47 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Annual
Maintenance and from Khulna(S) 230/132kVend.
| 08:27 | 16:53 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT Scheduled S/D Due to Annual Maintenance.
| 08:27 | 16:54 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Scheduled S/D Due to Annual Maintenance.
| 08:27 | 15:49 | C.nawabganj-Rajshahi 132 kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to Annual
Maintenance
| 08:27 | 16:23 | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Barishal 230/132kV end Due to Annual Maintenance
| 08:30 | 19:42 | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Maintainace
| 08:30 | 19:42 | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to Maintainance
| 08:34 | 16:36 | Ghorasal-Joydeb-B 132kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to Annual
maintenance work
| 08:44 | 15:15 | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance.
| 08:45 | 16:47 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D
| 08:45 | 16:48 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Scheduled S/D Due to Annual
Maintenance
| 08:46 | 17:51 | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Annual Maintenance
| 08:46 | 17:50 | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Annual Maintenance
| 08:54 | 17:16 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Deadline checking and from Meghnaghat 400/230kV end Due to 400 kV Aminbazar ckt- 02
shutdown instructed by NLDC.
| 08:54 | 16:19 | Sirajganj 132/33kV S/S T4-(445) LT Scheduled S/D Due to Annual Maintenance Work
| 08:54 | 16:18 | Sirajganj 132/33kV S/S T4-(445) HT Scheduled S/D Due to Annual Maintenance Work
| 08:55 | 15:36 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
Maintenance (Dead line cheacking)
| 09:05 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
R-Phase CVT Failed
| 09:05 | 12:19 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to None | [7 empty] | 80.0MW load
interrup.
| 09:05 | 12:18 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to None
| 09:07 | 15:26 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 27.0MW load
interrup.
| 09:08 | 15:26 | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 27.0MW load
interrup.
| 09:12 | 15:54 | Magura 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Annual Maintenance of Transformer
- 1
| 09:13 | 15:50 | Magura 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Annual Maintenance of Transformer
- 1.
| 09:18 | 16:27 | Kazla 132/33kV S/S GT-2 HT Scheduled S/D Due to Yearly Maintenance Purpose
| 09:25 | 16:56 | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to
Annual Maintenance and from Sreemongol 132/33kV end Due to For annual maintenance.
| 09:25 | 14:18 | Rahanpur 132/33kV S/S Bus-1 Scheduled S/D Due to Annual maintenance | [7 empty] | 5.0MW load
interrup.
| 09:26 | 14:19 | Rahanpur 132/33kV S/S Bus-2 Scheduled S/D Due to Annual Maintenance
| 09:28 | 17:29 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
Maintenance Work.
| 09:30 | 14:16 | Rahanpur 400/132kV S/S Rahanpur-Chowdala 132 KV Line Ckt-01 Forced S/D Due to Due to | [7 empty] | 9.0MW load
|  |  | Annual maintenance work. | [7 empty] | interrup.
| 09:31 | 14:17 | Rahanpur 400/132kV S/S Rahanpur-Chowdala 132 KV Line Ckt-02 Forced S/D Due to Due to | [7 empty] | 9.0MW load
|  |  | Annual maintenance work. | [7 empty] | interrup.
| 09:35 | 15:17 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Scheduled S/D Due to Annual maintenance
| 09:36 | 15:16 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Scheduled S/D Due to Annual maintenance
| 09:55 |  | Bhola 225MW CCPP GT-2 was synchronized
| 09:57 | 16:29 | Mahasthangar-Palashbari 132kV Ckt-2 Scheduled S/D from Mahasthangarh 132/33kV end Due to
Annual Maintenance
| 10:02 | 16:24 | Maniknagar 132/33kV S/S Kazla Ckt -2 Scheduled S/D Due to Annual Maintenance
| 10:08 | 13:24 | Haripur 230/132kV S/S 132kV Main Bus Sec-2 Scheduled S/D Due to Annual maintenance
| 10:08 | 13:24 | Haripur 230/132kV S/S 132kV Bus Coupler Scheduled S/D Due to Annaual maitenance For Bus
Section-2
| 10:08 | 16:31 | Mahasthangar-Palashbari 132kV Ckt-2 Scheduled S/D from Palashbari 132/33kV end Due to
Annual maintenance
| 10:15 | 16:20 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Scheduled S/D Due to Annual
maintenance
| 10:15 | 16:20 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Scheduled S/D Due to Annual
maintenance
| 10:24 | 15:10 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Deadline Checking
| 10:24 | 11:43 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Maintenance Work
| 10:24 | 11:42 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Maintenance Work.
| 10:25 | 18:03 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance work
| 10:36 |  | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end.
| 10:36 |  | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end.
| 11:23 |  | Siddhirganj 335 MW CCPP ST was synchronized
| 11:32 | 11:36 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to For Tap change of Unit
transformer.
| 11:38 | 15:24 | Ghatail 132/33kV S/S Bus-2 Scheduled S/D
|  | 11:42 | KSRM 132/33kV S/S Transformer-02 HT is restored.
| 11:45 | 17:50 | KSRM 132/33kV S/S Transformer-03 HT Scheduled S/D Due to cleaning purpose
| 11:46 | 12:35 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to For tap change of unit
transformer.
| 12:00 |  | Day Peak Generation: 10128 MW.
| 12:24 |  | Rampal 1320 MW (BIFPCL) unit-1 tripped
| 12:27 |  | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by Ghorashal via NLDC
| 12:27 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by Ghorashal via NLDC
| 12:33 | 12:55 | Saidpur 132/33kV S/S TR-01 HT Forced S/D Due to Transformer oil sample collection
| 12:36 | 16:40 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to Annual Maintenace.
| 12:37 | 16:44 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to Annual Maintenace.
| 12:46 | 12:51 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing OC, R Ph | [7 empty] | 147.0MW load
|  |  | Trip, Y Ph Trip, B Ph Trip. relays Due to Over Current | [7 empty] | interrup. Rampura
230/132kV end
|  | 12:46 | Sherpur 132/33kV S/S Transformer- 02 HT is restored.
|  | 12:47 | Sherpur 132/33kV S/S Transformer- 02 LT is restored.
|  | 15:26 | Jamalpur-Mymensingh 132kV Ckt-1 is restored.
| 15:37 | 16:57 | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D Due to Relay Test By SPMD | [7 empty] | 20.0MW load
interrup.
| 15:37 | 16:58 | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to Relay Test by SPMD | [7 empty] | 20.0MW load
interrup.
|  | 16:02 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
|  | 16:02 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
|  | 16:11 | Moghbazar-Rampura 132kV Ckt-1 is restored.
|  | 16:58 | Bashundhara-Rampura 132 kV Ckt-2 is restored.
|  | 17:13 | Bhaluka-Mymensingh 132 kV Ckt-2 is restored.
|  | 17:50 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 18:00 |  | Evening peak generation: 11046 MW
| 19:25 | 22:50 | Haripur-Siddirganj 230kV Ckt-2 Forced S/D from Siddhirganj 132/33kV end Due to Shutdown
taken for red hot of Y-phase of T-clamp (loop) between DS-673M & DS-674M at 132 kV
Haripur-2.
| 19:26 | 22:50 | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to
Instruction of backup NLDC
| 19:42 |  | Chandpur 132/33kV S/S 402T (T-01) LT Scheduled S/D Due to Load Share
| 01:21 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- ST
| 05:54 | 07:40 | Bhulta 132/33kV S/S GT1 HT Tripped showing SIMENS SIPROTEC 7UT82 relays Due to 33 KV | [7 empty] | 60.0MW load
interrup.
| 07:20 |  | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Annual Maintenance Work. | [7 empty] | 5.0MW load
interrup.
| 07:20 |  | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Annual Maintenance Work. | [7 empty] | 5.0MW load
interrup.
| 07:40 |  | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-1 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8380800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 551000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 3708020 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 34.3 | 127800 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 54 | 81910 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 96816 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 432000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 528840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 76320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 768033 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 95 | 557136 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 101 | 665280 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 90274 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 335 | 10736723 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1552.3 | 26800952
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132570 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 19680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 972000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5173010 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 158072 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 20160 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 458400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20164 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 33622 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 36000 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 171840 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 856 | 19990907 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 780 | 17047272.73 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 2092 | 44233697.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4690000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 16 | 2066300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 752000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 6963500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1016360 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 140509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2390498 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 46 | 293280 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 112 | 2367360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 306320 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 405636 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 983 | 21391763
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 1169280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 151200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 858000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 214840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 82080 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 129 | 2482000
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 61870 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 16 | 687000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 721680 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 679872 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1624320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 82 | 1826870 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 379000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 280560 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 211 | 5156000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 487 | 11417172
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 4 | 58545 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 901 | 18725090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 205 | 5774976 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 326880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 592 | 17359999 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1702 | 42245490
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 8256725 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 108 | 2193000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1080 | 20708363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5285186 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2506 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1911 | 36445780.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 159976 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 182 | 4639209 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 400 | 8898909 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 26 | 42048 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 10740 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1382 | 25191170 | On test
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 155248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 162410 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1990 | 39259710
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 60 | 1455272 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 235488 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 26082.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 276275 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 133625 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 720000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 200 | 2846742.36
Eastern Grid Total |  |  |  |  | 17395.105 | 5243.3 | 106325584.73
Western Grid Total |  |  |  |  | 10984.003 | 5803 | 120797723
National Grid Total |  |  |  |  | 28379.108 | 11046.3 | 227123307.73
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7503.75 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3320 | MW
i) Dhaka area |  |  | 4161.75 |  | MW | i) Khulna area |  |  |  | 1251 | MW
ii) Chattogram area |  |  | 1144 |  | MW | ii) Barishal area |  |  |  | 309 | MW
iii) Cumilla area |  |  | 938 |  | MW | iii) Rajshahi area |  |  |  | 986 | MW
iv) Mymensingh area |  |  | 861 |  | MW | iv) Rangpur area |  |  |  | 774 | MW
v) Sylhet area |  |  | 399 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10823.75 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 77 | 12:00 | 133 | Netrakona | 103 | 18:30
2 | AKSML | 129 | 14:00 | 68 | Hathazari | 56 | 13:00 | 134 | New | 74 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Hatirjheel | 32 | 13:00 | 135 | Niamatpur | 46 | 13:00
4 | Agargaon | 79 | 18:30 | 70 | Ishurdi | 49 | 18:30 | 136 | Noapara | 41 | 19:00
5 | Agrabad | 44 | 18:00 | 71 | Jaldhaka | 60 | 18:00 | 137 | PHP | 9 | 10:00
6 | Amnura | 29 | 11:00 | 72 | Jamalpur | 93 | 18:00 | 138 | Pabna | 72 | 18:00
7 | Ashuganj | 57 | 14:00 | 73 | Jashore | 109 | 13:00 | 139 | Palashbari | 80 | 18:00
8 | BSRM | 199 | 08:00 | 74 | Jhenaidah | 96 | 18:00 | 140 | Panchagarh | 48 | 18:00
9 | Bagerhat | 58 | 18:00 | 75 | Joydebpur | 93 | 18:30 | 141 | Patiya | 9 | 21:00
10 | Bajitpur | 55 | 18:00 | 76 | Joypurhat | 42 | 20:00 | 142 | Patuakhali | 45 | 20:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 10.5 | 00:00 | 143 | Payra | 22 | 20:00
12 | Bakulia | 65 | 18:00 | 78 | KSRM | 18 | 03:00 | 144 | Postogola | 40 | 13:00
13 | Banani | 41 | 12:00 | 79 | Kabirpur | 189 | 18:00 | 145 | Purbachal | 20 | 00:00
14 | Bangabhaban | 13 | 11:00 | 80 | Kachua | 47 | 19:00 | 146 | Purbasadipur | 111 | 18:00
15 | Barapukuria | 50 | 18:00 | 81 | Kallyanpur | 75 | 13:00 | 147 | Rahanpur | 24 | 18:00
16 | Barguna | 10 | 18:00 | 82 | Kalurghat | 30 | 15:00 | 148 | Rahim | 35 | 16:00
17 | Barishal | 85 | 12:00 | 83 | Kamrangirchar | 62 | 13:00 | 149 | Rajbari | 59 | 18:00
18 | Barishal-230 | 64 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 105 | 19:00
19 | Baroaulia | 49 | 18:00 | 85 | Kasba | 22 | 19:00 | 151 | Rajshahi | 79 | 13:00
20 | Baroirhat | 47 | 18:00 | 86 | Kazla | 68 | 19:00 | 152 | Rajshahi-230 | 58 | 13:00
21 | Bashundhara | 148 | 12:00 | 87 | Keranigonj | 52 | 13:00 | 153 | Ramganj | 68 | 13:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 27 | 14:00
23 | Beanibazar | 46 | 18:00 | 89 | Khulna | 48 | 12:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 38 | 18:00 | 90 | Khulshi | 169 | 18:30 | 156 | Rangpur | 98 | 13:00
25 | Bhaluka | 125 | 18:00 | 91 | Kishoreganj | 82 | 18:00 | 157 | Ruppur | 2.4 | 11:00
26 | Bhandaria | 36 | 20:00 | 92 | Kodda | 270 | 18:00 | 158 | SSM | 3 | 00:00
27 | Bhangura | 23 | 18:00 | 93 | Kulaura | 28 | 18:00 | 159 | Saidpur | 86 | 10:00
28 | Bheramara(GK) | 41 | 18:00 | 94 | Kurigram | 48 | 18:00 | 160 | Satkhira | 87 | 18:30
29 | Bhulta | 197 | 12:00 | 95 | Kushtia | 117 | 13:00 | 161 | Satmasjid | 74 | 14:00
30 | Bog-Sherpur | 58 | 18:00 | 96 | Laksam | 21 | 13:00 | 162 | Savar | 159 | 18:00
31 | Bogura | 112 | 18:00 | 97 | Lakshmipur | 23 | 19:00 | 163 | SevenRings | 17.76 | 12:00
32 | Borhanuddin | 64 | 21:00 | 98 | Lalbag | 54 | 18:00 | 164 | ShahCement | 32 | 00:00
33 | Brahmanbaria | 86 | 18:00 | 99 | Lalmonirhat | 46 | 18:00 | 165 | Shahjadpur | 55 | 18:30
34 | Cantonment | 82 | 13:00 | 100 | MI_Cement | 15.7 | 23:00 | 166 | Shahjibazar | 78 | 18:00
35 | Chandina | 8 | 13:00 | 101 | Madanganj | 26 | 13:00 | 167 | Shahmirpur | 38 | 18:00
36 | Chandpur | 56 | 18:00 | 102 | Madaripur | 70 | 19:30 | 168 | Shariatpur | 54 | 20:00
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 55 | 13:00 | 169 | Sherpur | 106 | 18:00
38 | Chapai | 54 | 12:00 | 104 | Madunaghat | 39 | 18:00 | 170 | Shikalbaha | 22 | 12:00
39 | Charsaidpur | 42 | 15:00 | 105 | Magura | 52 | 18:00 | 171 | Shitalakhya | 62.6 | 13:00
40 | Chauddagram | 47 | 11:00 | 106 | Mahasthangarh | 44 | 18:00 | 172 | Sholosohor | 34 | 18:00
41 | Chhatak | 17 | 18:00 | 107 | Maijdee | 28 | 19:30 | 173 | Shyampur | 138 | 11:00
42 | Chowmuhani | 101 | 18:00 | 108 | Manikganj | 92 | 18:00 | 174 | Siddhirganj | 88 | 18:00
43 | Chuadanga | 73 | 18:00 | 109 | Maniknagar | 53 | 13:00 | 175 | Sirajganj | 80 | 18:30
44 | Coxsbazar | 107 | 18:00 | 110 | Matarbari | 35 | 18:00 | 176 | Sonargaon | 146 | 18:30
45 | Cumilla(N) | 93 | 13:00 | 111 | Matuail | 54 | 11:00 | 177 | Sreemongol | 54 | 18:00
46 | Cumilla(S) | 123 | 13:00 | 112 | Metrorail_Motijheel | 16 | 09:00 | 178 | Sreepur | 89 | 15:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 8 | 18:30 | 179 | Srinagar | 30.08 | 13:00
48 | Daudkandi | 106 | 19:00 | 114 | Millgate | 77 | 13:00 | 180 | Sunamganj | 38 | 18:00
49 | DhakaUniversity | 60 | 13:00 | 115 | Mirpur | 110 | 13:00 | 181 | Sylhet | 40 | 13:00
50 | Dhamrai | 104 | 16:00 | 116 | Mirsorai | 9 | 09:00 | 182 | Sylhet-132 | 74 | 13:00
51 | Dhanmondi | 76 | 13:00 | 117 | Mirzapur | 38 | 18:00 | 183 | TK | 15.5 | 13:00
52 | Dohazari | 66 | 20:00 | 118 | Mithapukur | 50 | 18:00 | 184 | Tangail | 116 | 18:00
53 | Faridpur | 106 | 18:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:00
54 | Fatullah | 89 | 10:00 | 120 | Mogbazar | 67.4 | 18:00 | 186 | Tasnim | 14 | 01:00
55 | Fenchuganj | 27 | 14:00 | 121 | Mongla | 34 | 10:00 | 187 | Thakurgaon | 81 | 18:00
56 | Feni | 67 | 18:00 | 122 | Motijheel | 28 | 13:00 | 188 | Tongi | 103 | 15:00
57 | GPH | 98 | 02:00 | 123 | Muktagacha | 28 | 13:00 | 189 | Ullahpara | 25 | 18:00
58 | Ghatail | 58 | 18:00 | 124 | Munshiganj | 70 | 13:00 | 190 | Ullon | 38 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 24 | 19:30 | 191 | Uttara | 71 | 18:00
60 | Ghorashal-230 | 83 | 11:00 | 126 | Mymensingh | 133 | 13:00 | 192 | UttaraNew | 47 | 14:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 84 | 13:00 | 193 | Zigatola | 56 | 10:00
62 | Gollamari | 62 | 12:00 | 128 | Narail | 40 | 18:00
63 | Gopalganj | 77 | 18:00 | 129 | Narinda | 59 | 13:00
64 | Gulshan | 74 | 13:00 | 130 | Narshingdi | 136 | 18:30
65 | Halishahar | 51 | 13:00 | 131 | Natore | 100 | 18:00
66 | HaripurSBU | 105 | 06:00 | 132 | Nawabganj | 28.2 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8942 | 0 |  | 8942
1:00 | 8468 | 0 |  | 8468
2:00 | 8001 | 0 |  | 8001
3:00 | 7696 | 0 |  | 7696
4:00 | 7477 | 0 |  | 7477
5:00 | 7367 | 0 |  | 7367
6:00 | 7824 | 0 |  | 7824
7:00 | 8329.54 | 0 |  | 8329.54
8:00 | 9066.97 | 0 |  | 9066.97
9:00 | 9596.22 | 0 |  | 9596.22
10:00 | 9564.12 | 0 |  | 9564.12
11:00 | 9629.29 | 0 |  | 9629.29
12:00 | 10131.8 | 0 |  | 10131.8
13:00 | 10518.31 | 0 |  | 10518.31
14:00 | 10075.03 | 0 |  | 10075.03
15:00 | 9688.07 | 0 |  | 9688.07
16:00 | 9543.46 | 0 |  | 9543.46
17:00 | 9781.55 | 0 |  | 9781.55
18:00 | 11046.3 | 0 |  | 11046.3
19:00 | 10922.8 | 0 |  | 10922.8
19:30 | 10689 | 0 |  | 10689
20:00 | 10683 | 0 |  | 10683
21:00 | 10471.26 | 0 |  | 10471.26
22:00 | 9821.81 | 0 |  | 9821.81
23:00 | 9416.7 | 0 |  | 9416.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4329 | 4613 | 8942 | DAILY GENERATION CURVE
00:30 | 4227 | 4478 | 8705
01:00 | 4125 | 4343 | 8468 | 21-12-2025
01:30 | 4016.5 | 4218 | 8234.5
02:00 | 3908 | 4093 | 8001
02:30 | 3771 | 4077.5 | 7848.5
03:00 | 3634 | 4062 | 7696
03:30 | 3601 | 3985.5 | 7586.5
04:00 | 3568 | 3909 | 7477
04:30 | 3498.5 | 3923.5 | 7422
05:00 | 3429 | 3938 | 7367
05:30 | 3600.5 | 3995 | 7595.5
06:00 | 3772 | 4052 | 7824
06:30 | 3956.835 | 4119.935 | 8076.77
07:00 | 4141.67 | 4187.87 | 8329.54
07:30 | 4204.55 | 4493.705 | 8698.255
08:00 | 4267.43 | 4799.54 | 9066.97
08:30 | 4292.54 | 5039.055 | 9331.595
09:00 | 4317.65 | 5278.57 | 9596.22
09:30 | 4323.155 | 5257.015 | 9580.17
10:00 | 4328.66 | 5235.46 | 9564.12
10:30 | 4246.565 | 5350.14 | 9596.705
11:00 | 4164.47 | 5464.82 | 9629.29
11:30 | 4380.18 | 5500.365 | 9880.545
12:00 | 4595.89 | 5535.91 | 10131.8
12:30 | 4735.19 | 5589.865 | 10325.055
13:00 | 4874.49 | 5643.82 | 10518.31
13:30 | 4779.605 | 5517.065 | 10296.67
14:00 | 4684.72 | 5390.31 | 10075.03
14:30 | 4654.58 | 5226.97 | 9881.55
15:00 | 4624.44 | 5063.63 | 9688.07
15:30 | 4578.455 | 5037.31 | 9615.765
16:00 | 4532.47 | 5010.99 | 9543.46
16:30 | 4592.97 | 5069.535 | 9662.505
17:00 | 4653.47 | 5128.08 | 9781.55
17:30 | 4948.385 | 5465.54 | 10413.925
18:00 | 5243.3 | 5803 | 11046.3
18:30 | 5178.55 | 5806 | 10984.55
19:00 | 5113.8 | 5809 | 10922.8
19:30 | 4873 | 5816 | 10689
20:00 | 4892 | 5791 | 10683
20:30 | 4869.5 | 5707.63 | 10577.13 |  | Executive Engineer
21:00 | 4847 | 5624.26 | 10471.26 |  | Network Operation Division
21:30 | 4783 | 5363.535 | 10146.535
22:00 | 4719 | 5102.81 | 9821.81
22:30 | 4616.5 | 5002.755 | 9619.255
23:00 | 4514 | 4902.7 | 9416.7

## En-Curve
QF-LDC-12
Date | 21-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2796 | 956 | 780 | 0 | 92 | 978 | 40 | 3276 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2792 | 955.5 | 763 | 0 | 90 | 913.5 | 40 | 3139 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21-12-2025
01:00 | 2788 | 955 | 746 | 0 | 88 | 849 | 40 | 3002 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2788 | 888 | 622 | 0 | 86 | 845 | 40 | 2965.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 227.1233 |  | MKWHr
02:00 | 2788 | 821 | 498 | 0 | 84 | 841 | 40 | 2929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2700 | 788 | 497.5 | 0 | 84 | 841 | 40 | 2898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 227.1233 |  | MKWHr
03:00 | 2612 | 755 | 497 | 0 | 84 | 841 | 40 | 2867 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2590.5 | 750 | 427 | 0 | 84 | 840 | 40 | 2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2569 | 745 | 357 | 0 | 84 | 839 | 40 | 2843 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2554 | 705 | 357 | 0 | 84 | 837.5 | 40 | 2844.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2539 | 665 | 357 | 0 | 84 | 836 | 40 | 2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2589 | 762 | 404 | 0 | 85 | 836 | 40 | 2879.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2639 | 859 | 451 | 0 | 86 | 836 | 40 | 2913 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2753.5 | 870.5 | 522 | 0 | 87 | 835.5 | 40 | 2963 | 4.27 | 0 | 1 | 0 | 0 | 0 | 0
07:00 | 2868 | 882 | 593 | 0 | 88 | 835 | 40 | 3013 | 8.54 | 0 | 2 | 0 | 0 | 0 | 0
07:30 | 2877 | 864.5 | 692.5 | 0 | 92 | 881.715 | 40 | 3184 | 43.04 | 0 | 23.5 | 0 | 0 | 0 | 0
08:00 | 2886 | 847 | 792 | 0 | 96 | 928.43 | 40 | 3355 | 77.54 | 0 | 45 | 0 | 0 | 0 | 0
08:30 | 2758 | 888 | 840 | 0 | 95 | 975.825 | 40 | 3574.5 | 115.27 | 0 | 45 | 0 | 0 | 0 | 0
09:00 | 2630 | 929 | 888 | 0 | 94 | 1023.22 | 40 | 3794 | 153 | 0 | 45 | 0 | 0 | 0 | 0
09:30 | 2596 | 919.75 | 888 | 0 | 96 | 1027.495 | 40 | 3747.5 | 195.425 | 0 | 70 | 0 | 0 | 0 | 0
10:00 | 2562 | 910.5 | 888 | 0 | 98 | 1031.77 | 40 | 3701 | 237.85 | 0 | 95 | 0 | 0 | 0 | 0
10:30 | 2572.5 | 896.5 | 887.5 | 0 | 98 | 1034.345 | 40 | 3631.5 | 339.36 | 0 | 97 | 0 | 0 | 0 | 0
11:00 | 2583 | 882.5 | 887 | 0 | 98 | 1036.92 | 40 | 3562 | 440.87 | 0 | 99 | 0 | 0 | 0 | 0
11:30 | 2659.5 | 899 | 887.5 | 0 | 107 | 1035.705 | 40 | 3695.5 | 457.34 | 0 | 99 | 0 | 0 | 0 | 0
12:00 | 2736 | 915.5 | 888 | 0 | 116 | 1034.49 | 40 | 3829 | 473.81 | 0 | 99 | 0 | 0 | 0 | 0
12:30 | 2791.5 | 954 | 887.5 | 0 | 119 | 1076 | 40 | 3847.5 | 471.555 | 0 | 138 | 0 | 0 | 0 | 0
13:00 | 2847 | 992.5 | 887 | 0 | 122 | 1117.51 | 40 | 3866 | 469.3 | 0 | 177 | 0 | 0 | 0 | 0
13:30 | 2750.5 | 912.75 | 894 | 0 | 121 | 1121.255 | 40 | 3806.5 | 438.665 | 0 | 212 | 0 | 0 | 0 | 0
14:00 | 2654 | 833 | 901 | 0 | 120 | 1125 | 40 | 3747 | 408.03 | 0 | 247 | 0 | 0 | 0 | 0
14:30 | 2680.5 | 814 | 901 | 0 | 115 | 1078 | 40 | 3644 | 339.55 | 0 | 269.5 | 0 | 0 | 0 | 0
15:00 | 2707 | 795 | 901 | 0 | 110 | 1031 | 40 | 3541 | 271.07 | 0 | 292 | 0 | 0 | 0 | 0
15:30 | 2731 | 815 | 901 | 0 | 105 | 1027 | 40 | 3524.5 | 192.265 | 8 | 272 | 0 | 0 | 0 | 0
16:00 | 2755 | 835 | 901 | 0 | 100 | 1023 | 40 | 3508 | 113.46 | 16 | 252 | 0 | 0 | 0 | 0
16:30 | 2701 | 803 | 901 | 0 | 92 | 1050.5 | 40 | 3601.5 | 62.005 | 16 | 395.5 | 0 | 0 | 0 | 0
17:00 | 2647 | 771 | 901 | 0 | 84 | 1078 | 40 | 3695 | 10.55 | 16 | 539 | 0 | 0 | 0 | 0
17:30 | 2759.5 | 780 | 901 | 0 | 98 | 1230 | 40 | 3783 | 5.275 | 16 | 801.15 | 0 | 0 | 0 | 0
18:00 | 2872 | 789 | 901 | 0 | 112 | 1382 | 40 | 3871 | 0 | 16 | 1063.3 | 0 | 0 | 0 | 0
18:30 | 2882 | 819 | 901 | 0 | 112 | 1417.5 | 40 | 3893.5 | 0 | 16 | 903.55 | 0 | 0 | 0 | 0
19:00 | 2892 | 849 | 901 | 0 | 112 | 1453 | 40 | 3916 | 0 | 16 | 743.8 | 0 | 0 | 0 | 0
19:30 | 2840 | 850 | 901 | 0 | 106 | 1450 | 40 | 3938 | 0 | 16 | 548 | 0 | 0 | 0 | 0
20:00 | 2846 | 862 | 901 | 0 | 114 | 1460 | 40 | 4019 | 0 | 16 | 425 | 0 | 0 | 0 | 0
20:30 | 2877 | 855.5 | 901 | 0 | 109 | 1389.13 | 40 | 4075 | 0 | 8 | 322.5 | 0 | 0 | 0 | 0
21:00 | 2908 | 849 | 901 | 0 | 104 | 1318.26 | 40 | 4131 | 0 | 0 | 220 | 0 | 0 | 0 | 0
21:30 | 2842 | 849.5 | 901 | 0 | 104 | 1261.535 | 40 | 3998 | 0 | 0 | 150.5 | 0 | 0 | 0 | 0
22:00 | 2776 | 850 | 901 | 0 | 104 | 1204.81 | 40 | 3865 | 0 | 0 | 81 | 0 | 0 | 0 | 0
22:30 | 2790 | 809 | 901 | 0 | 102 | 1168.755 | 40 | 3750.5 | 0 | 0 | 58 | 0 | 0 | 0 | 0
23:00 | 2804 | 768 | 901 | 0 | 100 | 1132.7 | 40 | 3636 | 0 | 0 | 35 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 410 | 04:00 | 381 | 14:00 | Meghnaghat | 411 | 04:00 | 384 | 14:00
Ashuganj | 416 | 7:00 | 388 | 14:00 | Payra | 417 | 02:00 | 407 | 13:00
Bhulta | 413 | 06:00 | 381 | 14:00 | Rahanpur | 417 | 02:00 | 400 | 18:30
Bibiana | 403 | 02:00 | 383 | 14:00 | Rampal | 411 | 02:00 | 389 | 14:00
BIPTC | 409 | 03:00 | 391 | 10:00
Bogura | 413 | 05:00 | 391 | 18:30
Gopalganj | 413 | 04:00 | 390 | 14:00
Kaliakoir | 404 | 04:00 | 374 | 14:00
Korerhat | 413 | 06:00 | 390 | 14:00
Madunaghat | 407 | 03:00 | 392 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 220 | 12:00 | Kachua | 235 | 02:00 | 227 | 12:00
AKSML | 237 | 06:00 | 225 | 14:00 | Kaliakoir | 239 | 02:00 | 217 | 12:00
Aminbazar | 240 | 04:00 | 220 | 14:00 | Keranigonj | 239 | 06:00 | 220 | 12:00
Ashuganj | 240 | 02:00 | 225 | 12:00 | Khulna(S) | 239 | 02:00 | 226 | 13:00
Ashuganj-400 | 240 | 7:00 | 224 | 14:00 | Korerhat | 239 | 03:00 | 226 | 14:00
Baghabari | 241 | 02:00 | 228 | 18:00 | Madunaghat | 236 | 04:00 | 226 | 13:00
Barapukuria | 230 | 05:00 | 217 | 09:00 | Madunaghat-400 | 236 | 03:00 | 228 | 12:00
Barapukuria-230 | 228 | 6:00 | 217 | 9:00 | Maniknagar | 238 | 06:00 | 222 | 12:00
Barishal | 246 | 04:00 | 235 | 14:00 | Meghnaghat | 246 | 05:00 | 230 | 12:00
Bheramara | 239 | 06:00 | 223 | 13:00 | Meghnaghat-400 | 241 | 04:00 | 224 | 12:00
Bhulta | 241 | 04:00 | 222 | 12:00 | Mirsorai | 239 | 05:00 | 227 | 12:00
Bibiana | 240 | 03:00 | 226 | 14:00 | Rajshahi | 238 | 03:00 | 223 | 13:00
BIPTC | 241 | 06:00 | 223 | 18:30 | Rampal | 237 | 03:00 | 224 | 13:00
Bogura | 243 | 04:00 | 229 | 18:30 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 242 | 05:00 | 229 | 13:00 | Rampura | 240 | 04:00 | 222 | 12:00
Borhanuddin | 246 | 03:00 | 239 | 13:00 | Shikalbaha | 234 | 03:00 | 225 | 12:00
BSRM | 238 | 04:00 | 227 | 12:00 | Shyampur | 240 | 04:00 | 221 | 12:00
Cumilla(N) | 239 | 05:00 | 224 | 14:00 | Siddhirganj | 241 | 05:00 | 222 | 12:00
Faridpur | 244 | 04:00 | 231 | 13:00 | Sirajgonj | 246 | 04:00 | 236 | 18:00
Fenchuganj | 239 | 03:00 | 229 | 14:00 | Sreepur | 238 | 05:00 | 224 | 13:00
Feni | 239 | 04:00 | 225 | 12:00 | Tongi | 235 | 04:00 | 213 | 11:00
Ghorashal | 240 | 00:00 | 228 | 12:00
Ghorashal-230 | 233 | 04:00 | 215 | 14:00
Gopalganj | 245 | 04:00 | 231 | 14:00
GPH | 237 | 04:00 | 227 | 12:00
Haripur | 241 | 04:00 | 224 | 13:00
Hasnabad | 238 | 01:00 | 219 | 14:00
Hathazari | 235 | 05:00 | 224 | 20:00
Ishurdi | 242 | 06:00 | 226 | 18:00
Jhenaidah | 238 | 03:00 | 222 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 124 | 12:00 | Laksam | 139 | 07:00 | 131 | 14:00 | UttaraNew | 137 | 01:00 | 119 | 12:00
Agargaon | 138 | 06:00 | 137 | 04:00 | Lakshmipur | 135 | 06:00 | 127 | 13:00 | Zigatola | 137 | 04:00 | 124 | 12:00
Agrabad | 137 | 05:00 | 129 | 15:00 | Lalbag | 137 | 04:00 | 124 | 12:00
AKS | 134 | 01:00 | 129 | 10:00 | Lalmonirhat | 132 | 05:00 | 122 | 08:00
Aminbazar | 138 | 04:00 | 126 | 12:00 | Madanganj | 140 | 06:00 | 128 | 12:00
Amnura | 139 | 05:00 | 130 | 12:00 | Madaripur | 138 | 01:00 | 133 | 14:00
Ashuganj | 141 | 04:00 | 134 | 13:00 | Madartek | 135 | 02:00 | 125 | 12:00
Bagerhat | 133 | 03:00 | 122 | 18:00 | Madunaghat | 138 | 04:00 | 132 | 12:00
Bajitpur | 136 | 01:00 | 128 | 13:00 | Magura | 138 | 05:00 | 124 | 13:00
Bakerganj | 137 | 03:00 | 132 | 14:00 | Mahasthangarh | 137 | 03:00 | 129 | 09:00
Bakulia | 138 | 03:00 | 131 | 12:00 | Maijdee | 134 | 03:00 | 130 | 19:00
Banani | 136 | 02:00 | 125 | 12:00 | Manikganj | 133 | 02:00 | 116 | 14:00
Bangabhaban | 139 | 06:00 | 127 | 12:00 | Maniknagar | 139 | 04:00 | 127 | 12:00
Barapukuria | 138 | 05:00 | 129 | 09:00 | Matarbari | 130 | 07:00 | 120 | 18:00
Barguna | 138 | 05:00 | 133 | 13:00 | Matuail | 141 | 02:00 | 131 | 12:00
Barishal | 141 | 03:00 | 134 | 12:00 | Metrorail_Motijheel | 139 | 04:00 | 127 | 12:00
Barishal-230 | 142 | 04:00 | 134 | 13:00 | Metrorail_Uttara | 137 | 01:00 | 119 | 11:00
Baroaulia | 137 | 04:00 | 130 | 12:00 | Millgate | 136 | 02:00 | 119 | 14:00
Baroirhat | 135 | 01:00 | 129 | 13:00 | Mirpur | 137 | 04:00 | 124 | 12:00
Bashundhara | 137 | 03:00 | 116 | 12:00 | Mirzapur | 137 | 04:00 | 127 | 14:00
BashundharaCement | 140 | 04:00 | 128 | 12:00 | Mithapukur | 136 | 03:00 | 124 | 09:00
Beanibazar | 136 | 03:00 | 130 | 12:00 | MI_Cement | 139 | 03:00 | 125 | 12:00
Benapole | 135 | 04:00 | 120 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 137 | 05:00 | 127 | 13:00 | Mogbazar | 138 | 03:00 | 125 | 12:00
Bhandaria | 140 | 07:00 | 130 | 22:00 | Mongla | 132 | 06:00 | 122 | 18:00
Bhangura | 140 | 03:00 | 132 | 13:00 | Motijheel | 139 | 06:00 | 127 | 12:00
Bheramara | 142 | 06:00 | 135 | 13:00 | Muktagacha | 135 | 10:00 | 125 | 13:00
Bheramara(GK) | 141 | 03:00 | 135 | 13:00 | Munshiganj | 140 | 06:00 | 130 | 12:00
Bhulta | 131 | 03:00 | 123 | 14:00 | Muradnagar | 139 | 03:00 | 129 | 13:00
Bog-Sherpur | 138 | 02:00 | 130 | 13:00 | Mymensingh | 136 | 10:00 | 122 | 13:00
Bogura | 139 | 04:00 | 130 | 13:00 | Naogaon | 135 | 04:00 | 126 | 13:00
Bogura-230 | 139 | 04:00 | 131 | 13:00 | Narail | 139 | 03:00 | 124 | 13:00
Brahmanbaria | 136 | 03:00 | 127 | 12:00 | Narinda | 139 | 4:00 | 127 | 12:00
Cantonment | 138 | 05:00 | 125 | 14:00 | Narshingdi | 138 | 05:00 | 125 | 12:00
Chandina | 141 | 04:00 | 132 | 12:00 | Natore | 138 | 02:00 | 130 | 13:00
Chandpur | 138 | 05:00 | 133 | 12:00 | Nawabganj | 137 | 03:00 | 124 | 12:00
Chandraghona | 139 | 06:00 | 133 | 12:00 | Netrakona | 130 | 04:00 | 120 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 05:00 | 133 | 19:30 | New | 135 | 04:00 | 119 | 12:00
Charsaidpur | 141 | 06:00 | 130 | 12:00 | Niamatpur | 140 | 04:00 | 132 | 18:30
Chauddagram | 138 | 01:00 | 129 | 11:00 | Noapara | 136 | 03:00 | 120 | 13:00
Chhatak | 136 | 03:00 | 128 | 14:00 | Pabna | 140 | 03:00 | 133 | 13:00
Chowmuhani | 133 | 04:00 | 126 | 13:00 | Palashbari | 134 | 05:00 | 123 | 13:00
Chuadanga | 137 | 04:00 | 124 | 18:00 | Panchagarh | 139 | 04:00 | 120 | 09:00
Coxsbazar | 125 | 02:00 | 119 | 19:30 | Patiya | 137 | 04:00 | 131 | 12:00
Cumilla(N) | 140 | 06:00 | 131 | 12:00 | Patuakhali | 135 | 02:00 | 132 | 13:00
Cumilla(S) | 141 | 04:00 | 124 | 13:00 | Payra | 138 | 04:00 | 133 | 18:00
Daganbhuiyan | 136 | 05:00 | 129 | 13:00 | PHP | 136 | 02:00 | 129 | 12:00
Daudkandi | 138 | 06:00 | 128 | 12:00 | Postogola | 140 | 06:00 | 127 | 12:00
DhakaUniversity | 136 | 02:00 | 125 | 12:00 | Purbachal | 137 | 03:00 | 125 | 12:00
Dhamrai | 140 | 04:00 | 128 | 14:00 | Purbasadipur | 132 | 02:00 | 118 | 09:00
Dhanmondi | 142 | 04:00 | 132 | 12:00 | Rahanpur | 140 | 01:00 | 134 | 18:00
Dohazari | 135 | 06:00 | 128 | 12:00 | Rahanpur-400 | 140 | 01:00 | 134 | 18:30
Faridpur | 140 | 03:00 | 133 | 12:00 | Rahim | 140 | 01:00 | 131 | 12:00
Fatullah | 139 | 04:00 | 125 | 12:00 | Rajbari | 140 | 03:00 | 132 | 13:00
Fenchuganj | 140 | 04:00 | 133 | 14:00 | Rajendrapur | 139 | 02:00 | 128 | 13:00
Feni | 136 | 04:00 | 128 | 12:00 | Rajshahi | 137 | 04:00 | 130 | 13:00
Feni-230 | 137 | 04:00 | 129 | 13:00 | Rajshahi-230 | 138 | 04:00 | 129 | 13:00
Ghatail | 133 | 06:00 | 123 | 13:00 | Ramganj | 136 | 06:00 | 129 | 12:00
Ghorashal | 136 | 01:00 | 126 | 11:00 | Rampur | 137 | 06:00 | 130 | 12:00
Goalpara | 135 | 03:00 | 126 | 13:00 | Rampura | 136 | 03:00 | 126 | 12:00
Gollamari | 135 | 06:00 | 127 | 18:00 | Rangamati | 137 | 02:00 | 132 | 12:00
Gopalganj | 138 | 04:00 | 130 | 13:00 | Rangpur | 135 | 06:00 | 126 | 09:00
Gopalganj-400 | 141 | 02:00 | 134 | 13:00 | Ruppur | 141 | 02:00 | 134 | 18:00
Gulshan | 136 | 06:00 | 124 | 12:00 | Saidpur | 134 | 05:00 | 123 | 08:00
Halishahar | 137 | 06:00 | 131 | 12:00 | Satkhira | 133 | 04:00 | 123 | 18:00
Haripur | 142 | 04:00 | 131 | 15:00 | Satmasjid | 137 | 02:00 | 125 | 14:00
HaripurSBU | 142 | 04:00 | 133 | 15:00 | Savar | 136 | 03:00 | 125 | 14:00
Hasnabad | 139 | 04:00 | 126 | 12:00 | SevenRings | 137 | 04:00 | 122 | 12:00
Hathazari | 138 | 05:00 | 132 | 13:00 | ShahCement | 141 | 06:00 | 130 | 12:00
Hatirjheel | 137 | 04:00 | 125 | 12:00 | Shahjadpur | 140 | 00:00 | 135 | 13:00
Ishurdi | 143 | 04:00 | 135 | 18:30 | Shahjibazar | 137 | 06:00 | 128 | 14:00
Jaldhaka | 133 | 05:00 | 119 | 09:00 | Shahmirpur | 137 | 01:00 | 132 | 12:00
Jamalpur | 133 | 10:00 | 120 | 01:00 | Shariatpur | 141 | 04:00 | 132 | 13:00
Jashore | 136 | 03:00 | 119 | 13:00 | Sherpur | 131 | 10:00 | 118 | 01:00
Jhenaidah | 138 | 03:00 | 121 | 18:00 | Shikalbaha | 127 | 04:00 | 121 | 12:00
Jhenaidah-230 | 139 | 03:00 | 126 | 13:00 | Shikalbaha-230 | 138 | 04:00 | 132 | 12:00
Joydebpur | 136 | 05:00 | 121 | 12:00 | Shitalakhya | 139 | 03:00 | 125 | 12:00
Joypurhat | 133 | 06:00 | 125 | 12:00 | Sholosohor | 136 | 01:00 | 132 | 12:00
Juldah | 137 | 07:00 | 131 | 12:00 | Shyampur | 139 | 05:00 | 127 | 12:00
Kabirpur | 136 | 04:00 | 117 | 12:00 | Shyampur-230 | 139 | 04:00 | 128 | 12:00
Kachua | 140 | 02:00 | 133 | 12:00 | Siddhirganj | 141 | 02:00 | 131 | 12:00
Kaliakoir | 142 | 02:00 | 130 | 12:00 | Sirajganj | 136 | 00:00 | 129 | 18:30
Kallyanpur | 137 | 05:00 | 125 | 12:00 | Sonargaon | 138 | 04:00 | 130 | 04:00
Kalurghat | 138 | 05:00 | 132 | 12:00 | Sreemongol | 136 | 01:00 | 130 | 14:00
Kamrangirchar | 136 | 02:00 | 124 | 14:00 | Sreepur | 139 | 03:00 | 13 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 06:00 | 124 | 14:00
Kasba | 139 | 03:00 | 129 | 12:00 | SSM | 140 | 02:00 | 134 | 12:00
Kazla | 139 | 05:00 | 126 | 13:00 | Sunamganj | 133 | 04:00 | 128 | 13:00
Keranigonj | 136 | 03:00 | 125 | 12:00 | Sylhet | 136 | 04:00 | 130 | 13:00
Khagrachori | 137 | 04:00 | 131 | 12:00 | Sylhet-132 | 136 | 01:00 | 131 | 14:00
Khulna | 133 | 04:00 | 124 | 13:00 | Tangail | 133 | 05:00 | 124 | 12:00
Khulna(S) | 135 | 04:00 | 127 | 13:00 | Taraganj | 133 | 04:00 | 125 | 09:00
Khulshi | 135 | 02:00 | 129 | 12:00 | Tasnim | 140 | 04:00 | 130 | 12:00
Kishoreganj | 134 | 04:00 | 127 | 12:00 | Thakurgaon | 137 | 04:00 | 116 | 09:00
Kodda | 137 | 03:00 | 122 | 14:00 | TK | 138 | 06:00 | 132 | 12:00
KSRM | 137 | 01:00 | 130 | 12:00 | Tongi | 137 | 04:00 | 122 | 11:00
Kulaura | 139 | 04:00 | 133 | 12:00 | Ullahpara | 139 | 04:00 | 131 | 13:00
Kurigram | 134 | 05:00 | 121 | 09:00 | Ullon | 136 | 03:00 | 125 | 12:00
Kushtia | 138 | 12:00 | 128 | 13:00 | Uttara | 137 | 02:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division