## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-12-2025 | during | 23-12-2025 | during | 23-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 343 | 368 | 412 | 412 | 392 | 392 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 105 | 105 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 7 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 50.5 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 53 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26 | 23 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 8 | 52.19 | 52.19 | 52 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 116 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 142 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 380 | 360 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1254 | 1726.5 | 5762.15 | 5741.15 | 2714.37 | 2686.37
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 224 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 89 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 33 | 33 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 19 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.98 | 0 | 3.22 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 580 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 830 | 830 | 830 | 830 | 830 | 830 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 2282.98 | 1910 | 3667.94 | 3665.72 | 3140.72 | 3138.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 200 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 165 | 45 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0.01 | 0.01 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 350 | 393 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 5 | 0 | 46.7 | 46.7 | 5 | 5 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 109 | 105 | 163 | 163 | 130 | 130 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 111 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 116 | 110 | 160 | 160 | 122 | 122 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 14 | 24.5 | 24.5 | 18 | 18 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 5 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 4 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1067 | 1138 | 2790.56 | 2725.56 | 1940.56 | 1875.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-12-2025 | during | 23-12-2025 | during | 23-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 34 | 157.5 | 157.5 | 77 | 77 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.49 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 10 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 108.49 | 121 | 361.5 | 314 | 233.5 | 186
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 34 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 157 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 211 | 211 | 210 | 210 | 210 | 210 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 540 | 566 | 598 | 598 | 598 | 598
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 185 | 140 | 410 | 410 | 265 | 265 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 52.81 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 374 | 593 | 0 | 0 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1513.81 | 1639 | 2332 | 2272 | 1432.1 | 1372.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 250 | 503 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 118 | 130 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 900 | 1075 | 1085.32 | 1085.32 | 1025.32 | 1025.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0.02 | 0.02 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.45 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1488.45 | 1928 | 1988.32 | 1988.32 | 1488.34 | 1488.34
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 46.06 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 174 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.05 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 838.98 | 1428.22 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.3 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 85 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1611.39 | 2016.22 | 3079.87 | 2913.87 | 2576.49 | 2410.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 55 | 58 | 58 | 58 | 58 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Coal shortage
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 54 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 142 | 0 | 146.88 | 0 | 146.88 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 234.4 | 159 | 486.08 | 306 | 466.08 | 286
System Total |  |  |  |  | 28823.2 | 28379.108 | 10100.52 | 11203.72 | 21066.42 | 20524.62 | 14590.16 | 14041.36
Forecast Scenario (23-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9120 |  | 0 |  | 9120
|  |  |  | 1:00 | 8530 |  | 0 |  | 8530
|  |  |  | 2:00 | 8040 |  | 0 |  | 8040
|  |  |  | 3:00 | 7770 |  | 0 |  | 7770
|  |  |  | 4:00 | 7550 |  | 0 |  | 7550
|  |  |  | 5:00 | 7440 |  | 0 |  | 7440
|  |  |  | 6:00 | 7680 |  | 0 |  | 7680
|  |  |  | 7:00 | 8240 |  | 0 |  | 8240
|  |  |  | 8:00 | 9260 |  | 0 |  | 9260
|  |  |  | 9:00 | 9660 |  | 0 |  | 9660
|  |  |  | 10:00 | 9480 |  | 0 |  | 9480
|  |  |  | 11:00 | 9630 |  | 0 |  | 9630
|  |  |  | 12:00 | 10200 |  | 0 |  | 10200
|  |  |  | 13:00 | 10570 |  | 0 |  | 10570
|  |  |  | 14:00 | 10170 |  | 0 |  | 10170
|  |  |  | 15:00 | 9740 |  | 0 |  | 9740
|  |  |  | 16:00 | 8850 |  | 0 |  | 8850
|  |  |  | 17:00 | 9880 |  | 0 |  | 9880
|  |  |  | 18:00 | 11300 |  | 0 |  | 11300
|  |  |  | 18:30 | 11200 |  | 0 |  | 11200
|  |  |  | 19:00 | 11130 |  | 0 |  | 11130
|  |  |  | 19:30 | 11030 |  | 0 |  | 11030
|  |  |  | 20:00 | 10780 |  | 0 |  | 10780
|  |  |  | 21:00 | 10610 |  | 0 |  | 10610
|  |  |  | 22:00 | 10170 |  | 0 |  | 10170
|  |  |  | 23:00 | 9600 |  | 0 |  | 9600
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 10200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 225.40 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:27 hrs on 23-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-12-2025 | [28 empty] | Date: | 22-12-2025 | [28 empty] | Date: | 22-12-2025 | [28 empty] | Date: | 22-12-2025 | [28 empty] | Date: | 22-12-2025 | [17 empty] | Date: | 22-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 780 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 1007 | 0 | 0 | 0 | 340 | 10 | 0 | 51 | 0 | 199 | 0 | 0 | 110 | 0 | 0 | 18 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 16 | 27 | 0 | 16 | 0 | 34 | 0 | 0 | 0 | 4442 | 807 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493 | 0 | 4 | 0 | 1014.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 180 | 0 | 288 | 900 | 0 | 4584.27 | 9026.27 | 98.48
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 780 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 335 | 16 | 0 | 51 | 0 | 185 | 0 | 0 | 110 | 0 | 0 | 13 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 17 | 27 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 4265 | 783 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 4 | 0 | 938.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 180 | 0 | 250 | 750 | 0 | 4173.82 | 8438.82 | 98.48
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 680 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 335 | 20 | 0 | 51 | 0 | 194 | 5 | 0 | 110 | 0 | 0 | 13 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 5 | 20 | 0 | 17 | 63 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 4034 | 714 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 4 | 0 | 843.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 180 | 0 | 250 | 650 | 0 | 3914.12 | 7948.12 | 98.48
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 640 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 732 | 0 | 0 | 0 | 360 | 80 | 0 | 5 | 0 | 203 | 5 | 0 | 50 | 0 | 0 | 13 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 5 | 20 | 0 | 17 | 67 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 3866 | 713 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 4 | 0 | 839.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 180 | 0 | 250 | 540 | 0 | 3813.28 | 7679.28 | 98.48
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 580 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 701 | 0 | 0 | 0 | 350 | 95 | 0 | 5 | 0 | 199 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 5 | 20 | 0 | 17 | 67 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 3794 | 616 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 4 | 0 | 838.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 180 | 0 | 250 | 500 | 0 | 3665.12 | 7459.12 | 98.47
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 580 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 652 | 0 | 0 | 0 | 325 | 120 | 0 | 5 | 0 | 202 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 5 | 20 | 0 | 17 | 81 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 3689 | 616 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 5 | 0 | 842.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3660.11 | 7349.11 | 98.47
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 580 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 658 | 0 | 0 | 0 | 305 | 140 | 0 | 10 | 0 | 194 | 5 | 0 | 50 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 41 | 20 | 0 | 17 | 97 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 3819.5 | 666 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 4 | 0 | 840.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 580 | 0 | 3762.55 | 7582.05 | 98.47
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 40 | 0 | 34 | 650 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 750 | 1 | 0 | 0 | 330 | 160 | 0 | 48 | 0 | 199 | 5 | 0 | 111 | 0 | 0 | 11 | 0 | 90 | 0 | 1 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 0 | 17 | 0 | 77 | 20 | 0 | 17 | 97 | 0 | 16 | 0 | 55 | 0 | 0.56 | 0 | 4218.64 | 713 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 404 | 0 | 4 | 0 | 839.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87 | 0 | 0 | 0 | 1.06 | 0 | 0 | 178 | 0 | 0 | 0 | 334 | 0 | 0.11 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 670 | 0 | 3929.23 | 8147.87 | 98.47
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 40 | 0 | 7 | 780 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 919 | 8 | 0 | 0 | 360 | 245 | 0 | 51 | 0 | 202 | 5 | 0 | 111 | 0 | 0 | 11 | 0 | 92 | 0 | 8 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 3 | 17 | 0 | 77 | 30 | 0 | 17 | 97 | 0 | 35 | 2 | 55 | 0 | 3.79 | 0 | 4736.73 | 807 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 465 | 0 | 0 | 0 | 939.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.88 | 8 | 0 | 0 | 8.29 | 0 | 0 | 181 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 63 | 0 | 2 | 0 | 0 | 0 | 0 | 0.4 | 12 | 0.05 | 0 | 0 | 118 | 220 | 0 | 300 | 758 | 0 | 4425.51 | 9162.24 | 98.46
09:00 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 13 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 40 | 0 | 2 | 780 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 1000 | 13 | 0 | 0 | 330 | 335 | 0 | 51 | 0 | 192 | 5 | 0 | 111 | 0 | 0 | 11 | 0 | 98 | 0 | 32 | 0 | 0 | 0 | 212 | 41 | 30 | 0 | 7 | 8 | 0 | 77 | 30 | 0 | 17 | 97 | 0 | 57 | 8 | 45 | 1 | 8.79 | 0 | 4932.71 | 902 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 466 | 0 | 0 | 0 | 922.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.46 | 28 | 0 | 0 | 21.71 | 0 | 0 | 180 | 0 | 0 | 0 | 314 | 0 | 2.17 | 0 | 64 | 0 | 5 | 0 | 0 | 0 | 0 | 1.1 | 27 | 0.12 | 0 | 0 | 118 | 220 | 0 | 300 | 840 | 0 | 4628.18 | 9560.89 | 98.46
10:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 375 | 0 | 0 | 280 | 0 | 0 | 19 | 0 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.69 | 40 | 0 | 9 | 780 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1050 | 17 | 0 | 0 | 345 | 120 | 0 | 51 | 0 | 196 | 5 | 0 | 110 | 0 | 0 | 11 | 0 | 106 | 0 | 53 | 0 | 0 | 0 | 211 | 41 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 97 | 0 | 57 | 8 | 32 | 1 | 27.04 | 0 | 4883.73 | 902 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 395 | 0 | 0 | 0 | 840.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.18 | 56 | 0 | 0 | 37.26 | 0 | 0 | 172 | 0 | 0 | 0 | 310 | 0 | 3.39 | 0 | 64 | 0 | 8 | 0 | 0 | 0 | 0 | 1.5 | 57 | 0.38 | 0 | 0 | 118 | 220 | 0 | 250 | 840 | 0 | 4500.75 | 9384.48 | 98.46
11:00 | 0 | 6 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 35 | 0 | 60 | 0 | 0 | 54 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 23 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 40 | 0 | 3 | 780 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1076 | 19 | 0 | 0 | 325 | 0 | 0 | 51 | 0 | 188 | 5 | 0 | 110 | 0 | 0 | 11 | 0 | 102 | 0 | 59 | 0 | 0 | 0 | 211 | 42 | 30 | 0 | 11 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 24 | 8 | 32 | 2 | 42.7 | 0 | 4800.78 | 901 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 370 | 0 | 0 | 0 | 844.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.18 | 80 | 0 | 0 | 47.24 | 0 | 0 | 171 | 0 | 0 | 0 | 390 | 0 | 4.28 | 0 | 58 | 0 | 25 | 0 | 0 | 0 | 0 | 3.6 | 131 | 0.47 | 0 | 0 | 118 | 220 | 0 | 250 | 870 | 0 | 4734.25 | 9535.03 | 98.46
12:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 50 | 0 | 60 | 0 | 0 | 54 | 0 | 0 | 0 | 380 | 0 | 0 | 250 | 0 | 0 | 27 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.98 | 40 | 0 | 9 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1160 | 20 | 0 | 0 | 350 | 165 | 0 | 51 | 0 | 200 | 5 | 0 | 109 | 0 | 0 | 11 | 0 | 116 | 0 | 60 | 0 | 0 | 0 | 211 | 42 | 30 | 0 | 10 | 17 | 0 | 80 | 30 | 0 | 0 | 120 | 0 | 24 | 8 | 33 | 2 | 41.49 | 0 | 5252.47 | 902 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.81 | 374 | 0 | 0 | 0 | 838.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.06 | 85 | 0 | 0 | 48.3 | 0 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 4.05 | 0 | 58 | 0 | 29 | 0 | 0 | 0 | 0 | 5.4 | 142 | 0.45 | 0 | 0 | 118 | 220 | 0 | 250 | 900 | 0 | 4848.05 | 10100.52 | 98.45
13:00 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 67 | 9 | 60 | 0 | 0 | 72 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 25 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.95 | 40 | 0 | 20 | 830 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1197 | 0 | 0 | 0 | 370 | 250 | 0 | 51 | 0 | 197 | 5 | 0 | 106 | 0 | 0 | 11 | 0 | 112 | 0 | 55 | 0 | 0 | 0 | 211 | 42 | 30 | 0 | 10 | 17 | 0 | 80 | 30 | 0 | 0 | 132 | 0 | 24 | 8 | 33 | 2 | 39.37 | 0 | 5466.32 | 902 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.5 | 374 | 0 | 0 | 0 | 926.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.33 | 82 | 0 | 0 | 44.19 | 0 | 0 | 177 | 0 | 0 | 0 | 414 | 0 | 3.52 | 0 | 58 | 0 | 25 | 0 | 0 | 0 | 0 | 5.1 | 134 | 0.47 | 0 | 0 | 118 | 220 | 0 | 250 | 987 | 0 | 5004.22 | 10470.54 | 98.45
14:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 96 | 15 | 45 | 0 | 0 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 300 | 0 | 0 | 21 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.83 | 40 | 0 | 13 | 770 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 1194 | 0 | 0 | 0 | 230 | 250 | 0 | 51 | 0 | 158 | 0 | 0 | 104 | 0 | 0 | 11 | 0 | 118 | 0 | 52 | 0 | 0 | 0 | 211 | 37 | 30 | 0 | 9 | 17 | 0 | 80 | 30 | 0 | 0 | 142 | 0 | 24 | 8 | 33 | 1 | 32.99 | 0 | 5214.82 | 902 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.02 | 381 | 0 | 0 | 0 | 852.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.91 | 70 | 0 | 0 | 35.1 | 0 | 0 | 181 | 0 | 0 | 0 | 389 | 0 | 3.28 | 0 | 58 | 0 | 20 | 0 | 0 | 0 | 0 | 4.2 | 110 | 0.34 | 0 | 0 | 126 | 220 | 0 | 250 | 1000 | 0 | 4854.88 | 10069.7 | 98.45
15:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 96 | 0 | 45 | 0 | 0 | 72 | 0 | 0 | 0 | 317 | 0 | 0 | 280 | 0 | 0 | 15 | 0 | 26.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 40 | 0 | 9 | 770 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1192 | 12 | 0 | 0 | 220 | 135 | 0 | 51 | 0 | 178 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 112 | 0 | 41 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 2 | 17 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 24 | 8 | 33 | 1 | 18.46 | 0 | 5000.58 | 902 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.86 | 373 | 0 | 0 | 0 | 924.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.8 | 44 | 0 | 0 | 19.84 | 0 | 0 | 179 | 0 | 0 | 0 | 392 | 0 | 2.27 | 0 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 2.8 | 72 | 0.24 | 0 | 0 | 126 | 180 | 0 | 250 | 900 | 0 | 4647.19 | 9647.77 | 98.45
16:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 96 | 0 | 45 | 0 | 0 | 72 | 0 | 0 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 40 | 0 | 8 | 765 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 220 | 10 | 0 | 51 | 0 | 203 | 0 | 0 | 104 | 0 | 0 | 11 | 0 | 114 | 0 | 21 | 0 | 0 | 0 | 211 | 34 | 30 | 0 | 2 | 17 | 0 | 82 | 30 | 0 | 0 | 157 | 0 | 24 | 8 | 33 | 0 | 8.71 | 0 | 4194.48 | 903 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.03 | 376 | 0 | 0 | 0 | 936.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.23 | 21 | 0 | 0 | 6.85 | 0 | 0 | 177 | 0 | 0 | 0 | 414 | 0 | 0.65 | 0 | 55 | 0 | 5 | 0 | 0 | 0 | 0 | 1.2 | 27 | 0.1 | 0 | 0 | 136 | 180 | 0 | 250 | 900 | 0 | 4562.99 | 8757.47 | 98.44
17:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 35 | 0 | 108 | 0 | 195 | 0 | 42 | 140 | 0 | 0 | 0 | 337 | 0 | 42 | 250 | 0 | 0 | 1 | 0 | 25 | 22 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 0.04 | 40 | 6 | 15 | 830 | 0 | 0 | 5 | 0 | 30 | 223 | 0 | 0 | 0 | 580 | 0 | 36 | 0 | 240 | 28 | 0 | 51 | 0 | 186 | 0 | 0 | 105 | 26 | 0 | 11 | 0 | 110 | 0 | 1 | 0 | 0 | 0 | 212 | 34 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 156 | 0 | 57 | 18 | 33 | 0 | 0.55 | 0 | 4824.59 | 900 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.39 | 482 | 0 | 0 | 0 | 1131.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 2 | 0 | 0 | 0.61 | 0 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0.07 | 0 | 55 | 50 | 1 | 49 | 0 | 0 | 0 | 0.1 | 3 | 0.01 | 0 | 0 | 100 | 180 | 0 | 450 | 980 | 0 | 4958.53 | 9783.12 | 98.44
18:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 50.5 | 0 | 116 | 0 | 195 | 0 | 53 | 142 | 0 | 0 | 0 | 360 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 40 | 15 | 19 | 830 | 0 | 0 | 19 | 0 | 89 | 224 | 0 | 0 | 0 | 580 | 0 | 100 | 0 | 393 | 45 | 0 | 51 | 0 | 200 | 0 | 4 | 105 | 111 | 5 | 14 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 211 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 59 | 18 | 34 | 0 | 0 | 10 | 5461.5 | 902 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593 | 0 | 4 | 0 | 1428.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 50 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 220 | 0 | 503 | 1075 | 0 | 5742.22 | 11203.72 | 98.44
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 48 | 0 | 116 | 0 | 95 | 0 | 55 | 143 | 0 | 0 | 0 | 405 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 10 | 15 | 830 | 0 | 0 | 0 | 0 | 90 | 227 | 0 | 0 | 0 | 583 | 0 | 80 | 0 | 393 | 50 | 0 | 51 | 0 | 198 | 0 | 0 | 106 | 117 | 0 | 18 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 212 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 59 | 18 | 34 | 0 | 0 | 12 | 5284 | 902 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 5 | 0 | 1430.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 55 | 50 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 502 | 1080 | 0 | 5754.11 | 11038.11 | 98.44
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 47 | 0 | 116 | 0 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 400 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 17 | 830 | 0 | 0 | 0 | 0 | 90 | 225 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 393 | 130 | 0 | 51 | 0 | 191 | 0 | 0 | 107 | 113 | 0 | 18 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 212 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 59 | 18 | 34 | 0 | 0 | 12 | 5209 | 902 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 4 | 0 | 1420.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 53 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 502 | 1080 | 0 | 5726.06 | 10935.06
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 41.2 | 0 | 116 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 400 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 20 | 830 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 393 | 155 | 0 | 51 | 0 | 188 | 0 | 0 | 107 | 113 | 0 | 20 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 212 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 59 | 0 | 34 | 0 | 0 | 0 | 5073.2 | 901 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 0 | 4 | 0 | 1421.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 503 | 1070 | 0 | 5606.4 | 10679.6 | 98.43
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 830 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 870 | 0 | 0 | 0 | 393 | 240 | 0 | 51 | 0 | 200 | 0 | 0 | 108 | 34 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 211 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 59 | 0 | 34 | 0 | 0 | 0 | 4970.5 | 902 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 4 | 0 | 1440.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 503 | 1070 | 0 | 5544.94 | 10515.44 | 98.43
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 830 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 245 | 295 | 0 | 51 | 0 | 184 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 211 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 59 | 0 | 34 | 0 | 0 | 0 | 4891.5 | 902 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 0 | 4 | 0 | 1307.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 395 | 1000 | 0 | 5186.76 | 10078.26 | 98.43
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 830 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 225 | 300 | 0 | 51 | 0 | 179 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 212 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 58 | 0 | 34 | 0 | 0 | 0 | 4828.5 | 902 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 4 | 0 | 1118.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 300 | 900 | 0 | 4714.5 | 9543 | 98.43
Total KWH | 0 | 240000 | 167520 | 0 | 0 | 0 | 0 | 0 | 8388000 | 0 | 0 | 160560 | 0 | 1131408 | 24000 | 819218 | 0 | 156725 | 996480 | 0 | 0 | 0 | 8757752 | 0 | 115563 | 6725621 | 0 | 0 | 153733 | 0 | 465000 | 425160 | 0 | 0 | 41400 | 41651 | 0 | 0 | 0 | 0 | 0 | 0 | 32640 | 149760 | 19680 | 960000 | 44300 | 372480 | 18247272.73 | 0 | 0 | 40320 | 0 | 281854 | 5316292 | 0 | 0 | 0 | 21327270 | 86535 | 257600 | 0 | 7687000 | 3614300 | 0 | 1118344 | 0 | 4795000 | 65088 | 22080 | 2359063 | 429600 | 10080 | 353640 | 0 | 2397120 | 0 | 378245 | 0 | 0 | 0 | 5176000 | 908000 | 723840 | 0 | 49760 | 423312 | 0 | 1579200 | 656448 | 0 | 136000 | 2763180 | 0 | 774000 | 129600 | 902400 | 9750 | 223410 | 30000 | 113660254.73 | 20119272 | 4133376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289440 | 11120000 | 0 | 54364 | 0 | 23802545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214884 | 488878 | 0 | 0 | 269248 | 0 | 0 | 4345482 | 0 | 0 | 0 | 8808581 | 0 | 22740 | 0 | 1354909 | 186648 | 132311 | 162057 | 0 | 0 | 0 | 25954.92 | 711360 | 2572 | 0 | 0 | 2905000 | 5247952 | 0 | 7637892 | 21248000 | 0 | 113283465.92 | 226943720.65

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10100.52 | MW | 12:00 Hr. | Energy Generated |  |  | 226.9437 |  | MKWHr.
| Day Peak Demand |  |  | 10100.52 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11203.72 | MW | 18:00 Hr. | Energy Demand |  |  | 226.9437 |  | MKWHr.
| Evening Peak Demand |  |  | 11203.72 | MW | 18:00 Hr. | Maximum Temperature |  |  | 27.5 |  | °C
| Minimum Generation of the Day |  |  | 7349.11 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 662.34 |  | MMCFD
| Maximum Generation of the Day |  |  | 11203.72 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.611 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.7615 | 0 | 3.8115 | 0 | 0 | 0.15373 | 0 | 0 | 28.7267 | Gas | 89.2059 | Gas | 311472484.83
| Chattogram Zone |  |  | 5.6888 | 39.5745 | 0.63192 | 0 | 0.96 | 0.10622 | 0 | 0 | 46.9615 | Coal | 80.9353 | Coal | 536266998.4169
| Cumilla Zone |  |  | 19.9924 | 0 | 0.71936 | 0 | 0 | 0.37824 | 2.3971 | 0 | 23.4872 | HFO | 6.4451 | HFO | 106431671.91
| Mymensingh Zone |  |  | 0.9024 | 0 | 0.9336 | 0 | 0 | 0.23316 | 0 | 0 | 2.0692 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 12.366 | 0 | 0 | 0 | 0 | 0.04976 | 0 | 0 | 12.4157 | Hydro | 0.96 | Hydro | 96000
| Khulna Zone |  |  | 4.1877 | 11.12 | 0 | 0 | 0 | 0.28944 | 20.1193 | 0 | 35.7165 | Solar | 3.0785 | Solar | 48051123.974
| Barishal Zone |  |  | 8.153 | 28.8859 | 0 | 0 | 0 | 0.002572 | 0 | 0 | 37.0414 | Import | 46.3189 | Import | 271069280.76
| Rajshahi Zone |  |  | 13.1541 | 0 | 0 | 0 | 0 | 0.99575 | 23.8025 | 0 | 37.9524 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 1.3549 | 0.3487 | 0 | 0 | 0.86963 | 0 | 0 | 2.5732
| Total |  |  | 89.2059 | 80.9353 | 6.4451 | 0 | 0.96 | 3.0785 | 46.3189 | 0 | 226.9437
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 311472484.83 |  | Hydro | 96000
|  |  |  | Coal | 536266998.4169 |  | Solar | 48051123.974
|  |  |  | HFO | 106431671.91 |  | Import | 271069280.76
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 127,33,87,559 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.1193 | Peak Hr Flow | 902.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 19821673.1 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.8025 | Peak Hr Flow | 1428.22 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2259 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3971 | Peak Hr Flow | 110.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2398 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.3189 | Peak Hr Flow | 2440.22 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4151
|  |  |  | Chattogram |  | 0 |  | 1190
|  |  |  | Cumilla |  | 0 |  | 945
|  |  |  | Mymensingh |  | 0 |  | 845
|  |  |  | Sylhet |  | 0 |  | 403
|  |  |  | Khulna |  | 0 |  | 1271
|  |  |  | Barishal |  | 0 |  | 308
|  |  |  | Rajshahi |  | 0 |  | 1000
|  |  |  | Rangpur |  | 0 |  | 750
|  |  |  | Total |  | 0 |  | 10863
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 16:45 | Benapole-Jashore 132 kV Ckt-1 Scheduled S/D from Benapole 132/33kV end Due to Annual
Maintenance and from Jashore 132/33kV end Due to A/M
| 08:21 | 15:02 | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintanance
| 08:22 | 17:11 | Kallyanpur-Lalbag 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to Bay
maintenance
| 08:25 | 16:47 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to Maintenance Work
| 08:25 | 16:46 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to Maintenance Work
| 08:25 | 17:11 | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Barishal 230/132kV end Due to Annual Maintenance
| 08:25 | 12:28 | Bashundhara-Rampura 132 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance
| 08:29 | 16:16 | Ghorasal-Joydeb-B 132kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to Annual
Maintenance
| 08:31 | 15:24 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Annual
maintenance and from Khulna(S) 230/132kVend.
| 08:31 |  | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to Line Re
Routing Work
| 08:35 | 13:32 | C.nawabganj-Rajshahi 132 kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to Annual
maintenance
| 08:35 | 10:14 | Natore 132/33kV S/S TR-1 (405 T) LT Forced S/D
| 08:35 | 10:14 | Natore 132/33kV S/S TR-2 (415 T) LT Forced S/D
| 08:36 | 12:10 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT Scheduled S/D Due to Annual Maintenance
| 08:36 | 10:13 | Natore 132/33kV S/S TR-1 (405 T) HT Forced S/D
| 08:36 | 12:10 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Scheduled S/D Due to Annual Maintenance
| 08:37 | 10:13 | Natore 132/33kV S/S TR-2 (415 T) HT Forced S/D
| 08:38 | 12:04 | Patuakhali 132/33kV S/S 425T (T-3) LT Scheduled S/D Due to Due to Tan-Delta test .
| 08:39 | 12:03 | Patuakhali 132/33kV S/S 425T (T-3) HT Scheduled S/D Due to Due to Tan-Delta test.
| 08:43 | 17:09 | Khulna(S) 230/132kV S/S TR-3 LT Scheduled S/D Due to Annual maintenance Work
| 08:43 | 15:52 | BSRM-GPH 230 kV Ckt-1 Scheduled S/D from BSRM 230/33kV end Due to Annual Maintenance
Work.
| 08:44 | 17:06 | Khulna(S) 230/132kV S/S TR-3 HT Scheduled S/D
| 08:48 | 16:56 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Scheduled S/D Due to Annual
maintenance
| 08:48 | 18:24 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Work for Roads and Highway
| 08:49 |  | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Daganbhuiyan 132/33kV end Due to S/D
taken by Chowmuhani SS End
| 08:49 | 16:56 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D
| 08:49 | 15:52 | BSRM-GPH 230 kV Ckt-2 Scheduled S/D from GPH 230/33kV end Due to annual maintenance
| 08:50 | 17:23 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D Due to yearly Maintenance
| 08:51 | 17:22 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to yearly Maintenance
| 08:52 | 16:46 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to Deadline
check work for Annual maintenance work.
| 08:55 | 13:32 | Fenchuganj 230/132/33kV S/S AT-01 LT Scheduled S/D Due to Annual Maintenance
| 08:56 | 12:11 | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to Am
| 08:56 | 13:33 | Fenchuganj 230/132/33kV S/S AT-01 HT Scheduled S/D Due to Annual Maintenance
| 08:56 | 12:12 | Kodda 132/33kV S/S Tr-1 (406T) LT Scheduled S/D Due to AM
| 08:57 | 16:44 | Shahjibazar-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to
Annual Maintenance and from Shahjibazar 132/33kV end Due to Shatdown For Annual
Maintenance.
| 08:57 | 12:10 | Kodda 132/33kV S/S Tr-1 (406T) HT Scheduled S/D Due to AM
| 08:57 | 12:10 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to Am
| 09:01 | 18:12 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance (Deep Cleaning)
| 09:13 | 17:17 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to dead line
checking.
| 09:15 | 15:52 | Magura 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Annual Maintenance.
| 09:16 | 15:55 | Magura 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Annual Maintenance.
| 09:18 | 18:13 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Deadline checking and Disc Cleaning and from Meghnaghat 400/230kV end Due to Requested by
NLDC
| 09:19 | 16:25 | Rahanpur 400/132kV S/S Bus Reactor 400 KV Scheduled S/D Due to Due to Maintenance work.
| 09:21 | 16:16 | Bogura 400/230kV S/S ATR-03 LT Scheduled S/D Due to Annual Maintenance
| 09:21 | 16:15 | Bogura 400/230kV S/S ATR-03 HT Scheduled S/D Due to Annual Maintenance
| 09:21 | 16:32 | Mongla 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
| 09:21 | 16:32 | Mongla 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
| 09:28 |  | Chandraghona-Rangamati 132 kV Ckt-1 Scheduled S/D from Rangamati 132/33kV end Due to
Deadline Checking and from Chandraghona 132/33kV end Due to Maintenance Work
| 09:37 | 15:43 | Aminbazar-Manikgonj PP 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Deadline Checking by Savar Grid Substation
| 09:48 | 16:19 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Scheduled S/D Due to Annual maintenance
| 09:49 | 16:18 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Scheduled S/D Due to Annual maintenance
| 09:54 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- ST
| 09:55 | 17:06 | Chattak-Sunamganj 132 kV Ckt-1 Scheduled S/D from Sunamganj 132/33kV end Due to Dead Line
Checking
| 09:56 | 17:03 | Chhatak 132/33kV S/S Sunamganj 1 Scheduled S/D Due to 132 kv chhatak-sunamgang ckt-1 Dead
Line Cheaking
| 10:02 | 15:59 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D
| 10:02 | 15:58 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D
| 10:11 | 16:04 | Mahasthangar-Palashbari 132kV Ckt-2 Scheduled S/D from Mahasthangarh 132/33kV end Due to
Annual Maintenance
| 10:23 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 10:31 | 15:19 | Joydebpur 132/33kV S/S GT-2 HT Scheduled S/D Due to Oil Leakage Inspection
| 10:37 | 16:50 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Scheduled S/D Due to Annual Maintenance
| 10:45 | 15:51 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-2 Scheduled S/D Due to Annual maintenance
| 10:45 | 15:59 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-1 Scheduled S/D Due to Annual maintenance
| 10:55 | 16:15 | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to SMPD Annual Maintenance
| 10:55 | 16:15 | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to SPMD annual Maintenance
|  | 10:57 | Sherpur 132/33kV S/S Transformer- 04 HT is restored.
| 10:57 | 18:08 | Kabirpur-Kaliakoir 132kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual maintenance
|  | 10:58 | Sherpur 132/33kV S/S Transformer- 04 LT is restored.
| 11:06 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 11:13 | 17:58 | Kabirpur-Kaliakoir 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Annual
maintenance
| 11:20 | 16:12 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to PT burst
| 11:21 | 16:12 | Palashbari 132/33kV S/S TR1-414T HT Forced S/D Due to PT burst
| 11:35 | 18:06 | Rampur 230/132/33 S/S ATR-01 (706T) HT Project Work S/D Due to 132kv Loop Restored
| 11:35 | 18:08 | Rampur 230/132/33 S/S ATR-01 (706T) LT Project Work S/D Due to 132kv Loop Restored
| 11:38 | 14:09 | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Project Work and from Madunaghat 132/33kV end Due to transformer movement work under this
line by project 01
| 11:51 |  | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Project Work S/D Due to CB Open by NLDC
| 11:52 |  | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Project Work S/D Due to CB open by NLDC
| 11:59 | 14:15 | Chandpur 132/33kV S/S 402T (T-01) HT Forced S/D Due to Due to Bus section-1 problem
| 11:59 | 14:25 | Chandpur 132/33kV S/S 33 kV T-1 Section Forced S/D Due to Voltage fluctuate in CDR2 | [7 empty] | 8.0MW load
|  |  | feeder | [7 empty] | interrup.
| 12:00 |  | Day Peak Generation: 10096 MW.
| 12:10 | 14:24 | Chandraghona-Madunaghat 132 kV Ckt-2 Project Work S/D from Madunaghat 132/33kV end Due to
Transformer movement work under this line by project -01. and from Chandraghona 132/33kV
end Due to Project Work
| 12:14 | 15:18 | Patuakhali 132/33kV S/S 405T (T-1) LT Scheduled S/D Due to Due to Transformer Tan Delta
test .
| 12:17 | 15:17 | Patuakhali 132/33kV S/S 405T (T-1) HT Scheduled S/D Due to Due to Transformer Tan Delta
test .
| 12:20 | 16:12 | Ghatail 132/33kV S/S Main Bus-2 Scheduled S/D Due to Annual Maintenance work
| 12:27 | 14:27 | Ghatail 132/33kV S/S T-1 LT Forced S/D Due to Remove of nest in D/S.
| 12:28 | 14:26 | Ghatail 132/33kV S/S T-1 HT Forced S/D Due to Remove of nest in D/S.
| 13:02 | 15:37 | Patuakhali 132/33kV S/S 415T (T-2) LT Scheduled S/D Due to Due to Transformer 2 tan delta
test
| 13:02 | 15:36 | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Due to Transformer 2 tan delta
test
| 13:34 | 14:42 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to Red hot Maintenance
| 13:34 | 14:41 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Forced S/D Due to Red Hot Maintenance
| 14:27 | 16:17 | Ghatail 132/33kV S/S T-2 HT Forced S/D Due to Remove of nest in main bus-2 D/S.
| 14:27 | 16:18 | Ghatail 132/33kV S/S T-2 LT Forced S/D Due to Remove of nest in main bus-2 D/S.
|  | 15:56 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-1 is restored.
| 15:58 |  | SS Power Tripped with remarks:- unit-1
| 15:58 |  | SS Power Bashkhali Unit-1 tripped.
| 15:58 |  | SS Power Tripped with remarks:- unit-1
| 15:59 |  | SS Power Synchronized with remarks:- unit-2 ( False )
| 15:59 |  | SS Power Synchronized with remarks:- unit-2 ( False )
|  | 16:08 | Mahasthangar-Palashbari 132kV Ckt-2 is restored.
| 16:22 |  | Korerhat- Chowmohoni 230kV circuit-1 & 3 were switched ON for the first time at 16:22
hrs. and 16:23 hrs. respectively.
|  | 18:08 | Kabirpur-Kaliakoir 132kV Ckt-1 is restored.
| 19:02 |  | Ashugonj North 360 MW ST was sync.
| 19:02 |  | Ashugonj North 360 MW ST was sync.
| 19:12 |  | SS Power Bashkhali Unit-1 was sync.
| 19:38 | 20:25 | Rangpur 132/33kV S/S T-3 (424T) HT Tripped showing No micom Relay relays Due to E/F of | [7 empty] | 4.0MW load
|  |  | 33 KV Paglapir Feeder | [7 empty] | interrup.
| 19:38 | 20:53 | Rangpur 132/33kV S/S T-3 (424T) LT Tripped showing micom relay relays Due to E/F of 33 KV | [7 empty] | 4.0MW load
|  |  | Paglapir Feeder | [7 empty] | interrup.
|  | 20:28 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
|  | 20:45 | Ghorasal-Tongi 230kV Ckt-1 is restored.
|  | 20:54 | Ghorasal-Tongi 230kV Ckt-2 is restored.
| 22:55 | 00:50 | Rangpur 132/33kV S/S T-2 (404T) LT Forced S/D Due to 33kV Haragach feeder BUS conector
red hot.
| 22:55 | 00:50 | Rangpur 132/33kV S/S T-2 (404T) HT Forced S/D
| 00:34 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 03:48 |  | Ashuganj (N) tripped, showing generator protection trip.
| 03:48 |  | Ashuganj 450 MW CCPP(North) Tripped with remarks:- ST
| 04:00 |  | Minimum Generation: 7407 MW.
| 04:32 | 04:51 | Bhandaria 132/33kV S/S Transformer-1 LT Tripped showing Protection 51N E/F IDMT Trip | [7 empty] | 13.0MW load
|  |  | relays Due to Tripped feeder rajapur 33kv pbs trial. Rajapur feeder CB don’t open so T1A | [7 empty] | interrup.
is trip.
| 04:32 | 04:51 | Bhandaria 132/33kV S/S Transformer-2 LT Tripped showing Protection 51N E/F IDMT trip | [7 empty] | 13.0MW load
|  |  | relays Due to Tripped feeder rajapur 33kv pbs trial. Rajapur feeder CB don’t open so T1A | [7 empty] | interrup.
is trip.
| 07:17 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Scheduled S/D Due to Annual Maintenances
| 07:18 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT Scheduled S/D Due to Annual Maintenances
| 07:18 |  | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Annual Maintenances | [7 empty] | 10.0MW load
interrup.
| 07:18 |  | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Annual Maintenances | [7 empty] | 10.0MW load
interrup.
| 07:22 |  | Ashuganj (N) GT was synch.
| 07:22 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 07:32 |  | Meghnaghat 400/230kV S/S ATR -03 LT Project Work S/D Due to Project work
| 07:32 |  | Meghnaghat 400/230kV S/S ATR -03 HT Project Work S/D Due to project work
| 07:42 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to Annual
Maintenance
| 07:44 |  | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
| 07:47 |  | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual Maintenance
| 07:59 |  | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 368 | 8388000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6725621 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 50.5 | 160560 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 24000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 53 | 156725 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 115563 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 465000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 425160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 167520 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 819218 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 116 | 1131408 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 240000 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 142 | 996480 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 153733 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 360 | 8757752 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1726.5 | 28726740
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 86535 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 40320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5316292 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 89 | 281854 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 32640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 19 | 372480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 41651 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 44300 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 149760 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 41400 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 21327270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 830 | 18247272.73 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 1910 | 46961454.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 200 | 4795000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 45 | 3614300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 7687000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 65088 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1118344 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 257600 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 105 | 2359063 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 111 | 429600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 110 | 2397120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 353640 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 5 | 10080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 4 | 22080 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 378245 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1138 | 23487160
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 902400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 129600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 774000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 223410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 10 | 30000 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 121 | 2069160
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 49760 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 34 | 908000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 656448 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1579200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 2763180 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 136000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 423312 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 211 | 5176000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 566 | 12415740
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 4 | 54364 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 20119272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 140 | 4133376 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 289440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 593 | 11120000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1639 | 35716452
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 7637892 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2905000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1075 | 21248000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5247952 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Plant is on standby as per NLDC requirement
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2572 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1928 | 37041416
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 214884 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4345482 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8808581 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22740 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1428.22 | 23802545 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 269248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 488878 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2016.22 | 37952358
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1354909 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 54 | 162057 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25954.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 186648 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 132311 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 711360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 159 | 2573239.92
Eastern Grid Total |  |  |  |  | 17395.105 | 5461.5 | 113660254.73
Western Grid Total |  |  |  |  | 10984.003 | 5742.22 | 113283465.92
National Grid Total |  |  |  |  | 28379.108 | 11203.72 | 226943720.65
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7534.91 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3328.5 | MW
i) Dhaka area |  |  | 4151.41 |  | MW | i) Khulna area |  |  |  | 1271 | MW
ii) Chattogram area |  |  | 1190.5 |  | MW | ii) Barishal area |  |  |  | 307.5 | MW
iii) Cumilla area |  |  | 945 |  | MW | iii) Rajshahi area |  |  |  | 1000 | MW
iv) Mymensingh area |  |  | 845 |  | MW | iv) Rangpur area |  |  |  | 750 | MW
v) Sylhet area |  |  | 403 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10863.41 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 77 | 19:00 | 133 | Netrakona | 94 | 19:30
2 | AKSML | 126 | 16:00 | 68 | Hathazari | 59 | 13:00 | 134 | New | 80 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Hatirjheel | 32 | 13:00 | 135 | Niamatpur | 48 | 18:00
4 | Agargaon | 85 | 13:00 | 70 | Ishurdi | 49 | 18:00 | 136 | Noapara | 40 | 19:00
5 | Agrabad | 44 | 14:00 | 71 | Jaldhaka | 54 | 18:00 | 137 | PHP | 8 | 23:00
6 | Amnura | 22 | 10:00 | 72 | Jamalpur | 92 | 19:00 | 138 | Pabna | 76 | 18:00
7 | Ashuganj | 53 | 16:00 | 73 | Jashore | 108 | 13:00 | 139 | Palashbari | 74 | 18:30
8 | BSRM | 198 | 11:00 | 74 | Jhenaidah | 96 | 18:00 | 140 | Panchagarh | 46 | 18:00
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 86 | 18:00 | 141 | Patiya | 6.5 | 18:00
10 | Bajitpur | 59 | 18:00 | 76 | Joypurhat | 43 | 18:00 | 142 | Patuakhali | 47 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 11 | 00:00 | 143 | Payra | 22 | 18:30
12 | Bakulia | 64 | 13:00 | 78 | KSRM | 16 | 07:00 | 144 | Postogola | 37 | 13:00
13 | Banani | 18 | 12:00 | 79 | Kabirpur | 193 | 12:00 | 145 | Purbachal | 20 | 13:00
14 | Bangabhaban | 13 | 11:00 | 80 | Kachua | 41 | 18:00 | 146 | Purbasadipur | 111 | 18:00
15 | Barapukuria | 51 | 18:00 | 81 | Kallyanpur | 72 | 13:00 | 147 | Rahanpur | 23 | 12:00
16 | Barguna | 10 | 18:00 | 82 | Kalurghat | 32 | 15:00 | 148 | Rahim | 47 | 11:00
17 | Barishal | 81 | 12:00 | 83 | Kamrangirchar | 63 | 13:00 | 149 | Rajbari | 61 | 18:00
18 | Barishal-230 | 66 | 18:30 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 116 | 18:00
19 | Baroaulia | 51 | 12:00 | 85 | Kasba | 22 | 14:00 | 151 | Rajshahi | 76 | 18:00
20 | Baroirhat | 48 | 18:00 | 86 | Kazla | 83 | 14:00 | 152 | Rajshahi-230 | 56 | 13:00
21 | Bashundhara | 131 | 14:00 | 87 | Keranigonj | 60 | 13:00 | 153 | Ramganj | 72 | 18:30
22 | BashundharaCement | 13 | 11:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 27 | 14:00
23 | Beanibazar | 46 | 18:00 | 89 | Khulna | 50 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 38 | 08:00 | 90 | Khulshi | 168 | 18:30 | 156 | Rangpur | 104 | 18:00
25 | Bhaluka | 123 | 18:00 | 91 | Kishoreganj | 92 | 18:00 | 157 | Ruppur | 2.6 | 15:00
26 | Bhandaria | 36 | 19:30 | 92 | Kodda | 248 | 18:30 | 158 | SSM | 2 | 01:00
27 | Bhangura | 23 | 13:00 | 93 | Kulaura | 30 | 18:00 | 159 | Saidpur | 94 | 18:00
28 | Bheramara(GK) | 41 | 18:00 | 94 | Kurigram | 44 | 08:00 | 160 | Satkhira | 88 | 08:00
29 | Bhulta | 188 | 12:00 | 95 | Kushtia | 119 | 13:00 | 161 | Satmasjid | 74 | 13:00
30 | Bog-Sherpur | 58 | 18:00 | 96 | Laksam | 23 | 13:00 | 162 | Savar | 162 | 12:00
31 | Bogura | 112 | 19:00 | 97 | Lakshmipur | 24 | 19:00 | 163 | SevenRings | 14.23 | 05:00
32 | Borhanuddin | 64 | 20:00 | 98 | Lalbag | 56 | 13:00 | 164 | ShahCement | 32 | 01:00
33 | Brahmanbaria | 86 | 19:30 | 99 | Lalmonirhat | 42 | 18:00 | 165 | Shahjadpur | 58 | 18:00
34 | Cantonment | 84 | 13:00 | 100 | MI_Cement | 17.5 | 23:00 | 166 | Shahjibazar | 80 | 18:00
35 | Chandina | 8 | 18:00 | 101 | Madanganj | 29 | 23:00 | 167 | Shahmirpur | 37 | 18:00
36 | Chandpur | 56 | 19:30 | 102 | Madaripur | 71 | 20:00 | 168 | Shariatpur | 54 | 19:30
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 56 | 14:00 | 169 | Sherpur | 108 | 19:00
38 | Chapai | 57 | 12:00 | 104 | Madunaghat | 37 | 13:00 | 170 | Shikalbaha | 24 | 21:00
39 | Charsaidpur | 41 | 16:00 | 105 | Magura | 47 | 18:00 | 171 | Shitalakhya | 61.4 | 12:00
40 | Chauddagram | 50 | 13:00 | 106 | Mahasthangarh | 46 | 18:00 | 172 | Sholosohor | 34 | 17:00
41 | Chhatak | 23 | 19:30 | 107 | Maijdee | 28 | 18:00 | 173 | Shyampur | 116 | 00:00
42 | Chowmuhani | 110 | 18:00 | 108 | Manikganj | 81 | 17:00 | 174 | Siddhirganj | 85 | 13:00
43 | Chuadanga | 73 | 18:00 | 109 | Maniknagar | 57 | 13:00 | 175 | Sirajganj | 82 | 19:00
44 | Coxsbazar | 101 | 19:00 | 110 | Matarbari | 37 | 18:00 | 176 | Sonargaon | 148 | 19:30
45 | Cumilla(N) | 84 | 12:00 | 111 | Matuail | 58 | 12:00 | 177 | Sreemongol | 56 | 18:00
46 | Cumilla(S) | 119 | 14:00 | 112 | Metrorail_Motijheel | 18 | 12:00 | 178 | Sreepur | 90 | 19:30
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 13 | 19:00 | 179 | Srinagar | 32.4 | 13:00
48 | Daudkandi | 112 | 18:00 | 114 | Millgate | 76 | 12:00 | 180 | Sunamganj | 37 | 19:00
49 | DhakaUniversity | 60 | 13:00 | 115 | Mirpur | 114 | 13:00 | 181 | Sylhet | 41 | 18:00
50 | Dhamrai | 114 | 18:00 | 116 | Mirsorai | 10 | 11:00 | 182 | Sylhet-132 | 71 | 18:00
51 | Dhanmondi | 80 | 13:00 | 117 | Mirzapur | 36 | 18:00 | 183 | TK | 22 | 19:00
52 | Dohazari | 69 | 18:00 | 118 | Mithapukur | 46 | 18:00 | 184 | Tangail | 120 | 18:00
53 | Faridpur | 114 | 18:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 09:00
54 | Fatullah | 97 | 12:00 | 120 | Mogbazar | 71.5 | 14:00 | 186 | Tasnim | 11 | 17:00
55 | Fenchuganj | 25 | 18:00 | 121 | Mongla | 34 | 18:00 | 187 | Thakurgaon | 80 | 18:30
56 | Feni | 67 | 18:00 | 122 | Motijheel | 29 | 13:00 | 188 | Tongi | 68 | 00:00
57 | GPH | 93 | 10:00 | 123 | Muktagacha | 28 | 13:00 | 189 | Ullahpara | 27 | 18:00
58 | Ghatail | 58 | 18:00 | 124 | Munshiganj | 72 | 21:00 | 190 | Ullon | 38 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 24 | 20:00 | 191 | Uttara | 68 | 13:00
60 | Ghorashal-230 | 82 | 12:00 | 126 | Mymensingh | 129 | 13:00 | 192 | UttaraNew | 42 | 13:00
61 | Goalpara | 33 | 13:00 | 127 | Naogaon | 88 | 13:00 | 193 | Zigatola | 52 | 13:00
62 | Gollamari | 62 | 13:00 | 128 | Narail | 40 | 18:00
63 | Gopalganj | 75 | 18:00 | 129 | Narinda | 56 | 13:00
64 | Gulshan | 78 | 13:00 | 130 | Narshingdi | 131 | 18:30
65 | Halishahar | 52.5 | 11:00 | 131 | Natore | 103 | 18:00
66 | HaripurSBU | 86 | 10:00 | 132 | Nawabganj | 34.8 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9026.27 | 0 |  | 9026.27
1:00 | 8438.82 | 0 |  | 8438.82
2:00 | 7948.12 | 0 |  | 7948.12
3:00 | 7679.28 | 0 |  | 7679.28
4:00 | 7459.12 | 0 |  | 7459.12
5:00 | 7349.11 | 0 |  | 7349.11
6:00 | 7582.05 | 0 |  | 7582.05
7:00 | 8147.87 | 0 |  | 8147.87
8:00 | 9162.24 | 0 |  | 9162.24
9:00 | 9560.89 | 0 |  | 9560.89
10:00 | 9384.48 | 0 |  | 9384.48
11:00 | 9535.03 | 0 |  | 9535.03
12:00 | 10100.52 | 0 |  | 10100.52
13:00 | 10470.54 | 0 |  | 10470.54
14:00 | 10069.7 | 0 |  | 10069.7
15:00 | 9647.77 | 0 |  | 9647.77
16:00 | 8757.47 | 0 |  | 8757.47
17:00 | 9783.12 | 0 |  | 9783.12
18:00 | 11203.72 | 0 |  | 11203.72
19:00 | 11038.11 | 0 |  | 11038.11
19:30 | 10935.06 | 0 |  | 10935.06
20:00 | 10679.6 | 0 |  | 10679.6
21:00 | 10515.44 | 0 |  | 10515.44
22:00 | 10078.26 | 0 |  | 10078.26
23:00 | 9543 | 0 |  | 9543
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4442 | 4584.27 | 9026.27 | DAILY GENERATION CURVE
00:30 | 4353.5 | 4379.045 | 8732.545
01:00 | 4265 | 4173.82 | 8438.82 | 22-12-2025
01:30 | 4149.5 | 4043.97 | 8193.47
02:00 | 4034 | 3914.12 | 7948.12
02:30 | 3950 | 3863.7 | 7813.7
03:00 | 3866 | 3813.28 | 7679.28
03:30 | 3830 | 3739.2 | 7569.2
04:00 | 3794 | 3665.12 | 7459.12
04:30 | 3741.5 | 3662.615 | 7404.115
05:00 | 3689 | 3660.11 | 7349.11
05:30 | 3754.25 | 3711.33 | 7465.58
06:00 | 3819.5 | 3762.55 | 7582.05
06:30 | 4019.07 | 3845.89 | 7864.96
07:00 | 4218.64 | 3929.23 | 8147.87
07:30 | 4477.685 | 4177.37 | 8655.055
08:00 | 4736.73 | 4425.51 | 9162.24
08:30 | 4834.72 | 4526.845 | 9361.565
09:00 | 4932.71 | 4628.18 | 9560.89
09:30 | 4908.22 | 4564.465 | 9472.685
10:00 | 4883.73 | 4500.75 | 9384.48
10:30 | 4842.255 | 4617.5 | 9459.755
11:00 | 4800.78 | 4734.25 | 9535.03
11:30 | 5026.625 | 4791.15 | 9817.775
12:00 | 5252.47 | 4848.05 | 10100.52
12:30 | 5359.395 | 4926.135 | 10285.53
13:00 | 5466.32 | 5004.22 | 10470.54
13:30 | 5340.57 | 4929.55 | 10270.12
14:00 | 5214.82 | 4854.88 | 10069.7
14:30 | 5107.7 | 4751.035 | 9858.735
15:00 | 5000.58 | 4647.19 | 9647.77
15:30 | 4597.53 | 4605.09 | 9202.62
16:00 | 4194.48 | 4562.99 | 8757.47
16:30 | 4509.535 | 4760.76 | 9270.295
17:00 | 4824.59 | 4958.53 | 9783.12
17:30 | 5143.045 | 5350.375 | 10493.42
18:00 | 5461.5 | 5742.22 | 11203.72
18:30 | 5372.75 | 5748.165 | 11120.915
19:00 | 5284 | 5754.11 | 11038.11
19:30 | 5209 | 5726.06 | 10935.06
20:00 | 5073.2 | 5606.4 | 10679.6
20:30 | 5021.85 | 5575.67 | 10597.52 |  | Executive Engineer
21:00 | 4970.5 | 5544.94 | 10515.44 |  | Network Operation Division
21:30 | 4931 | 5365.85 | 10296.85
22:00 | 4891.5 | 5186.76 | 10078.26
22:30 | 4860 | 4950.63 | 9810.63
23:00 | 4828.5 | 4714.5 | 9543

## En-Curve
QF-LDC-12
Date | 22-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2741 | 778 | 807 | 0 | 100 | 1014.27 | 40 | 3530 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2712 | 768.5 | 795 | 0 | 94 | 976.545 | 40 | 3338.5 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 22-12-2025
01:00 | 2683 | 759 | 783 | 0 | 88 | 938.82 | 40 | 3147 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2711.5 | 708 | 748.5 | 0 | 84 | 890.97 | 40 | 3010.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 226.9437 |  | MKWHr
02:00 | 2740 | 657 | 714 | 0 | 80 | 843.12 | 40 | 2874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2765 | 631 | 713.5 | 0 | 82 | 841.2 | 40 | 2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 226.9437 |  | MKWHr
03:00 | 2790 | 605 | 713 | 0 | 84 | 839.28 | 40 | 2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2786.5 | 611 | 664.5 | 0 | 80 | 838.7 | 40 | 2548.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2783 | 617 | 616 | 0 | 76 | 838.12 | 40 | 2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2765.5 | 596 | 616 | 0 | 78 | 840.115 | 40 | 2468.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2748 | 575 | 616 | 0 | 80 | 842.11 | 40 | 2448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2754.5 | 614.75 | 641 | 0 | 85 | 841.33 | 40 | 2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2761 | 654.5 | 666 | 0 | 90 | 840.55 | 40 | 2530 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2847 | 688.75 | 689.5 | 0 | 90 | 839.87 | 40 | 2658 | 3.84 | 0 | 8 | 0 | 0 | 0 | 0
07:00 | 2933 | 723 | 713 | 0 | 90 | 839.19 | 40 | 2786 | 7.68 | 0 | 16 | 0 | 0 | 0 | 0
07:30 | 3011 | 761.5 | 760 | 0 | 91 | 889.54 | 40 | 3035.5 | 40.015 | 0 | 26.5 | 0 | 0 | 0 | 0
08:00 | 3089 | 800 | 807 | 0 | 92 | 939.89 | 40 | 3285 | 72.35 | 0 | 37 | 0 | 0 | 0 | 0
08:30 | 3098 | 793 | 854.5 | 0 | 95 | 931.255 | 40 | 3367.5 | 127.81 | 3.5 | 51 | 0 | 0 | 0 | 0
09:00 | 3107 | 786 | 902 | 0 | 98 | 922.62 | 40 | 3450 | 183.27 | 7 | 65 | 0 | 0 | 0 | 0
09:30 | 2976.5 | 799 | 902 | 0 | 102 | 881.33 | 40 | 3414.5 | 248.855 | 16 | 92.5 | 0 | 0 | 0 | 0
10:00 | 2846 | 812 | 902 | 0 | 106 | 840.04 | 40 | 3379 | 314.44 | 25 | 120 | 0 | 0 | 0 | 0
10:30 | 2793 | 796 | 901.5 | 0 | 104 | 842.26 | 40 | 3391.5 | 412.995 | 28 | 150.5 | 0 | 0 | 0 | 0
11:00 | 2740 | 780 | 901 | 0 | 102 | 844.48 | 40 | 3404 | 511.55 | 31 | 181 | 0 | 0 | 0 | 0
11:30 | 2870.5 | 798 | 901.5 | 0 | 109 | 841.73 | 40 | 3488 | 544.045 | 36.5 | 188.5 | 0 | 0 | 0 | 0
12:00 | 3001 | 816 | 902 | 0 | 116 | 838.98 | 40 | 3572 | 576.54 | 42 | 196 | 0 | 0 | 0 | 0
12:30 | 3064.5 | 830.5 | 902 | 0 | 114 | 882.545 | 40 | 3634 | 553.985 | 50.5 | 213.5 | 0 | 0 | 0 | 0
13:00 | 3128 | 845 | 902 | 0 | 112 | 926.11 | 40 | 3696 | 531.43 | 59 | 231 | 0 | 0 | 0 | 0
13:30 | 3034.5 | 829.5 | 902 | 0 | 115 | 889.07 | 40 | 3674.5 | 489.55 | 58 | 238 | 0 | 0 | 0 | 0
14:00 | 2941 | 814 | 902 | 0 | 118 | 852.03 | 40 | 3653 | 447.67 | 57 | 245 | 0 | 0 | 0 | 0
14:30 | 2883 | 764.7 | 902 | 0 | 115 | 888.205 | 40 | 3596.5 | 374.83 | 49.5 | 245 | 0 | 0 | 0 | 0
15:00 | 2825 | 715.4 | 902 | 0 | 112 | 924.38 | 40 | 3540 | 301.99 | 42 | 245 | 0 | 0 | 0 | 0
15:30 | 2786.5 | 699.7 | 902.5 | 0 | 113 | 930.655 | 40 | 3233 | 210.265 | 42 | 245 | 0 | 0 | 0 | 0
16:00 | 2748 | 684 | 903 | 0 | 114 | 936.93 | 40 | 2926 | 118.54 | 42 | 245 | 0 | 0 | 0 | 0
16:30 | 2637 | 711 | 901.5 | 0 | 112 | 1034.245 | 40 | 3151.5 | 65.55 | 42 | 575.5 | 0 | 0 | 0 | 0
17:00 | 2526 | 738 | 900 | 0 | 110 | 1131.56 | 40 | 3377 | 12.56 | 42 | 906 | 0 | 0 | 0 | 0
17:30 | 2759.5 | 775.5 | 901 | 0 | 110 | 1279.89 | 40 | 3506.5 | 6.28 | 42 | 1072.75 | 0 | 0 | 0 | 0
18:00 | 2993 | 813 | 902 | 0 | 110 | 1428.22 | 40 | 3636 | 0 | 42 | 1239.5 | 0 | 0 | 0 | 0
18:30 | 2999.5 | 835.5 | 902 | 0 | 110 | 1429.165 | 40 | 3638 | 0 | 21 | 1145.75 | 0 | 0 | 0 | 0
19:00 | 3006 | 858 | 902 | 0 | 110 | 1430.11 | 40 | 3640 | 0 | 0 | 1052 | 0 | 0 | 0 | 0
19:30 | 3062 | 852 | 902 | 0 | 112 | 1420.06 | 40 | 3757 | 0 | 0 | 790 | 0 | 0 | 0 | 0
20:00 | 3069 | 857 | 901 | 0 | 106 | 1421.4 | 40 | 3836 | 0 | 0 | 449.2 | 0 | 0 | 0 | 0
20:30 | 3076 | 857.25 | 901.5 | 0 | 103 | 1431.17 | 40 | 3877.5 | 0 | 0 | 311.1 | 0 | 0 | 0 | 0
21:00 | 3083 | 857.5 | 902 | 0 | 100 | 1440.94 | 40 | 3919 | 0 | 0 | 173 | 0 | 0 | 0 | 0
21:30 | 3006.5 | 846 | 902 | 0 | 102 | 1374.35 | 40 | 3877.5 | 0 | 0 | 148.5 | 0 | 0 | 0 | 0
22:00 | 2930 | 834.5 | 902 | 0 | 104 | 1307.76 | 40 | 3836 | 0 | 0 | 124 | 0 | 0 | 0 | 0
22:30 | 2909.5 | 819.5 | 902 | 0 | 102 | 1213.13 | 40 | 3712 | 0 | 0 | 112.5 | 0 | 0 | 0 | 0
23:00 | 2889 | 804.5 | 902 | 0 | 100 | 1118.5 | 40 | 3588 | 0 | 0 | 101 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 409 | 06:00 | 389 | 12:00 | Meghnaghat | 410 | 06:00 | 390 | 12:00
Ashuganj | 416 | 5:00 | 394 | 11:00 | Payra | 417 | 04:00 | 409 | 14:00
Bhulta | 411 | 06:00 | 389 | 15:00 | Rahanpur | 416 | 03:00 | 398 | 18:00
Bibiana | 402 | 04:00 | 390 | 14:00 | Rampal | 411 | 06:00 | 395 | 18:00
BIPTC | 407 | 03:00 | 387 | 10:00
Bogura | 413 | 04:00 | 389 | 18:30
Gopalganj | 412 | 05:00 | 367 | 18:00
Kaliakoir | 402 | 05:00 | 383 | 12:00
Korerhat | 411 | 04:00 | 394 | 13:00
Madunaghat | 408 | 04:00 | 395 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 04:00 | 225 | 12:00 | Kachua | 239 | 03:00 | 231 | 12:00
AKSML | 236 | 03:00 | 227 | 13:00 | Kaliakoir | 241 | 04:00 | 226 | 12:00
Aminbazar | 241 | 05:00 | 226 | 12:00 | Keranigonj | 239 | 04:00 | 224 | 12:00
Ashuganj | 236 | 07:00 | 226 | 15:00 | Khulna(S) | 238 | 06:00 | 227 | 18:00
Ashuganj-400 | 236 | 07:00 | 226 | 15:00 | Korerhat | 239 | 03:00 | 228 | 13:00
Baghabari | 240 | 01:00 | 229 | 18:00 | Madunaghat | 235 | 04:00 | 227 | 12:00
Barapukuria | 228 | 05:00 | 213 | 18:00 | Madunaghat-400 | 236 | 04:00 | 220 | 13:00
Barapukuria-230 | 228 | 05:00 | 213 | 18:00 | Maniknagar | 238 | 03:00 | 226 | 12:00
Barishal | 244 | 04:00 | 236 | 20:00 | Meghnaghat | 245 | 04:00 | 233 | 15:00
Bheramara | 238 | 06:00 | 221 | 18:00 | Meghnaghat-400 | 241 | 06:00 | 228 | 12:00
Bhulta | 241 | 06:00 | 227 | 12:00 | Mirsorai | 239 | 03:00 | 228 | 13:00
Bibiana | 240 | 04:00 | 229 | 14:00 | Rajshahi | 238 | 05:00 | 222 | 18:00
BIPTC | 240 | 06:00 | 221 | 18:00 | Rampal | 236 | 06:00 | 226 | 18:00
Bogura | 241 | 04:00 | 227 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 241 | 04:00 | 228 | 18:00 | Rampura | 241 | 05:00 | 226 | 12:00
Borhanuddin | 246 | 03:00 | 240 | 19:30 | Shikalbaha | 232 | 01:00 | 224 | 15:00
BSRM | 238 | 04:00 | 228 | 13:00 | Shyampur | 239 | 05:00 | 225 | 12:00
Cumilla(N) | 236 | 07:00 | 227 | 12:00 | Siddhirganj | 240 | 05:00 | 228 | 11:00
Faridpur | 244 | 03:00 | 235 | 13:00 | Sirajgonj | 244 | 02:00 | 236 | 18:00
Fenchuganj | 239 | 03:00 | 233 | 08:00 | Sreepur | 236 | 06:00 | 225 | 18:00
Feni | 239 | 06:00 | 228 | 13:00 | Tongi | 236 | 04:00 | 225 | 11:00
Ghorashal | 240 | 23:00 | 230 | 12:00
Ghorashal-230 | 234 | 06:00 | 214 | 18:00
Gopalganj | 244 | 05:00 | 235 | 13:00
GPH | 237 | 06:00 | 227 | 12:00
Haripur | 240 | 06:00 | 227 | 12:00
Hasnabad | 237 | 02:00 | 225 | 12:00
Hathazari | 234 | 05:00 | 225 | 11:00
Ishurdi | 242 | 06:00 | 224 | 18:00
Jhenaidah | 238 | 06:00 | 222 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 127 | 16:00 | Lakshmipur | 135 | 06:00 | 128 | 13:00 | 135 | 18:30 | 126 | 09:00
Agargaon | 138 | 04:00 | 129 | 12:00 | Lalbag | 133 | 07:00 | 126 | 12:00 | 138 | 05:00 | 127 | 12:00
Agrabad | 137 | 06:00 | 130 | 13:00 | Lalmonirhat | 150 | 18:00 | 120 | 18:00
AKS | 134 | 03:00 | 129 | 12:00 | Madanganj | 136 | 00:00 | 133 | 07:00
Aminbazar | 138 | 05:00 | 130 | 12:00 | Madaripur | 140 | 05:00 | 135 | 13:00
Amnura | 138 | 01:00 | 129 | 18:00 | Madartek | 137 | 06:00 | 127 | 12:00
Ashuganj | 140 | 01:00 | 136 | 12:00 | Madunaghat | 138 | 04:00 | 132 | 12:00
Bagerhat | 132 | 04:00 | 122 | 18:00 | Magura | 136 | 02:00 | 125 | 13:00
Bajitpur | 136 | 05:00 | 128 | 12:00 | Mahasthangarh | 137 | 06:00 | 127 | 18:00
Bakerganj | 137 | 07:00 | 133 | 18:00 | Maijdee | 134 | 03:00 | 128 | 12:00
Bakulia | 136 | 03:00 | 131 | 14:00 | Manikganj | 133 | 03:00 | 122 | 12:00
Banani | 137 | 04:00 | 127 | 15:00 | Maniknagar | 139 | 05:00 | 129 | 12:00
Bangabhaban | 139 | 06:00 | 129 | 12:00 | Matarbari | 130 | 16:00 | 118 | 18:00
Barapukuria | 137 | 04:00 | 127 | 18:00 | Matuail | 140 | 03:00 | 132.6 | 12:00
Barguna | 137 | 03:00 | 133 | 18:00 | Metrorail_Motijheel | 139 | 05:00 | 129 | 12:00
Barishal | 140 | 04:00 | 135 | 18:00 | Metrorail_Uttara | 135 | 18:30 | 126 | 08:00
Barishal-230 | 141 | 04:00 | 136 | 12:00 | Millgate | 134 | 02:00 | 123 | 12:00
Baroaulia | 138 | 06:00 | 130 | 13:00 | Mirpur | 138 | 05:00 | 128 | 12:00
Baroirhat | 134 | 07:00 | 130 | 12:00 | Mirzapur | 138 | 05:00 | 129 | 21:00
Bashundhara | 137 | 05:00 | 124 | 12:00 | Mithapukur | 135 | 04:00 | 125 | 20:00
BashundharaCement | 136 | 00:00 | 133 | 07:00 | MI_Cement | 139 | 06:00 | 128 | 12:00
Beanibazar | 135 | 04:00 | 131 | 12:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 133 | 04:00 | 120 | 12:00 | Mogbazar | 139 | 03:00 | 129 | 12:00
Bhaluka | 135 | 03:00 | 127 | 12:00 | Mongla | 132 | 06:00 | 122 | 18:00
Bhandaria | 138 | 03:00 | 134 | 18:00 | Motijheel | 139 | 06:00 | 129 | 12:00
Bhangura | 139 | 04:00 | 132 | 18:00 | Muktagacha | 135 | 10:00 | 125 | 20:00
Bheramara | 142 | 06:00 | 133 | 18:00 | Munshiganj | 139 | 04:00 | 131 | 12:00
Bheramara(GK) | 141 | 03:00 | 134 | 18:00 | Muradnagar | 139 | 04:00 | 131 | 12:00
Bhulta | 134 | 07:00 | 125 | 12:00 | Mymensingh | 136 | 10:00 | 123 | 18:00
Bog-Sherpur | 138 | 04:00 | 129 | 18:00 | Naogaon | 134 | 04:00 | 126 | 18:00
Bogura | 137 | 05:00 | 130 | 20:00 | Narail | 137 | 04:00 | 125 | 13:00
Bogura-230 | 138 | 04:00 | 129 | 18:00 | Narinda | 139 | 05:00 | 129 | 12:00
Brahmanbaria | 135 | 04:00 | 129 | 12:00 | Narshingdi | 139 | 06:00 | 126 | 11:00
Cantonment | 137 | 02:00 | 128 | 12:00 | Natore | 138 | 05:00 | 129 | 18:00
Chandina | 140 | 04:00 | 133 | 12:00 | Nawabganj | 137 | 05:00 | 127 | 12:00
Chandpur | 139 | 18:00 | 133 | 12:00 | Netrakona | 131 | 01:00 | 120 | 12:00
Chandraghona | 138 | 04:00 | 133 | 12:00 | New | 134 | 05:00 | 124 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 138 | 02:00 | 132 | 18:00 | Niamatpur | 139 | 05:00 | 132 | 18:00
Charsaidpur | 140 | 03:00 | 132 | 12:00 | Noapara | 135 | 05:00 | 120 | 13:00
Chauddagram | 138 | 03:00 | 131 | 12:00 | Pabna | 141 | 06:00 | 131 | 18:00
Chhatak | 135 | 05:00 | 130 | 18:00 | Palashbari | 133 | 06:00 | 123 | 18:00
Chowmuhani | 133 | 02:00 | 127 | 16:00 | Panchagarh | 141 | 05:00 | 124 | 20:00
Chuadanga | 137 | 04:00 | 125 | 13:00 | Patiya | 136 | 02:00 | 130 | 13:00
Coxsbazar | 126 | 02:00 | 119 | 20:00 | Patuakhali | 134 | 03:00 | 132 | 00:00
Cumilla(N) | 139 | 06:00 | 132 | 12:00 | Payra | 137 | 02:00 | 134 | 14:00
Cumilla(S) | 140 | 03:00 | 123 | 12:00 | PHP | 136 | 04:00 | 129 | 13:00
Daganbhuiyan | 136 | 04:00 | 130 | 12:00 | Postogola | 139 | 02:00 | 130 | 12:00
Daudkandi | 138 | 05:00 | 129 | 12:00 | Purbachal | 137 | 06:00 | 128 | 12:00
DhakaUniversity | 136 | 04:00 | 127 | 12:00 | Purbasadipur | 134 | 05:00 | 122 | 13:00
Dhamrai | 139 | 06:00 | 133 | 12:00 | Rahanpur | 140 | 05:00 | 133 | 18:00
Dhanmondi | 142 | 06:00 | 134 | 12:00 | Rahanpur-400 | 140 | 02:00 | 134 | 18:00
Dohazari | 134 | 04:00 | 127 | 21:00 | Rahim | 140 | 04:00 | 132 | 12:00
Faridpur | 140 | 03:00 | 134 | 18:00 | Rajbari | 140 | 04:00 | 133 | 13:00
Fatullah | 139 | 05:00 | 128 | 12:00 | Rajendrapur | 137 | 04:00 | 128 | 15:00
Fenchuganj | 139 | 04:00 | 134 | 12:00 | Rajshahi | 137 | 03:00 | 129 | 18:00
Feni | 135 | 05:00 | 130 | 11:00 | Rajshahi-230 | 137 | 05:00 | 128 | 18:00
Feni-230 | 136 | 02:00 | 130 | 13:00 | Ramganj | 135 | 03:00 | 130 | 12:00
Ghatail | 134 | 10:00 | 124 | 18:00 | Rampur | 137 | 04:00 | 130 | 12:00
Ghorashal | 136 | 04:00 | 130 | 12:00 | Rampura | 136 | 04:00 | 127 | 12:00
Goalpara | 133 | 04:00 | 125 | 13:00 | Rangamati | 137 | 03:00 | 131 | 13:00
Gollamari | 134 | 05:00 | 128 | 13:00 | Rangpur | 135 | 05:00 | 120 | 12:00
Gopalganj | 138 | 05:00 | 131 | 13:00 | Ruppur | 141 | 03:00 | 133 | 18:00
Gopalganj-400 | 141 | 04:00 | 135 | 18:00 | Saidpur | 134 | 04:00 | 122 | 20:00
Gulshan | 136 | 05:00 | 127 | 12:00 | Satkhira | 133 | 05:00 | 123 | 18:00
Halishahar | 137 | 02:00 | 130 | 12:00 | Satmasjid | 138 | 04:00 | 128 | 13:00
Haripur | 141 | 06:00 | 133 | 12:00 | Savar | 137 | 18:30 | 127 | 12:00
HaripurSBU | 140 | 06:00 | 132 | 12:00 | SevenRings | 136 | 03:00 | 130 | 12:00
Hasnabad | 136 | 03:00 | 129 | 12:00 | ShahCement | 140 | 04:00 | 132 | 12:00
Hathazari | 136 | 05:00 | 133 | 11:00 | Shahjadpur | 142 | 03:00 | 136 | 18:00
Hatirjheel | 137 | 05:00 | 128 | 12:00 | Shahjibazar | 136 | 06:00 | 130 | 12:00
Ishurdi | 143 | 06:00 | 134 | 18:00 | Shahmirpur | 137 | 04:00 | 131 | 12:00
Jaldhaka | 133 | 05:00 | 122 | 08:00 | Shariatpur | 140 | 03:00 | 134 | 13:00
Jamalpur | 136 | 10:00 | 121 | 21:00 | Sherpur | 134 | 10:00 | 118 | 00:00
Jashore | 135 | 05:00 | 120 | 13:00 | Shikalbaha | 126 | 01:00 | 121 | 12:00
Jhenaidah | 137 | 05:00 | 120 | 18:00 | Shikalbaha-230 | 138 | 04:00 | 132 | 15:00
Jhenaidah-230 | 138 | 03:00 | 127 | 18:00 | Shitalakhya | 139 | 06:00 | 128 | 12:00
Joydebpur | 137 | 05:00 | 127 | 12:00 | Sholosohor | 137 | 02:00 | 132 | 12:00
Joypurhat | 133 | 01:00 | 124 | 18:00 | Shyampur | 138 | 06:00 | 130 | 13:00
Juldah | 137 | 02:00 | 131 | 13:00 | Shyampur-230 | 139 | 06:00 | 129 | 13:00
Kabirpur | 137 | 18:30 | 121 | 12:00 | Siddhirganj | 140 | 03:00 | 133 | 12:00
Kachua | 140 | 03:00 | 134 | 15:00 | Sirajganj | 138 | 03:00 | 128 | 18:00
Kaliakoir | 142 | 04:00 | 134 | 12:00 | Sonargaon | 136 | 23:00 | 131 | 12:00
Kallyanpur | 137 | 04:00 | 129 | 12:00 | Sreemongol | 136 | 04:00 | 130 | 13:00
Kalurghat | 137 | 04:00 | 132 | 12:00 | Sreepur | 138 | 06:00 | 130 | 12:00
Kamrangirchar | 136 | 04:00 | 126 | 12:00 | Srinagar | 137 | 06:00 | 127 | 12:00
Kaptai | 136 | 03:00 | 130 | 12:00 | SSM | 138 | 00:00 | 137 | 22:00
Kasba | 139 | 06:00 | 130 | 13:00 | Sunamganj | 134 | 04:00 | 128 | 13:00
Kazla | 138 | 04:00 | 129 | 12:00 | Sylhet | 135 | 02:00 | 131 | 12:00
Keranigonj | 137 | 05:00 | 126 | 12:00 | Sylhet-132 | 135 | 01:00 | 132 | 12:00
Khagrachori | 137 | 03:00 | 131 | 13:00 | Tangail | 134 | 05:00 | 125 | 21:00
Khulna | 133 | 04:00 | 125 | 13:00 | Taraganj | 133 | 04:00 | 123 | 20:00
Khulna(S) | 134 | 04:00 | 127 | 18:00 | Tasnim | 140 | 06:00 | 131 | 12:00
Khulshi | 135 | 04:00 | 128 | 13:00 | Thakurgaon | 139 | 05:00 | 121 | 20:00
Kishoreganj | 135 | 05:00 | 126 | 12:00 | TK | 137 | 04:00 | 132 | 13:00
Kodda | 137 | 04:00 | 129 | 08:00 | Tongi | 136 | 04:00 | 129 | 11:00
KSRM | 137 | 07:00 | 131 | 12:00 | Ullahpara | 139 | 05:00 | 130 | 18:00
Kulaura | 138 | 03:00 | 134 | 12:00 | Ullon | 136 | 04:00 | 127 | 12:00
Kurigram | 133 | 02:00 | 121 | 20:00 | Uttara | 138 | 04:00 | 124 | 13:00
Kushtia | 138 | 03:00 | 126 | 18:00 | Uttara New | 135 | 18:30 | 126 | 9:00
Laksam | 139 | 02:00 | 134 | 12:00 | Zigatola | 138 | 5:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division