## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: November 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-11-02 |  | 2025-10-01 |  | 2024-11-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13748.2 | 2025-11-04 | 15644.99 | 2025-10-27 | 13253 | 2024-11-04 | 16794 | 2025-07-23
|  |  | 19:00 Hr. |  | 19:00 Hr. |  | 19:30 |  | 21:00 Hr.
2 | Minimum Generation (MW) | 7121.94 | 2025-11-29 | 9833.03 | 2025-10-03 | 6915 | 2024-11-23 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13748.2 | 2025-11-04 | 15644.99 | 2025-10-27 | 13253 | 2024-11-04 | 16794 | 2025-07-23
|  |  | 19:00 Hr. |  | 19:00 Hr. |  | 19:30 |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 12272.32 | 2025-11-06 | 13866.67 | 2025-10-26 | 11963 | 2024-11-05 | 14965.88 | 2025-09-30
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 13820.31 | 2025-11-04 | 15801.33 | 2025-10-22 | 13253 | 2024-11-03 | 17200 | 2024-04-29
|  |  | 19:00 Hr. |  | 19:00 Hr. |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11918.526 |  | 14385.22 |  | 11495.5667 |  | - | -
7 | Average Generation (MW) at Day Peak | 10521.848 |  | 12788.9568 |  | 10157.8333 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 977 | 2025-11-06 | 978 | 2025-10-23 | 955 | 2024-11-15 | 979 | 2025-09-09
|  |  | 13:30 |  | 2:30 |  | 13:00 |  | 5:00
9 | Maximum Power Import from Tripura, India (MW) | 124 | 2025-11-30 | 90 | 2025-10-24 | 92 | 2024-10-19 | 194 | 12/06/19
|  |  | 12:00 |  | 1:00 |  | 13:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 456 | 2025-11-06 | 570 | 2025-10-19 | 343 | 2024-11-03 | 4395 | 04/10/2022
|  |  | 19:30 |  | 19:30 |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13324.87 | 2025-11-06 | 14354.83 | 2025-10-19 | 13041 | 45599 | 14965 | 2024-05-16
|  |  | 19:30 |  | 19:30 |  | 0.79167 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-11-02 | 0 | 2025-10-01 | 0 | 45597 | - | -
|  |  | 18:00 |  | 21:00 |  | 19:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13365.5 | 2025-11-02 | 14115.2 | 2025-10-01 | 12302 | 2024-11-01 | - | -
|  |  | 18:00 |  | 21:00 |  | 19:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 34 | 2025-11-01 | 381 | 2025-10-21 | 647 | 45599 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 11598.36 | 2025-11-01 | 13404.96 | 2025-10-21 | 11422 | 45599 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-11-02 | 0 | 2025-10-01 | 0 | 45597 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 12204.77 | 2025-11-02 | 11978.24 | 2025-10-01 | 11199 | 45597 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 10 |  | 23 |  | 5 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 3 |  | 14 |  | 4 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 832.7518 |  | 1137.6177 |  | 1293.3147 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 19.0745 |  | 26.7752 |  | 41.8445 |  | - | -
22 | Net Generation of BPDB (MKWH) | 813.6773 |  | 1110.8425 |  | 1251.4702 |  | - | -
23 | Net Generation of IPP (MKWH) | 1689.1048 |  | 2815.9484 |  | 2454.9734 |  | - | -
23b | Net Generation by Generation Companies | 3435.8483 |  | 3978.1653 |  | 2098.615
24 | Net Generation of REB (MKWH) | 47.2089 |  | 46.923 |  | 89.5936 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 84.163 |  | 113.3794 |  | 78.2023 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 6070.0024 |  | 8065.2585 |  | 5972.8546 |  | - | -
27 | Energy Generation by Gas (MKWH) | 3146.3842 |  | 3762.6905 |  | 3635.3513 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 0.79368 |  | 0.006 |  | 15.5319 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 433.2598 |  | 1037.4024 |  | 693.3667 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 68.3025 |  | 161.6253 |  | 83.5571 |  | - | -
31 | Energy Generation by Solar (MKWH) | 121.7275 |  | 120.6303 |  | 108.5987 |  | - | -
31b | Energy Generation by Wind (MKWH) | 4.536 |  | 2.9122 |  | 2.9731 |  | - | -
32 | Energy Generation by Coal (MKWH) | 2314.0732 |  | 3006.767 |  | 1475.3202 |  | - | -
33 | Enegry Import from India (MKWH) | 1370.0138 |  | 1576.7518 |  | 1144.5135 |  | - | -
34 | Monthly Load Factor (%) | 75.3542 |  | 83.0661 |  | 75.0272 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: November 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13748.2 | 2025-11-04 | 19:00 Hr.
Generation Period
| Dhaka | MW | 5080.35
| Chattogram | MW | 1442.8
| Cumilla | MW | 1328.16
| Mymensingh | MW | 973
| Sylhet | MW | 618
a) | Total supply in East zone | MW | 9442.31
| Khulna | MW | 1457
| Barisal | MW | 395
| Rajshahi | MW | 1123.6
| Rangpur | MW | 747
b) | Total supply in West zone | MW | 3722.6
c) | Total supply in both zone ( a+b) | MW | 13164.91
Ref: | 27.21.0000.603.16.087.20.949 | Date: 15/12/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: November 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 643 | 2025-11-10 | 10:00
|  | MW | 252
| b) Ghorashal end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 0 | - | -
|  | MW | 0
| b) Ghorashal end | AMPS | 293 | 2025-11-07 | 0:00
|  | MW | 102
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 5816 | 2025-11-08 | N/A
| b) Ghorashal end | MWh | 0 | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0 | -
| b) Ghorashal end | MWh | 2522.64 | 2025-11-07 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 101026.038
| b) Ghorashal end | MWh | 0
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 97995.25
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1940 | 2025-11-05 | 10:00
|  | MW | 780
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Serajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur | AMPS | 1934 | 2025-10-27 | 10:00
|  | MW | 744
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Serajganj end | MWh | 8038 | 2025-11-09 | 15:00
| b) Sreepur | MWh | 0
27 | Daily Maximum Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | - | - | -
28 | Total Energy Export through EWI/ NO-2
| a)Serajganj end | MWh | 408042 | - | -
| b) Sreepur | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | 395108.3 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 3.17 | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 3052 | 2025-11-10 | 21:00
|  | MW | 2042
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 3045 | 2025-11-10 | 21:00
|  | MW | 2041
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 43240 | 2025-11-21 | N/A
| b) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| b) Aminbazar end | MWh | 41425 | 2025-11-21
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1164235
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1183299.16
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | -1.637
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: November 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Ghatail 132/33kV | T-1 | 2025-11-01 10:05 | 2025-11-01 10:28 | 0.015972 | T | Due to 33 kV Dhanbari Feeder (MPBS-1) CT ) Brust. REC 650, ABB | 18 | 6.9 | Power interruption
Ghatail 132/33kV | T-2 | 2025-11-01 10:05 | 2025-11-01 10:29 | 0.016667 | T | Due to 33 kV Dhanbari Feeder (MPBS-1) CT ) Brust. REC 650, ABB | 0 | 0 | No interruption
Jamalpur 132/33kV | T-3 | 2025-11-25 12:40 | 2025-11-26 12:44 | 1899-12-31 00:04 | T | OTI trip Micom | 0 | 0 | No interruption
Mirpur 132/33kV | T3 | 2025-11-17 10:40 | 2025-11-17 13:58 | 0.1375 | T | Main-1 Diff Relay Operated Siemens SIPROTEC | 56 | 184.8 | Power interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2025-11-03 06:30 | 2025-11-03 07:02 | 0.022222 | T | PBS 33 Kv Three Feeder(Baowkomerjani,Square,Vadgram) Trip at a time O/C | 12 | 6.4 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-11-21 10:39 | 2025-11-21 10:46 | 0.0048611 | T | df/dt FBCPU | 23 | 2.6833 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-11-21 10:39 | 2025-11-21 10:46 | 0.0048611 | T | df/dt FBCPU | 38 | 4.4333 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-11-02 22:48 | 2025-11-03 01:37 | 0.11736 | E/O | T-2, 33 kv BUS DS Redhot maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 1 | 2025-11-22 08:59 | 2025-11-22 14:37 | 0.23472 | E/O | maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2025-11-15 09:10 | 2025-11-15 12:22 | 0.13333 | E/O | Emergency maint.work | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2025-11-01 12:32 | 2025-11-01 14:00 | 0.061111 | E/O | maintenance work on 33kv bus loop at kachuadanga feeder. | 10 | 14.6667 | Power interruption
Tangail 132/33kV | Tr-2 | 2025-11-06 08:42 | 2025-11-06 10:22 | 0.069444 | E/O | 33kv Kachuadanga feeder Maintenance. | 50 | 83.3333 | Power interruption
|  |  | Total : | 1899-12-31 19:42 |  | Unserved Energy: |  | 303.2167
Dhaka (South) Grid Circle :
Haripur 230/132kV | Auto TR-1 | 2025-11-21 10:38 | 2025-11-21 12:20 | 0.070833 | T | Earthquake. N/A | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhult | 2025-11-21 10:38 | 2025-11-21 11:41 | 0.04375 | T | Earthquake. N/A | 0 | 0 | No interruption
Haripur 230/132kV | Bus-2 | 2025-11-21 10:38 | 2025-11-21 12:22 | 0.072222 | T | Earthquake MVAJ: 86B11,86B12,86B13, 86B14,86B15, 86B16, 86B17, 86B18, 86B19, 86B20. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-11-02 06:44 | 2025-11-02 08:06 | 0.056944 | T | 33kV Nawabganj-1 feeder trip Differential over current | 25 | 34.1667 | Power interruption
Keranigonj 230/132/33kV | ATR-3 | 2025-11-20 11:10 | 2025-11-20 13:38 | 0.10278 | T | prv-01/02 trip trip relay operated | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 | 2025-11-21 07:57 | 2025-11-21 07:57 | 0 | T | Unknown ABB-REF615,Micom-P632 | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2025-11-13 21:18 | 2025-11-13 21:33 | 0.010417 | T | For 33 kv pbs sholla feeder fault. Over current protection P142, lockout Relay -1 &2. | 14.7 | 3.675 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-11-13 21:18 | 2025-11-13 21:36 | 0.0125 | T | For 33 kv pbs sholla feeder fault. Over current protection p142, lockout relay1 &2. | 14.7 | 4.41 | Power interruption
Nawabganj 132/33kV | TR-1 | 2025-11-20 06:12 | 2025-11-20 06:25 | 0.0090278 | T | 33 kv PBS sholla feeder doesn't trip. Overcurrent Protection p142, Lockout relay-1, Lockout relay -2 | 9.8 | 2.1233 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-11-20 06:12 | 2025-11-20 06:33 | 0.014583 | T | 33 kv PBS sholla feeder doesn't trip. Overcurrent Protection p142, Lockout relay-1, Lockout relay -2 | 9.8 | 3.43 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-11-22 17:15 | 2025-11-22 17:28 | 0.0090278 | T | 33kV Nawabganj feeder fault Overcurrent protection relay & Earth fault. | 0 | 0 | No interruption
Shyampur 230/132kV | Bus-2 (132kV) | 2025-11-10 10:00 | 2025-11-10 15:12 | 0.21667 | T | GIS SF6 Circuit Breaker Chamber Explosion of 132KV fatullah-1(E06). F21 & Busbar Relay. | 0 | 0 | No interruption
Shyampur 230/132kV | Auto TR-1 | 2025-11-10 10:00 | 2025-11-10 15:12 | 0.21667 | T | GIS SF6 Circuit Breaker Chamber Explosion of 132KV fatullah-1(E06) Busbar protection | 0 | 0 | No interruption
Shyampur 230/132kV | Auto TR-2 | 2025-11-10 10:00 | 2025-11-10 19:37 | 0.40069 | T | GIS SF6 Circuit Breaker Chamber Explosion of 132KV fatullah-1(E06) Busbar Protection. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-11-13 13:55 | 2025-11-13 14:10 | 0.010417 | T | Due to salam steel cable fault DIR O/C & E/F RELAY | 42 | 10.5 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2025-11-30 16:07 | 2025-11-30 16:59 | 0.036111 | T | lockout SPS | 62 | 53.7333 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-11-30 16:07 | 2025-11-30 17:00 | 0.036806 | T | None Lockout SPS | 52 | 45.9333 | Power interruption
Shyampur 230/132kV | Bus-1 (132kV) | 2025-11-10 10:01 | 2025-11-10 10:01 | 0 | E/O | Shyampur-1 CB gas quality poor and 132kV BFP operated. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2025-11-13 06:29 | 2025-11-13 12:57 | 0.26944 | E/O | 33 kv trip on Earth fault NB: Load share by T-1 & T-3 Transformer | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 14:08 |  | Unserved Energy: |  | 157.9717
Chattogram Grid Circle :
Coxsbazar 132/33kV | 405T-T1 | 2025-11-05 12:23 | 2025-11-05 12:54 | 0.021528 | T | Kolatoli-1 triped due to eagle fall in line 1. OC/EF 2.Lockout | 38 | 19.6333 | Power interruption
Coxsbazar 132/33kV | 405T-T1 | 2025-11-16 11:20 | 2025-11-16 11:43 | 0.015972 | T | Due to 33kv kolatoli-1, kolatoli-2 Tripped. Over current | 26 | 9.9667 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-11-20 01:46 | 2025-11-20 02:06 | 0.013889 | T | Due to Keranihat 33 kv feeder O/C & E/F. Earth fault Pro trip,Lockout Relay K861,K862 Trip. | 48 | 16 | Power interruption
Halishahar 132/33kV | 405T(TR-1) | 2025-11-18 16:57 | 2025-11-18 23:15 | 0.2625 | T | 33 Kv XLPE(R-phase) Cable punctured. F-51 | 0 | 0 | Power interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-11-06 08:32 | 2025-11-06 14:19 | 0.24097 | T | 33 KV BUS flashing REF615, RET 650, RET 670 | 0 | 0 | Power interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-11-06 08:36 | 2025-11-06 09:00 | 0.016667 | T | 33KV Bus flashing REF 615, RET650, RET670 | 18 | 7.2 | Power interruption
Bakulia 132/33kV | Bus-A | 2025-11-08 16:19 | 2025-11-08 17:07 | 0.033333 | E/O | Emergency maint.work | 0 | 0 | No interruption
GPH 230/33kV | Transformer-01(D05) | 2025-11-05 09:55 | 2025-11-05 17:07 | 0.3 | E/O | bushing check of 11kv . | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-02 | 2025-11-05 14:21 | 2025-11-07 09:31 | 1899-12-31 19:10 | E/O | oil leakage | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 | 2025-11-27 10:40 | 2025-11-27 12:50 | 0.090278 | E/O | 33 kV B Ph CT nut-bolt tight | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-11-09 08:15 | 2025-11-09 10:31 | 0.094444 | E/O | For 33 KV Incoming CT Oil Leakage Check | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-03 | 2025-11-09 10:33 | 2025-11-09 16:45 | 0.25833 | E/O | for 33 KV Incoming CT Oil Leakage Check | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 03:31 |  | Unserved Energy: |  | 52.8
Cumilla Grid Circle :
Chandina 132/33kV | TR-3 | 2025-11-07 12:15 | 2025-11-08 17:25 | 1899-12-31 05:10 | T | From SAS: 1)Protection Trip to LVS K86L1 2)Protection Trip to LVS K86L2 3)Lockout Relay trip From CRP: T86 operate Mechanical Trip 1)Lockout Relay -1 2)Lockout Relay -2 3)Bay Control Unit-1 | 5 | 13.75 | Power interruption
Chandina 132/33kV | TR-2 | 2025-11-19 09:32 | 2025-11-19 09:32 | 0 | T | Diff Trip, REF K86 L-1&2, F87T2 Transformer Main-2 Relay. | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2025-11-29 15:16 | 2025-12-02 11:57 | 1900-01-01 20:41 | T | 33 KV CB Phase B Blasted TR Backup relay | 7 | 15.6333 | Power interruption 15:16 to 17:30
Chhatak 132/33kV | T-1 | 2025-11-06 10:35 | 2025-11-06 10:41 | 0.0041667 | T | feeder Fault MCGG | 5 | 0.5 | Power interruption
Chhatak 132/33kV | T-3 | 2025-11-06 10:35 | 2025-11-06 10:39 | 0.0027778 | T | Feeder Fault MCGG | 11 | 0.73333 | Power interruption
Chowmuhani 132/33kV | T-2 | 2025-11-30 11:29 | 2025-11-30 12:10 | 0.028472 | T | 33kv Lakshmipur-01 fault . Directional E/F | 28 | 19.1333 | Power interruption
Chowmuhani 132/33kV | TR3-435T | 2025-11-30 11:29 | 2025-11-30 11:42 | 0.0090278 | T | 33kv Lakshmipur PBS-01 O/C, E/F | 28 | 6.0667 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2025-11-04 23:30 | 2025-11-04 23:55 | 0.017361 | T | 33 KV Kotbari feeder fault RET 670 REF615 | 16 | 6.6667 | Power interruption
Kulaura 132/33kV | TR-2 | 2025-11-03 13:53 | 2025-11-03 14:08 | 0.010417 | T | Winding Temperature increase 1. Differential Protection Relay 2. Logout Relay -1 3. Logout Relay -2 | 3 | 0.75 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-11-01 15:50 | 2025-11-01 16:12 | 0.015278 | T | Earth fault in Bisic Feeder and Line to Line fault in Jamuna Feeder Lockout relay, 132 kv OC/EF Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-11-01 15:50 | 2025-11-01 16:12 | 0.015278 | T | Earth fault in Bisic Feeder and Line to Line fault in Jamuna Feeder Lockout Relay, OC/EF Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-11-17 00:45 | 2025-11-17 00:57 | 0.0083333 | T | Shaistaganj Feeder Phase to Ground Fault and Chunarughat Feeder Under Frequency Fault. Over Current and Earth Fault. | 18 | 3.6 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-11-18 10:59 | 2025-11-18 11:08 | 0.00625 | T | PBS's Shayestaganj 33 kv feeder Trip 33 kv OC/EF | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-11-17 10:38 | 2025-11-17 17:08 | 0.27083 | E/O | To check LT side conductor | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 403T | 2025-11-10 12:10 | 2025-11-10 13:28 | 0.054167 | E/O | 33 KV Circuit Breaker Maintenance by BPDB | 0 | 0 | No interruption
Chandpur 132/33kV | 200KVA Aux. T-1 | 2025-11-15 07:00 | 2025-11-16 08:30 | 1899-12-31 01:30 | E/O | Auxiliary Power alternate from ST-1 to ST-2 | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR3-435T | 2025-11-30 14:38 | 2025-11-30 16:16 | 0.068056 | E/O | 33kV LPBS-1 feeder bus loop maintenance. | 35 | 57.1667 | Power interruption
Feni 230/132kV | ATR-3 | 2025-11-21 11:46 | 2025-11-21 14:18 | 0.10556 | E/O | due to oil leakage of neutral bushing at 230 kv side | 0 | 0 | No interruption
Feni 230/132kV | ATR-2 | 2025-11-21 13:03 | 2025-11-21 14:21 | 0.054167 | E/O | due to oil leakage | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-11-01 11:39 | 2025-11-01 14:29 | 0.11806 | E/O | Red Hot remove. | 10 | 28.3333 | Power interruption
Lakshmipur 132/33kV | Transformer-1 | 2025-11-05 16:27 | 2025-11-05 16:52 | 0.017361 | E/O | Metering Test. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR1 | 2025-11-12 10:02 | 2025-11-12 16:50 | 0.28333 | E/O | 132 kv GCB Replace. | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-11-08 14:24 | 2025-11-08 17:45 | 0.13958 | E/O | Sylhet-Chhatak Ckt-II CB pole( Y phase) Replacement. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 08:50 |  | Unserved Energy: |  | 152.3333
Khulna Grid Circle :
Barishal 230/132kV | T-5 | 2025-11-15 19:47 | 2025-11-16 00:37 | 0.20139 | T | Over current, differtial trip Over current , differtial relay | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2025-11-21 16:43 | 2025-11-21 17:08 | 0.017361 | T | Trip due to 33kv Babugang, Banaripara, Rahmatpur fedders trip. Over current | 20 | 8.3333 | Power interruption
Barishal 230/132kV | T-5 | 2025-11-21 16:43 | 2025-11-21 17:08 | 0.017361 | T | Trip due to 33kv Babugang, Banaripara, Rahmatpur fedders trip. Over current | 20 | 8.3333 | Power interruption
Khulna (C) | Tr-2 415 T | 2025-11-09 02:35 | 2025-11-09 03:12 | 0.025694 | T | 33 KV khulna Sadar PBS feeder fault. OC IDMT | 9 | 5.55 | Power interruption
Khulna (C) | TR-1 425T | 2025-11-09 02:35 | 2025-11-09 03:01 | 0.018056 | T | 33 kV khulna Sadar PBS feeder fault No | 18 | 7.8 | Power interruption
Khulna (C) | Tr-2 415 T | 2025-11-18 07:05 | 2025-11-18 13:33 | 0.26944 | T | Unidentify No relay | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-11-26 00:02 | 2025-11-28 11:13 | 1900-01-01 11:11 | T | Incoming cable fault differential | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2025-11-26 00:02 | 2025-11-26 01:50 | 0.075 | T | Tr 1 incoming cable fault no relay | 8 | 14.4 | Power interruption
Barishal 230/132kV | ATR-2 | 2025-11-07 16:32 | 2025-11-07 20:53 | 0.18125 | E/O | OLTC PRD trip | 0 | 0 | No interruption
Borhanuddin 230/33kV | Tr-Load | 2025-11-07 15:52 | 2025-11-07 18:10 | 0.095833 | E/O | 33 kv Bass bar riser red hot for maintenance & replacement . | 62 | 142.6 | Power interruption
Gopalganj 132/33kV | T2 | 2025-11-04 07:23 | 2025-11-04 13:45 | 0.26528 | E/O | 33 kv section bus D.S. maintenance | 20 | 127.3333 | Power interruption
Gopalganj 132/33kV | T1 | 2025-11-05 15:23 | 2025-11-05 17:28 | 0.086806 | E/O | 33kv Incomer-1 Trip by Under frequency -1 & 2, trip ckt unhealthy | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-01 | 2025-11-05 16:02 | 2025-11-05 16:39 | 0.025694 | E/O | Emergency maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-02 | 2025-11-05 16:41 | 2025-11-05 16:56 | 0.010417 | E/O | Emergency maint.work | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-11-11 16:25 | 2025-11-11 17:29 | 0.044444 | E/O | 33KV Joragate-2 ,Red Hot Maintenance. | 0 | 0 | No interruption
Patuakhali 132/33kV | 415T (T-2) | 2025-11-12 12:03 | 2025-11-12 13:07 | 0.044444 | E/O | Oil leakage | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2025-11-28 08:31 | 2025-11-28 11:06 | 0.10764 | E/O | 33 kv CT leakage maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 22:51 |  | Unserved Energy: |  | 314.35
HVDC Grid Circle :
Baghabari 230/132kV | T-2 Bank | 2025-11-08 06:02 | 2025-11-08 13:50 | 0.325 | T | Buchhulz relay trip Buchhulz relay | 0 | 0 | No interruption
Bheramara 230/132kV | Transformer-2 | 2025-11-27 04:59 | 2025-11-27 04:59 | 0 | T | R phase Connecting insulation kit Fire differential | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-3 | 2025-11-08 08:56 | 2025-11-08 09:19 | 0.015972 | T | 33kV feeder fault Instantaneous over current | 9 | 3.45 | Power interruption
Shahjadpur 132/33kV | T-2(415T) | 2025-11-03 15:08 | 2025-11-03 22:50 | 0.32083 | T | 96B1 | 0 | 0 | No interruption
Baghabari 230/132kV | T-2 Bank | 2025-11-26 17:38 | 2025-11-26 19:39 | 0.084028 | E/O | T2 X-Former CVT R-Phase এর Top Cover এ Red Hot দেখা দিলে Emergency S/D নেওয়া হয়। | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2025-11-01 19:20 | 2025-11-01 19:57 | 0.025694 | E/O | Red hot 33 kv side | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-11-02 11:04 | 2025-11-02 15:01 | 0.16458 | E/O | Transformer Oli leakage Maintenance work. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2025-11-27 14:10 | 2025-11-27 15:33 | 0.057639 | E/O | Emergency maint.work | 28 | 38.7333 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2025-11-06 10:01 | 2025-11-06 11:32 | 0.063194 | E/O | OLTC oil refilling. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 01:22 |  | Unserved Energy: |  | 42.1833
Bogura Grid Circle:
Amnura 132/33kV | T-3 (426T) | 2025-11-01 04:37 | 2025-11-01 05:06 | 0.020139 | T | 33kV Amnura feeder faults Gen. Trip | 0 | 0 | No interruption
Amnura 132/33kV | T-1 (406T) | 2025-11-25 22:12 | 2025-11-26 13:56 | 0.65556 | T | Siemens 7UT61 | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2025-11-30 08:29 | 2025-11-30 09:08 | 0.027083 | T | Feeder CB fault P142 | 15 | 9.75 | Power interruption
Chapai 132/33kV | T-3 (425T) | 2025-11-30 08:29 | 2025-11-30 09:09 | 0.027778 | T | P142 | 15 | 10 | Power interruption
Jaldhaka 132/33kV | 406T-1 | 2025-11-01 09:29 | 2025-11-01 09:47 | 0.0125 | T | Due to RPBS Khaprikhal 33 kv feeder triped. U/F realy | 19 | 5.7 | Power interruption
Jaldhaka 132/33kV | 416T-2 | 2025-11-01 09:29 | 2025-11-01 09:47 | 0.0125 | T | Due to RPBS Khaprikhal 33 kv feeder triped E/F realy | 19 | 5.7 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-11-10 03:35 | 2025-11-10 14:26 | 0.45208 | T | N/A | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-11-21 19:46 | 2025-11-21 19:54 | 0.0055556 | T | টি-১ ৩৩কেভি বাসে সংযুক্ত Chapai ৩৩ কেভি পবিস ফিডারে O/C ,E/F ( নিয়ামতপুর গ্রিড হতে ৪০ কিমি দুরে ইনশুলেটর ক্র্যাক করে ) এর কারণে গ্রিড এর 33kV T-1 transformer ট্রিপ করে। Simens 7SJ62 | 12 | 1.6 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-11-22 12:50 | 2025-11-22 13:05 | 0.010417 | T | টি-১ ৩৩কেভি বাসে সংযুক্ত Chapai ৩৩ কেভি পবিস ফিডারে O/C ,E/F এর কারণে গ্রিড এর 33kV T-1 transformer ট্রিপ করে। Simens 7SJ62 | 12 | 3 | Power interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2025-11-30 06:38 | 2025-11-30 07:04 | 0.018056 | T | Birds Siprotech,siemens | 40 | 17.3333 | Power interruption
Amnura 132/33kV | T-1 (406T) | 2025-11-06 11:43 | 2025-11-06 12:09 | 0.018056 | E/O | Load Shift for Bus-2 | 0 | 0 | No interruption
Amnura 132/33kV | T-3 (426T) | 2025-11-06 11:44 | 2025-11-06 11:56 | 0.0083333 | E/O | Load Shift for Bus-2 | 0 | 0 | No interruption
Amnura 132/33kV | T-2 (416T) | 2025-11-06 11:44 | 2025-11-06 12:10 | 0.018056 | E/O | Load Shift for Bus-2 | 6 | 2.6 | Power interruption
Amnura 132/33kV | T-1 (406T) | 2025-11-07 14:10 | 2025-11-07 14:40 | 0.020833 | E/O | 132kV Bus-2 হইতে Bus-1এ স্থানান্তর | 5 | 2.5 | Power interruption
Amnura 132/33kV | T-2 (416T) | 2025-11-07 14:10 | 2025-11-07 14:42 | 0.022222 | E/O | 132kV Bus-2 হইতে Bus-1এ স্থানান্তর. | 5 | 2.6667 | Power interruption
Amnura 132/33kV | T-3 (426T) | 2025-11-07 14:12 | 2025-11-07 15:42 | 0.0625 | E/O | 132kV Bus-2 হইতে Bus-1এ স্থানান্তর. | 3 | 4.5 | Power interruption
Amnura 132/33kV | T-1 (406T) | 2025-11-26 10:14 | 2025-11-26 13:59 | 0.15625 | E/O | Winding Temperature High Trip | 0 | 0 | No interruption
Jaldhaka 132/33kV | 416T-2 | 2025-11-19 11:48 | 2025-11-19 14:25 | 0.10903 | E/O | LA Change Phase -R | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2025-11-22 09:53 | 2025-11-22 17:11 | 0.30417 | E/O | Due to 33kV bus maintenance by Nilphamari PBS | 0 | 0 | No interruption
Natore 132/33kV | TR-4 (435 T) | 2025-11-05 19:14 | 2025-11-05 20:01 | 0.032639 | E/O | Red Hot Maintenance Work | 27 | 21.15 | Power interruption
|  |  | Total : | 1899-12-31 23:51 |  | Unserved Energy: |  | 86.5
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-18 22:15 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: November 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Kallyanpur-02 | 2025-11-01 17:32 | 2025-11-01 18:33 | 0.042361 | T | Earth Fault | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2025-11-26 08:40 | 2025-11-26 10:36 | 0.080556 | T | General Trip Distance Trip O/L Relay SOTF | 73 | 141.1333 | Power interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-02 | 2025-11-26 08:40 | 2025-11-26 09:10 | 0.020833 | T | General Trip Distance Trip SOFT | 73 | 36.5 | Power interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2025-11-01 17:31 | 2025-11-01 18:36 | 0.045139 | T | Tripped | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2025-11-25 11:01 | 2025-11-25 12:04 | 0.04375 | E/O | For Rite of way | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2025-11-11 12:09 | 2025-11-11 14:31 | 0.098611 | E/O | Emergency maint.work | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2025-11-25 13:07 | 2025-11-25 13:57 | 0.034722 | E/O | Kailakur ss annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | Kadda-1 | 2025-11-22 18:34 | 2025-11-22 19:29 | 0.038194 | E/O | Poly removing of Kabirpur-kadda ckt-1(Tower no 26) | 0 | 0 | No interruption
|  |  | Total : | 0.40417 |  | Unserved Energy: |  | 177.6333
Dhaka (South) Grid Circle :
Bhulta 400/230kV | Ghorashal-01 | 2025-11-21 10:38 | 2025-11-27 18:32 | 1900-01-05 07:54 | T | None | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2025-11-21 10:38 | 2025-11-27 18:33 | 1900-01-05 07:55 | T | None | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Shyampur-1 | 2025-11-09 11:55 | 2025-11-09 12:09 | 0.0097222 | T | 0 | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-11-05 09:40 | 2025-11-05 10:25 | 0.03125 | T | Unknown | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Siddhirganj-1 | 2025-11-16 20:02 | 2025-11-17 11:30 | 0.64444 | T | LA Burst | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2025-11-01 17:25 | 2025-11-01 17:42 | 0.011806 | T | 50/67N EF , Zone-01,distance 11.6km, R phase IL1=5.46 | 11 | 3.1167 | Power interruption
|  |  | Total : | 1900-01-12 08:33 |  | Unserved Energy: |  | 3.1167
Chattogram Grid Circle :
Baroirhat 132/33kV | Hat-2 | 2025-11-04 10:20 | 2025-11-04 11:25 | 0.045139 | E/O | Emergency maint.work | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2025-11-20 14:48 | 2025-11-20 16:37 | 0.075694 | E/O | Emergency Condition related to Near BMA | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -02 | 2025-11-20 14:49 | 2025-11-20 16:38 | 0.075694 | E/O | Emergency Condition related to near BMA | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2025-11-20 14:47 | 2025-11-20 16:39 | 0.077778 | E/O | Emergency Works | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-2 | 2025-11-20 14:47 | 2025-11-20 16:40 | 0.078472 | E/O | Emergency works | 0 | 0 | No interruption
Hathazari 230/132/33kV | Raojan-01 | 2025-11-19 11:07 | 2025-11-19 15:05 | 0.16528 | E/O | Hathazari-Rawzan 230 kV circuir-01, R-phase has a shorted wire on the conductor, requiring an emergency shutdown to remove it. Load sharing with Rawzan Circuit-02 | 0 | 0 | No interruption
|  |  | Total : | 0.51806 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-11-29 09:30 | 2025-11-29 12:26 | 0.12222 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-11-29 09:30 | 2025-11-29 12:26 | 0.12222 | T | Tripped | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-11-17 16:22 | 2025-11-17 16:29 | 0.0048611 | E/O | Ashuganj end CB problem. | 0 | 0 | No interruption
|  |  | Total : | 0.24931 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna (C) | 132kV Central-Goalpara-1 | 2025-11-14 18:18 | 2025-11-15 17:35 | 0.97014 | T | Not identify | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-11-04 16:14 | 2025-11-04 16:41 | 0.01875 | E/O | Charger load shift | 22 | 9.9 | Power interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2025-11-14 20:39 | 2025-11-15 17:40 | 0.87569 | E/O | Shutdoun for maintenence works. order by Aldc khulna. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2025-11-22 09:27 | 2025-11-22 10:44 | 0.053472 | E/O | SPMD work at Amtoli end. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 22:02 |  | Unserved Energy: |  | 9.9
HVDC Grid Circle :
BIPTC | 10CF13 | 2025-11-01 11:44 | 2025-11-01 12:37 | 0.036806 | T | Tripped | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-11-05 13:04 | 2025-11-05 14:01 | 0.039583 | T | Tripped by bird flashover | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-11-05 13:04 | 2025-11-05 14:01 | 0.039583 | T | Tripped by bird flashover | 0 | 0 | No interruption
BIPTC | 10CF26 | 2025-11-07 10:28 | 2025-11-07 15:32 | 0.21111 | T | Two dead birds were notice. | 0 | 0 | No interruption
BIPTC | 10CF16 | 2025-11-15 07:22 | 2025-11-15 13:39 | 0.26181 | T | No birds or such abnormalities were noticed. | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-11-05 09:40 | 2025-11-05 10:53 | 0.050694 | T | distance protection operated | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-11-15 12:14 | 2025-11-15 12:46 | 0.022222 | T | Ghorasal end CB Tripped Ishwardi end CB Close | 0 | 0 | No interruption
Bhangura 132/33kV | Bhangura-Bhagabari ckt-1 | 2025-11-02 11:21 | 2025-11-02 17:15 | 0.24583 | E/O | Optical Fiber Installation from Baghabari to Sathia Grid Substation | 15 | 88.5 | Power interruption
BIPTC | 10CF16 | 2025-11-15 10:25 | 2025-11-15 13:39 | 0.13472 | E/O | C1 unbalance 60/61 Instant L1 | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2025-11-27 14:42 | 2025-11-27 15:35 | 0.036806 | E/O | SF6 pressure Low. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-11-02 10:04 | 2025-11-02 16:01 | 0.24792 | E/O | Emergency maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -1 | 2025-11-03 08:28 | 2025-11-03 16:27 | 0.33264 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 15:50 |  | Unserved Energy: |  | 88.5
Bogura Grid Circle:Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-17 02:32 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | 132 kv Bus 02 | 2025-11-06 09:59 | 2025-11-06 12:53 | 2:54 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-11-12 06:28 | 2025-11-12 08:43 | 2:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 132 kv Bus 02 | 2025-11-12 06:57 | 2025-11-12 13:48 | 6:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-11-26 08:30 | 2025-11-26 16:55 | 8:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-11-27 09:23 | 2025-11-27 18:20 | 8:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-11-29 09:08 | 2025-11-29 17:03 | 7:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-1 | 2025-11-18 10:16 | 2025-11-18 13:55 | 3:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-2 | 2025-11-19 09:50 | 2025-11-19 13:20 | 3:30 | S/O | None | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-1 | 2025-11-19 13:35 | 2025-11-19 14:37 | 1:02 | S/O | Annual maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2025-11-30 10:30 | 2025-11-30 13:50 | 3:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2025-11-12 07:50 | 2025-11-12 14:18 | 6:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2025-11-15 08:47 | 2025-11-15 20:53 | 12:06 | S/O | Annual maintenance work | 14 | 169.4 | Power interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2025-11-15 09:15 | 2025-11-15 17:20 | 8:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2025-11-16 07:17 | 2025-11-16 10:05 | 2:48 | S/O | Annual maintenance | 10 | 28 | Power interruption
Dhamrai 132/33kV | Transformer-2 | 2025-11-03 08:36 | 2025-11-03 11:23 | 2:47 | S/O | PBS work | 60 | 167 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2025-11-24 08:52 | 2025-11-24 09:03 | 0:11 | S/O | Kaliakoir end work | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2025-11-24 08:52 | 2025-11-24 09:03 | 0:11 | S/O | Kaliakoir end work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-4 | 2025-11-02 10:18 | 2025-11-02 17:10 | 6:52 | S/O | Annual maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-4 | 2025-11-03 09:42 | 2025-11-03 17:00 | 7:18 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-4 | 2025-11-04 09:32 | 2025-11-04 16:42 | 7:10 | S/O | Annual maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-4 | 2025-11-05 09:15 | 2025-11-05 11:36 | 2:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV | T-3 | 2025-11-08 09:35 | 2025-11-08 16:50 | 7:15 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-3 | 2025-11-09 09:35 | 2025-11-09 15:58 | 6:23 | S/O | Annual maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2025-11-16 09:10 | 2025-11-16 17:15 | 8:05 | S/O | Annual maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2025-11-17 09:32 | 2025-11-17 16:45 | 7:13 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2025-11-18 09:45 | 2025-11-18 15:50 | 6:05 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-1 | 2025-11-19 11:10 | 2025-11-19 11:10 | 0:00 | S/O | Prject Work | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-3 | 2025-11-15 08:53 | 2025-11-15 16:09 | 7:16 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-3 | 2025-11-16 09:08 | 2025-11-16 16:06 | 6:58 | S/O | Annual maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-4 | 2025-11-17 09:02 | 2025-11-17 16:01 | 6:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-2 | 2025-11-19 09:07 | 2025-11-19 16:17 | 7:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-2 | 2025-11-20 09:04 | 2025-11-20 12:40 | 3:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-4 | 2025-11-20 12:54 | 2025-11-20 14:04 | 1:10 | S/O | None | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-2 | 2025-11-23 07:13 | 2025-11-23 15:35 | 8:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-11-01 11:09 | 2025-11-01 17:31 | 6:22 | S/O | After HDD boring work,Cable connect& remove | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-11-05 16:02 | 2025-11-05 17:50 | 1:48 | S/O | 33 kv Nabinagar feeder bus DS redhot maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-11-12 07:16 | 2025-11-12 12:34 | 5:18 | S/O | TR-2 33 KV bus DS Maintenance work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-11-02 09:08 | 2025-11-02 19:20 | 10:12 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-11-03 08:23 | 2025-11-03 13:03 | 4:40 | S/O | annual maintenance work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 230kV Bus 1 | 2025-11-08 08:52 | 2025-11-08 14:50 | 5:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-11-13 17:26 | 2025-11-13 21:45 | 4:19 | S/O | project work shutdown | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-11-15 10:14 | 2025-11-15 14:53 | 4:39 | S/O | project Works Shutdown | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-11-15 15:27 | 2025-11-15 23:17 | 7:50 | S/O | Project works. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-11-16 11:25 | 2025-11-16 18:52 | 7:27 | S/O | Project Work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2025-11-24 08:54 | 2025-11-24 08:54 | 0:00 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2025-11-24 09:11 | 2025-11-24 14:12 | 5:01 | S/O | Corrective Maintenance Work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 230kV Bus 2 | 2025-11-26 11:50 | 2025-11-26 12:30 | 0:40 | S/O | To open 230/132kV HT side DS which is connected with 230kV Bus 2. DS is mechanically locked | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR2 | 2025-11-29 16:01 | 2025-11-29 17:02 | 1:01 | S/O | Protection works. | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-2 (132kV) | 2025-11-16 08:53 | 2025-11-16 18:20 | 9:27 | S/O | annul maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-2 (132kV) | 2025-11-17 08:56 | 2025-11-17 18:12 | 9:16 | S/O | Annaul Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | Main bus | 2025-11-26 09:08 | 2025-11-26 16:33 | 7:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bus-A | 2025-11-03 10:43 | 2025-11-03 16:28 | 5:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-11-03 14:39 | 2025-11-03 15:18 | 0:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2025-11-03 15:23 | 2025-11-03 16:07 | 0:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Tr-1 (406T) | 2025-11-16 06:45 | 2025-11-16 08:28 | 1:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Tr-1 (406T) | 2025-11-22 09:30 | 2025-11-22 15:18 | 5:48 | S/O | Maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Tr-1 (406T) | 2025-11-23 09:59 | 2025-11-23 14:27 | 4:28 | S/O | AM | 0 | 0 | No interruption
Kodda 132/33kV | Tr-2 (416T) | 2025-11-25 09:51 | 2025-11-25 15:58 | 6:07 | S/O | A/M | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-11-26 09:35 | 2025-11-26 14:40 | 5:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-11-27 09:47 | 2025-11-27 15:21 | 5:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Tr-2 (416T) | 2025-11-29 09:34 | 2025-11-29 09:34 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-11-22 07:59 | 2025-11-22 17:13 | 9:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-11-23 08:22 | 2025-11-23 15:40 | 7:18 | S/O | Annual Maintanence | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-11-24 08:05 | 2025-11-24 17:45 | 9:40 | S/O | Annual maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-11-25 08:30 | 2025-11-25 16:12 | 7:42 | S/O | Annual maintenance work | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-11-26 08:05 | 2025-11-26 16:40 | 8:35 | S/O | Annual maintenance work | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-11-29 08:25 | 2025-11-29 17:04 | 8:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2025-11-30 07:51 | 2025-11-30 17:17 | 9:26 | S/O | Annual Maintenacce | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2025-11-23 09:20 | 2025-11-23 16:22 | 7:02 | S/O | Annual Maintenance on Bay equipment of Uttara sector-18 ckt | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-11-24 09:21 | 2025-11-24 16:41 | 7:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-11-29 08:40 | 2025-11-29 17:06 | 8:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2025-11-26 10:43 | 2025-11-26 11:48 | 1:05 | S/O | Semeins Work | 15 | 16.25 | Power interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2025-11-26 12:03 | 2025-11-26 12:20 | 0:17 | S/O | project work | 10 | 2.8333 | Power interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2025-11-01 12:28 | 2025-11-01 12:30 | 0:02 | S/O | protection test. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2025-11-14 08:43 | 2025-11-14 08:43 | 0:00 | S/O | G2G project work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus A | 2025-11-15 08:02 | 2025-11-15 14:21 | 6:19 | S/O | G2G project work | 0 | 0 | No interruption
Netrakona 132/33kV | Transformer-1 (415T) | 2025-11-11 09:32 | 2025-11-11 17:16 | 7:44 | S/O | Annual Maintanance | 0 | 0 | No interruption
New Tongi | T1(403T) | 2025-11-10 09:45 | 2025-11-10 15:47 | 6:02 | S/O | Annual Maintenance. | 0 | 0 | No interruption
New Tongi | Tr-1 (4061 | 2025-11-11 09:36 | 2025-11-11 16:47 | 7:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
New Tongi | Tr-1 (4061 | 2025-11-12 10:14 | 2025-11-12 15:17 | 5:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
New Tongi | Tr-1 (4061 | 2025-11-13 11:15 | 2025-11-13 13:15 | 2:00 | S/O | Annual Maintanance. | 0 | 0 | No interruption
New Tongi | Tr-2(4161 | 2025-11-16 11:10 | 2025-11-16 16:04 | 4:54 | S/O | Annual Maintanance. | 0 | 0 | No interruption
New Tongi | T2(413T) | 2025-11-18 09:40 | 2025-11-18 17:03 | 7:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
New Tongi | Bus-1 | 2025-11-23 10:57 | 2025-11-23 19:33 | 8:36 | S/O | Annual Maintanance. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-1 | 2025-11-10 09:18 | 2025-11-10 18:14 | 8:56 | S/O | Annual Maintenance 2025 | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-11-12 09:02 | 2025-11-12 16:52 | 7:50 | S/O | Yearly Maintenence Work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-3 | 2025-11-17 09:07 | 2025-11-17 16:58 | 7:51 | S/O | Annual Maintenance 2025 | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-11-08 07:25 | 2025-11-08 17:06 | 9:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-11-08 07:50 | 2025-11-08 17:00 | 9:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-A | 2025-11-08 07:50 | 2025-11-08 17:10 | 9:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-11-09 07:22 | 2025-11-09 17:05 | 9:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2025-11-09 07:25 | 2025-11-09 16:45 | 9:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2025-11-09 07:33 | 2025-11-09 17:01 | 9:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2025-11-10 07:23 | 2025-11-10 15:07 | 7:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-11-10 07:27 | 2025-11-10 15:02 | 7:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-11-11 07:07 | 2025-11-11 16:20 | 9:13 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2025-11-11 07:25 | 2025-11-11 16:18 | 8:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-A | 2025-11-11 07:35 | 2025-11-11 16:28 | 8:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2025-11-12 07:12 | 2025-11-13 15:45 | 32:33 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2025-11-12 07:15 | 2025-11-12 20:32 | 13:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2025-11-12 07:16 | 2025-11-12 20:35 | 13:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-11-13 07:25 | 2025-11-13 15:53 | 8:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2025-11-13 07:27 | 2025-11-13 15:55 | 8:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-11-15 07:16 | 2025-11-15 16:40 | 9:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-11-15 07:28 | 2025-11-15 16:35 | 9:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-A | 2025-11-15 07:40 | 2025-11-15 16:25 | 8:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2025-11-16 07:35 | 2025-11-16 14:01 | 6:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-11-16 07:35 | 2025-11-16 14:09 | 6:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-11-17 07:43 | 2025-11-17 15:22 | 7:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2025-11-17 07:55 | 2025-11-17 15:05 | 7:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-11-17 08:46 | 2025-11-17 15:10 | 6:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-11-22 10:47 | 2025-11-22 16:19 | 5:32 | S/O | Control cable change | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-11-23 08:38 | 2025-11-23 17:15 | 8:37 | S/O | Control cable change | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-11-24 08:52 | 2025-11-24 17:25 | 8:33 | S/O | T-3 Transformer waring change work. | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2025-11-29 08:24 | 2025-11-29 14:30 | 6:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-11-29 08:25 | 2025-11-29 14:34 | 6:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Bus-A | 2025-11-29 08:46 | 2025-11-29 14:55 | 6:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2025-11-30 09:22 | 2025-11-30 16:18 | 6:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2025-11-30 09:28 | 2025-11-30 16:22 | 6:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Bus A | 2025-11-03 09:15 | 2025-11-06 15:20 | 78:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-11-05 09:26 | 2025-11-05 12:39 | 3:13 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-11-05 13:15 | 2025-11-05 14:49 | 1:34 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2025-11-05 15:07 | 2025-11-05 16:36 | 1:29 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2025-11-06 09:32 | 2025-11-06 15:10 | 5:38 | S/O | Annual maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-11-11 09:25 | 2025-11-11 16:20 | 6:55 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-11-12 09:12 | 2025-11-12 17:12 | 8:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-11-13 08:10 | 2025-11-13 17:09 | 8:59 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-11-17 08:13 | 2025-11-17 16:12 | 7:59 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-11-18 08:14 | 2025-11-18 16:47 | 8:33 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-11-19 08:34 | 2025-11-19 16:43 | 8:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-11-20 08:19 | 2025-11-20 16:38 | 8:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2025-11-25 08:20 | 2025-11-25 16:36 | 8:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2025-11-26 08:13 | 2025-11-26 16:49 | 8:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2025-11-27 08:18 | 2025-11-27 16:33 | 8:15 | S/O | Annual maintenance. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-1 | 2025-11-05 08:45 | 2025-11-05 17:02 | 8:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Tr-1 | 2025-11-06 10:32 | 2025-11-06 15:01 | 4:29 | S/O | Annaual Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2025-11-12 08:34 | 2025-11-12 16:21 | 7:47 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2025-11-13 08:55 | 2025-11-13 12:58 | 4:03 | S/O | Annaual Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 | 2025-11-15 08:44 | 2025-11-15 15:52 | 7:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 | 2025-11-16 08:27 | 2025-11-16 16:10 | 7:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Tr-3 | 2025-11-17 09:06 | 2025-11-17 17:05 | 7:59 | S/O | Annaual Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-3 | 2025-11-18 08:52 | 2025-11-18 15:54 | 7:02 | S/O | annual Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bus-1 | 2025-11-04 17:10 | 2025-11-04 17:20 | 0:10 | S/O | Maintenance work for Bus DS-671M | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bus-2 | 2025-11-10 13:38 | 2025-11-10 16:52 | 3:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bus-2 | 2025-11-12 10:10 | 2025-11-12 16:42 | 6:32 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bus-2 | 2025-11-13 10:10 | 2025-11-13 15:36 | 5:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2025-11-21 08:25 | 2025-11-21 11:44 | 3:19 | S/O | Oil refill Work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-02 | 2025-11-21 14:46 | 2025-11-21 22:25 | 7:39 | S/O | Due to idmt trip | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2025-11-28 08:24 | 2025-11-28 11:55 | 3:31 | S/O | Oil refill | 0 | 0 | No interruption
|  |  | Total : | 1900-02-10 13:17 |  | Unserved Energy: |  | 383.4833
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT2 | 2025-11-01 08:23 | 2025-11-01 10:22 | 1:59 | S/O | GT-2 HT & LT bushing maintenance | 90 | 178.5 | Power interruption
Bhulta 132/33kV | GT1 | 2025-11-22 08:36 | 2025-11-22 16:34 | 7:58 | S/O | Annual Maintanance | 50 | 398.3333 | Power interruption
Bhulta 132/33kV | GT2 | 2025-11-25 09:17 | 2025-11-25 17:25 | 8:08 | S/O | Annual Maintenance | 75 | 610 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-11-27 10:05 | 2025-11-27 19:25 | 9:20 | S/O | Annual maintenace | 45 | 420 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-11-29 08:42 | 2025-11-29 17:40 | 8:58 | S/O | A/M | 45 | 403.5 | Power interruption
Haripur 230/132kV | Auto TR-1 | 2025-11-11 08:12 | 2025-11-11 19:37 | 11:25 | S/O | Annual Maintenance,2025-26 | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsing | 2025-11-17 08:35 | 2025-11-17 17:35 | 9:00 | S/O | OFCN Work | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhult | 2025-11-17 09:59 | 2025-11-17 18:33 | 8:34 | S/O | other end | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsing | 2025-11-18 08:39 | 2025-11-18 17:29 | 8:50 | S/O | From Other End | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhult | 2025-11-18 09:50 | 2025-11-18 16:24 | 6:34 | S/O | From Other End | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsing | 2025-11-19 08:42 | 2025-11-19 19:11 | 10:29 | S/O | From other end. | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhult | 2025-11-20 08:56 | 2025-11-21 19:13 | 34:17 | S/O | For Other Side. | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhult | 2025-11-22 10:10 | 2025-11-22 18:22 | 8:12 | S/O | From Other End. | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhult | 2025-11-23 08:23 | 2025-11-23 21:30 | 13:07 | S/O | CT changing work. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2025-11-23 11:02 | 2025-11-23 15:44 | 4:42 | S/O | For Relay test | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-2 | 2025-11-24 09:40 | 2025-11-24 15:57 | 6:17 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-2 | 2025-11-25 09:07 | 2025-11-25 16:42 | 7:35 | S/O | Annual Maintenance 2025-26. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-2 | 2025-11-26 10:15 | 2025-11-26 17:01 | 6:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | Bus-1 | 2025-11-30 08:45 | 2025-11-30 17:14 | 8:29 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2025-11-03 07:43 | 2025-11-03 20:32 | 12:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-11-03 09:55 | 2025-11-03 13:40 | 3:45 | S/O | 33kV Nawabganj-1 feeder Reserve bus D/S red hot maintenance work. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2025-11-04 07:15 | 2025-11-04 20:05 | 12:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-11-09 07:32 | 2025-11-09 20:06 | 12:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-11-10 08:03 | 2025-11-10 19:01 | 10:58 | S/O | annual maintence | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-11-11 08:58 | 2025-11-11 12:54 | 3:56 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-11-12 07:34 | 2025-11-12 21:25 | 13:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-11-13 07:30 | 2025-11-13 20:45 | 13:15 | S/O | Annual maintence | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-11-14 08:25 | 2025-11-14 16:49 | 8:24 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2025-11-04 06:42 | 2025-11-04 09:44 | 3:02 | S/O | oil leakage. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-3 | 2025-11-04 08:44 | 2025-11-04 14:42 | 5:58 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2025-11-28 07:04 | 2025-11-28 16:03 | 8:59 | S/O | Annual maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2025-11-29 09:48 | 2025-11-29 13:20 | 3:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Maniknagar 132/33kV | Reserve Bus | 2025-11-08 09:36 | 2025-11-08 09:36 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus1 | 2025-11-09 09:24 | 2025-11-09 20:33 | 11:09 | S/O | Project work. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2025-11-21 09:05 | 2025-11-21 17:22 | 8:17 | S/O | project work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2025-11-22 07:15 | 2025-11-22 16:57 | 9:42 | S/O | Isolator upgradation work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2025-11-23 07:32 | 2025-11-23 16:13 | 8:41 | S/O | Isolator upgradation. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2025-11-27 10:25 | 2025-11-27 13:29 | 3:04 | S/O | For annual maintenance. | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR - 2 | 2025-11-06 07:01 | 2025-11-06 07:59 | 0:58 | S/O | Maintanace Work | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR-1 | 2025-11-06 08:15 | 2025-11-06 10:58 | 2:43 | S/O | ATR- 1 shutdown for maintenace work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 01 | 2025-11-09 09:18 | 2025-11-09 20:26 | 11:08 | S/O | 230 kV Bus- 01 shutdown instructed by NLDC. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 02 | 2025-11-21 08:36 | 2025-11-21 17:20 | 8:44 | S/O | 230 kV Bus Section- 2 shutdown instructed by NLDC | 0 | 0 | No interruption
Narshingdi 132/33kV | T-1 | 2025-11-16 08:40 | 2025-11-16 17:12 | 8:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | T-1 | 2025-11-17 08:50 | 2025-11-17 11:57 | 3:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-11-17 11:53 | 2025-11-17 16:07 | 4:14 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-2 | 2025-11-18 09:30 | 2025-11-18 16:06 | 6:36 | S/O | OUR of annual Maintenance. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-2 | 2025-11-19 08:40 | 2025-11-19 12:42 | 4:02 | S/O | Annual maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 | 2025-11-19 12:50 | 2025-11-19 16:33 | 3:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-11-20 08:40 | 2025-11-20 12:50 | 4:10 | S/O | For Annual maintenance work. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-11-22 08:40 | 2025-11-22 13:45 | 5:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-11-29 08:53 | 2025-11-29 12:33 | 3:40 | S/O | PT test | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2025-11-05 07:32 | 2025-11-05 17:36 | 10:04 | S/O | Due to Annual Maintenance Work. | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2025-11-06 07:27 | 2025-11-07 13:01 | 29:34 | S/O | For annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2025-11-07 14:48 | 2025-11-07 17:21 | 2:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2025-11-16 07:32 | 2025-11-16 13:15 | 5:43 | S/O | For annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2025-11-17 07:34 | 2025-11-17 12:50 | 5:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | 132kV Main Bus-1 | 2025-11-19 07:52 | 2025-11-19 13:53 | 6:01 | S/O | Annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | 132kV Main Bus-2 | 2025-11-19 15:24 | 2025-11-19 17:41 | 2:17 | S/O | For annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2025-11-29 08:15 | 2025-11-29 15:30 | 7:15 | S/O | Annual maintenance of 33 kv Busbar for T-1 and T-2, All 33 kv feeders with associated DS, CT, PT, CB, Aux. Tr-1 & 2, All work performed by Dhaka PBS-2 | 11 | 79.75 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-11-29 08:17 | 2025-11-29 15:27 | 7:10 | S/O | Annual maintenance of 33 kv Busbar for T-1 and T-2, All 33 kv feeders with associated DS, CT, PT, CB, Aux. Tr-1 & 2, All work performed by Dhaka PBS-2 | 11 | 78.8333 | Power interruption
Rampura 230/132kV | Bhulta Ckt- | 2025-11-15 06:45 | 2025-11-15 17:49 | 11:04 | S/O | Annual Maintenance of Bhulta-Rampura 230Kv Ckt-1 Bay. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt- | 2025-11-16 07:08 | 2025-11-16 17:21 | 10:13 | S/O | Annual Maintenance of Bhulta 230KV CKt-1 | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 04 | 2025-11-16 12:27 | 2025-11-16 16:42 | 4:15 | S/O | SCADA Integration work under G2G Project(CCCE) | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt- | 2025-11-17 12:19 | 2025-11-17 16:50 | 4:31 | S/O | Command by NLDC. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-19 07:20 | 2025-11-19 16:55 | 9:35 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt- | 2025-11-19 09:21 | 2025-11-19 17:22 | 8:01 | S/O | taken by Vulta Grid SS , instructed by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-20 07:16 | 2025-11-20 16:28 | 9:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-20 14:32 | 2025-11-20 18:03 | 3:31 | S/O | Shutdown taken by OFCN. Command by NLDC. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-21 10:17 | 2025-11-21 17:04 | 6:47 | S/O | Shutdown taken by Bhalta Grid.Command by NLDC. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-22 11:16 | 2025-11-22 17:01 | 5:45 | S/O | Bhulta 230KV CKt-4 shutdown due to OPGW install for Bhulta-Rupshi 132kV Transmission line by OFCN. Bhulta SS taken the shutdown by NLDC in request of OFCN for safety puspose. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-24 07:02 | 2025-11-24 19:18 | 12:16 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-25 10:33 | 2025-11-25 15:20 | 4:47 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2025-11-26 06:53 | 2025-11-26 16:29 | 9:36 | S/O | Annual maintenance 2025-26 | 0 | 0 | No interruption
Shyampur 230/132kV | Auto TR-1 | 2025-11-07 07:02 | 2025-11-07 16:32 | 9:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shyampur 230/132kV | Auto TR-1 | 2025-11-18 09:12 | 2025-11-19 20:08 | 34:56 | S/O | SF6 Gas change. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-11-14 08:41 | 2025-11-14 09:08 | 0:27 | S/O | Maintenance of PBS Barpa 33kv feeder Heat shrink | 45 | 20.25 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-11-14 14:50 | 2025-11-14 16:18 | 1:28 | S/O | Maintenance works on PBS 33KV Borpa feeder | 25 | 36.6667 | Power interruption
Sonargaon 132/33kV | BUS A | 2025-11-18 08:58 | 2025-11-18 16:15 | 7:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 | 2025-11-28 08:37 | 2025-11-28 11:15 | 2:38 | S/O | PBS Kabilgaj feeder's Load side underground cable removal. | 52 | 136.9333 | Power interruption
Srinagar 132/33kV | Tr-01 | 2025-11-05 08:04 | 2025-11-05 18:31 | 10:27 | S/O | 132/33 kv TR-01 bay annual maintenance. | 0 | 0 | No interruption
Srinagar 132/33kV | 33 kV bus | 2025-11-05 08:13 | 2025-11-05 11:35 | 3:22 | S/O | 132/33 kv TR-01 bay annual maintenance. | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-01 | 2025-11-06 08:33 | 2025-11-06 16:32 | 7:59 | S/O | 132/33 kv TR-01 bay annual maintenance. | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2025-11-11 08:11 | 2025-11-11 19:03 | 10:52 | S/O | 132/33 kv TR-02 bay 105 annual maintenance. | 7 | 76.0667 | Power interruption
Srinagar 132/33kV | Tr-02 | 2025-11-12 11:10 | 2025-11-12 14:15 | 3:05 | S/O | 132/33 kv TR-02 bay annual maintenance. | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2025-11-13 08:16 | 2025-11-13 14:31 | 6:15 | S/O | 132/33 kv TR-02 bay annual maintenance. | 0 | 0 | No interruption
Uttara 132/33kV | GT-01 | 2025-11-30 09:15 | 2025-11-30 09:45 | 0:30 | S/O | Due to maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-27 04:20 |  | Unserved Energy: |  | 2438.8333
Chattogram Grid Circle :
Bakulia 132/33kV | T-4 (432T) | 2025-11-06 07:03 | 2025-11-06 14:08 | 7:05 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bakulia 132/33kV | T-1 (402T) | 2025-11-08 07:04 | 2025-11-08 16:05 | 9:01 | S/O | Annual Maintenance | 5 | 45.0833 | Power interruption
Baroaulia 132/33kV | T-1(405T) | 2025-11-16 07:40 | 2025-11-16 17:30 | 9:50 | S/O | Annual maintanance | 16 | 157.3333 | Power interruption
Baroaulia 132/33kV | T2(415T) | 2025-11-23 08:42 | 2025-11-23 16:48 | 8:06 | S/O | Annual Maintenance | 20 | 162 | Power interruption
Baroirhat 132/33kV | TR-1, 406T | 2025-11-17 08:32 | 2025-11-17 16:50 | 8:18 | S/O | Annual maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-2, 416T | 2025-11-18 08:21 | 2025-11-18 16:15 | 7:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV | Bus-A | 2025-11-19 08:34 | 2025-11-19 15:45 | 7:11 | S/O | Annual maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV | Bus-B | 2025-11-20 08:27 | 2025-11-20 13:37 | 5:10 | S/O | Annual maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-11-21 08:06 | 2025-11-21 09:44 | 1:38 | S/O | keranihat 33 kv feeder isolator maintenance | 35 | 57.1667 | Power interruption
GPH 230/33kV | Transformer -2 (D07) | 2025-11-02 07:12 | 2025-11-04 14:47 | 55:35 | S/O | Maintenance Works | 0 | 0 | No interruption
Halishahar 132/33kV | 405T(TR-1) | 2025-11-24 16:58 | 2025-11-24 17:32 | 0:34 | S/O | Due to pdb cable insulation faliure. | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 | 2025-11-15 08:40 | 2025-11-15 17:29 | 8:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-02 | 2025-11-22 09:11 | 2025-11-22 17:12 | 8:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-01 | 2025-11-26 09:49 | 2025-11-26 16:25 | 6:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Juldah 132/33kV | 132/33 KV 406T T-1 | 2025-11-04 07:11 | 2025-11-04 14:16 | 7:05 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV | 133/33 KV T-2 416T | 2025-11-05 07:43 | 2025-11-05 14:27 | 6:44 | S/O | ok | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-11-27 08:12 | 2025-11-27 12:37 | 4:25 | S/O | Transformer oil leakge | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-1 | 2025-11-08 08:36 | 2025-11-08 17:27 | 8:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-2 | 2025-11-09 07:13 | 2025-11-09 16:51 | 9:38 | S/O | Annual Bay Maintenance. | 0 | 0 | No interruption
Khagrachori 132/33kV | MAIN BUS-1 | 2025-11-10 08:25 | 2025-11-10 11:40 | 3:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV | MAIN BUS-2 | 2025-11-10 11:47 | 2025-11-10 15:50 | 4:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2025-11-12 10:00 | 2025-11-12 16:00 | 6:00 | S/O | due to oil leakage check | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2025-11-16 16:10 | 2025-11-16 16:40 | 0:30 | S/O | due to shutdown oil leakage check and transformer oil top up | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-11-18 11:18 | 2025-11-22 17:15 | 101:57 | S/O | due to shutdown oil leakage check and transformer oil top up . | 0 | 0 | No interruption
Mirsorai 230/33kV | TR-2, 728T | 2025-11-06 08:51 | 2025-11-06 15:39 | 6:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 | TR 02 (417T) | 2025-11-20 16:32 | 2025-11-20 16:32 | 0:00 | S/O | maintenance work | 0 | 0 | No interruption
Rangamati 132/33kV | Power Transformer TR1 (405T) | 2025-11-11 08:29 | 2025-11-11 15:42 | 7:13 | S/O | Rangamati 132/33KV T1 X-former taken shut down due to annual maintenance. | 0 | 0 | No interruption
Rangamati 132/33kV | Power Transformer TR2 (415T) | 2025-11-12 09:07 | 2025-11-12 17:34 | 8:27 | S/O | Annual Maintenence | 0 | 0 | No interruption
Rangamati 132/33kV | Main Bus 02 | 2025-11-13 12:09 | 2025-11-13 13:26 | 1:17 | S/O | Annual Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 08:01 |  |  |  | 421.5833
Cumilla Grid Circle :
Ashuganj 230/132/33kV | TR-OAT-11 | 2025-11-07 06:21 | 2025-11-07 19:27 | 13:06 | S/O | Bus shutdown -1 | 0 | 0 | No interruption
Ashuganj 230/132/33kV | 132kv Busbar-1 | 2025-11-07 08:32 | 2025-11-07 16:05 | 7:33 | S/O | 132 KV busbar-1 shutdown | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-11-13 09:35 | 2025-11-13 17:07 | 7:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-11-15 09:32 | 2025-11-15 16:24 | 6:52 | S/O | Maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-11-16 09:03 | 2025-11-16 16:25 | 7:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-11-20 08:32 | 2025-11-20 16:58 | 8:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-11-22 08:52 | 2025-11-22 15:58 | 7:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-11-23 09:08 | 2025-11-23 15:13 | 6:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-01 | 2025-11-17 08:38 | 2025-11-17 17:24 | 8:46 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-01 | 2025-11-18 08:26 | 2025-11-18 16:38 | 8:12 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-01 | 2025-11-19 08:16 | 2025-11-19 16:59 | 8:43 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-02 | 2025-11-24 08:31 | 2025-11-24 16:08 | 7:37 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-02 | 2025-11-25 08:40 | 2025-11-25 14:52 | 6:12 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-02 | 2025-11-26 08:36 | 2025-11-26 16:37 | 8:01 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 402T | 2025-11-15 07:36 | 2025-11-15 14:45 | 7:09 | S/O | AM | 20 | 143 | Power interruption
Brahmanbaria 132/33kV | 401T | 2025-11-25 08:51 | 2025-11-25 17:51 | 9:00 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 401T | 2025-11-26 09:15 | 2025-11-26 16:24 | 7:09 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 401T | 2025-11-27 09:45 | 2025-11-27 13:15 | 3:30 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 401T | 2025-11-29 09:18 | 2025-11-29 13:37 | 4:19 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 403T | 2025-11-29 13:44 | 2025-11-30 09:02 | 19:18 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 402T | 2025-11-30 09:35 | 2025-11-30 15:28 | 5:53 | S/O | AM | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2025-11-04 15:42 | 2025-11-04 17:51 | 2:09 | S/O | For tariff meter testing work by metering division power grid | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2025-11-04 17:52 | 2025-11-04 18:02 | 0:10 | S/O | For tariff meter testing work | 6 | 1 | Power interruption
Chandina 132/33kV | TR-3 | 2025-11-07 17:00 | 2025-11-08 17:25 | 24:25 | S/O | To solve the TR-3 mechanical fault . | 0 | 0 | No interruption
Chandpur 132/33kV | 200KVA Aux. T-2 | 2025-11-16 08:29 | 2025-11-24 07:00 | 190:31 | S/O | Maintainace | 0 | 0 | No interruption
Chandpur 132/33kV | 200KVA Aux. T-1 | 2025-11-24 07:00 | 2025-11-24 08:52 | 1:52 | S/O | MAINTAINACE | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2025-11-24 07:07 | 2025-11-24 08:52 | 1:45 | S/O | MAINTAINACE | 6 | 10.5 | Power interruption
Chandpur 132/33kV | 412T (T-2) | 2025-11-24 07:08 | 2025-11-24 08:50 | 1:42 | S/O | MAINTAINACE | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2025-11-24 11:30 | 2025-11-24 14:05 | 2:35 | S/O | Measurement for painting work | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2025-11-25 09:20 | 2025-11-25 14:20 | 5:00 | S/O | SPMD annual Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2025-11-25 14:45 | 2025-11-25 16:20 | 1:35 | S/O | SPMD ANNUAL MAINTENANCE | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 | 2025-11-01 11:20 | 2025-11-01 13:12 | 1:52 | S/O | 33kv busbar radhot maintans. | 30 | 56 | Power interruption
Chhatak 132/33kV | T-1 | 2025-11-13 07:12 | 2025-11-13 14:21 | 7:09 | S/O | Transformer T-1 Shutdown for annual maintenance. | 0 | 0 | No interruption
Chhatak 132/33kV | T-1 | 2025-11-15 07:14 | 2025-11-15 13:55 | 6:41 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Chhatak 132/33kV | T-1 | 2025-11-16 07:01 | 2025-11-16 14:53 | 7:52 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Chhatak 132/33kV | T-2 | 2025-11-20 07:14 | 2025-11-20 15:49 | 8:35 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Chhatak 132/33kV | T-2 | 2025-11-22 06:59 | 2025-11-22 15:06 | 8:07 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Chhatak 132/33kV | T-2 | 2025-11-23 07:02 | 2025-11-23 14:16 | 7:14 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2025-11-27 06:58 | 2025-11-27 14:40 | 7:42 | S/O | Annual Maintanance | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2025-11-29 07:05 | 2025-11-29 14:20 | 7:15 | S/O | Shutdown for Annual Maintenance. | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2025-11-30 07:24 | 2025-11-30 15:35 | 8:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-04 | 2025-11-15 08:00 | 2025-11-15 13:00 | 5:00 | S/O | Maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-1 | 2025-11-26 09:40 | 2025-11-26 14:57 | 5:17 | S/O | SPMD Yearly Maintenance Work | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2025-11-26 15:34 | 2025-11-26 17:25 | 1:51 | S/O | Relay Testing By SPMD , Cumilla | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-02B | 2025-11-29 09:34 | 2025-11-29 14:34 | 5:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-02 | 2025-11-30 09:11 | 2025-11-30 13:42 | 4:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) | 2025-11-15 09:22 | 2025-11-15 09:38 | 0:16 | S/O | 132kV T-2 Transformer Bus Coupler Breaker to Main Breaker Load Shift. | 0 | 0 | No interruption
Kachua 230/132/33kV | ATR-2 | 2025-11-05 16:06 | 2025-11-05 16:17 | 0:11 | S/O | for meter accuracy checking | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-11-02 08:47 | 2025-11-02 08:56 | 0:09 | S/O | TR -1 ( A) Annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-11-02 16:27 | 2025-11-02 16:43 | 0:16 | S/O | TR -1 ( A) Annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-11-03 08:47 | 2025-11-03 15:03 | 6:16 | S/O | TR- 1 ( A+B) annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-11-04 08:23 | 2025-11-04 09:52 | 1:29 | S/O | 33 Kv bus DS Redhot maintenance | 20 | 29.6667 | Power interruption
Kulaura 132/33kV | TR-2 | 2025-11-04 10:00 | 2025-11-04 15:30 | 5:30 | S/O | Annual maintenance of TR-02 | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-11-04 13:52 | 2025-11-04 16:41 | 2:49 | S/O | 33 KV Bus DS Redhot maintenance | 34 | 95.7667 | Power interruption
Kulaura 132/33kV | TR-2 | 2025-11-05 11:02 | 2025-11-05 16:50 | 5:48 | S/O | Annual maintenance of TR-02 | 0 | 0 | No interruption
Kulaura 132/33kV | TR-2 | 2025-11-06 08:54 | 2025-11-06 14:49 | 5:55 | S/O | Annual maintenance of TR-02 | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-11-18 08:48 | 2025-11-18 16:35 | 7:47 | S/O | TR-01(AB) shutdown for annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-11-19 08:40 | 2025-11-19 14:30 | 5:50 | S/O | Annual maintenance of TR-1 (AB) | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2025-11-05 17:00 | 2025-11-05 17:05 | 0:05 | S/O | Metering Test. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2025-11-09 14:38 | 2025-11-09 15:28 | 0:50 | S/O | 33 kv CB Maintenance . | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2025-11-10 10:24 | 2025-11-10 12:02 | 1:38 | S/O | 33kv BREB Red Hot maintanance work | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2025-11-10 10:28 | 2025-11-10 12:05 | 1:37 | S/O | 33kv BREB Red Hot maintanance work | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2025-11-23 08:33 | 2025-11-23 13:57 | 5:24 | S/O | Silicon painting work, top surface of GIS building | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2025-11-24 08:15 | 2025-11-24 15:11 | 6:56 | S/O | Silicon paint work on top surface of GIS building. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2025-11-13 16:08 | 2025-11-13 17:13 | 1:05 | S/O | SCADA Work. | 10 | 10.8333 | Power interruption
Muradnagar 132/33kV | 132KV Busbar-1 | 2025-11-16 12:51 | 2025-11-16 20:31 | 7:40 | S/O | SCADA Integration | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Busbar-1 | 2025-11-17 14:52 | 2025-11-17 17:13 | 2:21 | S/O | SCADA Integration | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Busbar-1 | 2025-11-25 11:13 | 2025-11-25 17:02 | 5:49 | S/O | SCADA INTEGRATION | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2025-11-25 14:31 | 2025-11-25 16:57 | 2:26 | S/O | SCADA INTEGRATION | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-02 | 2025-11-26 12:08 | 2025-11-27 13:30 | 25:22 | S/O | SCADA INTEGRATION | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2025-11-27 14:18 | 2025-11-27 15:16 | 0:58 | S/O | SCADA INTEGRATION | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Busbar-1 | 2025-11-27 15:16 | 2025-11-27 15:55 | 0:39 | S/O | SCADA INTEGRATION | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-11-08 08:46 | 2025-11-08 14:37 | 5:51 | S/O | Shutdown taken by pbs Due to Feeder shifting. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-11-08 09:02 | 2025-11-08 14:30 | 5:28 | S/O | Shutdown taken by pbs Due to Feeder shifting. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-11-11 08:40 | 2025-11-11 17:25 | 8:45 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-11-12 09:12 | 2025-11-12 17:02 | 7:50 | S/O | Tr-2 Shutdown for Annual Maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-11-13 08:56 | 2025-11-13 17:18 | 8:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-11-15 09:11 | 2025-11-15 16:32 | 7:21 | S/O | Shutdown taken for Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-11-16 09:06 | 2025-11-16 16:22 | 7:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-11-17 08:22 | 2025-11-17 16:22 | 8:00 | S/O | Annaul Maintenance. | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-1AB | 2025-11-08 09:16 | 2025-11-08 16:20 | 7:04 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-1AB | 2025-11-09 08:24 | 2025-11-09 15:20 | 6:56 | S/O | Annual Maintanance Works. | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-1AB | 2025-11-10 08:23 | 2025-11-10 16:13 | 7:50 | S/O |  | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-2 | 2025-11-22 09:41 | 2025-11-22 17:01 | 7:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-11-22 09:41 | 2025-11-22 17:01 | 7:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-2 | 2025-11-23 08:10 | 2025-11-23 16:10 | 8:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-11-23 08:10 | 2025-11-23 16:08 | 7:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-2 | 2025-11-24 10:38 | 2025-11-24 16:55 | 6:17 | S/O | Hand over shift duty to the next shift in-charge with healthy condition. | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-11-24 10:38 | 2025-11-24 16:55 | 6:17 | S/O | Hand over shift duty to the next shift in-charge with healthy condition. | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2025-11-10 06:02 | 2025-11-10 10:32 | 4:30 | S/O | Due to annual maintenance | 45 | 202.5 | Power interruption
Sunamganj 132/33kV | Tr-1 | 2025-11-11 08:25 | 2025-11-11 13:54 | 5:29 | S/O | Due to annual maintenance | 8 | 43.8667 | Power interruption
Sunamganj 132/33kV | Tr-1 | 2025-11-12 06:55 | 2025-11-12 10:10 | 3:15 | S/O | Due to Annual Maintenance | 2 | 6.5 | Power interruption
Sunamganj 132/33kV | Tr-1 | 2025-11-17 06:19 | 2025-11-17 09:30 | 3:11 | S/O | Annual Maintenance | 30 | 95.5 | Power interruption
Sunamganj 132/33kV | Tr-2 | 2025-11-18 07:06 | 2025-11-18 11:06 | 4:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-2 | 2025-11-19 08:28 | 2025-11-19 11:48 | 3:20 | S/O |  | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-11-24 07:15 | 2025-11-24 13:02 | 5:47 | S/O | Annual Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-11-25 07:16 | 2025-11-25 13:14 | 5:58 | S/O | Annunal maintenance . | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-11-29 07:18 | 2025-11-29 13:40 | 6:22 | S/O | Annual Maintanance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-30 18:45 |  |  |  | 695.1333
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-1 (403T) | 2025-11-10 15:44 | 2025-11-10 16:57 | 0.050694 | S/O | 33 kv bus section 1 shutdown by pbs for 33 kv Morelganj feeder red hot maintenance. | 23 | 27.9833 | Power interruption
Barishal 132/33kV | 132 kV Bus-coupler | 2025-11-02 07:10 | 2025-11-02 16:00 | 0.36806 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2025-11-04 16:18 | 2025-11-04 16:35 | 0.011806 | S/O | Charger load shift | 30 | 8.5 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2025-11-04 16:19 | 2025-11-04 16:35 | 0.011111 | S/O | Charger load shift | 50 | 13.3333 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-11-05 07:10 | 2025-11-05 16:14 | 0.37778 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2025-11-06 07:12 | 2025-11-06 16:36 | 0.39167 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2025-11-26 07:22 | 2025-11-26 18:50 | 0.47778 | S/O | Due to the burning of the source side A-phase isolator finger of the Korapur 1 No 33 kv feeder maintenance work by PBS. | 8 | 91.7333 | Power interruption
Benapole 132/33kV | Bus-A | 2025-11-04 08:25 | 2025-11-04 16:46 | 0.34792 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2025-11-10 08:11 | 2025-11-10 16:19 | 0.33889 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2025-11-11 08:11 | 2025-11-11 16:19 | 0.33889 | S/O | 132/33 KV Transformer annual maintenance. | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-2(416T) | 2025-11-15 08:18 | 2025-11-15 16:37 | 0.34653 | S/O | Annual maintenance of T2 | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-2(416T) | 2025-11-16 08:20 | 2025-11-16 16:35 | 0.34375 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV | Bus-B | 2025-11-19 08:16 | 2025-11-19 15:46 | 0.3125 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-11-04 08:57 | 2025-11-04 16:44 | 0.32431 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-11-05 08:35 | 2025-11-05 17:10 | 0.35764 | S/O | Annual maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-1 | 2025-11-08 09:02 | 2025-11-08 16:41 | 0.31875 | S/O |  | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-1 | 2025-11-09 08:36 | 2025-11-09 16:50 | 0.34306 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-2 | 2025-11-10 09:17 | 2025-11-10 20:06 | 0.45069 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-2 | 2025-11-11 08:51 | 2025-11-11 16:41 | 0.32639 | S/O | Annual maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV | Bus-A | 2025-11-17 09:21 | 2025-11-17 16:41 | 0.30556 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-11-25 11:20 | 2025-11-25 16:24 | 0.21111 | S/O |  | 0 | 0 | No interruption
Goalpara 132/33kV | Bus 1 | 2025-11-02 09:43 | 2025-11-02 15:42 | 0.24931 | S/O | Annual maintanance shutdown | 0 | 0 | No interruption
Goalpara 132/33kV | Bus 1 | 2025-11-03 08:57 | 2025-11-03 17:02 | 0.33681 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-1 | 2025-11-09 08:52 | 2025-11-09 15:50 | 0.29028 | S/O | Annual Maintenance 2025 | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-1 | 2025-11-10 08:34 | 2025-11-10 14:00 | 0.22639 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2025-11-12 08:05 | 2025-11-12 14:27 | 0.26528 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2025-11-05 20:41 | 2025-11-05 20:49 | 0.0055556 | S/O | Protection Teat | 30 | 4 | Power interruption
Gopalganj 132/33kV | T1 | 2025-11-20 07:55 | 2025-11-21 00:50 | 0.70486 | S/O | Maintenance work by WZPDCL | 10 | 169.1667 | Power interruption
Gopalganj 400/132kV | ATR-01 | 2025-11-02 08:33 | 2025-11-02 16:59 | 0.35139 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-01 | 2025-11-03 08:17 | 2025-11-04 02:25 | 0.75556 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Bus-01 | 2025-11-04 09:29 | 2025-11-05 18:07 | 1899-12-31 08:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Bus-02 | 2025-11-06 09:40 | 2025-11-06 17:06 | 0.30972 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-02 | 2025-11-09 09:03 | 2025-11-09 22:48 | 0.57292 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230 kV Bus-01 | 2025-11-10 07:48 | 2025-11-10 17:27 | 0.40208 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230 kV Bus-02 | 2025-11-19 08:42 | 2025-11-19 17:35 | 0.37014 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-11-14 09:07 | 2025-11-14 13:28 | 0.18125 | S/O | 132KV South - 1, R-phase jack Bus Maintenance. | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-11-22 12:16 | 2025-11-22 13:59 | 0.071528 | S/O | Wz maintenance work | 0 | 0 | No interruption
Madaripur 132/33kV | Aux Tr-01 | 2025-11-03 10:30 | 2025-11-03 13:30 | 0.125 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV | TR1 (403-T) | 2025-11-12 07:37 | 2025-11-12 16:56 | 0.38819 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Narail 132/33kV | TR1 (403-T) | 2025-11-13 07:54 | 2025-11-22 12:25 | 1900-01-08 04:31 | S/O | For annual maintenance work purpose. | 0 | 0 | No interruption
Narail 132/33kV | TR2 (413-T) | 2025-11-17 07:37 | 2025-11-17 16:18 | 0.36181 | S/O | For annual maintenance work purpose | 0 | 0 | No interruption
Narail 132/33kV | TR2 (413-T) | 2025-11-18 07:41 | 2025-11-18 12:19 | 0.19306 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV | Auxiliary TR 1 | 2025-11-19 07:16 | 2025-11-19 10:39 | 0.14097 | S/O | Looping connection of new section DS of 33 kv bay extension work. | 20 | 67.6667 | Power interruption
Narail 132/33kV | Auxiliary TR 1 | 2025-11-22 08:14 | 2025-11-22 12:26 | 0.175 | S/O | Annual Maintenance of 132 kV Buber Section-1 | 0 | 0 | No interruption
Narail 132/33kV | 132 kV Busbar | 2025-11-22 08:34 | 2025-11-22 12:16 | 0.15417 | S/O | Annual Maintenance of 132 kV Buber Section-1 | 0 | 0 | No interruption
Narail 132/33kV | TR1 (403-T) | 2025-11-24 07:04 | 2025-11-24 08:14 | 0.048611 | S/O | 33 kv bay extension work | 20 | 23.3333 | Power interruption
Noapara 132/33kV | T-2 | 2025-11-06 09:38 | 2025-11-06 16:09 | 0.27153 | S/O |  | 0 | 0 | No interruption
Noapara 132/33kV | BUS A | 2025-11-08 08:37 | 2025-11-08 14:13 | 0.23333 | S/O | Annual Maintenance of 132kV BUS-A | 0 | 0 | No interruption
Noapara 132/33kV | BUS A | 2025-11-09 08:33 | 2025-11-09 13:13 | 0.19444 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-11-14 22:01 | 2025-11-14 23:32 | 0.063194 | S/O |  | 13 | 19.7167 | Power interruption
Noapara 132/33kV | BUS-B | 2025-11-23 08:52 | 2025-11-23 14:42 | 0.24306 | S/O |  | 0 | 0 | No interruption
Noapara 132/33kV | BUS-B | 2025-11-24 09:11 | 2025-11-24 14:38 | 0.22708 | S/O |  | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-2 | 2025-11-15 08:27 | 2025-11-15 15:44 | 0.30347 | S/O | RAJBARI PBS WORKS. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2025-11-22 08:35 | 2025-11-22 17:16 | 0.36181 | S/O | Annual maintenance by PBS | 10 | 86.8333 | Power interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-11-15 09:45 | 2025-11-15 13:54 | 0.17292 | S/O | Loop change of Ashasuni 33kV feeder. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-24 15:41 |  | Unserved Energy : |  | 512.2667
HVDC Grid Circle
Baghabari 230/132kV | T-1 | 2025-11-24 08:49 | 2025-11-24 19:41 | 10:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | T-2 Bank | 2025-11-26 08:41 | 2025-11-26 17:24 | 8:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | T-2 Bank | 2025-11-27 10:19 | 2025-11-27 16:16 | 5:57 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2025-11-23 09:25 | 2025-11-23 15:31 | 6:06 | S/O | বাৎসরিক মেরামত | 0 | 0 | No interruption
Bheramara 230/132kV | Kushti | 2025-11-13 08:35 | 2025-11-13 08:35 | 0:00 | S/O | A/M | 0 | 0 | No interruption
Bheramara 230/132kV | Transformer-1 | 2025-11-26 09:05 | 2025-11-26 15:16 | 6:11 | S/O | AM | 0 | 0 | No interruption
BIPTC | Block-01, Trafo-02 | 2025-11-23 11:09 | 2025-11-23 17:16 | 6:07 | S/O | Oil Leakage Rectification at 2MVA Auxiliary Transformer | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Kushtia 132kV Circuit-1( | 2025-11-13 08:31 | 2025-11-13 08:31 | 0:00 | S/O | Upgradation work | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaida | 2025-11-13 08:32 | 2025-11-13 08:32 | 0:00 | S/O | 132 kV Circuit Breaker Replacement Work | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia -Bheramar | 2025-11-13 08:34 | 2025-11-13 08:34 | 0:00 | S/O | 132 kV Circuit Breaker Replacement Work | 0 | 0 | No interruption
Kushtia 132/33kV | 132 KV Bus-A | 2025-11-28 10:58 | 2025-11-28 10:58 | 0:00 | S/O | ১৩২ কেভি বাসকাপলার ব্রেকার পরিবর্তন কাজ। | 0 | 0 | No interruption
Magura 132/33kV | T-3 (425T) | 2025-11-25 08:41 | 2025-11-26 17:27 | 32:46 | S/O | 33kV Bus side DS maintenance(project work of Energypac) | 0 | 0 | No interruption
Magura 132/33kV | T-1 (405T) | 2025-11-29 08:47 | 2025-11-29 15:38 | 6:51 | S/O | Annual maintenance of 33kV WZPDCL feeder. | 12 | 82.2 | Power interruption
Pabna 132/33kV | T-2 | 2025-11-20 07:09 | 2025-11-20 09:34 | 2:25 | S/O |  | 5 | 12.0833 | Power interruption
Shahjadpur 132/33kV | T-1(405T) | 2025-11-03 09:30 | 2025-11-03 16:03 | 6:33 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-2(415T) | 2025-11-05 08:30 | 2025-11-05 16:25 | 7:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-2(415T) | 2025-11-09 10:40 | 2025-11-09 16:30 | 5:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-3(425T) | 2025-11-10 08:00 | 2025-11-10 16:51 | 8:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-4(435T) | 2025-11-12 08:33 | 2025-11-12 16:20 | 7:47 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer -1 | 2025-11-15 08:28 | 2025-11-15 16:07 | 7:39 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer-2 | 2025-11-20 09:05 | 2025-11-20 12:53 | 3:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-11-05 13:32 | 2025-11-05 14:01 | 0:29 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF26 | 2025-11-07 14:49 | 2025-11-07 15:32 | 0:43 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-11-11 09:31 | 2025-11-11 16:25 | 6:54 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-11-12 09:08 | 2025-11-12 16:09 | 7:01 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 20DF21 | 2025-11-13 09:36 | 2025-11-13 15:47 | 6:11 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 20DF22 | 2025-11-16 09:06 | 2025-11-16 15:54 | 6:48 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 20DF23 | 2025-11-17 09:09 | 2025-11-17 14:45 | 5:36 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF13 | 2025-11-19 09:23 | 2025-11-19 16:48 | 7:25 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF14 | 2025-11-20 09:35 | 2025-11-20 15:20 | 5:45 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-11-23 09:19 | 2025-11-23 15:42 | 6:23 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF16 | 2025-11-24 09:45 | 2025-11-24 16:13 | 6:28 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF11 | 2025-11-26 09:44 | 2025-11-26 15:39 | 5:55 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF12 | 2025-11-27 09:38 | 2025-11-27 15:19 | 5:41 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF21 | 2025-11-30 09:32 | 2025-11-30 16:13 | 6:41 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-07 20:21 |  | Unserved Energy : |  | 94.2833
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) | 2025-11-08 08:22 | 2025-11-08 16:25 | 8:03 | S/O | Annual maintenance. | 0 | 0 | No interruption
Amnura 132/33kV | T-1 (406T) | 2025-11-09 08:23 | 2025-11-09 16:01 | 7:38 | S/O | Annual maintenance | 0 | 0 | No interruption
Amnura 132/33kV | T-2 (416T) | 2025-11-10 07:57 | 2025-11-10 15:35 | 7:38 | S/O | Annual Maintenance, Clearance ALDC, Bogura. | 0 | 0 | No interruption
Amnura 132/33kV | T-2 (416T) | 2025-11-11 08:04 | 2025-11-11 16:50 | 8:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV | T-3 (426T) | 2025-11-12 08:27 | 2025-11-12 16:25 | 7:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV | T-3 (426T) | 2025-11-13 08:38 | 2025-11-13 15:46 | 7:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV | Bus-2 | 2025-11-22 08:44 | 2025-11-22 17:14 | 8:30 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Amnura 132/33kV | T-1 (406T) | 2025-11-22 08:47 | 2025-11-22 17:15 | 8:28 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Amnura 132/33kV | T-2 (416T) | 2025-11-22 08:47 | 2025-11-22 17:04 | 8:17 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Amnura 132/33kV | T-3 (426T) | 2025-11-22 09:01 | 2025-11-22 16:44 | 7:43 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Amnura 132/33kV | Bus-33KV | 2025-11-22 09:01 | 2025-11-22 16:44 | 7:43 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Amnura 132/33kV | Bus-1 | 2025-11-22 09:02 | 2025-11-22 16:43 | 7:41 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2025-11-02 09:06 | 2025-11-02 16:51 | 7:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus B | 2025-11-02 09:57 | 2025-11-02 16:28 | 6:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2025-11-03 06:56 | 2025-11-03 16:56 | 10:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus A | 2025-11-03 10:26 | 2025-11-03 16:25 | 5:59 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-11-04 08:16 | 2025-11-04 09:17 | 1:01 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-11-05 07:21 | 2025-11-05 16:15 | 8:54 | S/O | Annual Maintenance work | 35 | 311.5 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2025-11-06 08:27 | 2025-11-06 15:44 | 7:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2025-11-08 09:49 | 2025-11-08 15:45 | 5:56 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus Coupler | 2025-11-09 09:47 | 2025-11-09 15:39 | 5:52 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus A | 2025-11-10 09:12 | 2025-11-10 15:44 | 6:32 | S/O | annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus B | 2025-11-15 09:35 | 2025-11-15 16:08 | 6:33 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132 KV Bus A | 2025-11-19 08:54 | 2025-11-19 16:45 | 7:51 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-11-02 12:57 | 2025-11-02 14:50 | 1:53 | S/O | MULTIPLICATION METER INSTALATION | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-4 | 2025-11-02 15:32 | 2025-11-02 17:19 | 1:47 | S/O | Multi function Meter installation to T-4 33 kv control penal | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-4 | 2025-11-30 07:53 | 2025-11-30 13:50 | 5:57 | S/O | For maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV | T-01 | 2025-11-29 08:37 | 2025-11-29 17:04 | 8:27 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bogura 230/132kV | T-01 | 2025-11-30 08:39 | 2025-11-30 12:20 | 3:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | 230 KV BUS-A (A1-A2) | 2025-11-20 11:12 | 2025-11-20 16:36 | 5:24 | S/O | Annual Maintanance | 0 | 0 | No interruption
Bogura 400/230kV | 230 KV BUS-B (B1-B2) | 2025-11-23 10:38 | 2025-11-23 15:53 | 5:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2025-11-26 09:45 | 2025-11-26 13:13 | 3:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 | 2025-11-26 14:00 | 2025-11-26 17:48 | 3:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chapai 132/33kV | Main Bus | 2025-11-07 07:20 | 2025-11-07 12:19 | 4:59 | S/O | TR-01 Bay upgradation. | 38 | 189.3667 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-11-29 08:26 | 2025-11-29 16:19 | 7:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-11-30 07:28 | 2025-11-30 16:30 | 9:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-1(404T) | 2025-11-02 09:54 | 2025-11-02 14:29 | 4:35 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-1(404T) | 2025-11-03 09:40 | 2025-11-03 15:10 | 5:30 | S/O | annual maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-11-04 09:56 | 2025-11-04 14:41 | 4:45 | S/O | for maintenance work | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-11-05 10:08 | 2025-11-05 14:37 | 4:29 | S/O | For annual maintenance work. | 0 | 0 | No interruption
Mithapukur 132/33kV | BUS-1 (132KV) | 2025-11-08 10:47 | 2025-11-08 14:50 | 4:03 | S/O | For annual maintenance work | 0 | 0 | No interruption
Mithapukur 132/33kV | BUS-2 (132KV) | 2025-11-09 10:46 | 2025-11-09 14:45 | 3:59 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 | 2025-11-01 08:14 | 2025-11-01 16:15 | 8:01 | S/O | Annual maintenace. | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 | 2025-11-02 08:09 | 2025-11-02 16:42 | 8:33 | S/O | Annual maintennce | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 | 2025-11-03 08:10 | 2025-11-03 17:25 | 9:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 | 2025-11-04 08:17 | 2025-11-04 16:12 | 7:55 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-11-05 08:19 | 2025-11-06 15:02 | 30:43 | S/O | Annual maintanence | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-11-15 08:17 | 2025-11-15 16:39 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-11-16 08:18 | 2025-11-16 16:12 | 7:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2025-11-17 08:32 | 2025-11-17 16:56 | 8:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2025-11-18 08:34 | 2025-11-18 15:48 | 7:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-3(426T) | 2025-11-19 08:03 | 2025-11-19 16:13 | 8:10 | S/O | Annual maintenace | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-3(426T) | 2025-11-20 08:30 | 2025-11-20 15:55 | 7:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | Bus-2 | 2025-11-21 12:18 | 2025-11-21 15:56 | 3:38 | S/O | Annual maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV | TR1-414T | 2025-11-10 08:30 | 2025-11-10 15:43 | 7:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR1-414T | 2025-11-11 08:21 | 2025-11-11 16:49 | 8:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR2-404T | 2025-11-12 08:20 | 2025-11-12 14:41 | 6:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR2-404T | 2025-11-13 08:23 | 2025-11-13 16:04 | 7:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR3-424T | 2025-11-15 08:28 | 2025-11-15 16:01 | 7:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR3-424T | 2025-11-16 08:45 | 2025-11-16 14:14 | 5:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR4-434T | 2025-11-17 08:31 | 2025-11-17 15:52 | 7:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR4-434T | 2025-11-18 09:03 | 2025-11-18 15:27 | 6:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-4 Transformer | 2025-11-25 09:24 | 2025-11-25 09:24 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-11-22 08:26 | 2025-11-22 16:22 | 7:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-01 | 2025-11-23 08:23 | 2025-11-23 17:55 | 9:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-11-24 08:26 | 2025-11-24 16:56 | 8:30 | S/O | Due to maintenance work. | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 | 2025-11-25 08:34 | 2025-11-25 16:27 | 7:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-11-05 08:02 | 2025-11-05 15:57 | 7:55 | S/O | Annual maintenance vwork. | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2025-11-15 07:35 | 2025-11-15 14:37 | 7:02 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2025-11-19 07:52 | 2025-11-19 14:23 | 6:31 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230/132 kV ATR-01 (704T) | 2025-11-25 07:36 | 2025-11-25 17:33 | 9:57 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230/132 kV ATR-02 (714T) | 2025-11-26 08:34 | 2025-11-26 16:11 | 7:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 230/132 kV ATR-02 (714T) | 2025-11-27 08:12 | 2025-11-27 12:37 | 4:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 132/33 kV T-01 (406T) | 2025-11-29 07:41 | 2025-11-29 16:37 | 8:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 132/33 kV T-01 (406T) | 2025-11-30 07:54 | 2025-11-30 17:09 | 9:15 | S/O | A/M | 0 | 0 | No interruption
Saidpur 132/33kV | TR-01 | 2025-11-05 10:35 | 2025-11-05 12:37 | 2:02 | S/O | Oil filling. | 0 | 0 | No interruption
Saidpur 132/33kV | TR-3 (424T) | 2025-11-05 13:21 | 2025-11-05 14:32 | 1:11 | S/O | Red hot maintenance. | 8 | 9.4667 | Power interruption
Saidpur 132/33kV | TR-5 (434T) | 2025-11-07 07:21 | 2025-11-07 09:25 | 2:04 | S/O | Project work. | 5 | 10.3333 | Power interruption
Saidpur 132/33kV | BUS B | 2025-11-07 07:40 | 2025-11-07 09:19 | 1:39 | S/O | Project work. | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2025-11-22 07:24 | 2025-11-22 10:25 | 3:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | BUS B | 2025-11-22 07:39 | 2025-11-22 10:08 | 2:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | BUS A | 2025-11-22 10:55 | 2025-11-22 11:40 | 0:45 | S/O | CCCE Project work. | 0 | 0 | No interruption
Taraganj 132/33kV | TR-03 (404T) | 2025-11-17 10:11 | 2025-11-17 10:57 | 0:46 | S/O | 132 KV SF6 gas pressure meter problem | 0 | 0 | No interruption
|  |  | Total : | 1900-01-21 18:09 |  | Unserved Energy : |  | 520.6667
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 4154:34 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | Satmosjid Ckt-1 | 2025-11-15 08:31 | 2025-11-15 15:41 | 7:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | Satmosjid Ckt-2 | 2025-11-19 08:30 | 2025-11-19 13:51 | 5:21 | S/O | Annual maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV | Cantonment Ckt-1 | 2025-11-23 08:44 | 2025-11-23 15:01 | 6:17 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV | Cantonment Ckt-2 | 2025-11-26 08:45 | 2025-11-26 14:56 | 6:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kallyanpur-01 | 2025-11-05 07:18 | 2025-11-05 17:01 | 9:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kallyanpur-01 | 2025-11-06 09:59 | 2025-11-06 16:38 | 6:39 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-11-06 19:13 | 2025-11-06 21:11 | 1:58 | S/O | PGNS Project works | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kallyanpur-02 | 2025-11-11 08:37 | 2025-11-11 17:04 | 8:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kallyanpur-02 | 2025-11-12 10:58 | 2025-11-12 13:28 | 2:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2025-11-18 10:59 | 2025-11-18 14:40 | 3:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2025-11-19 09:51 | 2025-11-19 15:26 | 5:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2025-11-22 10:37 | 2025-11-22 17:10 | 6:33 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-02 | 2025-11-24 09:01 | 2025-11-24 15:00 | 5:59 | S/O | Annual maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2025-11-03 10:56 | 2025-11-03 13:09 | 2:13 | S/O | Annual maintenance work at Kishoreganj s/s. | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2025-11-10 08:58 | 2025-11-10 16:35 | 7:37 | S/O | Annul Maintainance of Kishoreganj Grid Side | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2025-11-13 13:06 | 2025-11-13 15:17 | 2:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2025-11-15 15:16 | 2025-11-19 15:26 | 96:10 | S/O | Project work at ashuganj end. | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2025-11-18 10:20 | 2025-11-18 16:51 | 6:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2025-11-19 09:42 | 2025-11-19 14:38 | 4:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2025-11-19 15:43 | 2025-11-22 16:49 | 73:06 | S/O | 132 KV Ashuganj -Bajitpur Ckt-1 S/D Due to project work | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2025-11-22 08:37 | 2025-11-22 14:55 | 6:18 | S/O | Kishoreganj s/s end annual maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2025-11-23 09:20 | 2025-11-23 15:24 | 6:04 | S/O | AnnaulMaintenanceend at Kishoreganj S/S | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2025-11-24 10:19 | 2025-11-24 16:24 | 6:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-11-05 08:33 | 2025-11-05 14:51 | 6:18 | S/O | Annual maintenance work at Bhaluka end. | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-11-06 09:04 | 2025-11-06 15:23 | 6:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2025-11-09 07:09 | 2025-11-09 15:58 | 8:49 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV | Capacitor Bank- 01 | 2025-11-13 08:01 | 2025-11-13 12:58 | 4:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Capacitor Bank- 02 | 2025-11-13 08:01 | 2025-11-13 12:58 | 4:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2025-11-14 08:42 | 2025-11-14 13:27 | 4:45 | S/O | Work at Mymensingh end. | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2025-11-13 08:30 | 2025-11-13 16:25 | 7:55 | S/O | annual maintenance by kaliakoir grid SS. | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2025-11-16 08:42 | 2025-11-16 14:54 | 6:12 | S/O | Annual maintenance by kaliakoir grid SS. | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2025-11-24 19:07 | 2025-11-24 19:37 | 0:30 | S/O | Work by kaliakoir grid SS. | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2025-11-24 19:40 | 2025-11-24 20:02 | 0:22 | S/O | Work done by kaliakoir grid SS. | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-1 | 2025-11-08 08:49 | 2025-11-08 12:28 | 3:39 | S/O | Maintenance work by Muktagacha grid. | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-2 | 2025-11-08 12:43 | 2025-11-08 14:56 | 2:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-1 | 2025-11-29 09:17 | 2025-11-29 15:42 | 6:25 | S/O | Annual maintenance work of Muktagacha Grid SS | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-1 | 2025-11-30 09:04 | 2025-11-30 17:09 | 8:05 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-1 | 2025-11-10 08:43 | 2025-11-10 16:39 | 7:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-2 | 2025-11-12 08:46 | 2025-11-12 16:13 | 7:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | Manikganj-1 | 2025-11-25 08:13 | 2025-11-25 16:33 | 8:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2025-11-06 19:13 | 2025-11-06 21:10 | 1:57 | S/O | Testing purpose | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-1 | 2025-11-13 08:36 | 2025-11-13 16:25 | 7:49 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2025-11-16 08:43 | 2025-11-16 14:53 | 6:10 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2025-11-25 13:08 | 2025-11-25 13:57 | 0:49 | S/O | Isolating 132 kV Bus-2 from the 400/132 kV Transformer | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-11-05 07:17 | 2025-11-05 17:02 | 9:45 | S/O | Also Bay maintenance at Kallyanpur Grid. | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-11-06 08:41 | 2025-11-06 16:41 | 8:00 | S/O | Maintenance Work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2025-11-11 08:36 | 2025-11-11 17:09 | 8:33 | S/O | annul maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2025-11-13 08:42 | 2025-11-13 15:56 | 7:14 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-17 00:41 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Bhulta 400/230kV | Rampura-01 | 2025-11-15 06:45 | 2025-11-15 17:48 | 11:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-01 | 2025-11-16 07:09 | 2025-11-16 17:22 | 10:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Horipur-01 | 2025-11-17 09:57 | 2025-11-17 18:33 | 8:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-01 | 2025-11-17 12:11 | 2025-11-17 16:50 | 4:39 | S/O | For installing OPGW | 0 | 0 | No interruption
Bhulta 400/230kV | Horipur-01 | 2025-11-18 09:49 | 2025-11-18 16:23 | 6:34 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-02 | 2025-11-19 07:21 | 2025-11-19 16:55 | 9:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-01 | 2025-11-19 09:11 | 2025-11-19 17:22 | 8:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-02 | 2025-11-20 07:18 | 2025-11-20 16:28 | 9:10 | S/O | S/D taken by Rampura Grid Substation. | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-03 | 2025-11-20 14:26 | 2025-11-20 18:04 | 3:38 | S/O | OPGW Stringing | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-04 | 2025-11-21 10:19 | 2025-11-21 17:05 | 6:46 | S/O | For installing OPGW. | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-04 | 2025-11-22 11:17 | 2025-11-22 17:00 | 5:43 | S/O | For OPGW Installation. | 0 | 0 | No interruption
Bhulta 400/230kV | Horipur-02 | 2025-11-23 08:23 | 2025-11-23 21:31 | 13:08 | S/O | Annual.Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-03 | 2025-11-24 07:21 | 2025-11-24 19:18 | 11:57 | S/O | Scheduled S/D | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-03 | 2025-11-25 10:34 | 2025-11-25 15:21 | 4:47 | S/O | Annual Maintenance Work by Rampura Grid SS | 0 | 0 | No interruption
Bhulta 400/230kV | Rampura-04 | 2025-11-26 06:55 | 2025-11-26 16:30 | 9:35 | S/O | Due to Annual maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-01 | 2025-11-28 11:10 | 2025-11-28 17:59 | 6:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2025-11-28 11:11 | 2025-11-28 17:59 | 6:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-01 | 2025-11-29 07:19 | 2025-11-30 20:44 | 37:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2025-11-29 07:19 | 2025-11-30 20:44 | 37:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Hasnabad | 2025-11-21 14:34 | 2025-11-21 16:10 | 1:36 | S/O | NLDC | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-11-13 08:48 | 2025-11-13 15:28 | 6:40 | S/O | G2G project works | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-11-27 10:08 | 2025-11-27 17:59 | 7:51 | S/O | To replace LA which has been broken during Earthquake. | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Siddhirganj-1 | 2025-11-16 09:12 | 2025-11-16 19:34 | 10:22 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2025-11-17 07:50 | 2025-11-17 09:49 | 1:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | HPL-1 | 2025-11-18 09:28 | 2025-11-18 17:27 | 7:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | HPL-2 | 2025-11-19 09:33 | 2025-11-19 16:30 | 6:57 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-11-21 14:36 | 2025-11-21 16:12 | 1:36 | S/O | Red Hot maintenance | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2025-11-09 07:33 | 2025-11-09 17:13 | 9:40 | S/O | Annual maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2025-11-10 07:34 | 2025-11-10 14:46 | 7:12 | S/O | Annual maintenance work completed. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 1 | 2025-11-15 08:28 | 2025-11-15 14:51 | 6:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2025-11-18 09:59 | 2025-11-18 15:24 | 5:25 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2025-11-19 08:39 | 2025-11-19 15:20 | 6:41 | S/O | Annual maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 2 | 2025-11-22 09:14 | 2025-11-22 17:05 | 7:51 | S/O | Annual maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2025-11-25 11:01 | 2025-11-25 11:59 | 0:58 | S/O | Maintenance at Aminbazar SS end | 0 | 0 | No interruption
|  |  | Total : | 1900-01-11 13:11 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
AKS 132/33kV | Khulshi | 2025-11-15 07:58 | 2025-11-15 13:05 | 5:07 | S/O | Khulshi line shutdown due to khulshi sub -station annual maintenance. | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-01 | 2025-11-19 08:26 | 2025-11-19 11:16 | 2:50 | S/O | CB-605B spring auxiliary contact changing work. | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-02 | 2025-11-19 11:20 | 2025-11-19 15:34 | 4:14 | S/O | CB-605B Spring Auxiliary Contact changing work. | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Kulshi Ckt | 2025-11-20 09:02 | 2025-11-20 11:25 | 2:23 | S/O | Bakalia Khulshi CKT Bus-A Breaker 632B S/D due to Spring Auxiliary Contanct Change by G to G project. | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Modern Ckt | 2025-11-26 08:52 | 2025-11-26 19:51 | 10:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Kulshi Ckt | 2025-11-27 07:31 | 2025-11-27 13:46 | 6:15 | S/O | Annual maintenance(Bay-Equipment) | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-02 | 2025-11-30 08:03 | 2025-11-30 16:18 | 8:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Baroaulia 132/33kV | Kulshi | 2025-11-18 07:05 | 2025-11-18 15:08 | 8:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | FENI Ckt-2 | 2025-11-09 10:57 | 2025-11-09 16:56 | 5:59 | S/O | Project Work; S/D taken by Feni 230kv GSS | 0 | 0 | No interruption
BSRM 230/33kV | FENI Ckt-2 | 2025-11-10 09:08 | 2025-11-10 18:01 | 8:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | FENI Ckt-2 | 2025-11-19 08:52 | 2025-11-19 11:32 | 2:40 | S/O | Work | 0 | 0 | No interruption
BSRM 230/33kV | FENI Ckt-2 | 2025-11-21 06:55 | 2025-11-21 19:35 | 12:40 | S/O | ESPNER Project Work | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2025-11-19 08:33 | 2025-11-19 16:57 | 8:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2025-11-20 08:58 | 2025-11-20 16:26 | 7:28 | S/O | Annual maintenance. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2025-11-22 09:02 | 2025-11-22 18:02 | 9:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2025-11-23 08:54 | 2025-11-23 17:56 | 9:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2025-11-24 08:51 | 2025-11-24 17:08 | 8:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2025-11-25 07:45 | 2025-11-25 17:25 | 9:40 | S/O | Annual maintenance. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2025-11-26 08:16 | 2025-11-26 16:55 | 8:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2025-11-27 08:10 | 2025-11-27 15:37 | 7:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2025-11-30 08:16 | 2025-11-30 17:35 | 9:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Julda Ckt. line | 2025-11-09 08:38 | 2025-11-09 16:38 | 8:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Julda Ckt. line | 2025-11-10 09:40 | 2025-11-10 16:56 | 7:16 | S/O | Annual bay maintenance at julda grid end. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2025-11-23 07:19 | 2025-11-23 17:34 | 10:15 | S/O | due to annual bay maintenance work | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Rampur Ckt-1 | 2025-11-24 08:07 | 2025-11-24 19:01 | 10:54 | S/O | due to annual bay maintenance work. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Rampur Ckt-2 | 2025-11-25 08:01 | 2025-11-25 15:42 | 7:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-11-10 09:20 | 2025-11-10 16:56 | 7:36 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2025-11-11 08:57 | 2025-11-11 13:38 | 4:41 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Shahmirpur 1 | 2025-11-12 08:04 | 2025-11-12 14:16 | 6:12 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Shahmirpur 2 | 2025-11-13 07:42 | 2025-11-13 13:31 | 5:49 | S/O | Annual Maintanance. | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-AKSPL Line | 2025-11-15 07:53 | 2025-11-15 13:05 | 5:12 | S/O | Annual Maintenance(Bay Equioment) | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Baraulia Circuit-2 | 2025-11-18 07:06 | 2025-11-18 15:09 | 8:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-1(Rampur) | 2025-11-20 07:45 | 2025-11-20 16:24 | 8:39 | S/O | Annual maintenance at bay. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-09 05:52 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2025-11-09 09:55 | 2025-11-09 16:10 | 6:15 | S/O | Annual Maintenance of Syl-Fen T line 2 Bay | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2025-11-10 09:30 | 2025-11-10 16:10 | 6:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Fen Ckt-II | 2025-11-22 08:36 | 2025-11-22 15:51 | 7:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Fen Ckt-II | 2025-11-23 09:07 | 2025-11-23 16:05 | 6:58 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-11-01 09:40 | 2025-11-01 16:02 | 6:22 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-11-02 08:52 | 2025-11-02 15:57 | 7:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-11-05 09:30 | 2025-11-05 13:54 | 4:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-11-06 10:42 | 2025-11-06 16:24 | 5:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-11-08 09:52 | 2025-11-08 16:25 | 6:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2025-11-15 07:14 | 2025-11-15 10:20 | 3:06 | S/O | Maintenance | 10 | 31 | Power interruption
Chandpur 132/33kV | 100MW(GT) Power Plant Incomer (T4) | 2025-11-19 11:17 | 2025-11-22 15:32 | 76:15 | S/O | Maintainace | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2025-11-24 07:07 | 2025-11-24 08:52 | 1:45 | S/O | MAINTAINACE | 6 | 10.5 | Power interruption
Chandpur 132/33kV | 33 kV T-2 section | 2025-11-24 07:08 | 2025-11-24 08:52 | 1:44 | S/O | MAINTAINACE | 4 | 6.9333 | Power interruption
Chhatak 132/33kV | Sunamganj 1 | 2025-11-01 10:48 | 2025-11-01 16:04 | 5:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chhatak 132/33kV | Sunamganj 1 | 2025-11-02 07:05 | 2025-11-02 15:14 | 8:09 | S/O | Annual Maintanance | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2025-11-08 07:06 | 2025-11-10 10:25 | 51:19 | S/O | Shutdown for annual maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2025-11-02 07:58 | 2025-11-02 15:38 | 7:40 | S/O | Annual Maintenance work Meghnaghat end S/S | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-11-02 08:30 | 2025-11-02 17:25 | 8:55 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2025-11-03 07:43 | 2025-11-03 16:37 | 8:54 | S/O | Annual maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-11-03 08:43 | 2025-11-03 17:00 | 8:17 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2025-11-05 08:20 | 2025-11-05 16:27 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-11-05 09:30 | 2025-11-05 16:59 | 7:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2025-11-07 07:30 | 2025-11-07 16:49 | 9:19 | S/O | Annual Maintenance works | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-11-13 08:20 | 2025-11-13 16:11 | 7:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-11-15 08:30 | 2025-11-15 16:46 | 8:16 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-11-16 09:09 | 2025-11-16 15:57 | 6:48 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2025-11-16 11:06 | 2025-11-16 17:15 | 6:09 | S/O | SCADA operation test by Muradnagar S/S end. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-11-17 09:20 | 2025-11-17 16:15 | 6:55 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2025-11-19 08:56 | 2025-11-19 16:30 | 7:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Daudkandi Ckt-2 | 2025-11-19 16:12 | 2025-11-19 16:48 | 0:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2025-11-20 08:20 | 2025-11-20 16:00 | 7:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2025-11-22 09:31 | 2025-11-22 16:14 | 6:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Kachua | 2025-11-24 07:29 | 2025-11-24 17:21 | 9:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Kachua | 2025-11-25 07:36 | 2025-11-25 17:29 | 9:53 | S/O | Annual maintenance. | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2025-11-13 14:50 | 2025-11-13 17:33 | 2:43 | S/O | Maintenance at Muradnagar Substation | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2025-11-17 10:49 | 2025-11-17 16:57 | 6:08 | S/O | Maintenance work at Muradnagar Substation | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-2 | 2025-11-20 09:53 | 2025-11-20 14:04 | 4:11 | S/O | Maintenance work at Muradnagar Substation | 0 | 0 | No interruption
Daudkandi 132/33kV | Cumilla(N)-1 | 2025-11-25 11:01 | 2025-11-25 12:00 | 0:59 | S/O | Maintenance work at Muradnagar substation | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2025-11-01 09:31 | 2025-11-01 15:26 | 5:55 | S/O | For Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2025-11-02 09:52 | 2025-11-02 18:43 | 8:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-3 | 2025-11-05 08:58 | 2025-11-05 15:08 | 6:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-1 | 2025-11-10 08:33 | 2025-11-10 17:45 | 9:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-1 | 2025-11-11 08:29 | 2025-11-11 17:04 | 8:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-1 | 2025-11-12 08:31 | 2025-11-12 14:55 | 6:24 | S/O | Kulaura substation end annual maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2025-11-18 08:51 | 2025-11-18 17:33 | 8:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2025-11-19 08:37 | 2025-11-19 16:11 | 7:34 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2025-11-22 08:22 | 2025-11-22 15:51 | 7:29 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2025-11-23 08:52 | 2025-11-23 16:08 | 7:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2025-11-25 08:42 | 2025-11-25 16:09 | 7:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2025-11-26 08:37 | 2025-11-26 15:59 | 7:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2025-11-27 09:06 | 2025-11-27 17:19 | 8:13 | S/O | annual maintenance | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla South CKT | 2025-11-24 07:41 | 2025-11-24 17:22 | 9:41 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla South CKT | 2025-11-25 07:37 | 2025-11-25 17:30 | 9:53 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-1 | 2025-11-13 12:20 | 2025-11-13 13:10 | 0:50 | S/O | Test perform at Muradnagar end. | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-1 | 2025-11-17 14:10 | 2025-11-17 15:46 | 1:36 | S/O | Shutdown taken by Muradnagar for Scada work | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-2 | 2025-11-17 15:55 | 2025-11-17 16:33 | 0:38 | S/O | shutdown taken by muradnagar for scada work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-18 21:35 |  | Unserved Energy: |  | 48.4333
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-11-15 09:02 | 2025-11-15 16:54 | 7:52 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-11-16 08:38 | 2025-11-16 15:50 | 7:12 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 2 | 2025-11-18 08:55 | 2025-11-18 16:36 | 7:41 | S/O | Yearly maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-11-30 08:06 | 2025-11-30 23:08 | 15:02 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-2 | 2025-11-05 06:23 | 2025-11-13 18:05 | 203:42 | S/O | Barishal(N) -Patuakhali 230 kv line conductor stringing purpose. | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2025-11-15 08:48 | 2025-11-15 17:54 | 9:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2025-11-18 09:56 | 2025-11-18 19:31 | 9:35 | S/O | Barishal (N) -Patuakhali 230 kv line conductor stringing purpose Gopalgonj ckt-1 shutdown. | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-2 | 2025-11-18 09:56 | 2025-11-18 19:34 | 9:38 | S/O | Barishal (N) -Patuakhali 230 kv line conductor stringing purpose Gopalgonj ckt-2 shutdown. | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2025-11-26 11:03 | 2025-11-26 15:45 | 4:42 | S/O | Maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2025-11-27 08:52 | 2025-11-27 15:09 | 6:17 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2025-11-28 08:22 | 2025-11-28 15:50 | 7:28 | S/O | Shutdown taken by ALDC | 0 | 0 | No interruption
Bhandaria 132/33kV | Bagerhat (L3) | 2025-11-30 08:08 | 2025-11-30 23:06 | 14:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-1 | 2025-11-05 08:22 | 2025-11-05 10:37 | 2:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2025-11-05 10:38 | 2025-11-05 12:31 | 1:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | Out Door Capacitor bank | 2025-11-15 09:09 | 2025-11-15 14:00 | 4:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV 50MW Power Station ckt-1 | 2025-11-29 08:44 | 2025-11-29 15:25 | 6:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV 50MW Power Station ckt-1 | 2025-11-30 08:53 | 2025-11-30 15:24 | 6:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-02 | 2025-11-05 06:35 | 2025-11-13 18:06 | 203:31 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-1 | 2025-11-05 08:34 | 2025-11-05 10:37 | 2:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2025-11-05 10:38 | 2025-11-05 12:31 | 1:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-2 | 2025-11-05 12:40 | 2025-11-05 14:07 | 1:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2025-11-15 08:47 | 2025-11-15 17:53 | 9:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-11-15 09:23 | 2025-11-15 17:39 | 8:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-11-16 07:48 | 2025-11-16 18:05 | 10:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-11-17 08:26 | 2025-11-17 18:07 | 9:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-11-18 08:46 | 2025-11-18 17:58 | 9:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2025-11-18 09:54 | 2025-11-18 19:33 | 9:39 | S/O | G2G Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-02 | 2025-11-18 09:55 | 2025-11-18 19:34 | 9:39 | S/O | G2G Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2025-11-21 06:19 | 2025-11-21 15:42 | 9:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-1 | 2025-11-21 17:01 | 2025-11-21 17:32 | 0:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2025-11-22 08:36 | 2025-11-22 17:31 | 8:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Amtoli Ckt-2 | 2025-11-22 11:20 | 2025-11-22 16:16 | 4:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2025-11-23 08:17 | 2025-11-23 16:39 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2025-11-24 08:14 | 2025-11-24 15:59 | 7:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2025-11-25 09:09 | 2025-11-25 16:52 | 7:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-11-26 08:44 | 2025-11-26 16:29 | 7:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2025-11-26 10:03 | 2025-11-26 15:46 | 5:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2025-11-27 08:52 | 2025-11-27 15:09 | 6:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-11-27 09:10 | 2025-11-27 16:41 | 7:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2025-11-28 08:23 | 2025-11-28 15:51 | 7:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2025-11-14 08:53 | 2025-11-14 15:38 | 6:45 | S/O | 132KV South - 1, R-phase jack Bus Maintenance | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2025-11-14 08:53 | 2025-11-14 15:38 | 6:45 | S/O | 132KV South - 1, R-phase jack Bus Maintenance. | 0 | 0 | No interruption
Khulna (C) | North-WestCkt-1 | 2025-11-14 08:56 | 2025-11-14 13:29 | 4:33 | S/O | 132KV South - 1, R-phase jack Bus Maintenance. | 0 | 0 | No interruption
Khulna (C) | North- West Ckt-2 | 2025-11-14 08:56 | 2025-11-14 13:29 | 4:33 | S/O | 132KV South - 1, R-phase jack Bus Maintenance. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-14 09:17 | 2025-11-14 13:59 | 4:42 | S/O | 132KV South - 1, R-phase jack Bus Maintenance. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -2 | 2025-11-14 09:18 | 2025-11-14 13:22 | 4:04 | S/O | 132KV South - 1, R-phase jack Bus Maintenance. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -2 | 2025-11-20 07:45 | 2025-11-20 08:59 | 1:14 | S/O | movement of filing ring | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-21 07:30 | 2025-11-21 16:58 | 9:28 | S/O | shutdown for project work. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-21 07:30 | 2025-11-21 16:58 | 9:28 | S/O | shutdown for project work. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-22 06:23 | 2025-11-22 16:46 | 10:23 | S/O | For project work. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-23 06:18 | 2025-11-23 16:50 | 10:32 | S/O | Work for project | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-24 06:27 | 2025-11-24 16:26 | 9:59 | S/O | For project work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-25 08:19 | 2025-11-25 16:54 | 8:35 | S/O | Maintenance work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-11-26 08:33 | 2025-11-26 16:23 | 7:50 | S/O | for loop change | 0 | 0 | No interruption
Khulna (C) | North-WestCkt-1 | 2025-11-29 08:43 | 2025-11-29 15:38 | 6:55 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Khulna (C) | North- West Ckt-2 | 2025-11-30 08:57 | 2025-11-30 15:45 | 6:48 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-11-14 09:18 | 2025-11-14 13:58 | 4:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2025-11-14 09:19 | 2025-11-14 13:22 | 4:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2025-11-20 07:47 | 2025-11-20 08:58 | 1:11 | S/O | Project work Central ss end. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-11-21 07:29 | 2025-11-21 16:56 | 9:27 | S/O | Project work at central ss end. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-11-22 06:24 | 2025-11-22 16:46 | 10:22 | S/O | None | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2025-11-22 09:19 | 2025-11-22 15:35 | 6:16 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-11-23 06:14 | 2025-11-23 16:50 | 10:36 | S/O | Project Work at Central SS end. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-11-24 06:27 | 2025-11-24 16:25 | 9:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-11-25 08:20 | 2025-11-25 16:54 | 8:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2025-11-25 08:55 | 2025-11-25 14:49 | 5:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-11-26 08:33 | 2025-11-26 16:22 | 7:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-2 | 2025-11-28 06:27 | 2025-11-28 17:33 | 11:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-1 | 2025-11-28 06:33 | 2025-11-28 17:33 | 11:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2025-11-29 09:23 | 2025-11-29 11:28 | 2:05 | S/O | red hot | 0 | 0 | No interruption
|  |  | Total : | 1900-02-05 10:02 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2025-11-12 09:19 | 2025-11-12 16:50 | 7:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2025-11-19 09:08 | 2025-11-19 19:11 | 10:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2025-11-20 09:40 | 2025-11-20 17:08 | 7:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi-2 | 2025-11-22 08:53 | 2025-11-22 15:59 | 7:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi-2 | 2025-11-23 09:20 | 2025-11-23 16:48 | 7:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV | Auxiliary X-Former-01(Turtiary) | 2025-11-24 08:48 | 2025-11-24 19:41 | 10:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhangura 132/33kV | Bhangura-Bhagabari ckt-1 | 2025-11-01 10:12 | 2025-11-01 18:10 | 7:58 | S/O | OFCl project shutdown from Bhagabari | 12 | 95.6 | Power interruption
Bheramara 230/132kV | Ishurdi 1 | 2025-11-02 09:10 | 2025-11-02 16:01 | 6:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 2 | 2025-11-03 08:29 | 2025-11-03 16:27 | 7:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV | HVDC 1 | 2025-11-09 08:33 | 2025-11-09 16:27 | 7:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV | HVDC 2 | 2025-11-10 08:42 | 2025-11-10 17:22 | 8:40 | S/O | Annual Maintaince | 0 | 0 | No interruption
Bheramara 230/132kV | Rajbari 2 | 2025-11-17 08:52 | 2025-11-17 17:39 | 8:47 | S/O | Annual Maintaince | 0 | 0 | No interruption
Bheramara 230/132kV | Rajbari 1 | 2025-11-17 09:10 | 2025-11-17 17:40 | 8:30 | S/O | Annual Maintaince | 0 | 0 | No interruption
Bheramara 230/132kV | Rajbari 1 | 2025-11-18 08:16 | 2025-11-18 15:49 | 7:33 | S/O | Annual Maintaince | 0 | 0 | No interruption
Bheramara 230/132kV | Rajbari 2 | 2025-11-18 08:20 | 2025-11-18 15:50 | 7:30 | S/O | Annual Maintaince | 0 | 0 | No interruption
BIPTC | Jhenaidah 1 | 2025-11-01 08:26 | 2025-11-01 17:16 | 8:50 | S/O | Annual Maintaince | 0 | 0 | No interruption
BIPTC | Jhenaidah 1 | 2025-11-02 09:48 | 2025-11-02 16:48 | 7:00 | S/O | Annual Maintaince | 0 | 0 | No interruption
BIPTC | Jhenaidah 2 | 2025-11-04 09:07 | 2025-11-04 16:56 | 7:49 | S/O | Annual Maintaince | 0 | 0 | No interruption
BIPTC | Jhenaidah 2 | 2025-11-06 08:35 | 2025-11-06 18:00 | 9:25 | S/O | Annual Maintaince | 0 | 0 | No interruption
BIPTC | Bheramara-1 | 2025-11-09 08:33 | 2025-11-09 16:29 | 7:56 | S/O | Annual Maintaince | 0 | 0 | No interruption
BIPTC | Bheramara-2 | 2025-11-10 09:11 | 2025-11-10 17:21 | 8:10 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -1 | 2025-11-02 09:03 | 2025-11-02 16:01 | 6:58 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-11-03 08:28 | 2025-11-03 16:27 | 7:59 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Baghabari Line | 2025-11-03 10:50 | 2025-11-16 11:50 | 313:00 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2025-11-13 07:31 | 2025-11-13 13:32 | 6:01 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 1 | 2025-11-12 09:21 | 2025-11-12 16:52 | 7:31 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-11-13 08:47 | 2025-11-13 15:28 | 6:41 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 1 | 2025-11-19 09:08 | 2025-11-19 19:11 | 10:03 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 1 | 2025-11-20 09:30 | 2025-11-20 17:07 | 7:37 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 2 | 2025-11-22 08:33 | 2025-11-22 15:57 | 7:24 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 2 | 2025-11-23 09:20 | 2025-11-23 16:47 | 7:27 | S/O | Annual Maintaince | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-11-27 10:13 | 2025-11-27 17:59 | 7:46 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2025-11-22 09:46 | 2025-11-22 15:49 | 6:03 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2025-11-23 09:03 | 2025-11-23 18:01 | 8:58 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2025-11-24 08:52 | 2025-11-24 16:30 | 7:38 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2025-11-25 08:57 | 2025-11-25 17:37 | 8:40 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2025-11-26 08:54 | 2025-11-26 14:31 | 5:37 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2025-11-27 09:28 | 2025-11-27 13:49 | 4:21 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura, 132kV Circuit-1(L7) | 2025-11-15 08:40 | 2025-11-15 16:28 | 7:48 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura, 132kV Circuit-1(L7) | 2025-11-16 09:02 | 2025-11-16 16:15 | 7:13 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura, 132kV Circuit-1(L7) | 2025-11-17 09:17 | 2025-11-17 16:02 | 6:45 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura 132kV Circuit-2(L6) | 2025-11-19 09:00 | 2025-11-19 15:44 | 6:44 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura 132kV Circuit-2(L6) | 2025-11-20 09:02 | 2025-11-20 16:00 | 6:58 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah1-Jhenaidah2, 132kV Circuit-1(L4) | 2025-11-29 09:03 | 2025-11-29 15:43 | 6:40 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-1 | 2025-11-01 08:27 | 2025-11-01 17:15 | 8:48 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-1 | 2025-11-02 09:31 | 2025-11-02 16:48 | 7:17 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-2 | 2025-11-04 08:55 | 2025-11-04 16:53 | 7:58 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-2 | 2025-11-06 08:22 | 2025-11-06 18:01 | 9:39 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2025-11-22 09:47 | 2025-11-22 15:49 | 6:02 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2025-11-23 09:03 | 2025-11-23 18:00 | 8:57 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2025-11-24 08:54 | 2025-11-24 16:30 | 7:36 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2025-11-25 08:58 | 2025-11-25 17:37 | 8:39 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2025-11-26 08:54 | 2025-11-26 14:30 | 5:36 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2025-11-27 09:29 | 2025-11-27 13:48 | 4:19 | S/O | Annual Maintaince | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Jhenaidah (Old) Ckt-1 | 2025-11-29 09:02 | 2025-11-29 15:43 | 6:41 | S/O | Annual Maintaince | 0 | 0 | No interruption
|  |  | Total : | 1900-01-29 04:44 |  | Unserved Energy: |  | 95.6
Bogura Grid Circle :
Amnura 132/33kV | Amnura - 100MW PPP | 2025-11-05 08:20 | 2025-11-05 16:24 | 8:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV | Amnura - 100MW PPP | 2025-11-06 08:16 | 2025-11-06 14:44 | 6:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV | Amnura - Chapai Nawabganj | 2025-11-07 07:02 | 2025-11-07 14:38 | 7:36 | S/O | Shutdown taken by Chapainawabganj SS | 0 | 0 | No interruption
Amnura 132/33kV | Amnura - Rajshahi | 2025-11-22 08:44 | 2025-11-22 17:14 | 8:30 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Amnura 132/33kV | Amnura - 100MW PPP | 2025-11-22 08:44 | 2025-11-22 17:15 | 8:31 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Amnura 132/33kV | Amnura - Chapai Nawabganj | 2025-11-22 09:02 | 2025-11-22 16:43 | 7:41 | S/O | Annual Maintenance, Clearance ALDC, Bogura | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-11-15 08:36 | 2025-11-15 16:31 | 7:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-11-16 08:22 | 2025-11-16 16:05 | 7:43 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt1 | 2025-11-17 08:17 | 2025-11-17 16:22 | 8:05 | S/O | annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-11-18 08:22 | 2025-11-18 16:06 | 7:44 | S/O | Annual maintenance for dead line cheeking. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-11-19 08:10 | 2025-11-19 12:44 | 4:34 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2025-11-19 12:58 | 2025-11-19 16:33 | 3:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-11-20 08:32 | 2025-11-20 16:01 | 7:29 | S/O | Dead line cheeking | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2025-11-21 10:20 | 2025-11-21 10:20 | 0:00 | S/O | reconductoring work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | PS 230 KV Ckt2 | 2025-11-30 09:00 | 2025-11-30 16:06 | 7:06 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-1 | 2025-11-04 08:25 | 2025-11-04 15:34 | 7:09 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-1 | 2025-11-05 08:43 | 2025-11-05 16:13 | 7:30 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-1 | 2025-11-06 08:38 | 2025-11-06 15:25 | 6:47 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-2 | 2025-11-08 08:36 | 2025-11-08 16:05 | 7:29 | S/O | annual maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-2 | 2025-11-09 08:36 | 2025-11-09 13:13 | 4:37 | S/O | Annual maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-2 | 2025-11-10 08:49 | 2025-11-10 14:31 | 5:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-1 | 2025-11-11 08:23 | 2025-11-11 17:05 | 8:42 | S/O | Anual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-1 | 2025-11-12 08:44 | 2025-11-12 15:54 | 7:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-1 | 2025-11-13 08:47 | 2025-11-13 12:59 | 4:12 | S/O | Anual Maintenance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-2 | 2025-11-15 08:36 | 2025-11-15 17:05 | 8:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-2 | 2025-11-16 08:40 | 2025-11-16 15:17 | 6:37 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-2 | 2025-11-17 08:18 | 2025-11-17 15:01 | 6:43 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-1 | 2025-11-21 09:30 | 2025-11-21 15:28 | 5:58 | S/O | LA Change | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-1 | 2025-11-04 08:25 | 2025-11-04 15:34 | 7:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-1 | 2025-11-05 08:44 | 2025-11-05 16:13 | 7:29 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-1 | 2025-11-06 08:38 | 2025-11-06 15:27 | 6:49 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-2 | 2025-11-08 08:35 | 2025-11-08 16:05 | 7:30 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-2 | 2025-11-09 08:36 | 2025-11-09 13:12 | 4:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-2 | 2025-11-10 08:49 | 2025-11-10 14:33 | 5:44 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-1 | 2025-11-15 08:51 | 2025-11-15 15:49 | 6:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | Bogura (W) CKT-2 | 2025-11-17 08:31 | 2025-11-17 15:39 | 7:08 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-1 | 2025-11-21 09:30 | 2025-11-21 15:27 | 5:57 | S/O | Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-11-22 08:21 | 2025-11-22 19:44 | 11:23 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-11-23 08:15 | 2025-11-23 16:53 | 8:38 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-11-24 08:25 | 2025-11-24 16:34 | 8:09 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-11-25 08:28 | 2025-11-25 16:55 | 8:27 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-11-26 08:30 | 2025-11-26 15:27 | 6:57 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-11-27 08:41 | 2025-11-27 15:53 | 7:12 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-11-03 09:13 | 2025-11-03 16:01 | 6:48 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2025-11-04 09:02 | 2025-11-04 16:46 | 7:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-11-08 10:38 | 2025-11-08 16:46 | 6:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-11-10 09:25 | 2025-11-10 15:50 | 6:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-11-13 13:00 | 2025-11-30 12:20 | 407:20 | S/O | Solar aviation light, and ball setting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-11-13 13:00 | 2025-11-30 12:20 | 407:20 | S/O | Solar aviation light, and ball setting | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-1 | 2025-11-15 08:51 | 2025-11-15 15:48 | 6:57 | S/O | Annual Maintenances. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura 230 kV Ckt-2 | 2025-11-17 08:32 | 2025-11-17 15:39 | 7:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-11-27 12:52 | 2025-11-27 13:43 | 0:51 | S/O | Control PNL DC-1 and DC-2 Rectification work | 0 | 0 | No interruption
Chapai 132/33kV | Chapai-Rajshahi | 2025-11-07 07:14 | 2025-11-07 15:34 | 8:20 | S/O | Tr-01 bay upgrading. | 0 | 0 | No interruption
Chapai 132/33kV | Chapai-Amnura | 2025-11-07 07:14 | 2025-11-07 14:01 | 6:47 | S/O | Tr-01 bay upgrading | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2025-11-07 07:16 | 2025-11-07 12:19 | 5:03 | S/O | Tr-01 bay upgrading | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 2 | 2025-11-07 07:20 | 2025-11-07 16:04 | 8:44 | S/O | Tr-01 bay upgrading | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2025-11-15 08:47 | 2025-11-15 16:16 | 7:29 | S/O | Annual maintenance | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2025-11-16 08:20 | 2025-11-16 15:34 | 7:14 | S/O | Sheduled S/D | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 2 | 2025-11-18 08:17 | 2025-11-18 16:38 | 8:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 2 | 2025-11-19 08:36 | 2025-11-19 16:06 | 7:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Chapai 132/33kV | Chapai-Amnura | 2025-11-22 09:00 | 2025-11-22 16:42 | 7:42 | S/O | S/D Taken by Amnura grid. | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-01 | 2025-11-02 08:27 | 2025-11-02 17:43 | 9:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-01 | 2025-11-03 08:20 | 2025-11-03 17:50 | 9:30 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-01 | 2025-11-04 08:42 | 2025-11-04 17:57 | 9:15 | S/O | Annual maintenance work | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-02 | 2025-11-05 14:56 | 2025-11-05 16:31 | 1:35 | S/O | Anual Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-02 | 2025-11-06 08:25 | 2025-11-06 17:39 | 9:14 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-02 | 2025-11-08 08:38 | 2025-11-08 16:59 | 8:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-2 | 2025-11-29 07:40 | 2025-11-29 16:43 | 9:03 | S/O | Annul maintenance | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-1 | 2025-11-29 07:41 | 2025-11-29 15:58 | 8:17 | S/O | Annul maintenance | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-1 | 2025-11-29 07:41 | 2025-11-29 15:58 | 8:17 | S/O | Annul maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-02-21 22:50 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-06-30 06:55 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:November 2025
| Area | Previous Month (October' 2025) |  |  |  | Current Month (November '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 10 | 19 | 97 | 126 | 11 | 9 | 197 | 217
2 | Dhaka (South) Grid Circle. | 13 | 8 | 49 | 70 | 23 | 2 | 120 | 145
3 | Chattogram Grid Circle. | 13 | 19 | 81 | 113 | 6 | 12 | 62 | 80
4 | Cumilla Grid Circle. | 21 | 18 | 106 | 145 | 15 | 11 | 154 | 180
5 | Khulna Grid Circle. | 14 | 10 | 118 | 142 | 9 | 12 | 125 | 146
6 | HVDC Grid Circle | 15 | 9 | 33 | 57 | 11 | 10 | 90 | 111
7 | Bogura Grid Circle. | 29 | 21 | 100 | 150 | 10 | 10 | 153 | 173
8 | Others
9 | Total | 115 | 104 | 584 | 803 | 85 | 66 | 901 | 1052
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:November 2025
| Area | Previous Month (October' 2025) |  |  |  | Current Month (November '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 151.43 | 281.03 | 1099.75 | 1532.21 | 382.85 | 98 | 383.48 | 864.33
2 | Dhaka (South) Grid Circle. | 98.9 | 6 | 203.8 | 308.7 | 161.09 | - | 2438.83 | 2599.92
3 | Chattogram Grid Circle. | 157 | 190.37 | 855.38 | 1202.75 | 52 | - | 421.58 | 473.58
4 | Cumilla Grid Circle. | 244.64 | 238.5 | 842.69 | 1325.83 | 66.83 | 85.5 | 743.56 | 895.89
5 | Khulna Grid Circle. | 23 | 87.01 | 708.55 | 818.56 | 44.42 | 279.83 | 512.27 | 836.52
6 | HVDC Grid Circle | 339.35 | 81.98 | 2100.05 | 2521.38 | 3.45 | 127.23 | 189.88 | 320.56
7 | Bogura Grid Circle. | 101.77 | 415.31 | 633.88 | 1150.96 | 53.08 | 33.42 | 520.67 | 607.17
8 | Others
9 | Total | 1116.09 | 1300.2 | 6444.1 | 8860.39 | 763.72 | 623.98 | 5210.27 | 6597.97
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:November 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 7 | 5 | 12 | 4 | 1 | 7 | 686.7
2 | Dhaka (South) | 5031.6 | 8 | 11 | 19 | 6 | 2 | 11 | 2596.81
3 | Chattogram | 2042 | 4 | 4 | 8 | 3 | 1 | 4 | 474
4 | Khulna | 2434 | 7 | 10 | 17 | 5 |  | 12 | 826.62
5 | HVDC | 5954.3 | 2 | 2 | 4 | 1 |  | 3 | 136.47
6 | Bogura | 3145.6 | 12 | 4 | 16 | 7 | 4 | 5 | 607.17
7 | Cumilla | 2981 | 11 | 10 | 21 | 7 | 1 | 13 | 847.46
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 6175.23
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.98%
4 | Khulna | 99.96%
5 | HVDC | 99.99%
6 | Bogura | 99.98%
7 | Cumilla | 99.96% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:November 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 | - | 2 | 1 | - | 1 | 177.6333
2 | Dhaka (South) | 990.29 | - | 1 |  | 1 | 1 | - |  | 3.1167
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | 1 |  | 1 | 1 |  |  | 9.9
5 | HVDC | 1325 | - | 1 | 1 | 2 | - | - | 2 | 184.1
6 | Bogura | 1803.3 | - | - | - | - | - | - | - | -
7 | Cumilla | 1648.16 | - |  | 3 | 3 |  |  | 3 | 48.43
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 423.18
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 100%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 100%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:November 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm | [6 empty] | 2:50 | 0:27
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. |  | 1:23 | 5:54
2025-11-01 | 9 | - | 5 | 7 hr 2 min | 2 | 6 hr 21 min | [7 empty] | 0:32
1:30
0:47
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:November 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Ghatail 132/33kV | 1 | 0.015972 | 6.9
Mirpur 132/33kV | 1 | 0.1375 | 184.8
Mirzapur 132/33kV | 1 | 0.022222 | 6.4
Sreepur 230/132/33kV | 2 | 0:14 | 7.12
Tangail 132/33kV | 2 | 3:08 | 98
Aminbazar 400/230/132kV | 2 | 1:56 | 141.1333
Aminbazar 400/230/132kV | 1 | 0:30 | 36.5
Bhaluka 132/33kV | 2 | 14:54 | 197.4
Dhamrai 132/33kV | 1 | 0.11597 | 167
Mirzapur 132/33kV | 2 | 0.056944 | 19.08
Hasnabad 132/33kV | 1 | 0.056944 | 34.1667
Nawabganj 132/33kV | 4 | 0.046528 | 13.64
Sonargaon 132/33kV | 3 | 2:00 | 110.17
Keranigonj 230/132/33kV | 1 | 0:17 | 3.1167
Bhulta 132/33kV | 3 | 0.75347 | 1186.83
Ghorashal 230kV | 2 | 0.7625 | 823.5
Nawabganj 132/33kV | 2 | 342:00 | 158.58
Sonargaon 132/33kV | 3 | 4:33 | 193.85
Srinagar 132/33kV | 1 | 10:52 | 76.0667
Coxsbazar 132/33kV | 2 | 0:54 | 29.6
Dohazari 132/33kV | 1 | 0:20 | 16
Kalurghat 132/33kV | 1 | 0:24 | 7.2
Bakulia 132/33kV | 1 | 9:01 | 45.0833
Baroaulia 132/33kV | 2 | 17:56 | 319.33
Dohazari 132/33kV | 1 | 1:38 | 57.1667
Chandina 132/33kV | 2 | ;97:51 | 29.38
Chhatak 132/33kV | 2 | 0:10 | 1.23
Chowmuhani 132/33kV | 2 | 0:54 | 25.2
Cumilla(S) 132/33kV | 1 | 0:25 | 6.6667
Kulaura 132/33kV | 1 | 0:15 | 0.75
Shahjibazar 132/33kV | 2 | 0:12 | 3.6
Chowmuhani 132/33kV | 1 | 1:38 | 57.1667
Lakshmipur 132/33kV | 1 | 2:50 | 28.3333
Brahmanbaria 132/33kV | 1 | 7:09 | 143
Chandina 132/33kV | 2 | 0:10 | 1
Chandpur 132/33kV | 1 | 1:45 | 10.5
Chauddagram 132/33kV | 4 | 1:52 | 56
Kulaura 132/33kV | 2 | 4:18 | 125.43
Muradnagar 132/33kV | 1 | 1:05 | 10.8333
Sunamganj 132/33kV | 4 | 16:25 | 348.37
Chandpur 132/33kV | 3 | 6:35 | 48.43
Barishal 230/132kV | 2 | 0:50 | 16.67
Khulna (C) | 3 | 2:51 | 27.75
Borhanuddin 230/33kV | 1 | 2:18 | 142.6
Gopalganj 132/33kV | 1 | 6:22 | 127.3333
Barishal 132/33kV | 1 | 0:27 | 9.9
Bagerhat 132/33kV | 1 | 1:13 | 27.9833
Barishal 132/33kV | 2 | 0:33 | 21.83
Barishal 230/132kV | 1 | 11:28 | 91.7333
Gopalganj 132/33kV | 2 | 17:03 | 173.17
Narail 132/33kV | 2 | 4:33 | 91
Noapara 132/33kV | 1 | 1:31 | 19.7167
Rajbari 132/33kV | 1 | 8:41 | 86.8333
Bheramara(GK) 132/33kV | 1 | 0:23 | 3.45
Ishurdi 132/33kV | 1 | 1:23 | 38.7333
Bhangura 132/33kV | 1 | 5:54 | 88.5
Magura 132/33kV | 1 | 6:51 | 82.2
Pabna 132/33kV | 1 | 2:25 | 12.0833
Bhangura 132/33kV | 1 | 7:58 | 95.6
Chapai 132/33kV | 1 | 1:19 | 19.75
Jaldhaka 132/33kV | 2 | 0:36 | 11.4
Niamatpur 132/33kV | 2 | 0:23 | 4.6
Purbasadipur 132/33kV | 1 | 0:26 | 17.3333
Amnura 132/33kV | 4 | 2:58 | 12.27
Natore 132/33kV | 1 | 0:47 | 21.15
Barapukuria 230/132/33kV | 1 | 8:54 | 311.5
Chapai 132/33kV | 1 | 4:59 | 189.3667
Saidpur 132/33kV | 1 | 3:15 | 19.8
| 111 | 609:55 | 6598.78
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: November 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 15 | 2025-11-22 19:30
2 | AKSML | 167 | 2025-11-07 09:00
3 | Aftabnagar | 36 | 2025-11-01 00:00
4 | Agargaon | 122 | 2025-11-05 13:00
5 | Agrabad | 102 | 2025-11-02 18:00
6 | Amnura | 22 | 2025-11-17 18:00
7 | Ashuganj | 91 | 2025-11-03 15:00
8 | BSRM | 211 | 2025-11-28 18:00
9 | Bagerhat | 80 | 2025-11-01 18:00
10 | Bajitpur | 88 | 2025-11-01 18:00
11 | Bakulia | 96 | 2025-11-06 12:00
12 | Banani | 48 | 2025-11-09 13:00
13 | Bangabhaban | 25 | 2025-11-02 10:00
14 | Barapukuria | 54 | 2025-11-05 18:30
15 | Barguna | 18 | 2025-11-04 20:00
16 | Barishal | 120 | 2025-11-01 18:00
17 | Barishal-230 | 98 | 2025-11-05 18:00
18 | Baroaulia | 69 | 2025-11-02 17:00
19 | Baroirhat | 72 | 2025-11-01 18:00
20 | Bashundhara | 199 | 2025-11-06 18:00
21 | BashundharaCement | 14 | 2025-11-02 15:00
22 | Beanibazar | 78 | 2025-11-04 18:00
23 | Benapole | 58 | 2025-11-01 18:00
24 | Bhaluka | 144 | 2025-11-06 18:00
25 | Bhandaria | 60 | 2025-11-03 02:00
26 | Bhangura | 42 | 2025-11-01 19:00
27 | Bheramara(GK) | 56 | 2025-11-01 18:30
28 | Bhulta | 232 | 2025-11-05 22:00
29 | Bog-Sherpur | 60 | 2025-11-17 18:00
30 | Bogura | 147 | 2025-11-05 18:30
31 | Borhanuddin | 93 | 2025-11-01 00:00
32 | Brahmanbaria | 133 | 2025-11-04 21:00
33 | Cantonment | 158 | 2025-11-01 13:00
34 | Chandina | 18.64 | 2025-11-11 22:00
35 | Chandpur | 78 | 2025-11-01 00:00
36 | Chandraghona | 38 | 2025-11-01 18:00
37 | Chapai | 54 | 2025-11-01 18:00
38 | Charsaidpur | 39 | 2025-11-12 12:00
39 | Chauddagram | 70 | 2025-11-01 22:00
40 | Chhatak | 38 | 2025-11-01 00:00
41 | Chowmuhani | 169 | 2025-11-01 18:00
42 | Chuadanga | 104 | 2025-11-01 18:00
43 | Coxsbazar | 144 | 2025-11-01 20:00
44 | Cumilla(N) | 150 | 2025-11-05 01:00
45 | Cumilla(S) | 152 | 2025-11-01 18:00
46 | Daganbhuiyan | 0 | 2025-11-01 03:00
47 | Daudkandi | 145 | 2025-11-01 00:00
48 | DhakaUniversity | 88 | 2025-11-05 13:00
49 | Dhamrai | 122 | 2025-11-05 18:00
50 | Dhanmondi | 131 | 2025-11-01 13:00
51 | Dohazari | 105 | 2025-11-01 19:30
52 | Faridpur | 148 | 2025-11-05 19:00
53 | Fatullah | 116 | 2025-11-01 16:00
54 | Fenchuganj | 40 | 2025-11-01 00:00
55 | Feni | 116 | 2025-11-01 18:00
56 | GPH | 98 | 2025-11-17 08:00
57 | Ghatail | 78 | 2025-11-08 18:00
58 | Ghorashal | 0 | 2025-11-01 00:00
59 | Ghorashal-230 | 100 | 2025-11-07 00:00
60 | Goalpara | 36 | 2025-11-01 00:00
61 | Gollamari | 86 | 2025-11-05 18:00
62 | Gopalganj | 104 | 2025-11-05 18:00
63 | Gulshan | 120 | 2025-11-06 13:00
64 | Halishahar | 75 | 2025-11-01 09:00
65 | HaripurSBU | 168 | 2025-11-06 12:00
66 | Hasnabad | 94 | 2025-11-02 19:30
67 | Hathazari | 90 | 2025-11-01 18:00
68 | Ishurdi | 70 | 2025-11-01 18:00
69 | Jaldhaka | 70 | 2025-11-05 18:00
70 | Jamalpur | 99 | 2025-11-03 18:00
71 | Jashore | 134 | 2025-11-01 18:30
72 | Jhenaidah | 125 | 2025-11-01 18:00
73 | Joydebpur | 158 | 2025-11-05 18:00
74 | Joypurhat | 49 | 2025-11-29 18:00
75 | Juldah | 17 | 2025-11-04 15:00
76 | KSRM | 40 | 2025-11-05 23:00
77 | Kabirpur | 259 | 2025-11-05 15:00
78 | Kachua | 89 | 2025-11-01 18:00
79 | Kallyanpur | 105 | 2025-11-05 19:00
80 | Kalurghat | 54 | 2025-11-02 16:00
81 | Kamrangirchar | 76 | 2025-11-01 16:00
82 | Kaptai | N/A | N/A
83 | Kasba | 35 | 2025-11-04 21:00
84 | Kazla | 111 | 2025-11-05 18:30
85 | Keranigonj | 86 | 2025-11-06 18:30
86 | Khagrachori | 32 | 2025-11-01 18:00
87 | Khulna | 77 | 2025-11-09 13:00
88 | Khulshi | 193 | 2025-11-01 18:00
89 | Kishoreganj | 119 | 2025-11-01 00:00
90 | Kodda | 311 | 2025-11-05 12:00
91 | Kulaura | 49 | 2025-11-04 19:30
92 | Kurigram | 56 | 2025-11-05 18:00
93 | Kushtia | 146 | 2025-11-01 18:00
94 | Laksam | 34 | 2025-11-01 22:00
95 | Lakshmipur | 33 | 2025-11-01 20:00
96 | Lalbag | 64 | 2025-11-12 13:00
97 | Lalmonirhat | 52 | 2025-11-05 18:00
98 | MI_Cement | 17.9 | 2025-11-21 02:00
99 | Madanganj | 46 | 2025-11-14 17:00
100 | Madaripur | 99 | 2025-11-01 00:00
101 | Madartek | 94 | 2025-11-01 00:00
102 | Madunaghat | 56 | 2025-11-02 18:00
103 | Magura | 63 | 2025-11-01 18:00
104 | Mahasthangarh | 62 | 2025-11-05 18:00
105 | Maijdee | 38 | 2025-11-01 19:30
106 | Manikganj | 120 | 2025-11-05 18:30
107 | Maniknagar | 66 | 2025-11-06 13:00
108 | Matarbari | 53 | 2025-11-01 18:00
109 | Matuail | 74 | 2025-11-08 15:00
110 | Metrorail_Motijheel | 40 | 2025-11-04 09:00
111 | Metrorail_Uttara | 13 | 2025-11-02 18:00
112 | Millgate | 128 | 2025-11-05 12:00
113 | Mirpur | 133 | 2025-11-01 12:00
114 | Mirsorai | 37 | 2025-11-30 14:00
115 | Mirzapur | 46 | 2025-11-01 18:30
116 | Mithapukur | 58 | 2025-11-04 14:00
117 | Modern | N/A | N/A
118 | Mogbazar | 94 | 2025-11-04 13:00
119 | Mongla | 47 | 2025-11-19 18:30
120 | Motijheel | 43 | 2025-11-01 12:00
121 | Muktagacha | 33 | 2025-11-01 00:00
122 | Munshiganj | 112 | 2025-11-01 00:00
123 | Muradnagar | 41 | 2025-11-01 18:00
124 | Mymensingh | 188 | 2025-11-06 18:00
125 | Naogaon | 100 | 2025-11-06 20:00
126 | Narail | 55 | 2025-11-01 18:00
127 | Narinda | 73 | 2025-11-06 13:00
128 | Narshingdi | 178 | 2025-11-08 18:00
129 | Natore | 123 | 2025-11-04 18:00
130 | Nawabganj | 43.4 | 2025-11-02 14:00
131 | Netrakona | 129 | 2025-11-04 18:00
132 | New | 75 | 2025-11-09 13:00
133 | Niamatpur | 51 | 2025-11-06 21:00
134 | Noapara | 44 | 2025-11-01 21:00
135 | PHP | 10 | 2025-11-11 19:30
136 | Pabna | 97 | 2025-11-01 18:00
137 | Palashbari | 101 | 2025-11-05 18:30
138 | Panchagarh | 50 | 2025-11-04 18:00
139 | Patiya | 100 | 2025-11-01 19:30
140 | Patuakhali | 80 | 2025-11-01 21:00
141 | Payra | 34 | 2025-11-01 00:00
142 | Postogola | 65 | 2025-11-01 13:00
143 | Purbachal | 35 | 2025-11-01 13:00
144 | Purbasadipur | 102 | 2025-11-22 18:00
145 | Rahanpur | 26 | 2025-11-05 20:00
146 | Rahim | 48 | 2025-11-06 10:00
147 | Rajbari | 76 | 2025-11-01 18:00
148 | Rajendrapur | 124 | 2025-11-08 18:00
149 | Rajshahi | 119 | 2025-11-01 00:00
150 | Rajshahi-230 | 72 | 2025-11-19 13:00
151 | Ramganj | 112 | 2025-11-01 21:00
152 | Rampur | 46 | 2025-11-18 18:30
153 | Rangamati | 18 | 2025-11-01 18:00
154 | Rangpur | 133 | 2025-11-05 18:00
155 | Ruppur | 6.6 | 2025-11-03 10:00
156 | SSM | 15 | 2025-11-11 02:00
157 | Saidpur | 98 | 2025-11-05 18:00
158 | Satkhira | 108 | 2025-11-01 00:00
159 | Satmasjid | 100 | 2025-11-01 13:00
160 | Savar | 234 | 2025-11-30 16:00
161 | SevenRings | 20.44 | 2025-11-11 08:00
162 | ShahCement | 33 | 2025-11-17 01:00
163 | Shahjadpur | 84 | 2025-11-05 18:30
164 | Shahjibazar | 124 | 2025-11-01 00:00
165 | Shahmirpur | 57 | 2025-11-06 17:00
166 | Shariatpur | 83 | 2025-11-01 00:00
167 | Sherpur | 110 | 2025-11-03 18:00
168 | Shikalbaha | 41 | 2025-11-01 14:00
169 | Shitalakhya | 82.3 | 2025-11-01 16:00
170 | Sholosohor | 49 | 2025-11-04 18:00
171 | Shyampur | 138 | 2025-11-06 00:00
172 | Siddhirganj | 122 | 2025-11-01 12:00
173 | Sirajganj | 102 | 2025-11-05 18:30
174 | Sonargaon | 139 | 2025-11-08 16:00
175 | Sreemongol | 84 | 2025-11-04 18:00
176 | Sreepur | 117 | 2025-11-01 18:00
177 | Srinagar | 45.3 | 2025-11-01 00:00
178 | Sunamganj | 62 | 2025-11-04 22:00
179 | Sylhet | 51 | 2025-11-04 18:00
180 | Sylhet-132 | 127 | 2025-11-09 18:00
181 | TK | 24.5 | 2025-11-01 18:00
182 | Tangail | 156 | 2025-11-01 00:00
183 | Taraganj | 19 | 2025-11-05 18:00
184 | Tasnim | 36 | 2025-11-19 09:00
185 | Thakurgaon | 83 | 2025-11-04 18:00
186 | Tongi | 131 | 2025-11-08 15:00
187 | Ullahpara | 34 | 2025-11-04 18:00
188 | Ullon | 62 | 2025-11-01 00:00
189 | Uttara | 85 | 2025-11-01 13:00
190 | UttaraNew | 54 | 2025-11-02 04:00
191 | Zigatola | 74 | 2025-11-01 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: November 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5315.53 | 2025-11-06 | 12:00
Chattogram | 1625.5 | 2025-11-01 | 19:30
Cumilla | 1414.9 | 2025-11-01 | 0:00
Mymensingh | 1017 | 2025-11-01 | 0:00
Sylhet | 622 | 2025-11-04 | 18:30
Khulna | 1602 | 2025-11-05 | 18:00
Barishal | 468 | 2025-11-01 | 21:00
Rajshahi | 1205.8 | 2025-11-05 | 18:30
Rangpur | 851 | 2025-11-05 | 18:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 404 | 2025-11-29 03:00 | 372 | 2025-11-02 11:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 408 | 2025-11-02 06:00 | 373 | 2025-11-09 12:00
4 | Bibiana | 400 | 403 | 2025-11-29 03:00 | 380 | 2025-11-07 12:00
5 | BIPTC | 400 | 410 | 2025-11-26 04:00 | 389 | 2025-11-21 12:00
6 | Bogura | 400 | 410 | 2025-11-27 04:00 | 385 | 2025-11-22 21:00
7 | Gopalganj | 400 | 411 | 2025-11-29 03:00 | 387 | 2025-11-06 14:00
8 | Kaliakoir | 400 | 400 | 2025-11-29 03:00 | 357 | 2025-11-07 12:00
9 | Korerhat | 400 | 411 | 2025-11-29 03:00 | 380 | 2025-11-10 11:00
10 | Madunaghat | 400 | 407 | 2025-11-27 05:00 | 381 | 2025-11-10 11:00
11 | Meghnaghat | 400 | 405 | 2025-11-29 05:00 | 372 | 2025-11-06 12:00
12 | Payra | 400 | 419 | 2025-11-11 09:00 | 405 | 2025-11-01 18:00
13 | Rahanpur | 400 | 417 | 2025-11-26 04:00 | 394 | 2025-11-17 13:00
14 | Rampal | 400 | 415 | 2025-11-23 04:00 | 395 | 2025-11-01 13:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 244 | 2025-11-29 05:00 | 220 | 2025-11-02 11:00
2 | AKSML | 230 | 241 | 2025-11-26 03:00 | 223 | 2025-11-02 02:00
3 | Aminbazar | 230 | 243 | 2025-11-28 05:00 | 221 | 2025-11-01 12:00
4 | Ashuganj | 230 | 241 | 2025-11-30 01:00 | 215 | 2025-11-19 16:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 238 | 2025-11-02 18:30 | 226 | 2025-11-05 17:00
7 | Barapukuria | 230 | 228 | 2025-11-02 10:00 | 203 | 2025-11-06 07:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 245 | 2025-11-29 02:00 | 228 | 2025-11-01 19:30
10 | Bheramara | 230 | 238 | 2025-11-27 04:00 | 221 | 2025-11-01 12:00
11 | Bhulta | 230 | 237 | 2025-11-29 05:00 | 209 | 2025-11-02 11:00
12 | Bibiana | 230 | 239 | 2025-11-29 04:00 | 224 | 2025-11-01 23:00
13 | BIPTC | 230 | 240 | 2025-11-16 05:00 | 223 | 2025-11-01 12:00
14 | Bogura | 230 | 238 | 2025-11-26 04:00 | 223 | 2025-11-06 14:00
15 | Bogura-400 | 230 | 246 | 2025-11-01 06:00 | 223 | 2025-11-29 18:00
16 | Borhanuddin | 230 | 245 | 2025-11-26 03:00 | 232 | 2025-11-01 23:00
17 | BSRM | 230 | 241 | 2025-11-29 03:00 | 219 | 2025-11-01 16:00
18 | Cumilla(N) | 230 | 238 | 2025-11-28 05:00 | 217 | 2025-11-03 15:00
19 | Faridpur | 230 | 244 | 2025-11-29 03:00 | 225 | 2025-11-01
20 | Fenchuganj | 230 | 240 | 2025-11-20 06:00 | 226 | 2025-11-03 16:00
21 | Feni | 230 | 238 | 2025-11-30 04:00 | 224 | 2025-11-24 12:00
22 | Ghorashal | 230 | 240 | 2025-11-14 01:00 | 220 | 2025-11-03 14:00
23 | Ghorashal-230 | 230 | 241 | 2025-11-27 09:00 | 214 | 2025-11-22 19:00
24 | Gopalganj | 230 | 244 | 2025-11-29 03:00 | 223 | 2025-11-11 23:00
25 | GPH | 230 | 243 | 2025-11-29 03:00 | 215 | 2025-11-25 05:00
26 | Haripur | 230 | 237 | 2025-11-28 05:00 | 214 | 2025-11-02 12:00
27 | Hasnabad | 230 | 239 | 2025-11-28 06:00 | 216 | 2025-11-01 11:00
28 | Hathazari | 230 | 240 | 2025-11-28 06:00 | 222 | 2025-11-01 15:00
29 | Ishurdi | 230 | 241 | 2025-11-27 04:00 | 225 | 2025-11-01 13:00
30 | Jhenaidah | 230 | 240 | 2025-11-27 04:00 | 218 | 2025-11-05 18:00
31 | Kachua | 230 | 240 | 2025-11-27 03:00 | 214 | 2025-11-02 01:00
32 | Kaliakoir | 230 | 241 | 2025-11-13 20:00 | 223 | 2025-11-16 12:00
33 | Keranigonj | 230 | 241 | 2025-11-29 03:00 | 217 | 2025-11-06 12:00
34 | Khulna(S) | 230 | 243 | 2025-11-28 05:00 | 223 | 2025-11-17 17:00
35 | Korerhat | 230 | 242 | 2025-11-15 04:00 | 228 | 2025-11-10 10:00
36 | Madunaghat | 230 | 243 | 2025-11-29 03:00 | 226 | 2025-11-02 11:00
37 | Madunaghat-400 | 230 | 239 | 2025-11-11 03:00 | 216 | 2025-11-06 12:00
38 | Maniknagar | 230 | 235 | 2025-11-28 06:00 | 210 | 2025-11-06 12:00
39 | Meghnaghat | 230 | 243 | 2025-11-28 06:00 | 220 | 2025-11-03 12:00
40 | Meghnaghat-400 | 230 | 239 | 2025-11-29 05:00 | 216 | 2025-11-06 12:00
41 | Mirsorai | 230 | 241 | 2025-11-29 03:00 | 219 | 2025-11-01 23:00
42 | Rajshahi | 230 | 238 | 2025-11-27 04:00 | 219 | 2025-11-26 11:00
43 | Rampal | 230 | 240 | 2025-11-27 05:00 | 225 | 2025-11-01 15:00
44 | Rampur | 230 | N/A | N/A | N/A | N/A
45 | Rampura | 230 | 236 | 2025-11-28 05:00 | 212 | 2025-11-03 16:00
46 | Shikalbaha | 230 | 241 | 2025-11-27 04:00 | 223 | 2025-11-03 11:00
47 | Shyampur | 230 | 240 | 2025-11-29 03:00 | 216 | 2025-11-06 12:00
48 | Siddhirganj | 230 | 237 | 2025-11-29 03:00 | 214 | 2025-11-06 11:00
49 | Sirajgonj | 230 | 245 | 2025-11-01 06:00 | 231 | 2025-11-29 18:00
50 | Sreepur | 230 | 237 | 2025-11-18 17:00 | 219 | 2025-11-03 16:00
51 | Tongi | 230 | 237 | 2025-11-13 19:30 | 215 | 2025-11-08 15:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 137 | 2025-11-02 06:00 | 122 | 2025-11-03 16:00
2 | Agargaon | 132 | 140 | 2025-11-12 05:00 | 128 | 2025-11-01 13:00
3 | Agrabad | 132 | 139 | 2025-11-26 05:00 | 126 | 2025-11-01 16:00
4 | AKS | 132 | 137 | 2025-11-28 02:00 | 126 | 2025-11-01 13:00
5 | Aminbazar | 132 | 141 | 2025-11-13 18:30 | 127 | 2025-11-07 13:00
6 | Amnura | 132 | 141 | 2025-11-08 10:00 | 127 | 2025-11-01 12:00
7 | Ashuganj | 132 | 143 | 2025-11-03 08:00 | 135 | 2025-11-07 12:00
8 | Bagerhat | 132 | 138 | 2025-11-16 04:00 | 118 | 2025-11-14 13:00
9 | Bajitpur | 132 | 138 | 2025-11-14 06:00 | 125 | 2025-11-06 09:00
10 | Bakulia | 132 | 141 | 2025-11-28 08:00 | 128 | 2025-11-01 16:00
11 | Banani | 132 | 138 | 2025-11-15 06:00 | 122 | 2025-11-03 16:00
12 | Bangabhaban | 132 | 142 | 2025-11-15 03:00 | 126 | 2025-11-06 12:00
13 | Barapukuria | 132 | 139 | 2025-11-26 05:00 | 122 | 2025-11-06 07:00
14 | Barguna | 132 | 139 | 2025-11-11 09:00 | 133 | 2025-11-01 18:00
0 | Barishal | 132 | 141 | 2025-11-27 06:00 | 130 | 2025-11-01 19:30
16 | Barishal-230 | 132 | 141 | 2025-11-26 05:00 | 126 | 2025-11-11 17:00
17 | Baroaulia | 132 | 141 | 2025-11-28 09:00 | 128 | 2025-11-03 11:00
18 | Baroirhat | 132 | 139 | 2025-11-28 05:00 | 125 | 2025-11-02 01:00
19 | Bashundhara | 132 | 140 | 2025-11-11 05:00 | 121 | 2025-11-19 12:00
20 | BashundharaCement | 132 | 139 | 2025-11-20 04:00 | 120 | 2025-11-02 20:00
21 | Beanibazar | 132 | 135 | 2025-11-14 08:00 | 125 | 2025-11-01 19:00
22 | Benapole | 132 | 139 | 2025-11-24 03:00 | 117 | 2025-11-05 18:00
23 | Bhaluka | 132 | 136 | 2025-11-29 04:00 | 123 | 2025-11-03 16:00
24 | Bhandaria | 132 | 140 | 2025-11-04 07:00 | 123 | 2025-11-01 21:00
25 | Bhangura | 132 | 138 | 2025-11-11 04:00 | 129 | 2025-11-04 18:30
26 | Bheramara | 132 | 141 | 2025-11-10 04:00 | 130 | 2025-11-01 12:00
27 | Bheramara(GK) | 132 | 141 | 2025-11-27 04:00 | 130 | 2025-11-01 13:00
28 | Bhulta | 132 | 135 | 2025-11-15 04:00 | 121 | 2025-11-02 12:00
29 | Bog-Sherpur | 132 | 137 | 2025-11-28 04:00 | 127 | 2025-11-05 16:00
30 | Bogura | 132 | 137 | 2025-11-27 04:00 | 127 | 2025-11-29 18:00
31 | Bogura-230 | 132 | 136 | 2025-11-12 04:00 | 127 | 2025-11-06 07:00
32 | Brahmanbaria | 132 | 138 | 2025-11-26 06:00 | 127 | 2025-11-08 15:00
33 | Cantonment | 132 | 140 | 2025-11-13 03:00 | 127 | 2025-11-06 12:00
34 | Chandina | 132 | 141 | 2025-11-28 06:00 | 126 | 2025-11-01 23:00
35 | Chandpur | 132 | 141 | 2025-11-12 17:00 | 126 | 2025-11-02 03:00
36 | Chandraghona | 132 | 141 | 2025-11-26 02:00 | 131 | 2025-11-01 16:00
37 | Chapai | 132 | 142 | 2025-11-11 06:00 | 131 | 2025-11-16 13:00
39 | Charsaidpur | 132 | 138 | 2025-11-29 03:00 | 123 | 2025-11-01 11:00
40 | Chauddagram | 132 | 139 | 2025-11-28 08:00 | 123 | 2025-11-12 19:00
41 | Chhatak | 132 | 133 | 2025-11-16 05:00 | 122 | 2025-11-03 21:00
42 | Chowmuhani | 132 | 138 | 2025-11-15 08:00 | 124 | 2025-11-01 22:00
43 | Chuadanga | 132 | 142 | 2025-11-17 05:00 | 122 | 2025-11-05 18:00
44 | Coxsbazar | 132 | 131 | 2025-11-26 02:00 | 108 | 2025-11-01 17:00
45 | Cumilla(N) | 132 | 141 | 2025-11-28 06:00 | 126 | 2025-11-01 23:00
46 | Cumilla(S) | 132 | 140 | 2025-11-26 05:00 | 124 | 2025-11-10 21:00
47 | Daganbhuiyan | 132 | 139 | 2025-11-29 03:00 | 125 | 2025-11-01 22:00
48 | Daudkandi | 132 | 137 | 2025-11-29 03:00 | 118 | 2025-11-01 16:00
49 | DhakaUniversity | 132 | 137 | 2025-11-02 05:00 | 122 | 2025-11-03 15:00
50 | Dhamrai | 132 | 141 | 2025-11-29 01:00 | 122 | 2025-11-16 12:00
51 | Dhanmondi | 132 | 139 | 2025-11-28 05:00 | 123.6 | 2025-11-01 11:00
52 | Dohazari | 132 | 137 | 2025-11-28 05:00 | 122 | 2025-11-01 13:00
53 | Faridpur | 132 | 141 | 2025-11-15 05:00 | 132 | 2025-11-01 23:00
54 | Fatullah | 132 | 142 | 2025-11-29 03:00 | 124 | 2025-11-19 12:00
55 | Fenchuganj | 132 | 141 | 2025-11-17 06:00 | 132 | 2025-11-05 10:00
56 | Feni | 132 | 137 | 2025-11-16 05:00 | 120 | 2025-11-07 05:00
57 | Feni-230 | 132 | 140 | 2025-11-29 04:00 | 131 | 2025-11-24 12:00
58 | Ghatail | 132 | 135 | 2025-11-01 12:00 | 117 | 2025-11-05 21:00
59 | Ghorashal | 132 | 142 | 2025-11-14 06:00 | 128 | 2025-11-27 12:00
60 | Goalpara | 132 | 141 | 2025-11-15 06:00 | 119 | 2025-11-14 13:00
61 | Gollamari | 132 | 140 | 2025-11-11 06:00 | 129 | 2025-11-03 18:00
62 | Gopalganj | 132 | 140 | 2025-11-18 05:00 | 129 | 2025-11-03 18:00
63 | Gopalganj-400 | 132 | 142 | 2025-11-24 06:00 | 132 | 2025-11-03 18:00
64 | Gulshan | 132 | 137 | 2025-11-03 04:00 | 122 | 2025-11-19 11:00
65 | Halishahar | 132 | 141 | 2025-11-29 03:00 | 127 | 2025-11-01 16:00
66 | Haripur | 132 | 139 | 2025-11-28 06:00 | 124 | 2025-11-02 12:00
67 | HaripurSBU | 132 | 139 | 2025-11-28 06:00 | 125 | 2025-11-01 13:00
68 | Hasnabad | 132 | 140 | 2025-11-13 21:00 | 126 | 2025-11-17 13:00
69 | Hathazari | 132 | 140 | 2025-11-13 18:00 | 129 | 2025-11-01 11:00
70 | Ishurdi | 132 | 143 | 2025-11-29 03:00 | 132 | 2025-11-01 11:00
71 | Jaldhaka | 132 | 134 | 2025-11-09 19:30 | 117 | 2025-11-05 14:00
72 | Jamalpur | 132 | 135 | 2025-11-22 09:00 | 112 | 2025-11-21 07:00
73 | Jashore | 132 | 140 | 2025-11-27 03:00 | 118 | 2025-11-05 18:00
74 | Jhenaidah | 132 | 142 | 2025-11-17 03:00 | 120 | 2025-11-19 18:00
75 | Jhenaidah-230 | 132 | 145 | 2025-11-17 04:00 | 127 | 2025-11-05 18:00
76 | Joydebpur | 132 | 142 | 2025-11-07 02:00 | 122 | 2025-11-03 16:00
77 | Joypurhat | 132 | 134 | 2025-11-15 04:00 | 121 | 2025-11-06 15:00
78 | Juldah | 132 | 140 | 2025-11-26 03:00 | 128 | 2025-11-01 15:00
79 | Kabirpur | 132 | 140 | 2025-11-15 02:00 | 124 | 2025-11-29 16:00
80 | Kachua | 132 | 141 | 2025-11-29 01:00 | 127 | 2025-11-02 01:00
81 | Kaliakoir | 132 | 143 | 2025-11-15 03:00 | 127 | 2025-11-16 12:00
82 | Kallyanpur | 132 | 142 | 2025-11-13 19:00 | 128 | 2025-11-01 12:00
83 | Kalurghat | 132 | 143 | 2025-11-29 03:00 | 130 | 2025-11-01 16:00
84 | Kamrangirchar | 132 | 140 | 2025-11-13 05:00 | 127 | 2025-11-06 12:00
85 | Kaptai | 132 | N/A | N/A | N/A | N/A
86 | Kasba | 132 | 139 | 2025-11-28 05:00 | 121 | 2025-11-02 01:00
87 | Kazla | 132 | 142 | 2025-11-15 05:00 | 126 | 2025-11-06 13:00
88 | Keranigonj | 132 | 140 | 2025-11-13 06:00 | 128 | 2025-11-01 13:00
89 | Khagrachori | 132 | 140 | 2025-11-27 03:00 | 129 | 2025-11-01 16:00
90 | Khulna | 132 | 139 | 2025-11-11 05:00 | 118 | 2025-11-14 13:00
91 | Khulna(S) | 132 | 141 | 2025-11-26 05:00 | 129 | 2025-11-28 13:00
92 | Khulshi | 132 | 138 | 2025-11-26 01:00 | 124 | 2025-11-30 11:00
93 | Kishoreganj | 132 | 137 | 2025-11-17 05:00 | 123 | 2025-11-07 20:00
94 | Kodda | 132 | 140 | 2025-11-15 19:00 | 122 | 2025-11-02 11:00
95 | KSRM | 132 | 142 | 2025-11-28 08:00 | 128 | 2025-11-03 10:00
96 | Kulaura | 132 | 140 | 2025-11-14 05:00 | 132 | 2025-11-01 21:00
97 | Kurigram | 132 | 134 | 2025-11-13 04:00 | 114 | 2025-11-06 07:00
98 | Kushtia | 132 | 140 | 2025-11-10 03:00 | 126 | 2025-11-20 18:00
99 | Laksam | 132 | 141 | 2025-11-29 02:00 | 126 | 2025-11-02 02:00
100 | Lakshmipur | 132 | 138 | 2025-11-14 09:00 | 122 | 2025-11-01 22:00
101 | Lalbag | 132 | 140 | 2025-11-13 06:00 | 127 | 2025-11-01 13:00
102 | Lalmonirhat | 132 | 133 | 2025-11-01 18:00 | 120 | 2025-11-26 20:00
103 | Madanganj | 132 | 137 | 2025-11-28 09:00 | 124 | 2025-11-06 12:00
104 | Madaripur | 132 | 140 | 2025-11-26 05:00 | 131 | 2025-11-01 19:30
105 | Madartek | 132 | 138 | 2025-11-29 15:00 | 121 | 2025-11-01 13:00
106 | Madunaghat | 132 | 141 | 2025-11-27 03:00 | 130 | 2025-11-01 14:00
107 | Magura | 132 | 141 | 2025-11-27 04:00 | 123 | 2025-11-05 18:00
108 | Mahasthangarh | 132 | 135 | 2025-11-13 04:00 | 125 | 2025-11-06 14:00
109 | Maijdee | 132 | 139 | 2025-11-13 19:30 | 123 | 2025-11-01 22:00
110 | Manikganj | 132 | 139 | 2025-11-29 03:00 | 113 | 2025-11-16 01:00
111 | Maniknagar | 132 | 141 | 2025-11-14 04:00 | 127 | 2025-11-02 12:00
112 | Matarbari | 132 | 137 | 2025-11-21 18:00 | 115 | 2025-11-01 07:00
113 | Matuail | 132 | 139 | 2025-11-28 03:00 | 124 | 2025-11-02 11:00
114 | Metrorail_Motijheel | 132 | 141 | 2025-11-14 04:00 | 121 | 2025-11-12 14:00
115 | Metrorail_Uttara | 132 | 141 | 2025-11-12 04:00 | 124 | 2025-11-30 12:00
116 | Millgate | 132 | 142 | 2025-11-22 04:00 | 125 | 2025-11-29 17:00
117 | Mirpur | 132 | 141 | 2025-11-28 06:00 | 127 | 2025-11-01 11:00
118 | Mirzapur | 132 | 139 | 2025-11-15 05:00 | 124 | 2025-11-07 12:00
119 | Mithapukur | 132 | 136 | 2025-11-01 18:00 | 122 | 2025-11-27 18:00
120 | MI_Cement | 132 | 140.3 | 2025-11-14 06:00 | 140.3 | 2025-11-14 06:00
121 | Modern | 132 | N/A | N/A | N/A | N/A
122 | Mogbazar | 132 | 140 | 2025-11-03 06:00 | 124 | 2025-11-01 11:00
123 | Mongla | 132 | 138 | 2025-11-14 09:00 | 120 | 2025-11-14 13:00
124 | Motijheel | 132 | 142 | 2025-11-15 03:00 | 126 | 2025-11-06 12:00
125 | Muktagacha | 132 | 138 | 2025-11-24 09:00 | 116 | 2025-11-06 13:00
126 | Munshiganj | 132 | 137 | 2025-11-28 05:00 | 122 | 2025-11-01 11:00
127 | Muradnagar | 132 | 140 | 2025-11-29 05:00 | 122 | 2025-11-02 01:00
128 | Mymensingh | 132 | 138 | 2025-11-24 09:00 | 113 | 2025-11-05 21:00
129 | Naogaon | 132 | 135 | 2025-11-26 05:00 | 123 | 2025-11-06 07:00
130 | Narail | 132 | 142 | 2025-11-24 05:00 | 122 | 2025-11-05 18:00
131 | Narinda | 132 | 0 | 2025-11-18 18:00 | 0 | 2025-11-18 18:00
132 | Narshingdi | 132 | 139 | 2025-11-29 00:00 | 117 | 2025-11-02 15:00
133 | Natore | 132 | 137 | 2025-11-29 01:00 | 127 | 2025-11-01 13:00
134 | Nawabganj | 132 | 140 | 2025-11-12 05:00 | 127 | 2025-11-06 12:00
135 | Netrakona | 132 | 132 | 2025-11-13 17:00 | 117 | 2025-11-04 18:00
136 | New | 132 | 142 | 2025-11-13 05:00 | 125 | 2025-11-29 12:00
137 | Niamatpur | 132 | 142 | 2025-11-03 09:00 | 132 | 2025-11-16 13:00
139 | Noapara | 132 | 140 | 2025-11-27 04:00 | 126 | 2025-11-21 13:00
140 | Pabna | 132 | 140 | 2025-11-26 04:00 | 126 | 2025-11-13 13:00
141 | Palashbari | 132 | 134 | 2025-11-18 18:30 | 119 | 2025-11-27 18:00
142 | Panchagarh | 132 | 142 | 2025-11-18 19:00 | 119 | 2025-11-26 12:00
143 | Patiya | 132 | 141 | 2025-11-29 03:00 | 126 | 2025-11-01 16:00
144 | Patuakhali | 132 | 138 | 2025-11-09 17:00 | 132 | 2025-11-04 22:00
145 | Payra | 132 | 139 | 2025-11-11 09:00 | 134 | 2025-11-01 23:00
146 | PHP | 132 | 139 | 2025-11-28 06:00 | 121 | 2025-11-13 10:00
147 | Postogola | 132 | 141 | 2025-11-14 06:00 | 126 | 2025-11-19 12:00
148 | Purbachal | 132 | 138 | 2025-11-15 04:00 | 121 | 2025-11-03 16:00
149 | Purbasadipur | 132 | 136 | 2025-11-02 18:30 | 116 | 2025-11-06 07:00
150 | Rahanpur | 132 | 143 | 2025-11-11 05:00 | 132 | 2025-11-17 12:00
151 | Rahanpur-400 | 132 | 144 | 2025-11-09 21:00 | 132 | 2025-11-17 13:00
152 | Rahim | 132 | 139 | 2025-11-29 05:00 | 124 | 2025-11-02 11:00
153 | Rajbari | 132 | 142 | 2025-11-14 06:00 | 131 | 2025-11-01 19:30
154 | Rajendrapur | 132 | 137 | 2025-11-30 02:00 | 124 | 2025-11-03 14:00
155 | Rajshahi | 132 | 138 | 2025-11-28 03:00 | 127 | 2025-11-01 13:00
156 | Rajshahi-230 | 132 | 137 | 2025-11-22 04:00 | 122 | 2025-11-15 13:00
157 | Ramganj | 132 | 138 | 2025-11-29 06:00 | 123 | 2025-11-01 23:00
158 | Rampur | 132 | 140 | 2025-11-27 04:00 | 126 | 2025-11-01 16:00
159 | Rampura | 132 | 138 | 2025-11-15 06:00 | 122 | 2025-11-03 16:00
160 | Rangamati | 132 | 140 | 2025-11-26 04:00 | 130 | 2025-11-01 16:00
161 | Rangpur | 132 | 136 | 2025-11-02 18:30 | 122 | 2025-11-06 07:00
162 | Ruppur | 132 | 141 | 2025-11-28 05:00 | 131 | 2025-11-01 13:00
163 | Saidpur | 132 | 136 | 2025-11-28 05:00 | 119 | 2025-11-26 08:00
164 | Satkhira | 132 | 139 | 2025-11-15 06:00 | 125 | 2025-11-02 01:00
165 | Satmasjid | 132 | 141 | 2025-11-19 10:00 | 127 | 2025-11-01 13:00
166 | Savar | 132 | 141 | 2025-11-13 19:00 | 126 | 2025-11-01 11:00
167 | SevenRings | 132 | 143 | 2025-11-14 09:00 | 128 | 2025-11-03 15:00
168 | ShahCement | 132 | 138 | 2025-11-29 03:00 | 123 | 2025-11-01 11:00
169 | Shahjadpur | 132 | 142 | 2025-11-25 03:00 | 130 | 2025-11-20 00:00
170 | Shahjibazar | 132 | 139 | 2025-11-26 07:00 | 129 | 2025-11-08 15:00
171 | Shahmirpur | 132 | 141 | 2025-11-28 06:00 | 128 | 2025-11-03 12:00
172 | Shariatpur | 132 | 140 | 2025-11-15 04:00 | 128 | 2025-11-24 18:00
173 | Sherpur | 132 | 133 | 2025-11-01 14:00 | 108 | 2025-11-21 07:00
174 | Shikalbaha | 132 | 129 | 2025-11-27 02:00 | 111 | 2025-11-01 16:00
175 | Shikalbaha-230 | 132 | 141 | 2025-11-26 04:00 | 129 | 2025-11-03 11:00
176 | Shitalakhya | 132 | 140.3 | 2025-11-14 06:00 | 123.9 | 2025-11-19 16:00
177 | Sholosohor | 132 | 141 | 2025-11-27 03:00 | 130 | 2025-11-01 16:00
178 | Shyampur | 132 | 140 | 2025-11-12 03:00 | 128 | 2025-11-05 12:00
179 | Shyampur-230 | 132 | 143 | 2025-11-29 05:00 | 129 | 2025-11-19 12:00
180 | Siddhirganj | 132 | 139 | 2025-11-28 04:00 | 124 | 2025-11-02 11:00
181 | Sirajganj | 132 | 136 | 2025-11-14 09:00 | 125 | 2025-11-24 18:30
182 | Sonargaon | 132 | 137 | 2025-11-28 08:00 | 122 | 2025-11-01 16:00
183 | Sreemongol | 132 | 139 | 2025-11-30 01:00 | 129 | 2025-11-04 18:00
184 | Sreepur | 132 | 138 | 2025-11-16 03:00 | 126 | 2025-11-03 16:00
185 | Srinagar | 132 | 141 | 2025-11-28 06:00 | 127 | 2025-11-06 12:00
186 | SSM | 132 | 142 | 2025-11-26 08:00 | 129 | 2025-11-26 13:00
187 | Sunamganj | 132 | 132 | 2025-11-14 06:00 | 120 | 2025-11-04 21:00
188 | Sylhet | 132 | 135 | 2025-11-10 07:00 | 126 | 2025-11-05 13:00
189 | Sylhet-132 | 132 | 135 | 2025-11-10 06:00 | 127 | 2025-11-03 15:00
190 | Tangail | 132 | 134 | 2025-11-14 09:00 | 119 | 2025-11-05 20:00
191 | Taraganj | 132 | 135 | 2025-11-02 19:00 | 120 | 2025-11-27 07:00
192 | Tasnim | 132 | 140 | 2025-11-26 18:00 | 126 | 2025-11-19 12:00
193 | Thakurgaon | 132 | 141 | 2025-11-18 19:00 | 117 | 2025-11-26 12:00
194 | TK | 132 | 141 | 2025-11-27 05:00 | 130 | 2025-11-02 11:00
195 | Tongi | 132 | 142 | 2025-11-12 04:00 | 126 | 2025-11-30 18:30
196 | Ullahpara | 132 | 138 | 2025-11-26 05:00 | 128 | 2025-11-05 18:00
197 | Ullon | 132 | 137 | 2025-11-03 04:00 | 122 | 2025-11-03 15:00
198 | Uttara | 132 | 142 | 2025-11-26 04:00 | 125 | 2025-11-29 16:00
199 | UttaraNew | 132 | 141 | 2025-11-12 04:00 | 124 | 2025-11-30 11:00
200 | Zigatola | 132 | 140 | 2025-11-13 06:00 | 128 | 2025-11-01 12:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: November 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 29-11-2025 | 18:00 | 410 | 165 | 84.9915
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 29-11-2025 | 19:00 | 405 | 149 | 82.9883
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 29-11-2025 | 19:00 | 405 | 149 | 82.9883
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-11-2025 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 03-11-2025 | 12:00 | 281 | 113 | 58.2442
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 03-11-2025 | 12:00 | 281 | 113 | 58.2442
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 26-11-2025 | 11:00 | 199 | 86 | 41.69
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 17-11-2025 | 13:00 | 266 | 44 | 51.8489
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 05-11-2025 | 18:00 | 338 | 5 | 45.0716
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 05-11-2025 | 18:00 | 338 | 5 | 45.0716
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 05-11-2025 | 18:00 | 338 | 5 | 45.0716
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 01-11-2025 | 02:00 | 166 | 27 | 51.7481
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 01-11-2025 | 02:00 | 166 | 27 | 51.7481
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 01-11-2025 | 02:00 | 166 | 27 | 51.7481
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 01-11-2025 | 19:30 | 146 | 29 | 19.847
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 02-11-2025 | 11:00 | 272 | 120 | 57.172
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 24-11-2025 | 00:00 | 368 | 34 | 71.0706
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 05-11-2025 | 16:00 | 166 | 48 | 53.1694
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 22-11-2025 | 08:00 | 310 | 79 | 98.4332
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 20-11-2025 | 04:00 | 401 | 273 | 64.6811
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 21-11-2025 | 07:00 | 400 | 129 | 56.0382
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 21-11-2025 | 07:00 | 400 | 129 | 56.0382
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 05-11-2025 | 12:00 | 420 | 131 | 58.6608
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 05-11-2025 | 12:00 | 420 | 129 | 58.5819
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 29-11-2025 | 18:30 | 390 | 45 | 52.345
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 01-11-2025 | 18:00 | 243 | 21 | 46.9049
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 01-11-2025 | 18:00 | 238 | 20 | 45.9305
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 01-11-2025 | 00:00 | 57 | 17 | 18.3019
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 01-11-2025 | 00:00 | 57 | 17 | 18.3019
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 25-11-2025 | 13:00 | 113 | 16 | 21.9475
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 23-11-2025 | 13:00 | 113 | 14 | 21.8969
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 17-11-2025 | 09:00 | 220 | 30 | 74.012
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 17-11-2025 | 09:00 | 220 | 30 | 74.012
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 26-11-2025 | 16:00 | 192 | 43 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 26-11-2025 | 16:00 | 192 | 43 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 01-11-2025 | 12:00 | 166 | 49 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 24-11-2025 | 17:00 | 205 | 60 | 71.2
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 02-11-2025 | 18:00 | 230 | 35 | 77.5493
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 26-11-2025 | 18:00 | 135 | 32 | 46.2469
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 24-11-2025 | 17:00 | 119 | 23 | 53.8677
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 05-11-2025 | 18:00 | 135 | 22 | 60.7915
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 27-11-2025 | 18:00 | 188 | 38 | 85.2453
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 27-11-2025 | 18:00 | 245 | 22 | 81.9953
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 07-11-2025 | 18:00 | 197 | 16 | 65.8829
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 18-11-2025 | 10:00 | 148 | 3 | 49.3435
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 03-11-2025 | 10:00 | 95 | 36 | 45.1521
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 03-11-2025 | 10:00 | 95 | 36 | 45.1521
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 30-11-2025 | 18:00 | 120 | 14 | 53.6951
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 30-11-2025 | 18:00 | 120 | 14 | 53.6951
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 30-11-2025 | 18:00 | 161 | 25 | 54.3098
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 30-11-2025 | 18:00 | 161 | 25 | 54.3098
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 02-11-2025 | 02:00 | 120 | 46 | 57.1176
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 07-11-2025 | 18:30 | 133 | 24 | 60.0658
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 02-11-2025 | 02:00 | 130 | 50 | 61.9039
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 01-11-2025 | 21:00 | 156 | 69 | 56.8595
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 01-11-2025 | 21:00 | 193 | 88 | 70.7052
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 02-11-2025 | 01:00 | 92 | 0 | 73.6
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 02-11-2025 | 01:00 | 92 | 0 | 73.6
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 15-11-2025 | 17:00 | 153 | 65 | 73.8821
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 02-11-2025 | 12:00 | 109 | 67 | 56.8646
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 02-11-2025 | 12:00 | 104 | 72 | 56.2183
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 19-11-2025 | 12:00 | 107 | 54 | 53.2685
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 04-11-2025 | 09:00 | 127 | 62 | 62.8115
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 04-11-2025 | 09:00 | 127 | 62 | 62.8115
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 29-11-2025 | 18:00 | 84 | 34 | 60.4134
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 20-11-2025 | 23:00 | 59 | 31 | 44.4322
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 26-11-2025 | 16:00 | 95 | 41 | 68.9799
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 26-11-2025 | 16:00 | 95 | 41 | 68.9799
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 02-11-2025 | 13:00 | 80 | 31 | 38.1317
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 02-11-2025 | 13:00 | 80 | 31 | 38.1317
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 02-11-2025 | 13:00 | 75 | 29 | 35.7384
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 03-11-2025 | 18:00 | 179 | 34 | 60.7335
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 01-11-2025 | 18:00 | 212 | 52 | 72.7614
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 05-11-2025 | 16:00 | 166 | 48 | 57.6002
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 06-11-2025 | 18:30 | 190 | 64 | 66.8298
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 26-11-2025 | 16:00 | 235 | 38 | 79.3508
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-11-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 01-11-2025 | 00:00 | 123 | 30 | 56.2692
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 07-11-2025 | 21:00 | 133 | 22 | 59.9143
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 01-11-2025 | 00:00 | 158 | 34 | 53.8723
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 01-11-2025 | 19:00 | 109 | 12 | 36.5529
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 01-11-2025 | 19:00 | 109 | 12 | 36.5529
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 01-11-2025 | 19:00 | 109 | 12 | 36.5529
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 05-11-2025 | 13:00 | 148 | 63 | 53.617
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 05-11-2025 | 13:00 | 148 | 63 | 53.617
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 26-11-2025 | 13:00 | 118 | -16 | 39.6933
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 25-11-2025 | 08:00 | 111 | 7 | 37.0735
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-11-2025 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-11-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 16-11-2025 | 13:00 | 327 | 49 | 73.478
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 16-11-2025 | 13:00 | 327 | 49 | 73.478
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 16-11-2025 | 15:00 | 312 | 43 | 69.9887
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 01-11-2025 | 15:00 | 230 | 117 | 86.0161
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 01-11-2025 | 15:00 | 230 | 117 | 86.0161
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 10-11-2025 | 17:00 | 151 | 58 | 53.9187
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 07-11-2025 | 08:00 | 144 | 54 | 51.264
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 02-11-2025 | 11:00 | 118 | 8 | 39.4236
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 02-11-2025 | 11:00 | 118 | 8 | 39.4236
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 01-11-2025 | 00:00 | 237 | 85 | 83.9272
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 01-11-2025 | 00:00 | 237 | 85 | 83.9272
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 04-11-2025 | 18:00 | 185 | 25 | 82.9696
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 28-11-2025 | 11:00 | 180 | 0 | 80
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 28-11-2025 | 11:00 | 180 | 0 | 80
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: November 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: November 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-11-01 | 13024 | 13024 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-01 | 11598.36 | 11633.89 | 34 | 12:00 Hr. | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-02 | 13365.5 | 13365.5 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-02 | 12204.77 | 12204.77 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-03 | 13199.68 | 13199.68 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-03 | 11651.58 | 11651.58 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-04 | 13748.2 | 13820.31 | 69 | 19:00 Hr. | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-04 | 11814.82 | 11814.82 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-05 | 13660.84 | 13710.84 | 48 | 19:00 Hr. | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-05 | 11926.41 | 11926.41 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-06 | 13324.87 | 13801.39 | 456 | 19:30 Hr. | 10 | 20 | 80 | 80 | 0 | 140 | 0 | 76 | 50 | - | 2025-11-06 | 12272.32 | 12302.32 | 29 | 12:00 Hr. | 15 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-07 | 12480.06 | 12480.06 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-07 | 10747.41 | 10747.41 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-08 | 12776.98 | 12851.98 | 72 | 19:00 Hr. | 5 | 0 | 0 | 30 | 37 | 0 | 0 | 0 | 0 | - | 2025-11-08 | 10691.03 | 10703.57 | 12 | 12:00 Hr. | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | -
2025-11-09 | 12641.1 | 12851.15 | 201 | 18:00 Hr. | 28 | 31 | 9 | 52 | 10 | 46 | 7 | 8 | 10 | - | 2025-11-09 | 11213.44 | 11213.44 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-10 | 12657.5 | 12725.43 | 65 | 18:00 Hr. | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-10 | 10886.15 | 10886.15 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-11-11 | 12233.7 | 12280.73 | 45 | 18:00 Hr. | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-11 | 10681.07 | 10681.07 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-12 | 11746 | 11792 | 44 | 18:00 Hr. | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-12 | 10429.44 | 10429.44 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-13 | 11577.83 | 11577.83 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-13 | 10517.56 | 10517.56 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-14 | 9826 | 9826 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-14 | 9280 | 9280 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-15 | 11343 | 11343 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-15 | 9429.14 | 9429.14 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-16 | 11530 | 11530 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-16 | 10285.61 | 10285.61 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-17 | 11735.02 | 11735.02 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-17 | 10444.27 | 10444.27 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-18 | 11785.3 | 11816.3 | 30 | 18:00 Hr. | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-18 | 10494.94 | 10494.94 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-19 | 11997 | 11997 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-19 | 10654.26 | 10654.26 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-20 | 11972 | 11995 | 22 | 18:00 Hr. | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-20 | 10773.6 | 10773.6 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-21 | 9905.5 | 9905.5 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-21 | 8580.85 | 8580.85 | 0 | 09:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-22 | 11386.99 | 11386.99 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-22 | 9516.34 | 9516.34 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-23 | 11310.38 | 11310.38 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-23 | 10133.41 | 10133.41 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-24 | 11490.5 | 11490.5 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-24 | 10027.62 | 10027.62 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-25 | 11404.8 | 11404.8 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-25 | 10085.52 | 10085.52 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-26 | 11398.5 | 11398.5 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-26 | 10107.61 | 10107.61 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-27 | 11435.73 | 11435.73 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-27 | 10153.36 | 10153.36 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-28 | 9896 | 9896 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-28 | 9415.41 | 9415.41 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-29 | 11298.5 | 11298.5 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-29 | 9319.62 | 9319.62 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-11-30 | 11404.3 | 11404.3 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-11-30 | 10319.52 | 10319.52 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: November 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13748.2 | 2025-11-04 | 19:00 Hr.
2 | Maximum Day Peak Genaration | MW | 12272.32 | 2025-11-06 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 13820.31 | 2025-11-04 | 19:00 Hr.
4 | Minimum Generation | MW | 7121.94 | 2025-11-29 | 05:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 11918.526 | - | -
6 | Average of the daily day peak Genaration | MW | 10521.848 | - | -
7 | Maximum load shed (Evening Peak) | MW | 456 | 2025-11-06 | 19:30 Hr.
8 | Minimum load shed | MW | 0 | 2025-11-01 | 18:00 Hr.
9 | Total nos. of load shed days | Day | 10 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 35.0667 | - | -
11 | Total Generation | MkWh | 7459.0906 | - | -
12 | Total Generation by BPDB | MkWh | 832.7518 | % of total Gen. | 11.16%
13 | Total Generation by IPP | MkWh | 1689.1048 | '' | 22.64%
14 | A) Total Generation by Generation Companies | MkWh | 3435.8483 | '' | 46.06%
| B) Total Generation by REB | MkWh | 47.2089 | " | 0.6329%
| C) Total Generation by RENTAL | MkWh | 84.163 | " | 1.128%
| D) Total Imported from India (BIPTC) | MkWh | 632.4625 | " | 8.479%
| E) Total Imported from Tripura, India (A.C) | MkWh | 54.5261 | " | 0.731%
| F) Total Imported from Nepal | MkWh | 13.68 | " | 0.1834%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 669.3451 | " | 8.974%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3146.3842 | % of total Gen. | 42.18%
| B) Oil | MkWh | 434.0535 | '' | 5.819%
| C) Hydro | MkWh | 68.3025 | '' | 0.9157%
| D) Solar | MkWh | 121.7275 | '' | 1.632%
| E) Coal | MkWh | 2314.0732 | '' | 31.02%
| F) BIPTC (Import from India) | MkWh | 632.4625 | '' | 8.479%
| G) A.C (Import from Tripura, India) | MkWh | 54.5261 | '' | 0.731%
| H) Total Imported from Nepal | MkWh | 13.68 | '' | 0.1834%
| I) Adani (Import from India) | MkWh | 669.3451 | '' | 8.974%
| J) Wind | MkWh | 4.536 | '' | 0.06081%
16 | Maximun of the daily total Generation . | MkWh | 294.931 | 2025-11-01
17 | Monthly Load factor | % | 75.3542 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 43570.2861 | - | -
| A) Gas | M.Taka | 11169.153 | - | -
| B) Coal | M.Taka | 14820.2856 | - | -
| C) HFO | M.Taka | 7531.8718 | - | -
| D) HSD | M.Taka | 21.7388 | - | -
| E) Hydro | M.Taka | 6.8302 | - | -
| F) Solar | M.Taka | 1941.6055 | - | -
| G) Total Import | M.Taka | 8012.0766 | - | -
| H) Wind | M.Taka | 66.7246 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2051.2581 | 2025-11-06
| A) Gas | M.Taka | 478.7429 | 2025-11-01
| B) Coal | M.Taka | 567.7087 | 2025-11-01
| C) HFO | M.Taka | 758.9621 | 2025-11-06
| D) HSD | M.Taka | 9.8151 | 2025-11-30 | -
| E) Hydro | M.Taka | 0.52699 | 2025-11-01 | -
| F) Solar | M.Taka | 76.9201 | 2025-11-17 | -
| G) Total Import | M.Taka | 325.3586 | 2025-11-06
| H) Wind | M.Taka | 6.6301 | 2025-11-05
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.8412
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 5.9977
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 106.1 | 30/11/2025 | 06:00
b) | Actual | FT (MSL) | 99.7 | 30/11/2025 | 06:00
22 | Peak Genaration of November 2024 | MW | 13253 | 2024-11-04 | 19:30
23 | Peak Demand of October 2024 | MW | 13253 | 2024-11-04 | 19:30
24 | Maximum peak Generation recorded upto 30/11/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 30/11/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 30/11/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [40 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [15 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [16 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | [6 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [47 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [16 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | [22 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [40 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [37 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [14 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [19 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | [25 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [45 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable |  | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [14 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 |  |  |  | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [29 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: November 2025
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | [9 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 |  | √ |  | √ |  | √ |  |  |  | √ | √ | √ |  |  |  |  | √ |  |  |  |  | √ |  | √ | √ | √ | √ | √
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 |  |  |  | √ | √ | √ | √ | √ | √ | [7 empty] | √ | √ | √ | √ | [5 empty] | √ | √ | √ | √ | √
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | [11 empty] | √ | √ | √ | √ | √ | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | [5 empty] | √ | [19 empty] | √ | √ | √ | √ | √
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | [9 empty] | √ | [16 empty] | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 |  |  |  | √ |  | √ |  |  |  | √ | √ | √ |  |  |  |  | √ |  |  |  |  | √ |  |  |  |  | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 |  |  |  | √ | √ |  |  |  |  | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | [5 empty] | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ |  |  | √ | √ | √ | √ |  | √ |  |  | √ |  | √ |  |  | √
| Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √ |  | √ |  | √ |  |  | √
| JERA Meghnaghat Power Limited | IPP | Gas | 718 | [21 empty] | √
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | [25 empty] | √ | √ | √ | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622