## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-12-2025 | during | 24-12-2025 | during | 24-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 336 | 345 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 7 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 40 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 25 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 21 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 8 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 116 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 47 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 68 | 82 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | ST Under maint.& Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 308 | 414 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1120 | 1520 | 5762.15 | 5741.15 | 2544.07 | 2516.07
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 223 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 35 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 19 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.12 | 0 | 3.11 | 0 | 3.11 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 915 | 1147 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 830 | 830 | 830 | 830 | 830 | 830 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 2027.12 | 2344 | 3667.83 | 3665.72 | 3157.61 | 3155.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 202 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 250 | 49 | 353.35 | 353.35 | 353.35 | 353.35
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0.01 | 0.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 340 | 355 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 5 | 5 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 20 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 105 | 106 | 163 | 163 | 112 | 112 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 36 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 108 | 114 | 160 | 160 | 122 | 122 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 0 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 104 | 104 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 58 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1123 | 933 | 2785.56 | 2725.56 | 1924.06 | 1864.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-12-2025 | during | 24-12-2025 | during | 24-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 43 | 33 | 157.5 | 157.5 | 55 | 55 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 58 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.43 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 133.43 | 109 | 361.5 | 314 | 211.5 | 164
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 36 | 36 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 160 | 158 | 158 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 211 | 212 | 210 | 210 | 210 | 210 | GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 574 | 568 | 596 | 596 | 598 | 598
| Rupsha 800 MW CCPP | Gas/HSD | NWPGCL | 1*800 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 145 | 80 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 803 | 950 | 0 | 0 | 900 | 900 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1934 | 1922 | 2343 | 2278 | 2072.1 | 2007.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 250 | 410 | 0 | 0 | 500 | 500 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 133 | 136 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 665 | 965 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant is on standby as per NLDC instruction
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1268.53 | 1731 | 2009.32 | 2009.32 | 2069.32 | 2069.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 49.84 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 320 | 368 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 924 | 1325.37 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.56 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1575.4 | 1833.37 | 3079.87 | 2913.87 | 2572.49 | 2406.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 52 | 53 | 53 | 58 | 58 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Coal shortage
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.4 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 122 | 0 | 130.77 | 0 | 130.77 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 185.4 | 52 | 478.97 | 315 | 449.97 | 286
System Total |  |  |  |  | 28823.2 | 28379.108 | 9940.88 | 11012.37 | 21084.2 | 20558.62 | 15599.12 | 15066.54
Forecast Scenario (24-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9210 |  | 0 |  | 9210
|  |  |  | 1:00 | 8350 |  | 0 |  | 8350
|  |  |  | 2:00 | 8030 |  | 0 |  | 8030
|  |  |  | 3:00 | 7940 |  | 0 |  | 7940
|  |  |  | 4:00 | 7500 |  | 0 |  | 7500
|  |  |  | 5:00 | 7560 |  | 0 |  | 7560
|  |  |  | 6:00 | 7980 |  | 0 |  | 7980
|  |  |  | 7:00 | 8400 |  | 0 |  | 8400
|  |  |  | 8:00 | 9330 |  | 0 |  | 9330
|  |  |  | 9:00 | 9660 |  | 0 |  | 9660
|  |  |  | 10:00 | 9350 |  | 0 |  | 9350
|  |  |  | 11:00 | 9570 |  | 0 |  | 9570
|  |  |  | 12:00 | 10040 |  | 0 |  | 10040
|  |  |  | 13:00 | 10450 |  | 0 |  | 10450
|  |  |  | 14:00 | 10060 |  | 0 |  | 10060
|  |  |  | 15:00 | 9730 |  | 0 |  | 9730
|  |  |  | 16:00 | 9530 |  | 0 |  | 9530
|  |  |  | 17:00 | 9940 |  | 0 |  | 9940
|  |  |  | 18:00 | 11110 |  | 0 |  | 11110
|  |  |  | 18:30 | 11000 |  | 0 |  | 11000
|  |  |  | 19:00 | 11030 |  | 0 |  | 11030
|  |  |  | 19:30 | 10960 |  | 0 |  | 10960
|  |  |  | 20:00 | 10850 |  | 0 |  | 10850
|  |  |  | 21:00 | 10670 |  | 0 |  | 10670
|  |  |  | 22:00 | 10310 |  | 0 |  | 10310
|  |  |  | 23:00 | 9700 |  | 0 |  | 9700
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 10040.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11110.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11110.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 226.30 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:45 hrs on 24-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-12-2025 | [28 empty] | Date: | 23-12-2025 | [28 empty] | Date: | 23-12-2025 | [28 empty] | Date: | 23-12-2025 | [28 empty] | Date: | 23-12-2025 | [17 empty] | Date: | 23-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 830 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 179 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 212 | 34 | 30 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 4779.5 | 807 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 4 | 0 | 922.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 300 | 860 | 0 | 4337.45 | 9116.95 | 98.42
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 700 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 220 | 280 | 0 | 51 | 0 | 192 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 17 | 0 | 5 | 30 | 0 | 0 | 156 | 0 | 8 | 0 | 34 | 0 | 0 | 0 | 4320.5 | 783 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 0 | 4 | 0 | 864.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 250 | 700 | 0 | 3933.41 | 8253.91 | 98.42
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 660 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 720 | 0 | 0 | 0 | 220 | 280 | 0 | 5 | 0 | 150 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 156 | 0 | 8 | 0 | 54 | 0 | 0 | 0 | 3867.5 | 714 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 676 | 0 | 4 | 0 | 834.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 600 | 0 | 4063.47 | 7930.97 | 98.42
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 660 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 211 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 3740.5 | 713 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 0 | 4 | 0 | 822.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 540 | 0 | 4108.62 | 7849.12 | 98.42
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 660 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 625 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 211 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 3449.5 | 618 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 0 | 4 | 0 | 830.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3958.68 | 7408.18 | 98.42
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 660 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 211 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 3499.5 | 618 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 4 | 0 | 832.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3963.86 | 7463.36 | 98.41
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 660 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 31 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 3866.5 | 665 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 4 | 0 | 831.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 180 | 0 | 250 | 500 | 0 | 4020.02 | 7886.52 | 98.41
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 40 | 0 | 30 | 660 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 800 | 1 | 0 | 0 | 300 | 0 | 0 | 35 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 78 | 0 | 2 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 32 | 20 | 0 | 0 | 157 | 0 | 0 | 0 | 54 | 0 | 0.25 | 0 | 4038.88 | 712 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 797 | 0 | 4 | 0 | 828.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0 | 0 | 0 | 0.96 | 0 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 140 | 220 | 0 | 250 | 620 | 0 | 4270.02 | 8308.9 | 98.41
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 280 | 0 | 0 | 7 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 40 | 0 | 10 | 700 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 958 | 7 | 0 | 0 | 355 | 100 | 0 | 51 | 0 | 202 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 92 | 0 | 16 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 3 | 0 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 29 | 18 | 54 | 0 | 2.45 | 0 | 4659.35 | 805 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.31 | 819 | 0 | 4 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.97 | 7 | 0 | 0 | 4.24 | 0 | 0 | 140 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 9 | 0.1 | 0 | 0 | 136 | 220 | 0 | 300 | 747 | 0 | 4572.92 | 9232.27 | 98.4
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 280 | 0 | 0 | 15 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 40 | 0 | 3 | 830 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 964 | 12 | 0 | 0 | 320 | 100 | 0 | 51 | 0 | 198 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 102 | 0 | 34 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 1 | 8 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 57 | 18 | 46 | 0 | 6.13 | 0 | 4802.97 | 901 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 830 | 0 | 4 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.55 | 21 | 0 | 0 | 8.46 | 0 | 0 | 140 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 53 | 0 | 3 | 0 | 0 | 0 | 0 | 0.6 | 19 | 0.23 | 0 | 0 | 136 | 180 | 0 | 300 | 820 | 0 | 4759.84 | 9562.81 | 98.4
10:00 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 347 | 0 | 0 | 280 | 0 | 0 | 22 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.59 | 40 | 0 | 2 | 830 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 820 | 16 | 0 | 0 | 308 | 100 | 0 | 51 | 0 | 197 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 102 | 0 | 48 | 0 | 0 | 0 | 211 | 35 | 30 | 0 | 5 | 17 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 59 | 18 | 47 | 0 | 10.11 | 0 | 4733.7 | 901 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 808 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.74 | 36 | 0 | 0 | 19.62 | 0 | 0 | 140 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 1.1 | 36 | 0.38 | 0 | 0 | 100 | 180 | 0 | 250 | 600 | 0 | 4518.84 | 9252.54 | 98.4
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 27 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.02 | 40 | 0 | 2 | 830 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 809 | 18 | 0 | 0 | 305 | 210 | 0 | 51 | 0 | 190 | 0 | 0 | 106 | 0 | 0 | 11 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 211 | 35 | 30 | 0 | 9 | 17 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 45 | 8 | 46 | 0 | 26.14 | 0 | 4818.16 | 901 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 821 | 0 | 0 | 0 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.65 | 81 | 0 | 0 | 46.78 | 0 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 52 | 0 | 6 | 0 | 0 | 0 | 0 | 1.5 | 70 | 0.48 | 0 | 0 | 100 | 180 | 0 | 250 | 600 | 0 | 4656.41 | 9474.57 | 98.4
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 308 | 0 | 0 | 250 | 0 | 0 | 28 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 40 | 0 | 3 | 830 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 915 | 17 | 0 | 0 | 340 | 250 | 0 | 51 | 0 | 200 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 108 | 0 | 58 | 0 | 0 | 0 | 211 | 36 | 30 | 0 | 9 | 17 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 45 | 8 | 43 | 1 | 36.43 | 0 | 4977.55 | 901 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 803 | 0 | 12 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.84 | 93 | 0 | 0 | 48.56 | 0 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 52 | 0 | 10 | 0 | 0 | 0 | 0 | 1.4 | 122 | 0.53 | 0 | 0 | 133 | 220 | 0 | 250 | 665 | 0 | 4963.33 | 9940.88 | 98.39
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 382 | 0 | 0 | 250 | 0 | 0 | 27 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 40 | 0 | 12 | 830 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 976 | 18 | 0 | 0 | 220 | 254 | 0 | 51 | 0 | 180 | 0 | 0 | 103 | 0 | 0 | 11 | 0 | 118 | 0 | 54 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 9 | 17 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 45 | 8 | 43 | 2 | 35.09 | 0 | 5010.03 | 901 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 890 | 0 | 12 | 0 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.13 | 92 | 0 | 0 | 46.36 | 0 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 14 | 0 | 0 | 0 | 0 | 1.5 | 141 | 0.49 | 0 | 0 | 136 | 220 | 0 | 250 | 863 | 0 | 5348.48 | 10358.51 | 98.39
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 386 | 0 | 0 | 250 | 0 | 0 | 21 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 40 | 0 | 12 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 942 | 15 | 0 | 0 | 220 | 110 | 0 | 51 | 0 | 208 | 0 | 0 | 103 | 0 | 0 | 11 | 0 | 118 | 0 | 47 | 0 | 0 | 0 | 211 | 36 | 30 | 0 | 7 | 17 | 0 | 83 | 30 | 0 | 0 | 157 | 0 | 45 | 8 | 33 | 1 | 29.31 | 0 | 4804.14 | 902 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 868 | 0 | 36 | 0 | 915.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 74 | 0 | 0 | 37.24 | 0 | 0 | 140 | 0 | 0 | 0 | 352 | 0 | 3.63 | 0 | 52 | 0 | 13 | 0 | 0 | 0 | 0 | 2.4 | 113 | 0.37 | 0 | 0 | 136 | 180 | 0 | 250 | 850 | 0 | 5165.29 | 9969.43 | 98.39
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 383 | 0 | 0 | 250 | 0 | 0 | 14 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03 | 40 | 0 | 8 | 830 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 878 | 12 | 0 | 0 | 280 | 23 | 0 | 51 | 0 | 190 | 0 | 0 | 104 | 0 | 0 | 11 | 0 | 114 | 0 | 28 | 0 | 0 | 0 | 211 | 36 | 30 | 0 | 4 | 17 | 0 | 80 | 30 | 0 | 0 | 157 | 0 | 45 | 8 | 33 | 1 | 19.22 | 0 | 4667.25 | 901 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 805 | 0 | 35 | 0 | 927.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.09 | 47 | 0 | 0 | 22.41 | 0 | 0 | 140 | 0 | 0 | 0 | 341 | 0 | 2.11 | 0 | 52 | 0 | 14 | 0 | 0 | 0 | 0 | 1.5 | 74 | 0.25 | 0 | 0 | 136 | 180 | 0 | 250 | 850 | 0 | 4971.33 | 9638.58 | 98.39
16:00 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 412 | 0 | 0 | 250 | 0 | 0 | 6 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 40 | 0 | 10 | 830 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 841 | 6 | 0 | 0 | 345 | 40 | 0 | 51 | 0 | 200 | 0 | 0 | 105 | 0 | 0 | 11 | 0 | 104 | 0 | 13 | 0 | 0 | 0 | 211 | 36 | 30 | 0 | 2 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 45 | 8 | 33 | 0 | 7.03 | 0 | 4741.73 | 901 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 776 | 0 | 2 | 0 | 836.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.26 | 21 | 0 | 0 | 8.22 | 0 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0.66 | 0 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0.7 | 30 | 0.12 | 0 | 0 | 136 | 220 | 0 | 250 | 760 | 0 | 4696.63 | 9438.36 | 98.39
17:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 9 | 0 | 116 | 0 | 15 | 0 | 4 | 68 | 0 | 0 | 0 | 415 | 0 | 30 | 250 | 0 | 0 | 1 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0.04 | 40 | 0 | 16 | 830 | 0 | 0 | 0 | 0 | 2 | 223 | 0 | 0 | 0 | 995 | 0 | 5 | 0 | 325 | 45 | 0 | 51 | 0 | 193 | 0 | 0 | 105 | 2 | 0 | 11 | 0 | 82 | 0 | 1 | 0 | 0 | 0 | 211 | 36 | 30 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 160 | 0 | 58 | 8 | 33 | 0 | 0.48 | 0 | 4932.52 | 901 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 786 | 0 | 0 | 0 | 1044.04 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.96 | 2 | 0 | 0 | 0.82 | 0 | 0 | 140 | 0 | 0 | 0 | 342 | 0 | 0.09 | 0 | 52 | 35 | 1 | 0 | 0 | 0 | 0 | 0.1 | 2 | 0.02 | 0 | 0 | 136 | 220 | 0 | 348 | 800 | 0 | 4915.03 | 9847.55 | 98.38
18:00 | 0 | 47 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 40 | 0 | 116 | 0 | 45 | 0 | 25 | 82 | 0 | 0 | 0 | 414 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 19 | 830 | 0 | 0 | 0 | 0 | 35 | 223 | 0 | 0 | 0 | 1147 | 0 | 20 | 0 | 355 | 49 | 0 | 51 | 0 | 202 | 0 | 0 | 106 | 36 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 58 | 18 | 33 | 0 | 0 | 0 | 5474 | 892 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 1325.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 410 | 965 | 0 | 5538.37 | 11012.37 | 98.38
19:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 830 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1164 | 0 | 0 | 0 | 340 | 145 | 0 | 51 | 0 | 198 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 58 | 18 | 33 | 0 | 0 | 0 | 5114 | 892 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1271.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 54 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 507 | 990 | 0 | 5819.48 | 10933.48 | 98.38
19:30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 830 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 325 | 160 | 0 | 51 | 0 | 193 | 0 | 0 | 108 | 0 | 0 | 5 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 58 | 18 | 33 | 0 | 0 | 0 | 5059 | 892 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 1228.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 54 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 504 | 1030 | 0 | 5807.67 | 10866.67
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 830 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 330 | 170 | 0 | 51 | 0 | 192 | 0 | 0 | 108 | 0 | 0 | 7 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 59 | 18 | 47 | 0 | 0 | 0 | 5089 | 891 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1148.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 52 | 50 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 460 | 1030 | 0 | 5669.3 | 10758.3 | 98.37
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 830 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 325 | 210 | 0 | 51 | 0 | 191 | 0 | 0 | 109 | 0 | 0 | 11 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 45 | 8 | 47 | 0 | 0 | 0 | 5077 | 891 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 400 | 1045 | 0 | 5501 | 10578 | 98.37
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 830 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 315 | 300 | 0 | 51 | 0 | 187 | 0 | 0 | 108 | 0 | 0 | 11 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 45 | 8 | 47 | 0 | 0 | 0 | 5045 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 180 | 0 | 300 | 1030 | 0 | 5174 | 10219 | 98.37
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 830 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 310 | 280 | 0 | 51 | 0 | 203 | 0 | 0 | 108 | 0 | 0 | 20 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 161 | 0 | 45 | 0 | 53 | 0 | 0 | 0 | 4860.5 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 180 | 0 | 250 | 920 | 0 | 4618 | 9478.5 | 98.37
Total KWH | 0 | 273600 | 22080 | 0 | 0 | 0 | 0 | 0 | 8254800 | 0 | 0 | 66600 | 0 | 1165968 | 0 | 65236 | 0 | 51658 | 668160 | 0 | 0 | 0 | 8741212 | 0 | 94348 | 6678157 | 0 | 0 | 169205 | 6000 | 453600 | 528840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62400 | 16801 | 964000 | 0 | 341760 | 18705454.55 | 0 | 0 | 0 | 0 | 71927 | 5086283 | 0 | 0 | 0 | 21927270 | 119205 | 51854 | 0 | 7079000 | 3854500 | 0 | 1036608 | 0 | 4726000 | 0 | 0 | 2238535 | 109440 | 0 | 299310 | 0 | 2352960 | 0 | 357755 | 0 | 0 | 0 | 5158000 | 841000 | 720360 | 0 | 47560 | 271344 | 0 | 1490880 | 661920 | 0 | 0 | 3389950 | 0 | 894000 | 182400 | 951360 | 6600 | 171940 | 0 | 111427840.55 | 19650181 | 2674944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460080 | 20203630 | 0 | 129636 | 0 | 22488364 | 0 | 0 | 0 | 0 | 0 | 3737 | 0 | 0 | 0 | 256316 | 477986 | 0 | 0 | 243760 | 0 | 0 | 3644864 | 0 | 0 | 0 | 8636290 | 0 | 7320 | 0 | 1234473 | 172590 | 70789 | 65702 | 0 | 0 | 0 | 11508.6 | 608400 | 2949 | 0 | 0 | 3004000 | 5180771 | 0 | 7163636 | 19400727.27 | 0 | 115792653.87 | 227220494.42

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9940.88 | MW | 12:00 Hr. | Energy Generated |  |  | 227.2205 |  | MKWHr.
| Day Peak Demand |  |  | 9940.88 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11012.37 | MW | 18:00 Hr. | Energy Demand |  |  | 227.2205 |  | MKWHr.
| Evening Peak Demand |  |  | 11012.37 | MW | 18:00 Hr. | Maximum Temperature |  |  | 26.8 |  | °C
| Minimum Generation of the Day |  |  | 7408.18 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 658.36 |  | MMCFD
| Maximum Generation of the Day |  |  | 11012.37 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.5536 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.6566 | 0 | 2.4137 | 0 | 0 | 0.1692 | 0 | 0 | 27.2395 | Gas | 86.0739 | Gas | 299520746.83
| Chattogram Zone |  |  | 5.428 | 40.6327 | 0.13433 | 0 | 0.964 | 0.13601 | 0 | 0 | 47.2951 | Coal | 88.6352 | Coal | 589442639.4781
| Cumilla Zone |  |  | 19.234 | 0 | 0.16129 | 0 | 0 | 0.35775 | 2.353 | 0 | 22.106 | HFO | 4.0277 | HFO | 66331924.34
| Mymensingh Zone |  |  | 0.95136 | 0 | 1.0764 | 0 | 0 | 0.17854 | 0 | 0 | 2.2063 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 12.5335 | 0 | 0 | 0 | 0 | 0.04756 | 0 | 0 | 12.581 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 2.8046 | 20.2036 | 0 | 0 | 0 | 0.46008 | 19.6502 | 0 | 43.1185 | Solar | 3.0282 | Solar | 46829090.71
| Barishal Zone |  |  | 8.1848 | 26.5644 | 0 | 0 | 0 | 0.002949 | 0 | 0 | 34.7521 | Import | 44.4915 | Import | 259664534.84
| Rajshahi Zone |  |  | 12.2812 | 0 | 0.003737 | 0 | 0 | 0.98538 | 22.4884 | 0 | 35.7586 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 1.2345 | 0.23829 | 0 | 0 | 0.6907 | 0 | 0 | 2.1635
| Total |  |  | 86.0739 | 88.6352 | 4.0277 | 0 | 0.964 | 3.0282 | 44.4915 | 0 | 227.2205
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 299520746.83 |  | Hydro | 96400
|  |  |  | Coal | 589442639.4781 |  | Solar | 46829090.71
|  |  |  | HFO | 66331924.34 |  | Import | 259664534.84
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 126,18,85,336 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.6502 | Peak Hr Flow | 892.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42366981.83 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.4884 | Peak Hr Flow | 1325.37 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2179 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.353 | Peak Hr Flow | 114.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2455 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.4915 | Peak Hr Flow | 2331.37 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4187
|  |  |  | Chattogram |  | 0 |  | 1198
|  |  |  | Cumilla |  | 0 |  | 897
|  |  |  | Mymensingh |  | 0 |  | 864
|  |  |  | Sylhet |  | 0 |  | 407
|  |  |  | Khulna |  | 0 |  | 1267
|  |  |  | Barishal |  | 0 |  | 310
|  |  |  | Rajshahi |  | 0 |  | 1006
|  |  |  | Rangpur |  | 0 |  | 741
|  |  |  | Total |  | 0 |  | 10877
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 710
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 | 16:03 | Benapole-Jashore 132 kV Ckt-1 Scheduled S/D from Benapole 132/33kV end Due to 132 KV
Benapole-Jashore line-1 annual maintenance. and from Jashore 132/33kV end Due to Annual
Maintenance
| 08:15 | 15:48 | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Barishal 230/132kV end Due to Annual maintenance
| 08:22 | 17:26 | Chattak-Sunamganj 132 kV Ckt-1 Scheduled S/D from Sunamganj 132/33kV end Due to Due to
dead line checking
| 08:22 | 17:24 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-1 Scheduled S/D Due to Annual
Maintenance. Shutdown taken by Shikalbaha 230kV Grid.
| 08:23 | 17:26 | Chhatak 132/33kV S/S Sunamganj 1 Scheduled S/D Due to Dead Line Checking
| 08:28 | 18:12 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to Annual Maintenance.
| 08:28 | 18:10 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to Annual Maintenance.
| 08:31 | 16:31 | Kallyanpur-Lalbag 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to Annual
Maintenance.
| 08:31 | 15:13 | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end. and from Haripur
230/132kV end Due to Annual maintenance
| 08:38 | 18:43 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance work
| 08:41 | 17:46 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Bay Equipment
Annual maintenance work
| 08:43 | 15:31 | Shahjibazar-Sreemangal 132kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to
Annual Maintenance and from Sreemongol 132/33kV end Due to For annual maintenance.
| 08:47 | 13:58 | Chandpur 132/33kV S/S 115MW CPGL Power Plant Incomer (L5) Scheduled S/D Due to Annual
maintenance
| 08:52 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Annual
maintenance.
| 08:59 | 14:34 | Fenchuganj 230/132/33kV S/S AT-01 HT Scheduled S/D Due to Annual Maintenance
| 08:59 | 14:31 | Fenchuganj 230/132/33kV S/S AT-01 LT Scheduled S/D Due to Annual Maintenance
| 09:00 | 16:38 | Amnura-Chapainawabganj-132kV Ckt-1 Scheduled S/D from Amnura 132/33kV end Due to Annual
maintenance. and from Chapai 132/33kV end Due to Annual Maintenance
| 09:01 | 12:36 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to Tan Delta test
| 09:01 | 12:34 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D
| 09:13 | 17:49 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual Maintenance
| 09:18 | 18:13 | Kabirpur-Kaliakoir 132kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to By
NLDC and from Kabirpur 132/33kV end Due to Annual maintenance
| 09:18 | 12:22 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to Am | [7 empty] | 80.0MW load
interrup.
| 09:18 | 12:22 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Am | [7 empty] | 80.0MW load
interrup.
| 09:19 | 12:21 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to Am | [7 empty] | 80.0MW load
interrup.
| 09:19 | 12:21 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to Am | [7 empty] | 80.0MW load
interrup.
| 09:19 | 09:33 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Am | [7 empty] | 80.0MW load
interrup.
| 09:20 | 09:32 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to Am | [7 empty] | 80.0MW load
interrup.
| 09:26 | 14:42 | Magura 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Annual maintenance
| 09:27 | 14:45 | Magura 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Annual maintenance
| 09:31 | 16:46 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D
| 09:32 | 16:46 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D
| 09:33 |  | Rajendrapur 132/33kV S/S 132 kV BUS-2 Project Work S/D
| 09:36 | 15:52 | BSRM-GPH 230 kV Ckt-2 Scheduled S/D from GPH 230/33kV end Due to shedule maintenance
| 09:57 | 16:34 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Scheduled S/D Due to Annual Maintenance
| 10:05 | 17:02 | Mongla 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenances
| 10:05 | 17:01 | Mongla 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenances
| 10:15 | 19:39 | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to Annual Maintenance Work
| 10:16 |  | Bibiana 400/230kV S/S Summit STG Scheduled S/D Due to AM
| 10:21 | 12:06 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 HT Scheduled S/D Due to Relay Testing
| 10:22 | 14:55 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D Due to Yearly Maintenance
| 10:23 | 14:53 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to Yearly Maintenance
| 10:34 | 17:04 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to Ten -delta test
| 10:35 | 17:04 | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to ten-delta test
| 10:37 | 13:49 | Mahasthangar-Palashbari 132kV Ckt-2 Forced S/D from Palashbari 132/33kV end Due to
Annual Maintenance and from Mahasthangarh 132/33kV end Due to Annual Maintenance
| 10:37 | 17:11 | Bogura 400/230kV S/S ATR-03 LT Scheduled S/D Due to Annual Maintenance
| 10:37 | 17:11 | Bogura 400/230kV S/S ATR-03 HT Scheduled S/D Due to Annual Maintenance
| 10:41 | 15:43 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to
Transmission line maintenance work
|  | 11:05 | Meghnaghat 400/230kV S/S ATR -03 HT is restored.
|  | 11:05 | Meghnaghat 400/230kV S/S ATR -03 LT is restored.
| 11:32 | 21:05 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Project Work S/D Due to Project work done by
SPMD at BR Powergen End
| 11:33 | 21:05 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Project Work S/D Due to Project work done by
SPMD at BR Powergen End
|  | 11:33 | Sherpur 132/33kV S/S Transformer- 03 LT is restored.
|  | 11:33 | Sherpur 132/33kV S/S Transformer- 03 HT is restored.
| 12:14 | 13:12 | Satmasjid 132/33kV S/S 132/33 KV Transformer-2 HT Scheduled S/D Due to relay testing
|  | 12:19 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT is restored.
| 12:48 | 19:22 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Tan Delta test
| 12:49 | 19:24 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D
|  | 12:52 | Barishal 132/33kV S/S 132 kv Summit power is restored.
| 13:32 | 14:06 | Satmasjid 132/33kV S/S 132 KV Agargaon-Satmasjid Line-1 Scheduled S/D Due to Relay
testing
| 13:34 | 19:51 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Tan Delta test
| 13:34 | 19:49 | Barishal 230/132kV S/S T-4 HT Scheduled S/D
| 14:06 | 17:11 | Satmasjid 132/33kV S/S 132 KV Agargaon-Satmasjid Line-2 Scheduled S/D Due to Annual
Maintance
| 15:33 | 18:15 | Rampura-Ullon-2 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to SD by NLDC
|  | 16:13 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT is restored.
|  | 16:16 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT is restored.
|  | 16:52 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 is restored.
| 18:00 |  | Evening Peak generation: 11012 MW.
| 18:12 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
| 20:33 |  | Bheramara 410 MW CCPP ST Forced Shutdown with remarks:- Shutdown due to gas shortage
| 20:33 |  | Bheramara 410 MW CCPP Shutdown with remarks:- STG
| 21:15 |  | Bheramara 410 MW CCPP GT Forced Shutdown with remarks:- Shutdown due to gas shortage
| 21:15 |  | Bheramara 410 MW CCPP Shutdown with remarks:- GTG
|  | 23:09 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
| 05:00 |  | Minimum Generation: 7451 MW.
| 06:15 | 06:37 | Fenchuganj-Kulaura 132 kV Ckt-2 Tripped from Kulaura 132/33kV end showing Distance | [7 empty] | 8.0MW load
|  |  | Protection Relay relays. | [7 empty] | interrup. Kulaura
132/33kV end
| 06:15 | 06:35 | Fenchuganj-Kulaura 132 kV Ckt-1 Tripped from Kulaura 132/33kV end showing Distance | [7 empty] | 8.0MW load
|  |  | Protection Relay relays. | [7 empty] | interrup. Kulaura
132/33kV end
| 06:15 | 06:57 | Kulaura 132/33kV S/S TR-2 LT Tripped showing Differential relay relays. | [7 empty] | 7.0MW load
interrup.
| 06:15 | 06:50 | Kulaura 132/33kV S/S TR-2 HT Tripped showing Differential relay relays. | [7 empty] | 7.0MW load
interrup.
| 06:15 | 06:58 | Kulaura 132/33kV S/S TR-1 AB LT Tripped showing Differential relay relays. | [7 empty] | 10.0MW load
interrup.
| 06:15 | 06:48 | Kulaura 132/33kV S/S TR-1 AB HT Tripped showing Differential Relay Over current | [7 empty] | 10.0MW load
|  |  | protection relay relays Due to None | [7 empty] | interrup.
| 07:11 |  | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D Due to Due to Dead Line
Checking
| 07:20 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Tripped showing ABB relays.
| 07:20 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT Tripped showing ABB relays.
| 07:46 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual Maintenance
| 07:51 |  | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Piling work of RHD
| 07:53 |  | Jaldhaka 132/33kV S/S 406T-1 LT Scheduled S/D Due to PBS 33 kV feeder (New feeder) | [7 empty] | 13.0MW load
|  |  | Connect on 33 kV BUS section-1. | [7 empty] | interrup.
| 07:53 |  | Jaldhaka 132/33kV S/S 406T-1 HT Scheduled S/D Due to PBS 33 kV feeder (New feeder) | [7 empty] | 13.0MW load
|  |  | Connect on 33 kV BUS section-1 | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 8254800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6678157 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 40 | 66600 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 25 | 51658 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 94348 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 453600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 528840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 22080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 65236 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 116 | 1165968 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 47 | 273600 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 82 | 668160 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 169205 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 414 | 8741212 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 6000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1520 | 27239464
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119205 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 223 | 5086283 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 35 | 71927 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 19 | 341760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16801 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 62400 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1147 | 21927270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 830 | 18705454.55 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 2344 | 47295100.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 202 | 4726000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 49 | 3854500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 355 | 7079000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1036608 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 51854 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 106 | 2238535 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 36 | 109440 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 114 | 2352960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 0 | 299310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 357755 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 933 | 22105962
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 951360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 182400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 894000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 171940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 109 | 2206300
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 47560 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 36 | 841000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 661920 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1490880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3389950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 271344 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 212 | 5158000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 568 | 12581014
| Rupsha 800 MW CCPP |  | NWPGCL | 1*800 | 0 | 0 | 129636 | -
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 19650181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 80 | 2674944 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 460080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 950 | 20203630 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1922 | 43118471
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 410 | 7163636 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 136 | 3004000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 965 | 19400727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5180771 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2949 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1731 | 34752083.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 256316 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 3737 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3644864 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 368 | 8636290 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 7320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1325.37 | 22488364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 243760 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 477986 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1833.37 | 35758637
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1234473 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Coal shortage
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 65702 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 11508.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 172590 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 70789 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 608400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 52 | 2163462.6
Eastern Grid Total |  |  |  |  | 17395.105 | 5474 | 111427840.55
Western Grid Total |  |  |  |  | 10984.003 | 5538.37 | 115792653.87
National Grid Total |  |  |  |  | 28379.108 | 11012.37 | 227220494.42
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-12-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7553.15 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3324.1 | MW
i) Dhaka area |  |  | 4186.65 |  | MW | i) Khulna area |  |  |  | 1267 | MW
ii) Chattogram area |  |  | 1198.5 |  | MW | ii) Barishal area |  |  |  | 310.5 | MW
iii) Cumilla area |  |  | 897 |  | MW | iii) Rajshahi area |  |  |  | 1005.6 | MW
iv) Mymensingh area |  |  | 864 |  | MW | iv) Rangpur area |  |  |  | 741 | MW
v) Sylhet area |  |  | 407 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10877.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 73 | 12:00 | 133 | Netrakona | 105 | 18:00
2 | AKSML | 120 | 06:00 | 68 | Hathazari | 54 | 13:00 | 134 | New | 76.8 | 12:00
3 | Aftabnagar | 28 | 13:00 | 69 | Hatirjheel | 24 | 11:00 | 135 | Niamatpur | 46 | 08:00
4 | Agargaon | 80 | 13:00 | 70 | Ishurdi | 51 | 18:00 | 136 | Noapara | 40 | 18:00
5 | Agrabad | 42 | 18:00 | 71 | Jaldhaka | 52 | 18:30 | 137 | PHP | 9 | 15:00
6 | Amnura | 23 | 12:00 | 72 | Jamalpur | 91 | 18:00 | 138 | Pabna | 74 | 18:00
7 | Ashuganj | 63 | 13:00 | 73 | Jashore | 107 | 18:00 | 139 | Palashbari | 75 | 18:00
8 | BSRM | 195 | 02:00 | 74 | Jhenaidah | 89 | 18:30 | 140 | Panchagarh | 49 | 18:30
9 | Bagerhat | 62 | 18:00 | 75 | Joydebpur | 83 | 18:00 | 141 | Patiya | 6 | 18:00
10 | Bajitpur | 58 | 21:00 | 76 | Joypurhat | 43 | 18:30 | 142 | Patuakhali | 42 | 21:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 15 | 16:00 | 143 | Payra | 22 | 18:00
12 | Bakulia | 66 | 18:00 | 78 | KSRM | 18 | 09:00 | 144 | Postogola | 39 | 13:00
13 | Banani | 19 | 13:00 | 79 | Kabirpur | 195 | 18:00 | 145 | Purbachal | 20 | 18:00
14 | Bangabhaban | 13 | 13:00 | 80 | Kachua | 55 | 19:00 | 146 | Purbasadipur | 110 | 18:30
15 | Barapukuria | 50 | 18:30 | 81 | Kallyanpur | 69 | 14:00 | 147 | Rahanpur | 23 | 19:00
16 | Barguna | 14 | 18:30 | 82 | Kalurghat | 34 | 15:00 | 148 | Rahim | 48 | 14:00
17 | Barishal | 84 | 14:00 | 83 | Kamrangirchar | 60 | 12:00 | 149 | Rajbari | 57 | 18:00
18 | Barishal-230 | 67 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 121 | 19:00
19 | Baroaulia | 57 | 17:00 | 85 | Kasba | 22 | 19:30 | 151 | Rajshahi | 76 | 19:30
20 | Baroirhat | 50 | 18:00 | 86 | Kazla | 84 | 13:00 | 152 | Rajshahi-230 | 56 | 13:00
21 | Bashundhara | 129 | 12:00 | 87 | Keranigonj | 59 | 18:30 | 153 | Ramganj | 74 | 18:00
22 | BashundharaCement | 8 | 18:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 27 | 18:00
23 | Beanibazar | 46 | 18:00 | 89 | Khulna | 54 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 38 | 08:00 | 90 | Khulshi | 171 | 18:30 | 156 | Rangpur | 90 | 18:00
25 | Bhaluka | 124 | 18:30 | 91 | Kishoreganj | 86 | 18:00 | 157 | Ruppur | 2.4 | 15:00
26 | Bhandaria | 36 | 19:30 | 92 | Kodda | 257 | 17:00 | 158 | SSM | 3 | 03:00
27 | Bhangura | 23 | 18:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 96 | 18:00
28 | Bheramara(GK) | 41 | 18:00 | 94 | Kurigram | 47 | 08:00 | 160 | Satkhira | 87 | 18:00
29 | Bhulta | 198 | 12:00 | 95 | Kushtia | 114 | 18:00 | 161 | Satmasjid | 78 | 14:00
30 | Bog-Sherpur | 56 | 18:00 | 96 | Laksam | 21 | 13:00 | 162 | Savar | 164 | 12:00
31 | Bogura | 115 | 18:30 | 97 | Lakshmipur | 24 | 21:00 | 163 | SevenRings | 13.44 | 20:00
32 | Borhanuddin | 65 | 21:00 | 98 | Lalbag | 54 | 18:00 | 164 | ShahCement | 27 | 00:00
33 | Brahmanbaria | 86 | 18:00 | 99 | Lalmonirhat | 42 | 18:00 | 165 | Shahjadpur | 58 | 18:00
34 | Cantonment | 87 | 13:00 | 100 | MI_Cement | 17.3 | 01:00 | 166 | Shahjibazar | 81 | 18:00
35 | Chandina | 19 | 21:00 | 101 | Madanganj | 34 | 12:00 | 167 | Shahmirpur | 37 | 18:00
36 | Chandpur | 52 | 17:00 | 102 | Madaripur | 68 | 20:00 | 168 | Shariatpur | 56 | 21:00
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 54 | 13:00 | 169 | Sherpur | 100 | 18:00
38 | Chapai | 49 | 13:00 | 104 | Madunaghat | 38 | 12:00 | 170 | Shikalbaha | 25 | 12:00
39 | Charsaidpur | 40 | 00:00 | 105 | Magura | 47 | 18:00 | 171 | Shitalakhya | 64.1 | 12:00
40 | Chauddagram | 49 | 13:00 | 106 | Mahasthangarh | 46 | 18:00 | 172 | Sholosohor | 34 | 18:00
41 | Chhatak | 19 | 19:30 | 107 | Maijdee | 29 | 21:00 | 173 | Shyampur | 132 | 12:00
42 | Chowmuhani | 104 | 18:00 | 108 | Manikganj | 90 | 18:30 | 174 | Siddhirganj | 97 | 12:00
43 | Chuadanga | 76 | 18:00 | 109 | Maniknagar | 51 | 13:00 | 175 | Sirajganj | 82 | 18:30
44 | Coxsbazar | 112 | 18:00 | 110 | Matarbari | 35 | 18:00 | 176 | Sonargaon | 142 | 12:00
45 | Cumilla(N) | 78 | 13:00 | 111 | Matuail | 44 | 09:00 | 177 | Sreemongol | 54 | 18:00
46 | Cumilla(S) | 122 | 14:00 | 112 | Metrorail_Motijheel | 21 | 18:30 | 178 | Sreepur | 90 | 18:30
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 11 | 18:00 | 179 | Srinagar | 29.02 | 20:00
48 | Daudkandi | 106 | 20:00 | 114 | Millgate | 77 | 12:00 | 180 | Sunamganj | 38 | 18:00
49 | DhakaUniversity | 54 | 13:00 | 115 | Mirpur | 110 | 13:00 | 181 | Sylhet | 38 | 18:00
50 | Dhamrai | 98 | 18:00 | 116 | Mirsorai | 9 | 09:00 | 182 | Sylhet-132 | 81 | 18:00
51 | Dhanmondi | 67.6 | 13:00 | 117 | Mirzapur | 38 | 18:30 | 183 | TK | 18 | 01:00
52 | Dohazari | 72 | 19:00 | 118 | Mithapukur | 48 | 18:00 | 184 | Tangail | 116 | 18:00
53 | Faridpur | 115 | 19:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 26 | 18:00
54 | Fatullah | 97 | 12:00 | 120 | Mogbazar | 69.2 | 14:00 | 186 | Tasnim | 14 | 07:00
55 | Fenchuganj | 24 | 18:00 | 121 | Mongla | 40 | 18:00 | 187 | Thakurgaon | 83 | 18:30
56 | Feni | 68 | 13:00 | 122 | Motijheel | 27 | 13:00 | 188 | Tongi | 94 | 11:00
57 | GPH | 95 | 04:00 | 123 | Muktagacha | 25 | 08:00 | 189 | Ullahpara | 27 | 18:00
58 | Ghatail | 56 | 18:00 | 124 | Munshiganj | 76 | 13:00 | 190 | Ullon | 37 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 23 | 19:30 | 191 | Uttara | 68 | 13:00
60 | Ghorashal-230 | 83 | 18:30 | 126 | Mymensingh | 129 | 18:00 | 192 | UttaraNew | 42 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 88 | 19:00 | 193 | Zigatola | 54 | 14:00
62 | Gollamari | 66 | 13:00 | 128 | Narail | 40.5 | 18:30
63 | Gopalganj | 79 | 18:00 | 129 | Narinda | 59 | 13:00
64 | Gulshan | 78 | 13:00 | 130 | Narshingdi | 140 | 18:30
65 | Halishahar | 52 | 14:00 | 131 | Natore | 101 | 18:00
66 | HaripurSBU | 85 | 00:00 | 132 | Nawabganj | 29.4 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9116.95 | 0 |  | 9116.95
1:00 | 8253.91 | 0 |  | 8253.91
2:00 | 7930.97 | 0 |  | 7930.97
3:00 | 7849.12 | 0 |  | 7849.12
4:00 | 7408.18 | 0 |  | 7408.18
5:00 | 7463.36 | 0 |  | 7463.36
6:00 | 7886.52 | 0 |  | 7886.52
7:00 | 8308.9 | 0 |  | 8308.9
8:00 | 9232.27 | 0 |  | 9232.27
9:00 | 9562.81 | 0 |  | 9562.81
10:00 | 9252.54 | 0 |  | 9252.54
11:00 | 9474.57 | 0 |  | 9474.57
12:00 | 9940.88 | 0 |  | 9940.88
13:00 | 10358.51 | 0 |  | 10358.51
14:00 | 9969.43 | 0 |  | 9969.43
15:00 | 9638.58 | 0 |  | 9638.58
16:00 | 9438.36 | 0 |  | 9438.36
17:00 | 9847.55 | 0 |  | 9847.55
18:00 | 11012.37 | 0 |  | 11012.37
19:00 | 10933.48 | 0 |  | 10933.48
19:30 | 10866.67 | 0 |  | 10866.67
20:00 | 10758.3 | 0 |  | 10758.3
21:00 | 10578 | 0 |  | 10578
22:00 | 10219 | 0 |  | 10219
23:00 | 9478.5 | 0 |  | 9478.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4779.5 | 4337.45 | 9116.95 | DAILY GENERATION CURVE
00:30 | 4550 | 4135.43 | 8685.43
01:00 | 4320.5 | 3933.41 | 8253.91 | 23-12-2025
01:30 | 4094 | 3998.44 | 8092.44
02:00 | 3867.5 | 4063.47 | 7930.97
02:30 | 3804 | 4086.045 | 7890.045
03:00 | 3740.5 | 4108.62 | 7849.12
03:30 | 3595 | 4033.65 | 7628.65
04:00 | 3449.5 | 3958.68 | 7408.18
04:30 | 3474.5 | 3961.27 | 7435.77
05:00 | 3499.5 | 3963.86 | 7463.36
05:30 | 3683 | 3991.94 | 7674.94
06:00 | 3866.5 | 4020.02 | 7886.52
06:30 | 3952.69 | 4145.02 | 8097.71
07:00 | 4038.88 | 4270.02 | 8308.9
07:30 | 4349.115 | 4421.47 | 8770.585
08:00 | 4659.35 | 4572.92 | 9232.27
08:30 | 4731.16 | 4666.38 | 9397.54
09:00 | 4802.97 | 4759.84 | 9562.81
09:30 | 4768.335 | 4639.34 | 9407.675
10:00 | 4733.7 | 4518.84 | 9252.54
10:30 | 4775.93 | 4587.625 | 9363.555
11:00 | 4818.16 | 4656.41 | 9474.57
11:30 | 4897.855 | 4809.87 | 9707.725
12:00 | 4977.55 | 4963.33 | 9940.88
12:30 | 4993.79 | 5155.905 | 10149.695
13:00 | 5010.03 | 5348.48 | 10358.51
13:30 | 4907.085 | 5256.885 | 10163.97
14:00 | 4804.14 | 5165.29 | 9969.43
14:30 | 4735.695 | 5068.31 | 9804.005
15:00 | 4667.25 | 4971.33 | 9638.58
15:30 | 4704.49 | 4833.98 | 9538.47
16:00 | 4741.73 | 4696.63 | 9438.36
16:30 | 4837.125 | 4805.83 | 9642.955
17:00 | 4932.52 | 4915.03 | 9847.55
17:30 | 5203.26 | 5226.7 | 10429.96
18:00 | 5474 | 5538.37 | 11012.37
18:30 | 5294 | 5678.925 | 10972.925
19:00 | 5114 | 5819.48 | 10933.48
19:30 | 5059 | 5807.67 | 10866.67
20:00 | 5089 | 5669.3 | 10758.3
20:30 | 5083 | 5585.15 | 10668.15 |  | Executive Engineer
21:00 | 5077 | 5501 | 10578 |  | Network Operation Division
21:30 | 5061 | 5337.5 | 10398.5
22:00 | 5045 | 5174 | 10219
22:30 | 4952.75 | 4896 | 9848.75
23:00 | 4860.5 | 4618 | 9478.5

## En-Curve
QF-LDC-12
Date | 23-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2913 | 811.5 | 807 | 0 | 98 | 922.45 | 40 | 3490 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2840 | 716.5 | 795 | 0 | 92 | 893.43 | 40 | 3287 | 0 | 0 | 21.5 | 0 | 0 | 0 | 0 | 23-12-2025
01:00 | 2767 | 621.5 | 783 | 0 | 86 | 864.41 | 40 | 3084 | 0 | 0 | 8 | 0 | 0 | 0 | 0
01:30 | 2768 | 574.5 | 748.5 | 0 | 83 | 849.44 | 40 | 3021 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | Energy Generated | 227.2205 |  | MKWHr
02:00 | 2769 | 527.5 | 714 | 0 | 80 | 834.47 | 40 | 2958 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2734.5 | 537.5 | 713.5 | 0 | 80 | 828.545 | 40 | 2952 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | Total Energy Requirement | 227.2205 |  | MKWHr
03:00 | 2700 | 547.5 | 713 | 0 | 80 | 822.62 | 40 | 2946 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2562.5 | 540 | 665.5 | 0 | 81 | 826.65 | 40 | 2913 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2425 | 532.5 | 618 | 0 | 82 | 830.68 | 40 | 2880 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2458 | 535 | 618 | 0 | 81 | 831.77 | 40 | 2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2491 | 537.5 | 618 | 0 | 80 | 832.86 | 40 | 2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2558 | 612 | 641.5 | 0 | 82 | 832.12 | 40 | 2909 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2625 | 686.5 | 665 | 0 | 84 | 831.38 | 40 | 2954 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2662.5 | 725 | 688.5 | 0 | 81 | 829.795 | 40 | 3066.5 | 4.415 | 0 | 0 | 0 | 0 | 0 | 0
07:00 | 2700 | 763.5 | 712 | 0 | 78 | 828.21 | 40 | 3179 | 8.19 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 2805 | 808.25 | 758.5 | 0 | 85 | 827.605 | 40 | 3377.5 | 45.23 | 0 | 23.5 | 0 | 0 | 0 | 0
08:00 | 2910 | 853 | 805 | 0 | 92 | 827 | 40 | 3576 | 82.27 | 0 | 47 | 0 | 0 | 0 | 0
08:30 | 2879 | 828.5 | 853 | 0 | 97 | 824 | 40 | 3686.5 | 128.54 | 0 | 61 | 0 | 0 | 0 | 0
09:00 | 2848 | 804 | 901 | 0 | 102 | 821 | 40 | 3797 | 174.81 | 0 | 75 | 0 | 0 | 0 | 0
09:30 | 2808.5 | 771.5 | 901 | 0 | 102 | 828 | 40 | 3577.5 | 235.175 | 12 | 132 | 0 | 0 | 0 | 0
10:00 | 2769 | 739 | 901 | 0 | 102 | 835 | 40 | 3358 | 295.54 | 24 | 189 | 0 | 0 | 0 | 0
10:30 | 2810.5 | 721 | 901 | 0 | 101 | 836 | 40 | 3360 | 382.055 | 20.5 | 191.5 | 0 | 0 | 0 | 0
11:00 | 2852 | 703 | 901 | 0 | 100 | 837 | 40 | 3362 | 468.57 | 17 | 194 | 0 | 0 | 0 | 0
11:30 | 2905 | 719.5 | 901 | 0 | 104 | 880.5 | 40 | 3438.5 | 509.725 | 17 | 192.5 | 0 | 0 | 0 | 0
12:00 | 2958 | 736 | 901 | 0 | 108 | 924 | 40 | 3515 | 550.88 | 17 | 191 | 0 | 0 | 0 | 0
12:30 | 2949.5 | 774.5 | 901 | 0 | 113 | 921 | 40 | 3688 | 553.195 | 17 | 192.5 | 0 | 0 | 0 | 0
13:00 | 2941 | 813 | 901 | 0 | 118 | 918 | 40 | 3861 | 555.51 | 17 | 194 | 0 | 0 | 0 | 0
13:30 | 2841.5 | 796 | 901.5 | 0 | 118 | 916.825 | 40 | 3826.5 | 507.645 | 17 | 199 | 0 | 0 | 0 | 0
14:00 | 2742 | 779 | 902 | 0 | 118 | 915.65 | 40 | 3792 | 459.78 | 17 | 204 | 0 | 0 | 0 | 0
14:30 | 2713 | 776 | 901.5 | 0 | 116 | 921.81 | 40 | 3728.5 | 381.195 | 17 | 209 | 0 | 0 | 0 | 0
15:00 | 2684 | 773 | 901 | 0 | 114 | 927.97 | 40 | 3665 | 302.61 | 17 | 214 | 0 | 0 | 0 | 0
15:30 | 2747.5 | 810 | 901 | 0 | 109 | 882.32 | 40 | 3588 | 213.65 | 23 | 224 | 0 | 0 | 0 | 0
16:00 | 2811 | 847 | 901 | 0 | 104 | 836.67 | 40 | 3511 | 124.69 | 29 | 234 | 0 | 0 | 0 | 0
16:30 | 2757 | 850 | 901 | 0 | 93 | 940.355 | 40 | 3661 | 68.1 | 33.5 | 299 | 0 | 0 | 0 | 0
17:00 | 2703 | 853 | 901 | 0 | 82 | 1044.04 | 40 | 3811 | 11.51 | 38 | 364 | 0 | 0 | 0 | 0
17:30 | 2754 | 850 | 896.5 | 0 | 98 | 1184.705 | 40 | 4082.5 | 5.755 | 46.5 | 472 | 0 | 0 | 0 | 0
18:00 | 2805 | 847 | 892 | 0 | 114 | 1325.37 | 40 | 4354 | 0 | 55 | 580 | 0 | 0 | 0 | 0
18:30 | 2829.5 | 838 | 892 | 0 | 112 | 1298.425 | 40 | 4489.5 | 0 | 35.5 | 438 | 0 | 0 | 0 | 0
19:00 | 2854 | 829 | 892 | 0 | 110 | 1271.48 | 40 | 4625 | 0 | 16 | 296 | 0 | 0 | 0 | 0
19:30 | 2818 | 835 | 892 | 0 | 110 | 1228.67 | 40 | 4656 | 0 | 8 | 279 | 0 | 0 | 0 | 0
20:00 | 2844 | 844 | 891 | 0 | 104 | 1148.3 | 40 | 4622 | 0 | 0 | 265 | 0 | 0 | 0 | 0
20:30 | 2834.5 | 845 | 891 | 0 | 106 | 1133.15 | 40 | 4602 | 0 | 0 | 216.5 | 0 | 0 | 0 | 0
21:00 | 2825 | 846 | 891 | 0 | 108 | 1118 | 40 | 4582 | 0 | 0 | 168 | 0 | 0 | 0 | 0
21:30 | 2862.5 | 802 | 891.5 | 0 | 104 | 1071 | 40 | 4474.5 | 0 | 0 | 153 | 0 | 0 | 0 | 0
22:00 | 2900 | 758 | 892 | 0 | 100 | 1024 | 40 | 4367 | 0 | 0 | 138 | 0 | 0 | 0 | 0
22:30 | 2898 | 735.75 | 892 | 0 | 101 | 940.5 | 40 | 4150 | 0 | 0 | 91.5 | 0 | 0 | 0 | 0
23:00 | 2896 | 713.5 | 892 | 0 | 102 | 857 | 40 | 3933 | 0 | 0 | 45 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 407 | 03:00 | 387 | 19:00 | Meghnaghat | 409 | 06:00 | 390 | 13:00
Ashuganj | 416 | 3:00 | 395 | 15:00 | Payra | 417 | 05:00 | 409 | 18:00
Bhulta | 412 | 03:00 | 389 | 14:00 | Rahanpur | 417 | 06:00 | 397 | 18:00
Bibiana | 401 | 05:00 | 388 | 18:00 | Rampal | 410 | 04:00 | 397 | 13:00
BIPTC | 407 | 03:00 | 388 | 11:00
Bogura | 412 | 05:00 | 388 | 18:00
Gopalganj | 411 | 03:00 | 395 | 13:00
Kaliakoir | 398 | 03:00 | 380 | 14:00
Korerhat | 411 | 06:00 | 395 | 19:00
Madunaghat | 405 | 04:00 | 395 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 239 | 03:00 | 226 | 13:00 | Kachua | 236 | 23:00 | 229 | 13:00
AKSML | 235 | 03:00 | 228 | 16:00 | Kaliakoir | 241 | 03:00 | 226 | 19:00
Aminbazar | 240 | 04:00 | 225 | 12:00 | Keranigonj | 239 | 04:00 | 223 | 13:00
Ashuganj | 237 | 01:00 | 227 | 13:00 | Khulna(S) | 237 | 00:00 | 228 | 18:00
Ashuganj-400 | 237 | 3:00 | 226 | 15:00 | Korerhat | 238 | 06:00 | 229 | 13:00
Baghabari | 240 | 03:00 | 227 | 18:00 | Madunaghat | 235 | 05:00 | 228 | 18:00
Barapukuria | 229 | 05:00 | 220 | 18:00 | Madunaghat-400 | 235 | 04:00 | 228 | 13:00
Barapukuria-230 | 229 | 5:00 | 218 | 18:00 | Maniknagar | 237 | 02:00 | 226 | 13:00
Barishal | 243 | 02:00 | 236 | 18:00 | Meghnaghat | 245 | 06:00 | 232 | 13:00
Bheramara | 236 | 06:00 | 223 | 12:00 | Meghnaghat-400 | 240 | 03:00 | 228 | 13:00
Bhulta | 240 | 03:00 | 227 | 12:00 | Mirsorai | 238 | 04:00 | 229 | 13:00
Bibiana | 237 | 04:00 | 228 | 19:00 | Rajshahi | 236 | 01:00 | 222 | 13:00
BIPTC | 238 | 00:00 | 224 | 12:00 | Rampal | 236 | 06:00 | 227 | 13:00
Bogura | 241 | 03:00 | 225 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 240 | 03:00 | 226 | 18:00 | Rampura | 240 | 03:00 | 226 | 13:00
Borhanuddin | 245 | 01:00 | 240 | 18:00 | Shikalbaha | 233 | 06:00 | 225 | 12:00
BSRM | 237 | 03:00 | 229 | 19:00 | Shyampur | 239 | 06:00 | 225 | 13:00
Cumilla(N) | 239 | 03:00 | 228 | 13:00 | Siddhirganj | 236 | 00:00 | 226 | 12:00
Faridpur | 244 | 03:00 | 234 | 18:00 | Sirajgonj | 245 | 06:00 | 234 | 18:00
Fenchuganj | 239 | 06:00 | 231 | 18:00 | Sreepur | 235 | 01:00 | 223 | 18:00
Feni | 238 | 03:00 | 229 | 12:00 | Tongi | 233 | 07:00 | 223 | 11:00
Ghorashal | 240 | 00:00 | 235 | 08:00
Ghorashal-230 | 230 | 06:00 | 213 | 13:00
Gopalganj | 244 | 05:00 | 234 | 13:00
GPH | 236 | 03:00 | 228 | 19:00
Haripur | 239 | 03:00 | 227 | 13:00
Hasnabad | 239 | 02:00 | 225 | 13:00
Hathazari | 234 | 05:00 | 226 | 19:00
Ishurdi | 239 | 06:00 | 226 | 13:00
Jhenaidah | 236 | 06:00 | 221 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 127 | 12:00 | Laksam | 139 | 03:00 | 134 | 13:00
Agargaon | 138 | 03:00 | 129 | 13:00 | Lakshmipur | 134 | 03:00 | 128 | 13:00
Agrabad | 135 | 01:00 | 130 | 13:00 | Lalbag | 137 | 06:00 | 127 | 12:00
AKS | 134 | 04:00 | 129 | 12:00 | Lalmonirhat | 131 | 19:00 | 120 | 18:00
Aminbazar | 138 | 03:00 | 129 | 12:00 | Madanganj | 137 | 01:00 | 134 | 09:00
Amnura | 139 | 23:00 | 128 | 12:00 | Madaripur | 138 | 23:00 | 135 | 18:00
Ashuganj | 140 | 00:00 | 134 | 13:00 | Madartek | 135 | 03:00 | 127 | 12:00
Bagerhat | 135 | 07:00 | 122 | 18:00 | Madunaghat | 137 | 03:00 | 133 | 12:00
Bajitpur | 136 | 00:00 | 128 | 17:00 | Magura | 136 | 04:00 | 125 | 13:00
Bakerganj | 136 | 02:00 | 133 | 19:00 | Mahasthangarh | 136 | 01:00 | 123 | 18:00
Bakulia | 136 | 01:00 | 130 | 17:00 | Maijdee | 134 | 03:00 | 128 | 13:00
Banani | 139 | 03:00 | 126 | 13:00 | Manikganj | 131 | 03:00 | 122 | 18:00
Bangabhaban | 139 | 06:00 | 128 | 13:00 | Maniknagar | 139 | 05:00 | 129 | 13:00
Barapukuria | 138 | 05:00 | 119 | 18:00 | Matarbari | 129 | 04:00 | 117 | 18:30
Barguna | 137 | 04:00 | 134 | 12:00 | Matuail | 140 | 02:00 | 133 | 18:00
Barishal | 142 | 04:00 | 134 | 13:00 | Metrorail_Motijheel | 139 | 06:00 | 129 | 13:00
Barishal-230 | 141 | 06:00 | 134 | 13:00 | Metrorail_Uttara | 137 | 03:00 | 128 | 12:00
Baroaulia | 137 | 04:00 | 132 | 12:00 | Millgate | 136 | 02:00 | 124 | 13:00
Baroirhat | 136 | 03:00 | 130 | 18:00 | Mirpur | 137 | 04:00 | 126 | 13:00
Bashundhara | 136 | 02:00 | 126 | 15:00 | Mirzapur | 136 | 03:00 | 127 | 19:30
BashundharaCement | 137 | 01:00 | 134 | 09:00 | Mithapukur | 135 | 01:00 | 118 | 18:00
Beanibazar | 135 | 01:00 | 131 | 12:00 | MI_Cement | 138 | 04:00 | 127 | 12:00
Benapole | 133 | 03:00 | 117 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 135 | 05:00 | 124 | 18:00 | Mogbazar | 139 | 03:00 | 129 | 12:00
Bhandaria | 139 | 04:00 | 132 | 18:00 | Mongla | 130 | 05:00 | 122 | 18:00
Bhangura | 140 | 04:00 | 131 | 18:00 | Motijheel | 139 | 06:00 | 128 | 13:00
Bheramara | 139 | 00:00 | 132 | 18:00 | Muktagacha | 136 | 10:00 | 124 | 18:00
Bheramara(GK) | 140 | 04:00 | 132 | 18:00 | Munshiganj | 139 | 03:00 | 131 | 13:00
Bhulta | 130 | 07:00 | 125 | 12:00 | Muradnagar | 139 | 04:00 | 130 | 13:00
Bog-Sherpur | 138 | 05:00 | 127 | 18:00 | Mymensingh | 136 | 10:00 | 122 | 18:00
Bogura | 137 | 05:00 | 128 | 18:00 | Naogaon | 134 | 04:00 | 123 | 18:00
Bogura-230 | 137 | 03:00 | 127 | 18:00 | Narail | 138 | 04:00 | 124 | 13:00
Brahmanbaria | 133 | 00:00 | 128 | 18:00 | Narinda | 139 | 5:00 | 129 | 13:00
Cantonment | 138 | 03:00 | 129 | 12:00 | Narshingdi | 136 | 01:00 | 126 | 18:00
Chandina | 139 | 02:00 | 133 | 13:00 | Natore | 137 | 01:00 | 128 | 18:00
Chandpur | 138 | 02:00 | 134 | 19:00 | Nawabganj | 137 | 05:00 | 127 | 12:00
Chandraghona | 138 | 03:00 | 133 | 12:00 | Netrakona | 131 | 22:00 | 120 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 03:00 | 134 | 18:00 | New | 136 | 04:00 | 125 | 12:00
Charsaidpur | 140 | 06:00 | 133 | 12:00 | Niamatpur | 140 | 04:00 | 131 | 18:00
Chauddagram | 138 | 03:00 | 132 | 12:00 | Noapara | 135 | 05:00 | 119 | 13:00
Chhatak | 136 | 03:00 | 129 | 14:00 | Pabna | 139 | 06:00 | 131 | 18:00
Chowmuhani | 133 | 03:00 | 127 | 18:00 | Palashbari | 133 | 04:00 | 117 | 18:00
Chuadanga | 136 | 05:00 | 122 | 13:00 | Panchagarh | 140 | 19:00 | 117 | 18:00
Coxsbazar | 126 | 08:00 | 115 | 18:00 | Patiya | 137 | 04:00 | 131 | 12:00
Cumilla(N) | 140 | 03:00 | 133 | 14:00 | Patuakhali | 135 | 02:00 | 132 | 18:00
Cumilla(S) | 139 | 04:00 | 125 | 10:00 | Payra | 137 | 02:00 | 134 | 12:00
Daganbhuiyan | 136 | 05:00 | 130 | 14:00 | PHP | 136 | 04:00 | 129 | 13:00
Daudkandi | 136 | 03:00 | 130 | 12:00 | Postogola | 139 | 04:00 | 129 | 12:00
DhakaUniversity | 136 | 02:00 | 127 | 13:00 | Purbachal | 136 | 02:00 | 127 | 14:00
Dhamrai | 137 | 05:00 | 131 | 19:00 | Purbasadipur | 132 | 05:00 | 111 | 18:00
Dhanmondi | 141 | 03:00 | 135 | 13:00 | Rahanpur | 140 | 03:00 | 133 | 18:00
Dohazari | 134 | 06:00 | 126 | 19:00 | Rahanpur-400 | 140 | 01:00 | 133 | 18:00
Faridpur | 140 | 05:00 | 134 | 13:00 | Rahim | 140 | 03:00 | 131 | 13:00
Fatullah | 138 | 03:00 | 127 | 13:00 | Rajbari | 140 | 03:00 | 133 | 13:00
Fenchuganj | 139 | 05:00 | 134 | 12:00 | Rajendrapur | 136 | 04:00 | 125 | 18:00
Feni | 135 | 05:00 | 130 | 13:00 | Rajshahi | 137 | 04:00 | 129 | 13:00
Feni-230 | 136 | 03:00 | 131 | 12:00 | Rajshahi-230 | 137 | 01:00 | 129 | 12:00
Ghatail | 134 | 11:00 | 124 | 19:00 | Ramganj | 136 | 05:00 | 129 | 19:00
Ghorashal | 136 | 03:00 | 125 | 12:00 | Rampur | 136 | 02:00 | 130 | 13:00
Goalpara | 133 | 03:00 | 128 | 13:00 | Rampura | 136 | 03:00 | 127 | 13:00
Gollamari | 134 | 06:00 | 127 | 18:00 | Rangamati | 137 | 03:00 | 132 | 13:00
Gopalganj | 137 | 02:00 | 131 | 13:00 | Rangpur | 134 | 02:00 | 115 | 18:00
Gopalganj-400 | 141 | 04:00 | 135 | 13:00 | Ruppur | 142 | 04:00 | 132 | 18:00
Gulshan | 134 | 04:00 | 127 | 13:00 | Saidpur | 134 | 04:00 | 112 | 18:00
Halishahar | 137 | 06:00 | 131 | 12:00 | Satkhira | 133 | 06:00 | 123 | 18:00
Haripur | 140 | 02:00 | 133 | 13:00 | Satmasjid | 137 | 03:00 | 127 | 12:00
HaripurSBU | 140 | 02:00 | 134 | 12:00 | Savar | 134 | 04:00 | 127 | 12:00
Hasnabad | 139 | 03:00 | 130 | 12:00 | SevenRings | 137 | 06:00 | 123 | 13:00
Hathazari | 137 | 05:00 | 132 | 19:00 | ShahCement | 140 | 06:00 | 132 | 14:00
Hatirjheel | 136 | 03:00 | 127 | 13:00 | Shahjadpur | 143 | 03:00 | 133 | 18:00
Ishurdi | 141 | 03:00 | 133 | 18:00 | Shahjibazar | 134 | 00:00 | 130 | 11:00
Jaldhaka | 131 | 04:00 | 112 | 18:00 | Shahmirpur | 137 | 03:00 | 131 | 18:30
Jamalpur | 137 | 11:00 | 122 | 03:00 | Shariatpur | 141 | 04:00 | 134 | 13:00
Jashore | 134 | 04:00 | 120 | 13:00 | Sherpur | 134 | 10:00 | 118 | 07:00
Jhenaidah | 139 | 06:00 | 124 | 08:00 | Shikalbaha | 126 | 03:00 | 120 | 17:00
Jhenaidah-230 | 138 | 06:00 | 127 | 13:00 | Shikalbaha-230 | 138 | 06:00 | 132 | 12:00
Joydebpur | 135 | 06:00 | 117 | 12:00 | Shitalakhya | 138 | 04:00 | 127 | 12:00
Joypurhat | 134 | 06:00 | 122 | 18:00 | Sholosohor | 137 | 03:00 | 132 | 13:00
Juldah | 137 | 04:00 | 131 | 13:00 | Shyampur | 138 | 05:00 | 130 | 13:00
Kabirpur | 139 | 10:00 | 123 | 18:30 | Shyampur-230 | 139 | 06:00 | 129 | 13:00
Kachua | 140 | 03:00 | 135 | 13:00 | Siddhirganj | 140 | 06:00 | 133 | 12:00
Kaliakoir | 141 | 04:00 | 132 | 20:00 | Sirajganj | 137 | 03:00 | 127 | 18:00
Kallyanpur | 138 | 06:00 | 129 | 19:00 | Sonargaon | 139 | 06:00 | 132 | 12:00
Kalurghat | 137 | 02:00 | 133 | 13:00 | Sreemongol | 135 | 04:00 | 131 | 13:00
Kamrangirchar | 137 | 03:00 | 126 | 13:00 | Sreepur | 138 | 03:00 | 129 | 18:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 04:00 | 127 | 13:00
Kasba | 138 | 03:00 | 132 | 12:00 | SSM | 140 | 00:00 | 136 | 13:00
Kazla | 138 | 03:00 | 128 | 13:00 | Sunamganj | 133 | 02:00 | 128 | 13:00
Keranigonj | 136 | 03:00 | 126 | 13:00 | Sylhet | 135 | 01:00 | 131 | 13:00
Khagrachori | 137 | 02:00 | 132 | 12:00 | Sylhet-132 | 135 | 00:00 | 132 | 11:00
Khulna | 132 | 03:00 | 126 | 18:00 | Tangail | 133 | 10:00 | 124 | 18:00
Khulna(S) | 134 | 00:00 | 127 | 18:00 | Taraganj | 132 | 03:00 | 121 | 08:00
Khulshi | 135 | 04:00 | 129 | 13:00 | Tasnim | 139 | 03:00 | 126 | 22:00
Kishoreganj | 135 | 04:00 | 125 | 13:00 | Thakurgaon | 137 | 19:00 | 112 | 18:00
Kodda | 135 | 10:00 | 129 | 17:00 | TK | 138 | 04:00 | 133 | 12:00
KSRM | 136 | 01:00 | 131 | 19:00 | Tongi | 136 | 04:00 | 128 | 11:00
Kulaura | 138 | 02:00 | 134 | 12:00 | Ullahpara | 138 | 01:00 | 130 | 18:00
Kurigram | 132 | 04:00 | 112 | 18:00 | Ullon | 137 | 06:00 | 128 | 13:00
Kushtia | 137 | 06:00 | 125 | 18:00 | Uttara | 137 | 04:00 | 124 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division