## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-12-2025 | during | 25-12-2025 | during | 25-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Grid fault
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 342 | 331 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 280 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 33.5 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 33 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 22 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 87 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 53 | 54 | 162 | 162 | 146 | 146 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 405 | 345 | 583 | 583 | 450 | 450 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1148 | 1286.5 | 5781.35 | 5756.35 | 2446.37 | 2421.37
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 222 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 51 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 23 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.06 | 0 | 3.12 | 0 | 3.12 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1035 | 1125 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 830 | 830 | 830 | 830 | 830 | 830 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 2156.06 | 2341 | 3667.84 | 3668.72 | 3168.62 | 3169.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 180 | 159 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 364 | 353.35 | 353.35 | 320 | 320 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0.01 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 215 | 393 | 393 | 340 | 340 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 40 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 106 | 108 | 163 | 163 | 112 | 112 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 96 | 98 | 160 | 160 | 118 | 118 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1042 | 1106 | 2780.56 | 2725.56 | 1865.71 | 1810.71
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-12-2025 | during | 25-12-2025 | during | 25-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 43 | 43 | 157.5 | 157.5 | 55 | 55 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 18 | 20 | 20 | 20 | 20 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 29 | 59 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 12.2 | 0 | 36 | 0 | 36 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 102.2 | 120 | 351.5 | 314 | 184.5 | 147
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 36 | 36 | 36 | 36 | 36 | 36 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 156 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 212 | 212 | 210 | 210 | 210 | 210 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 575 | 569 | 592 | 592 | 592 | 592
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 922 | 1075 | 1148.28 | 1148.28 | 1118 | 1118 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1896 | 1977 | 3485.28 | 3420.28 | 2290.1 | 2225.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 300 | 500 | 0 | 0 | 500 | 500 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 136 | 133 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 910 | 1050 | 1085.32 | 1085.32 | 1025 | 1025 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant is on standby as per NLDC instruction
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 0.53 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1566.53 | 1903 | 2003.32 | 2002.32 | 2002.53 | 2002
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 12.88 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 280 | 254 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.9 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1027.92 | 1231 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 8.55 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 88 | 0 | 95 | 0 | 95 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1558.25 | 1625 | 3074.87 | 2913.87 | 2567.49 | 2406.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 54 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 36 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 31 | 0 | 121.8 | 0 | 121.8 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 94 | 125 | 452 | 297 | 438 | 283
System Total |  |  |  |  | 28823.2 | 28379.108 | 10138.04 | 11052.5 | 22188.72 | 21690.1 | 15555.32 | 15057.17
Forecast Scenario (25-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8900 |  | 0 |  | 8900
|  |  |  | 1:00 | 8400 |  | 0 |  | 8400
|  |  |  | 2:00 | 7850 |  | 0 |  | 7850
|  |  |  | 3:00 | 7490 |  | 0 |  | 7490
|  |  |  | 4:00 | 7200 |  | 0 |  | 7200
|  |  |  | 5:00 | 7230 |  | 0 |  | 7230
|  |  |  | 6:00 | 7450 |  | 0 |  | 7450
|  |  |  | 7:00 | 7560 |  | 0 |  | 7560
|  |  |  | 8:00 | 8280 |  | 0 |  | 8280
|  |  |  | 9:00 | 8170 |  | 0 |  | 8170
|  |  |  | 10:00 | 8010 |  | 0 |  | 8010
|  |  |  | 11:00 | 8110 |  | 0 |  | 8110
|  |  |  | 12:00 | 8820 |  | 0 |  | 8820
|  |  |  | 13:00 | 9400 |  | 0 |  | 9400
|  |  |  | 14:00 | 8020 |  | 0 |  | 8020
|  |  |  | 15:00 | 7490 |  | 0 |  | 7490
|  |  |  | 16:00 | 7540 |  | 0 |  | 7540
|  |  |  | 17:00 | 8050 |  | 0 |  | 8050
|  |  |  | 18:00 | 9340 |  | 0 |  | 9340
|  |  |  | 18:30 | 9450 |  | 0 |  | 9450
|  |  |  | 19:00 | 9600 |  | 0 |  | 9600
|  |  |  | 19:30 | 9560 |  | 0 |  | 9560
|  |  |  | 20:00 | 9570 |  | 0 |  | 9570
|  |  |  | 21:00 | 9590 |  | 0 |  | 9590
|  |  |  | 22:00 | 9440 |  | 0 |  | 9440
|  |  |  | 23:00 | 8890 |  | 0 |  | 8890
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 8820.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 9600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 200.40 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:34 hrs on 25-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-12-2025 | [28 empty] | Date: | 24-12-2025 | [28 empty] | Date: | 24-12-2025 | [28 empty] | Date: | 24-12-2025 | [28 empty] | Date: | 24-12-2025 | [17 empty] | Date: | 24-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 665 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 975 | 0 | 0 | 0 | 310 | 280 | 0 | 51 | 0 | 199 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 161 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 4561 | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 250 | 820 | 0 | 4430 | 8991 | 98.36
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 665 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 280 | 280 | 0 | 51 | 0 | 188 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 4240 | 785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 250 | 750 | 0 | 4272 | 8512 | 98.36
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 640 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 720 | 0 | 0 | 0 | 250 | 280 | 0 | 51 | 0 | 187 | 0 | 0 | 110 | 0 | 0 | 12 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 4160 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 250 | 650 | 0 | 3927 | 8087 | 98.36
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 640 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 250 | 280 | 0 | 5 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 3939 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 250 | 560 | 0 | 3812 | 7751 | 98.36
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 640 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 250 | 280 | 0 | 5 | 0 | 190 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 3895 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 0 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 560 | 0 | 3616 | 7511 | 98.35
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 640 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 250 | 280 | 0 | 5 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 159 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 3847 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 558 | 0 | 3604 | 7451 | 98.35
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 665 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 250 | 280 | 0 | 5 | 0 | 185 | 0 | 0 | 100 | 0 | 0 | 12 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 4187 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 250 | 560 | 0 | 3698 | 7885 | 98.35
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 40 | 0 | 37 | 675 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 735 | 1 | 0 | 0 | 250 | 280 | 0 | 40 | 0 | 206 | 0 | 0 | 111 | 0 | 0 | 12 | 0 | 82 | 0 | 2 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 8 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 54 | 0 | 0.11 | 0 | 4245.26 | 645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 788 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 0 | 0 | 0 | 0.17 | 0 | 0 | 140 | 0 | 0 | 0 | 345 | 0 | 0.03 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 220 | 0 | 250 | 560 | 0 | 3967.91 | 8213.17 | 98.35
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 40 | 0 | 18 | 830 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 850 | 6 | 0 | 0 | 250 | 280 | 0 | 51 | 0 | 197 | 0 | 0 | 111 | 0 | 0 | 12 | 0 | 96 | 0 | 13 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 2 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 18 | 54 | 0 | 2.44 | 0 | 4611.38 | 806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 820 | 0 | 0 | 0 | 982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | 4 | 0 | 0 | 2.38 | 0 | 0 | 140 | 0 | 0 | 0 | 344 | 0 | 0.23 | 0 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 7 | 0.07 | 0 | 0 | 136 | 220 | 0 | 300 | 640 | 0 | 4479.81 | 9091.19 | 98.34
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 40 | 0 | 9 | 780 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 900 | 12 | 0 | 0 | 250 | 280 | 0 | 51 | 0 | 189 | 0 | 0 | 108 | 0 | 0 | 12 | 0 | 100 | 0 | 31 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 3 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 35 | 8 | 54 | 0 | 5.8 | 0 | 4715.55 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 893 | 0 | 0 | 0 | 1027.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 9 | 0 | 0 | 4.11 | 0 | 0 | 140 | 0 | 0 | 0 | 305 | 0 | 0.43 | 0 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 16 | 0.26 | 0 | 0 | 136 | 180 | 0 | 350 | 762 | 0 | 4825.36 | 9540.91 | 98.34
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 40 | 0 | 9 | 780 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 902 | 15 | 0 | 0 | 250 | 290 | 0 | 51 | 0 | 201 | 0 | 0 | 108 | 0 | 0 | 12 | 0 | 98 | 0 | 48 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 5 | 17 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 25 | 8 | 43 | 0 | 8.36 | 0 | 4804.83 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 871 | 0 | 0 | 0 | 929.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.31 | 28 | 0 | 0 | 6.1 | 0 | 0 | 140 | 0 | 0 | 0 | 307 | 0 | 0.61 | 0 | 54 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 27 | 0.41 | 0 | 0 | 136 | 180 | 0 | 300 | 800 | 0 | 4749.76 | 9554.59 | 98.34
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 22 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.93 | 40 | 0 | 9 | 780 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 900 | 17 | 0 | 0 | 230 | 300 | 0 | 51 | 0 | 180 | 0 | 0 | 107 | 0 | 0 | 12 | 0 | 104 | 0 | 58 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 8 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 25 | 8 | 43 | 0 | 11.87 | 0 | 4812.8 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 821 | 0 | 0 | 0 | 936.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.16 | 54 | 0 | 0 | 7.66 | 0 | 0 | 140 | 0 | 0 | 0 | 292 | 0 | 0.86 | 0 | 55 | 0 | 4 | 0 | 0 | 0 | 0 | 1.3 | 31 | 0.47 | 0 | 0 | 136 | 180 | 0 | 300 | 835 | 0 | 4773.19 | 9585.99 | 98.34
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 405 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.06 | 40 | 0 | 12 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1035 | 15 | 0 | 0 | 230 | 300 | 0 | 51 | 0 | 180 | 0 | 0 | 106 | 0 | 0 | 20 | 0 | 96 | 0 | 59 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 9 | 17 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 29 | 18 | 43 | 0 | 12.2 | 0 | 5023.26 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 922 | 0 | 0 | 0 | 1027.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.88 | 88 | 0 | 0 | 8.55 | 0 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0.9 | 0 | 54 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 31 | 0.53 | 0 | 0 | 136 | 220 | 0 | 300 | 910 | 0 | 5114.78 | 10138.04 | 98.33
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 415 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1050 | 7 | 0 | 0 | 250 | 300 | 0 | 51 | 0 | 180 | 0 | 0 | 105 | 0 | 0 | 12 | 0 | 106 | 0 | 55 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 8 | 17 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 57 | 18 | 43 | 1 | 12.75 | 0 | 5114.75 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 1003 | 0 | 0 | 0 | 1138.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.75 | 86 | 0 | 0 | 8.82 | 0 | 0 | 140 | 0 | 0 | 0 | 264 | 0 | 0.91 | 0 | 54 | 0 | 7 | 0 | 0 | 0 | 0 | 2.1 | 35 | 0.44 | 0 | 0 | 136 | 220 | 0 | 350 | 1000 | 0 | 5434.84 | 10549.59 | 98.33
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 410 | 0 | 0 | 260 | 0 | 0 | 10 | 0 | 22.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.21 | 40 | 0 | 14 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1003 | 13 | 0 | 0 | 240 | 300 | 0 | 51 | 0 | 180 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 104 | 0 | 46 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 7 | 17 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 57 | 8 | 44 | 0 | 16.67 | 0 | 5036.38 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1019 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.39 | 69 | 0 | 0 | 8.7 | 0 | 0 | 140 | 0 | 0 | 0 | 234 | 0 | 0.84 | 0 | 54 | 0 | 11 | 0 | 0 | 0 | 0 | 2 | 55 | 0.39 | 0 | 0 | 118 | 190 | 0 | 300 | 900 | 0 | 5176.32 | 10212.7 | 98.33
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 380 | 0 | 0 | 250 | 0 | 0 | 13 | 0 | 22.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 40 | 0 | 9 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1000 | 9 | 0 | 0 | 240 | 300 | 0 | 51 | 0 | 180 | 0 | 0 | 104 | 0 | 0 | 12 | 0 | 92 | 0 | 33 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 3.65 | 17 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 57 | 8 | 44 | 1 | 12.17 | 0 | 4919.44 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 955 | 0 | 0 | 0 | 1081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7 | 45 | 0 | 0 | 7.02 | 0 | 0 | 140 | 0 | 0 | 0 | 227 | 0 | 0.48 | 0 | 55 | 0 | 11 | 0 | 0 | 0 | 0 | 1.6 | 49 | 0.26 | 0 | 0 | 133 | 190 | 0 | 300 | 892 | 0 | 5051.06 | 9970.5 | 98.33
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 330 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 22.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 40 | 0 | 11 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1167 | 4 | 0 | 0 | 240 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 105 | 0 | 0 | 12 | 0 | 92 | 0 | 15 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 2 | 17 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 57 | 8 | 44 | 0 | 3.62 | 0 | 4984.82 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 842 | 0 | 0 | 0 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2 | 20 | 0 | 0 | 3.83 | 0 | 0 | 140 | 0 | 0 | 0 | 210 | 0 | 0.39 | 0 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 1.1 | 27 | 0.13 | 0 | 0 | 133 | 220 | 0 | 300 | 830 | 0 | 4647.65 | 9632.47 | 98.32
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 365 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 40 | 0 | 17 | 830 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1142 | 0 | 0 | 0 | 240 | 309 | 0 | 51 | 0 | 180 | 0 | 0 | 106 | 0 | 0 | 12 | 0 | 100 | 0 | 1 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 59 | 18 | 44 | 0 | 0.11 | 0 | 5032.14 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 843 | 0 | 0 | 0 | 1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 3 | 0 | 0 | 0.47 | 0 | 0 | 140 | 0 | 0 | 0 | 180 | 0 | 0.05 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 4 | 0.02 | 0 | 0 | 133 | 220 | 0 | 400 | 864 | 0 | 4864.05 | 9896.19 | 98.32
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 21 | 0 | 48 | 0 | 45 | 0 | 30 | 80 | 0 | 0 | 0 | 370 | 0 | 25 | 280 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 40 | 0 | 16 | 830 | 0 | 0 | 0 | 0 | 5 | 222 | 0 | 0 | 0 | 1150 | 0 | 11 | 0 | 230 | 328 | 0 | 51 | 0 | 169 | 0 | 0 | 108 | 39 | 0 | 15 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 59 | 18 | 43 | 0 | 0 | 0 | 5370 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993 | 0 | 0 | 0 | 1277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 501 | 1038 | 0 | 5537 | 10907 | 98.32
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 33.5 | 0 | 87 | 0 | 45 | 0 | 33 | 54 | 0 | 0 | 0 | 345 | 0 | 35 | 280 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 23 | 830 | 0 | 0 | 0 | 0 | 51 | 222 | 0 | 0 | 0 | 1125 | 0 | 40 | 0 | 215 | 364 | 0 | 51 | 0 | 159 | 0 | 0 | 108 | 51 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 59 | 18 | 43 | 0 | 0 | 0 | 5422.5 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1075 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 54 | 35 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 500 | 1050 | 0 | 5630 | 11052.5 | 98.32
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 35 | 52 | 0 | 0 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 18 | 830 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 215 | 355 | 0 | 51 | 0 | 150 | 0 | 0 | 109 | 51 | 0 | 20 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 59 | 18 | 43 | 0 | 0 | 0 | 5225 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 0 | 0 | 0 | 1187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 53 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 500 | 1030 | 0 | 5568 | 10793 | 98.32
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 21 | 830 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 215 | 355 | 0 | 51 | 0 | 148 | 0 | 0 | 109 | 48 | 0 | 20 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 59 | 18 | 43 | 0 | 0 | 0 | 5194 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1086 | 0 | 0 | 0 | 1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 53 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 503 | 1040 | 0 | 5591 | 10785 | 98.31
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 830 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 230 | 300 | 0 | 51 | 0 | 164 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 45 | 8 | 46 | 0 | 0 | 0 | 4961 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 0 | 0 | 1168.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 53 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 220 | 0 | 503 | 1040 | 0 | 5605.3 | 10566.3 | 98.31
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 830 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1015 | 0 | 0 | 0 | 240 | 300 | 0 | 51 | 0 | 173 | 0 | 0 | 109 | 0 | 0 | 20 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 45 | 8 | 46 | 0 | 0 | 0 | 4785 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 987 | 0 | 0 | 0 | 1017.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 180 | 0 | 490 | 1000 | 0 | 5241.03 | 10026.03 | 98.31
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 830 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 935 | 0 | 0 | 0 | 225 | 300 | 0 | 51 | 0 | 181 | 0 | 0 | 110 | 0 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 35 | 0 | 0 | 22 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 24 | 8 | 47 | 0 | 0 | 0 | 4628.5 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803 | 0 | 0 | 0 | 1029.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 53 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 180 | 0 | 301 | 940 | 0 | 4814.2 | 9442.7 | 98.3
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8402400 | 0 | 0 | 52200 | 0 | 529344 | 0 | 61975 | 0 | 91086 | 580320 | 0 | 0 | 0 | 8605045 | 0 | 55547 | 6699694 | 0 | 0 | 68804 | 0 | 441600 | 494280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130560 | 17281 | 968000 | 0 | 424800 | 18603636.36 | 0 | 0 | 0 | 0 | 77781 | 5142911 | 0 | 0 | 0 | 22134543 | 94365 | 66909 | 0 | 5903500 | 7419500 | 0 | 1114560 | 0 | 4518000 | 0 | 0 | 2375288 | 211200 | 0 | 374670 | 0 | 2196480 | 0 | 358591 | 0 | 0 | 0 | 5159000 | 843000 | 716880 | 0 | 43310 | 320976 | 0 | 1489920 | 654528 | 0 | 0 | 4381550 | 0 | 746400 | 211200 | 1097280 | 3000 | 84000 | 0 | 113965914.36 | 19326545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440640 | 21294550 | 0 | 0 | 0 | 23585454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131892 | 414540 | 0 | 0 | 58496 | 0 | 0 | 3612945 | 0 | 0 | 0 | 7154254 | 0 | 5640 | 0 | 1254545 | 215131 | 52507 | 57696 | 0 | 0 | 0 | 12273.48 | 285840 | 3012 | 0 | 0 | 3103000 | 5262116 | 0 | 8029090 | 20401454.55 | 0 | 114701621.03 | 228667535.39

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10138.04 | MW | 12:00 Hr. | Energy Generated |  |  | 228.6675 |  | MKWHr.
| Day Peak Demand |  |  | 10138.04 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11052.5 | MW | 19:00 Hr. | Energy Demand |  |  | 228.6675 |  | MKWHr.
| Evening Peak Demand |  |  | 11052.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 24 |  | °C
| Minimum Generation of the Day |  |  | 7451 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 617.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 11052.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.4899 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.643 | 0 | 1.3705 | 0 | 0 | 0.068804 | 0 | 0 | 26.0823 | Gas | 85.7117 | Gas | 298383624.64
| Chattogram Zone |  |  | 5.5677 | 40.7382 | 0.20834 | 0 | 0.968 | 0.11165 | 0 | 0 | 47.5939 | Coal | 91.7178 | Coal | 611094595.1898
| Cumilla Zone |  |  | 21.7055 | 0 | 0.27811 | 0 | 0 | 0.35859 | 2.1965 | 0 | 24.5387 | HFO | 3.0873 | HFO | 50151478.19
| Mymensingh Zone |  |  | 1.0973 | 0 | 0.9576 | 0 | 0 | 0.087 | 0 | 0 | 2.1419 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 13.5659 | 0 | 0 | 0 | 0 | 0.04331 | 0 | 0 | 13.6092 | Hydro | 0.968 | Hydro | 96800
| Khulna Zone |  |  | 0 | 21.2946 | 0 | 0 | 0 | 0.44064 | 19.3265 | 0 | 41.0617 | Solar | 2.0742 | Solar | 31286740.186
| Barishal Zone |  |  | 8.3651 | 28.4305 | 0 | 0 | 0 | 0.003012 | 0 | 0 | 36.7987 | Import | 45.1085 | Import | 264337593.16
| Rajshahi Zone |  |  | 10.7672 | 0 | 0 | 0 | 0 | 0.61057 | 23.5855 | 0 | 34.9632 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 1.2545 | 0.27283 | 0 | 0 | 0.35062 | 0 | 0 | 1.878
| Total |  |  | 85.7117 | 91.7178 | 3.0873 | 0 | 0.968 | 2.0742 | 45.1085 | 0 | 228.6675
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 298383624.64 |  | Hydro | 96800
|  |  |  | Coal | 611094595.1898 |  | Solar | 31286740.186
|  |  |  | HFO | 50151478.19 |  | Import | 264337593.16
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 125,53,50,831 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.3265 | Peak Hr Flow | 902.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41634672.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.5855 | Peak Hr Flow | 1231.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2155 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.1965 | Peak Hr Flow | 98.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2305 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.1085 | Peak Hr Flow | 2231.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4004
|  |  |  | Chattogram |  | 0 |  | 1233
|  |  |  | Cumilla |  | 0 |  | 924
|  |  |  | Mymensingh |  | 0 |  | 847
|  |  |  | Sylhet |  | 0 |  | 386
|  |  |  | Khulna |  | 0 |  | 1243
|  |  |  | Barishal |  | 0 |  | 300
|  |  |  | Rajshahi |  | 0 |  | 955
|  |  |  | Rangpur |  | 0 |  | 721
|  |  |  | Total |  | 0 |  | 10613
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 710
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:12 | 16:53 | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Barishal 230/132kV end Due to Annual Maintenance
| 08:14 | 16:48 | Benapole-Jashore 132 kV Ckt-1 Scheduled S/D from Benapole 132/33kV end Due to Annual
maintenance and from Jashore 132/33kV end Due to Shutdown for benapole end
| 08:15 | 14:28 | Bakulia 132/33kV S/S Bus-B Scheduled S/D
| 08:28 | 14:58 | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Annual
maintenance
| 08:31 | 15:33 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Scheduled S/D Due to Annual
Maintenance
| 08:33 | 15:34 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D Due to Annual Maintenance
| 08:49 | 12:40 | Cumilla(S) 132/33kV S/S TR-3 LT Scheduled S/D Due to Protection test
| 08:49 | 12:39 | Cumilla(S) 132/33kV S/S TR-3 HT Scheduled S/D
| 08:53 |  | Bhulta-Haripur 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end. and from Haripur
230/132kV end Due to Annual Deadline checking.
| 08:57 | 15:12 | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to Annual Maintenance
| 08:58 | 15:15 | Shahjibazar-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to
annual maintenance and from Shahjibazar 132/33kV end Due to Shutdown for annual
maintenance.
| 09:00 |  | Ghorasal-Narsingdi 132 kV Ckt-2 Scheduled S/D from Narshingdi 132/33kV end Due to Annual
maintenance
| 09:05 | 17:46 | Mongla 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance.
| 09:06 | 17:46 | Mongla 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance.
| 09:08 | 13:43 | Magura 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to For Annual Maintenance.
| 09:09 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end.
| 09:09 | 13:38 | Magura 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to For Annual Maintenance.
| 09:10 | 18:01 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to 33 kV Bus-01 Emergency
Maintenance
| 09:13 |  | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-1 Scheduled S/D
| 09:18 | 15:59 | Amnura-Chapainawabganj-132kV Ckt-1 Scheduled S/D from Amnura 132/33kV end Due to Annual
Maintenance and from Chapai 132/33kV end Due to Annual maintenance
| 09:20 |  | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D
| 09:24 | 12:11 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to Relay test
| 09:25 | 11:58 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 09:30 | 14:14 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D Due to Annual maintenance
| 09:30 | 14:14 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D Due to Annual maintenance
| 09:38 | 11:44 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Project Work S/D from Daudkandi 132/33kV end.
| 09:39 | 15:48 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to A/M
| 09:39 | 11:08 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to For
Aminbazar maintenance work
| 09:41 | 15:48 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to A/M
| 09:44 | 17:51 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Development Work at
Ashuganj end
| 09:47 | 11:42 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-02 Project Work S/D Due to
Project Work Shutdown
| 09:53 |  | BSRM-GPH 230 kV Ckt-1 Scheduled S/D from BSRM 230/33kV end Due to Annual Maintenance
| 09:54 | 15:35 | BSRM-GPH 230 kV Ckt-2 Scheduled S/D from GPH 230/33kV end Due to Maintenance Works.
| 09:55 | 13:18 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Kaliakoir
SS Maintenance work
| 10:10 | 11:38 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 Project Work S/D Due to
Project Work Shutdown
| 10:20 | 16:45 | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end. and from
Kabirpur 132/33kV end Due to Annual maintenance (deadline checking)
| 11:00 | 15:25 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to Tower
painting
|  | 11:02 | Jaldhaka 132/33kV S/S 406T-1 HT is restored.
|  | 11:03 | Jaldhaka 132/33kV S/S 406T-1 LT is restored.
| 11:07 | 14:28 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to For T2 Transformer Tan Delta
Test
| 11:08 | 14:28 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to For T2 Transformer Tan Delta
Test
| 11:08 | 14:28 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to For T2 Transformer Tan Delta
Test
|  | 11:09 | Aminbazar-Meghnaghat 400kV Ckt-2 is restored.
| 11:18 |  | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Project work gas filling in GIS
Chamber.
| 11:18 |  | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to Project work gas filling in GIS
Chamber.
| 11:19 | 15:50 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) LT Forced S/D Due to OLTC Oil Refill
| 11:20 | 15:49 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) HT Forced S/D Due to OLTC Oil Refill.
| 11:48 | 12:40 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing Distance
relay,lockout relay relays Due to Transient fault
| 11:49 | 13:25 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Project Work S/D from Daudkandi 132/33kV end Due to 132
KV Muradnagar-1 shutdown by project work Muradnogor End.
| 11:49 | 13:24 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Daudkandi Ckt-01 Project Work S/D Due to
project work
| 12:00 | 13:20 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-02 Project Work S/D Due to
project work
| 12:00 |  | Day Peak Gen. 10138 MW
|  | 12:17 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
| 12:43 | 16:40 | Cumilla(S) 132/33kV S/S TR-4 LT Scheduled S/D Due to None
| 12:44 | 16:40 | Cumilla(S) 132/33kV S/S TR-4 HT Scheduled S/D Due to None
| 13:17 | 15:26 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Work by
kaliakoir grid SS.
| 13:54 | 14:36 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to Relay Test
| 14:45 | 16:20 | Kallyanpur 132/33kV S/S GT-3 (132kV) HT Scheduled S/D Due to Relay protection testing.
| 16:06 | 17:20 | Nawabganj 132/33kV S/S TR-1 LT Scheduled S/D Due to For Oil leakage repair at NIFPS
joint.
| 16:08 | 17:18 | Nawabganj 132/33kV S/S TR-1 HT Scheduled S/D Due to For Oil leakage repair at NIFPS
joint.
|  | 17:23 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 is restored.
|  | 17:27 | Aminbazar-Kaliakoir 230kV Ckt-1 is restored.
|  | 18:09 | Sonargaon 132/33kV S/S Bashundhara Line is restored.
| 19:16 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Project Work S/D from Purbasadipur 132/33kV end
Due to Project Work S/D for Reconductoring (connected with GIS)
|  | 19:39 | Ashuganj 230/132/33kV S/S 230kv Busbar-2 is restored.
|  | 20:17 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT is restored.
|  | 20:19 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT is restored.
| 23:30 | 00:00 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing Trip Relay(MVAJM) relays Due to Due to Pbs | [7 empty] | 65.0MW load
|  |  | Borfa, Kabilganj Feeder line trip | [7 empty] | interrup.
| 03:29 | 04:30 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to due to pbs 33KV Barpa feeder Bus Ds to | [7 empty] | 53.0MW load
|  |  | CT loop separate | [7 empty] | interrup.
| 03:30 | 04:29 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to due to pbs 33KV Barpa feeder Bus Ds to | [7 empty] | 53.0MW load
|  |  | CT loop separate | [7 empty] | interrup.
| 04:16 | 04:37 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Over current P142 relays Due to | [7 empty] | 13.0MW load
|  |  | NESCO 33kv Feeder Fault | [7 empty] | interrup.
| 04:16 | 04:38 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing Over current P142 relays Due to | [7 empty] | 13.0MW load
|  |  | NESCO 33kv Feeder Fault | [7 empty] | interrup.
| 04:44 | 05:32 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing Over current P142 relays Due to | [7 empty] | 13.0MW load
|  |  | Fasitola 33kv Feeder Fault | [7 empty] | interrup.
| 04:44 | 05:31 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Over current P142 relays Due to | [7 empty] | 13.0MW load
|  |  | Fasitola 33kv Feeder Fault | [7 empty] | interrup.
| 05:00 |  | Minimum Generation: 7230 MW.
| 05:43 |  | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Oil leakage in unit
transformer-2
|  | 06:23 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 07:35 |  | Kishoreganj-Mymensingh 132kV Ckt-1 Project Work S/D from Kishoreganj 132/33kV end Due to
Project work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 331 | 8402400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6699694 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.5 | 52200 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 33 | 91086 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 55547 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 441600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 494280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 61975 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 87 | 529344 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 580320 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 68804 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 345 | 8605045 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1286.5 | 26082295
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 94365 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 968000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5142911 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 77781 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 424800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 130560 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1125 | 22134543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 830 | 18603636.36 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 2341 | 47593877.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 159 | 4518000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 364 | 7419500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5903500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1114560 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 66909 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2375288 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 211200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 98 | 2196480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 374670 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 358591 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1106 | 24538698
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 43 | 1097280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 211200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 746400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 84000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 120 | 2141880
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 43310 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 36 | 843000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 716880 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 654528 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1489920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 156 | 4381550 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 320976 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 212 | 5159000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 569 | 13609164
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 19326545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 440640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1075 | 21294550 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1977 | 41061735
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 500 | 8029090 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 133 | 3103000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1050 | 20401454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5262116 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Plant is on standby as per NLDC instruction
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3012 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1903 | 36798672.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 131892 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3612945 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 254 | 7154254 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 5640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1231 | 23585454 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 58496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 414540 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1625 | 34963221
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1254545 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Coal shortage
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 36 | 57696 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 12273.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 215131 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 52507 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 285840 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 125 | 1877992.48
Eastern Grid Total |  |  |  |  | 17395.105 | 5422.5 | 113965914.36
Western Grid Total |  |  |  |  | 10984.003 | 5630 | 114701621.03
National Grid Total |  |  |  |  | 28379.108 | 11052.5 | 228667535.39
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-12-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7394.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3219.3 | MW
i) Dhaka area |  |  | 4004.01 |  | MW | i) Khulna area |  |  |  | 1243.4 | MW
ii) Chattogram area |  |  | 1233.2 |  | MW | ii) Barishal area |  |  |  | 299.5 | MW
iii) Cumilla area |  |  | 924 |  | MW | iii) Rajshahi area |  |  |  | 955.4 | MW
iv) Mymensingh area |  |  | 847 |  | MW | iv) Rangpur area |  |  |  | 721 | MW
v) Sylhet area |  |  | 386 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10613.51 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 63 | 11:00 | 133 | Netrakona | 101 | 18:00
2 | AKSML | 129 | 12:00 | 68 | Hathazari | 67 | 13:00 | 134 | New | 73 | 11:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 31 | 13:00 | 135 | Niamatpur | 48 | 13:00
4 | Agargaon | 82 | 13:00 | 70 | Ishurdi | 48 | 18:00 | 136 | Noapara | 40 | 18:30
5 | Agrabad | 42 | 18:00 | 71 | Jaldhaka | 50 | 18:00 | 137 | PHP | 8 | 16:00
6 | Amnura | 24 | 09:00 | 72 | Jamalpur | 92 | 08:00 | 138 | Pabna | 75 | 18:00
7 | Ashuganj | 57 | 12:00 | 73 | Jashore | 100 | 13:00 | 139 | Palashbari | 80 | 18:00
8 | BSRM | 206 | 04:00 | 74 | Jhenaidah | 97 | 18:00 | 140 | Panchagarh | 47 | 18:00
9 | Bagerhat | 62 | 18:00 | 75 | Joydebpur | 84 | 12:00 | 141 | Patiya | 6.5 | 18:00
10 | Bajitpur | 58 | 18:30 | 76 | Joypurhat | 44 | 20:00 | 142 | Patuakhali | 42.5 | 20:00
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 15.5 | 12:00 | 143 | Payra | 22 | 18:00
12 | Bakulia | 64 | 18:00 | 78 | KSRM | 25 | 17:00 | 144 | Postogola | 38 | 13:00
13 | Banani | 18.6 | 13:00 | 79 | Kabirpur | 179 | 18:00 | 145 | Purbachal | 21 | 18:00
14 | Bangabhaban | 12 | 11:00 | 80 | Kachua | 55 | 18:00 | 146 | Purbasadipur | 115 | 18:00
15 | Barapukuria | 54 | 18:00 | 81 | Kallyanpur | 70 | 14:00 | 147 | Rahanpur | 23 | 19:00
16 | Barguna | 14 | 10:00 | 82 | Kalurghat | 32 | 12:00 | 148 | Rahim | 37 | 17:00
17 | Barishal | 89 | 13:00 | 83 | Kamrangirchar | 62 | 13:00 | 149 | Rajbari | 60 | 18:00
18 | Barishal-230 | 64 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 114 | 08:00
19 | Baroaulia | 60 | 17:00 | 85 | Kasba | 22 | 19:00 | 151 | Rajshahi | 80 | 13:00
20 | Baroirhat | 49 | 13:00 | 86 | Kazla | 85 | 19:00 | 152 | Rajshahi-230 | 60 | 13:00
21 | Bashundhara | 124 | 13:00 | 87 | Keranigonj | 62 | 18:00 | 153 | Ramganj | 66 | 13:00
22 | BashundharaCement | 8 | 00:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 25 | 19:00
23 | Beanibazar | 48 | 18:00 | 89 | Khulna | 54 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 46 | 18:00 | 90 | Khulshi | 168 | 14:00 | 156 | Rangpur | 94 | 18:00
25 | Bhaluka | 122 | 19:00 | 91 | Kishoreganj | 86 | 18:30 | 157 | Ruppur | 2.4 | 15:00
26 | Bhandaria | 36 | 20:00 | 92 | Kodda | 260 | 18:00 | 158 | SSM | 3 | 03:00
27 | Bhangura | 24 | 18:00 | 93 | Kulaura | 29 | 18:00 | 159 | Saidpur | 94 | 18:00
28 | Bheramara(GK) | 40 | 18:30 | 94 | Kurigram | 46 | 18:00 | 160 | Satkhira | 89 | 18:30
29 | Bhulta | 183 | 16:00 | 95 | Kushtia | 112 | 18:30 | 161 | Satmasjid | 78 | 14:00
30 | Bog-Sherpur | 54 | 09:00 | 96 | Laksam | 23 | 18:00 | 162 | Savar | 162 | 12:00
31 | Bogura | 109 | 20:00 | 97 | Lakshmipur | 24 | 19:00 | 163 | SevenRings | 15.7 | 20:00
32 | Borhanuddin | 62 | 21:00 | 98 | Lalbag | 54 | 19:00 | 164 | ShahCement | 29 | 21:00
33 | Brahmanbaria | 82 | 19:30 | 99 | Lalmonirhat | 43 | 18:00 | 165 | Shahjadpur | 58 | 18:00
34 | Cantonment | 76 | 18:30 | 100 | MI_Cement | 17.3 | 00:00 | 166 | Shahjibazar | 83 | 18:00
35 | Chandina | 8 | 18:00 | 101 | Madanganj | 28 | 00:00 | 167 | Shahmirpur | 38 | 18:30
36 | Chandpur | 54 | 13:00 | 102 | Madaripur | 70 | 21:00 | 168 | Shariatpur | 55 | 20:00
37 | Chandraghona | 25 | 18:00 | 103 | Madartek | 54 | 13:00 | 169 | Sherpur | 112 | 18:30
38 | Chapai | 58 | 12:00 | 104 | Madunaghat | 29 | 18:00 | 170 | Shikalbaha | 17 | 08:00
39 | Charsaidpur | 41 | 11:00 | 105 | Magura | 53 | 18:00 | 171 | Shitalakhya | 62.8 | 12:00
40 | Chauddagram | 52 | 13:00 | 106 | Mahasthangarh | 46 | 18:00 | 172 | Sholosohor | 32 | 12:00
41 | Chhatak | 26 | 18:00 | 107 | Maijdee | 29 | 19:30 | 173 | Shyampur | 144 | 14:00
42 | Chowmuhani | 101 | 19:30 | 108 | Manikganj | 89 | 18:00 | 174 | Siddhirganj | 96 | 12:00
43 | Chuadanga | 75 | 18:00 | 109 | Maniknagar | 50 | 13:00 | 175 | Sirajganj | 82 | 18:30
44 | Coxsbazar | 105 | 19:00 | 110 | Matarbari | 35 | 18:00 | 176 | Sonargaon | 144 | 17:00
45 | Cumilla(N) | 93 | 20:00 | 111 | Matuail | 42 | 17:00 | 177 | Sreemongol | 50 | 18:30
46 | Cumilla(S) | 108 | 18:00 | 112 | Metrorail_Motijheel | 11 | 13:00 | 178 | Sreepur | 98 | 18:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 11 | 12:00 | 179 | Srinagar | 31.5 | 13:00
48 | Daudkandi | 110 | 19:00 | 114 | Millgate | 73 | 12:00 | 180 | Sunamganj | 39 | 18:00
49 | DhakaUniversity | 50 | 11:00 | 115 | Mirpur | 107 | 13:00 | 181 | Sylhet | 37 | 14:00
50 | Dhamrai | 102 | 18:00 | 116 | Mirsorai | 9 | 10:00 | 182 | Sylhet-132 | 78 | 18:00
51 | Dhanmondi | 78 | 14:00 | 117 | Mirzapur | 36 | 18:00 | 183 | TK | 15 | 09:00
52 | Dohazari | 73 | 18:00 | 118 | Mithapukur | 51 | 18:00 | 184 | Tangail | 114 | 18:00
53 | Faridpur | 107 | 18:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 27 | 18:30
54 | Fatullah | 95 | 11:00 | 120 | Mogbazar | 66.1 | 13:00 | 186 | Tasnim | 19 | 00:00
55 | Fenchuganj | 25 | 18:00 | 121 | Mongla | 38 | 08:00 | 187 | Thakurgaon | 82 | 18:30
56 | Feni | 70 | 18:00 | 122 | Motijheel | 26 | 13:00 | 188 | Tongi | 83 | 13:00
57 | GPH | 93 | 07:00 | 123 | Muktagacha | 26 | 18:00 | 189 | Ullahpara | 26 | 18:00
58 | Ghatail | 58 | 18:00 | 124 | Munshiganj | 69 | 19:00 | 190 | Ullon | 38 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 24 | 19:30 | 191 | Uttara | 58 | 13:00
60 | Ghorashal-230 | 83 | 12:00 | 126 | Mymensingh | 127 | 18:00 | 192 | UttaraNew | 41 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 89 | 18:00 | 193 | Zigatola | 52 | 13:00
62 | Gollamari | 72 | 13:00 | 128 | Narail | 43 | 18:30
63 | Gopalganj | 74.4 | 19:00 | 129 | Narinda | 56 | 13:00
64 | Gulshan | 72 | 14:00 | 130 | Narshingdi | 145 | 19:30
65 | Halishahar | 49 | 15:00 | 131 | Natore | 100 | 18:00
66 | HaripurSBU | 85 | 00:00 | 132 | Nawabganj | 35.8 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8991 | 0 |  | 8991
1:00 | 8512 | 0 |  | 8512
2:00 | 8087 | 0 |  | 8087
3:00 | 7751 | 0 |  | 7751
4:00 | 7511 | 0 |  | 7511
5:00 | 7451 | 0 |  | 7451
6:00 | 7885 | 0 |  | 7885
7:00 | 8213.17 | 0 |  | 8213.17
8:00 | 9091.19 | 0 |  | 9091.19
9:00 | 9540.91 | 0 |  | 9540.91
10:00 | 9554.59 | 0 |  | 9554.59
11:00 | 9585.99 | 0 |  | 9585.99
12:00 | 10138.04 | 0 |  | 10138.04
13:00 | 10549.59 | 0 |  | 10549.59
14:00 | 10212.7 | 0 |  | 10212.7
15:00 | 9970.5 | 0 |  | 9970.5
16:00 | 9632.47 | 0 |  | 9632.47
17:00 | 9896.19 | 0 |  | 9896.19
18:00 | 10907 | 0 |  | 10907
19:00 | 11052.5 | 0 |  | 11052.5
19:30 | 10793 | 0 |  | 10793
20:00 | 10785 | 0 |  | 10785
21:00 | 10566.3 | 0 |  | 10566.3
22:00 | 10026.03 | 0 |  | 10026.03
23:00 | 9442.7 | 0 |  | 9442.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4561 | 4430 | 8991 | DAILY GENERATION CURVE
00:30 | 4400.5 | 4351 | 8751.5
01:00 | 4240 | 4272 | 8512 | 24-12-2025
01:30 | 4200 | 4099.5 | 8299.5
02:00 | 4160 | 3927 | 8087
02:30 | 4049.5 | 3869.5 | 7919
03:00 | 3939 | 3812 | 7751
03:30 | 3917 | 3714 | 7631
04:00 | 3895 | 3616 | 7511
04:30 | 3871 | 3610 | 7481
05:00 | 3847 | 3604 | 7451
05:30 | 4017 | 3651 | 7668
06:00 | 4187 | 3698 | 7885
06:30 | 4216.13 | 3832.955 | 8049.085
07:00 | 4245.26 | 3967.91 | 8213.17
07:30 | 4428.32 | 4223.86 | 8652.18
08:00 | 4611.38 | 4479.81 | 9091.19
08:30 | 4663.465 | 4652.585 | 9316.05
09:00 | 4715.55 | 4825.36 | 9540.91
09:30 | 4760.19 | 4787.56 | 9547.75
10:00 | 4804.83 | 4749.76 | 9554.59
10:30 | 4808.815 | 4761.475 | 9570.29
11:00 | 4812.8 | 4773.19 | 9585.99
11:30 | 4918.03 | 4943.985 | 9862.015
12:00 | 5023.26 | 5114.78 | 10138.04
12:30 | 5069.005 | 5274.81 | 10343.815
13:00 | 5114.75 | 5434.84 | 10549.59
13:30 | 5075.565 | 5305.58 | 10381.145
14:00 | 5036.38 | 5176.32 | 10212.7
14:30 | 4977.91 | 5113.69 | 10091.6
15:00 | 4919.44 | 5051.06 | 9970.5
15:30 | 4952.13 | 4849.355 | 9801.485
16:00 | 4984.82 | 4647.65 | 9632.47
16:30 | 5008.48 | 4755.85 | 9764.33
17:00 | 5032.14 | 4864.05 | 9896.19
17:30 | 5201.07 | 5200.525 | 10401.595
18:00 | 5370 | 5537 | 10907
18:30 | 5396.25 | 5583.5 | 10979.75
19:00 | 5422.5 | 5630 | 11052.5
19:30 | 5225 | 5568 | 10793
20:00 | 5194 | 5591 | 10785
20:30 | 5077.5 | 5598.15 | 10675.65 |  | Executive Engineer
21:00 | 4961 | 5605.3 | 10566.3 |  | Network Operation Division
21:30 | 4873 | 5423.165 | 10296.165
22:00 | 4785 | 5241.03 | 10026.03
22:30 | 4706.75 | 5027.615 | 9734.365
23:00 | 4628.5 | 4814.2 | 9442.7

## En-Curve
QF-LDC-12
Date | 24-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2935 | 720 | 807 | 0 | 94 | 820 | 40 | 3567 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2894 | 696.5 | 796 | 0 | 89 | 819.5 | 40 | 3412.5 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24-12-2025
01:00 | 2853 | 673 | 785 | 0 | 84 | 819 | 40 | 3258 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2840 | 676 | 655 | 0 | 86 | 822 | 40 | 3180.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 228.6675 |  | MKWHr
02:00 | 2827 | 679 | 525 | 0 | 88 | 825 | 40 | 3103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2811.5 | 653.5 | 502.5 | 0 | 85 | 826 | 40 | 3000.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 228.6675 |  | MKWHr
03:00 | 2796 | 628 | 480 | 0 | 82 | 827 | 40 | 2898 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2740.5 | 610.5 | 431.5 | 0 | 82 | 824 | 40 | 2902.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2685 | 593 | 383 | 0 | 82 | 821 | 40 | 2907 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2660.5 | 590.5 | 383 | 0 | 85 | 822.5 | 40 | 2899.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2636 | 588 | 383 | 0 | 88 | 824 | 40 | 2892 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2718.5 | 647.5 | 394 | 0 | 86 | 824 | 40 | 2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2801 | 707 | 405 | 0 | 84 | 824 | 40 | 3024 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2801.5 | 727.5 | 525 | 0 | 83 | 825.5 | 40 | 3043.5 | 3.085 | 0 | 0 | 0 | 0 | 0 | 0
07:00 | 2802 | 748 | 645 | 0 | 82 | 827 | 40 | 3063 | 6.17 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 2792 | 778.5 | 725.5 | 0 | 89 | 904.5 | 40 | 3279 | 34.68 | 0 | 9 | 0 | 0 | 0 | 0
08:00 | 2782 | 809 | 806 | 0 | 96 | 982 | 40 | 3495 | 63.19 | 0 | 18 | 0 | 0 | 0 | 0
08:30 | 2780 | 793 | 854 | 0 | 98 | 1004.78 | 40 | 3617 | 98.77 | 0 | 30.5 | 0 | 0 | 0 | 0
09:00 | 2778 | 777 | 902 | 0 | 100 | 1027.56 | 40 | 3739 | 134.35 | 0 | 43 | 0 | 0 | 0 | 0
09:30 | 2783.5 | 785.5 | 902 | 0 | 99 | 978.445 | 40 | 3723 | 174.805 | 0 | 61.5 | 0 | 0 | 0 | 0
10:00 | 2789 | 794 | 902 | 0 | 98 | 929.33 | 40 | 3707 | 215.26 | 0 | 80 | 0 | 0 | 0 | 0
10:30 | 2768 | 795 | 902 | 0 | 101 | 933.035 | 40 | 3699 | 248.255 | 0 | 84 | 0 | 0 | 0 | 0
11:00 | 2747 | 796 | 902 | 0 | 104 | 936.74 | 40 | 3691 | 281.25 | 0 | 88 | 0 | 0 | 0 | 0
11:30 | 2735.5 | 823.5 | 902 | 0 | 100 | 982.33 | 40 | 3871 | 305.185 | 0 | 102.5 | 0 | 0 | 0 | 0
12:00 | 2724 | 851 | 902 | 0 | 96 | 1027.92 | 40 | 4051 | 329.12 | 0 | 117 | 0 | 0 | 0 | 0
12:30 | 2729.5 | 854.5 | 902 | 0 | 101 | 1083.37 | 40 | 4169 | 323.945 | 0 | 140.5 | 0 | 0 | 0 | 0
13:00 | 2735 | 858 | 902 | 0 | 106 | 1138.82 | 40 | 4287 | 318.77 | 0 | 164 | 0 | 0 | 0 | 0
13:30 | 2693.5 | 843.25 | 902 | 0 | 105 | 1108.41 | 40 | 4196.5 | 327.485 | 0 | 165 | 0 | 0 | 0 | 0
14:00 | 2652 | 828.5 | 902 | 0 | 104 | 1078 | 40 | 4106 | 336.2 | 0 | 166 | 0 | 0 | 0 | 0
14:30 | 2645.5 | 807 | 901.5 | 0 | 98 | 1079.5 | 40 | 4069 | 293.1 | 0 | 158 | 0 | 0 | 0 | 0
15:00 | 2639 | 785.5 | 901 | 0 | 92 | 1081 | 40 | 4032 | 250 | 0 | 150 | 0 | 0 | 0 | 0
15:30 | 2650 | 776.5 | 901.5 | 0 | 92 | 1007.5 | 40 | 4027.5 | 181.985 | 0 | 124.5 | 0 | 0 | 0 | 0
16:00 | 2661 | 767.5 | 902 | 0 | 92 | 934 | 40 | 4023 | 113.97 | 0 | 99 | 0 | 0 | 0 | 0
16:30 | 2667 | 787.75 | 901.5 | 0 | 96 | 1025.5 | 40 | 4078.5 | 63.58 | 0 | 104.5 | 0 | 0 | 0 | 0
17:00 | 2673 | 808 | 901 | 0 | 100 | 1117 | 40 | 4134 | 13.19 | 0 | 110 | 0 | 0 | 0 | 0
17:30 | 2689 | 814 | 901.5 | 0 | 104 | 1197 | 40 | 4350.5 | 6.595 | 0 | 299 | 0 | 0 | 0 | 0
18:00 | 2705 | 820 | 902 | 0 | 108 | 1277 | 40 | 4567 | 0 | 0 | 488 | 0 | 0 | 0 | 0
18:30 | 2709 | 813.5 | 902 | 0 | 103 | 1254 | 40 | 4600.5 | 0 | 0 | 557.75 | 0 | 0 | 0 | 0
19:00 | 2713 | 807 | 902 | 0 | 98 | 1231 | 40 | 4634 | 0 | 0 | 627.5 | 0 | 0 | 0 | 0
19:30 | 2756 | 770 | 902 | 0 | 100 | 1187 | 40 | 4643 | 0 | 0 | 395 | 0 | 0 | 0 | 0
20:00 | 2758 | 768 | 901 | 0 | 92 | 1169 | 40 | 4667 | 0 | 0 | 390 | 0 | 0 | 0 | 0
20:30 | 2753 | 767 | 901.5 | 0 | 95 | 1168.65 | 40 | 4667.5 | 0 | 0 | 283 | 0 | 0 | 0 | 0
21:00 | 2748 | 766 | 902 | 0 | 98 | 1168.3 | 40 | 4668 | 0 | 0 | 176 | 0 | 0 | 0 | 0
21:30 | 2744.5 | 746 | 902 | 0 | 92 | 1092.665 | 40 | 4522 | 0 | 0 | 157 | 0 | 0 | 0 | 0
22:00 | 2741 | 726 | 902 | 0 | 86 | 1017.03 | 40 | 4376 | 0 | 0 | 138 | 0 | 0 | 0 | 0
22:30 | 2739.5 | 723.25 | 902 | 0 | 85 | 1023.115 | 40 | 4119 | 0 | 0 | 102.5 | 0 | 0 | 0 | 0
23:00 | 2738 | 720.5 | 902 | 0 | 84 | 1029.2 | 40 | 3862 | 0 | 0 | 67 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 411 | 05:00 | 387 | 12:00 | Meghnaghat | 413 | 04:00 | 390 | 12:00
Ashuganj | 420 | 5:00 | 399 | 12:00 | Payra | 418 | 03:00 | 408 | 18:00
Bhulta | 417 | 05:00 | 394 | 12:00 | Rahanpur | 421 | 04:00 | 404 | 18:00
Bibiana | 402 | 02:00 | 388 | 18:00 | Rampal | 413 | 04:00 | 398 | 13:00
BIPTC | 409 | 04:00 | 389 | 11:00
Bogura | 418 | 04:00 | 397 | 18:00
Gopalganj | 415 | 04:00 | 396 | 13:00
Kaliakoir | 401 | 05:00 | 377 | 12:00
Korerhat | 414 | 04:00 | 394 | 12:00
Madunaghat | 409 | 05:00 | 397 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 05:00 | 225 | 12:00 | Kachua | 240 | 05:00 | 227 | 13:00
AKSML | 237 | 05:00 | 226 | 13:00 | Kaliakoir | 243 | 04:00 | 226 | 12:00
Aminbazar | 239 | 04:00 | 226 | 12:00 | Keranigonj | 241 | 05:00 | 224 | 12:00
Ashuganj | 240 | 06:00 | 227 | 13:00 | Khulna(S) | 243 | 05:00 | 229 | 18:00
Ashuganj-400 | 240 | 06:00 | 227 | 13:00 | Korerhat | 269 | 03:00 | 229 | 12:00
Baghabari | 239 | 03:00 | 230 | 18:00 | Madunaghat | 235 | 02:00 | 227 | 12:00
Barapukuria | 231 | 06:00 | 216 | 09:00 | Madunaghat-400 | 237 | 04:00 | 229 | 13:00
Barapukuria-230 | 231 | 06:00 | 216 | 09:00 | Maniknagar | 238 | 07:00 | 225 | 12:00
Barishal | 245 | 04:00 | 238 | 12:00 | Meghnaghat | 247 | 06:00 | 234 | 13:00
Bheramara | 238 | 03:00 | 222 | 09:00 | Meghnaghat-400 | 243 | 05:00 | 228 | 12:00
Bhulta | 243 | 04:00 | 228 | 12:00 | Mirsorai | 240 | 04:00 | 228 | 13:00
Bibiana | 236 | 02:00 | 228 | 12:00 | Rajshahi | 237 | 03:00 | 223 | 09:00
BIPTC | 240 | 06:00 | 223 | 18:00 | Rampal | 240 | 05:00 | 227 | 18:00
Bogura | 244 | 04:00 | 231 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 243 | 03:00 | 231 | 13:00 | Rampura | 243 | 05:00 | 228 | 12:00
Borhanuddin | 246 | 01:00 | 240 | 18:00 | Shikalbaha | 235 | 05:00 | 225 | 12:00
BSRM | 240 | 05:00 | 227 | 13:00 | Shyampur | 241 | 04:00 | 225 | 12:00
Cumilla(N) | 240 | 05:00 | 228 | 12:00 | Siddhirganj | 243 | 06:00 | 229 | 12:00
Faridpur | 246 | 04:00 | 235 | 12:00 | Sirajgonj | 247 | 05:00 | 237 | 18:00
Fenchuganj | 240 | 05:00 | 231 | 13:00 | Sreepur | 236 | 03:00 | 226 | 12:00
Feni | 240 | 04:00 | 228 | 12:00 | Tongi | 239 | 04:00 | 225 | 13:00
Ghorashal | 240 | 00:00 | 230 | 14:00
Ghorashal-230 | 240 | 22:00 | 213 | 11:00
Gopalganj | 246 | 05:00 | 234 | 13:00
GPH | 238 | 06:00 | 227 | 13:00
Haripur | 242 | 04:00 | 228 | 12:00
Hasnabad | 237 | 00:00 | 225 | 12:00
Hathazari | 234 | 05:00 | 225 | 15:00
Ishurdi | 241 | 03:00 | 226 | 09:00
Jhenaidah | 240 | 03:00 | 223 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 129 | 12:00 | Laksam | 141 | 04:00 | 134 | 12:00
Agargaon | 139 | 06:00 | 129 | 12:00 | Lakshmipur | 135 | 03:00 | 128 | 12:00
Agrabad | 137 | 04:00 | 130 | 13:00 | Lalbag | 136 | 02:00 | 127 | 12:00
AKS | 134 | 02:00 | 129 | 12:00 | Lalmonirhat | 134 | 05:00 | 120 | 09:00
Aminbazar | 138 | 04:00 | 129 | 12:00 | Madanganj | 138 | 00:00 | 134 | 13:00
Amnura | 140 | 06:00 | 128 | 11:00 | Madaripur | 141 | 05:00 | 135 | 19:00
Ashuganj | 141 | 04:00 | 137 | 12:00 | Madartek | 137 | 04:00 | 128 | 12:00
Bagerhat | 132 | 04:00 | 122 | 18:00 | Madunaghat | 138 | 03:00 | 132 | 13:00
Bajitpur | 137 | 06:00 | 131 | 15:00 | Magura | 137 | 05:00 | 126 | 13:00
Bakerganj | 137 | 05:00 | 133 | 18:00 | Mahasthangarh | 137 | 02:00 | 128 | 18:00
Bakulia | 136 | 03:00 | 130 | 12:00 | Maijdee | 135 | 04:00 | 128 | 12:00
Banani | 138 | 03:00 | 129 | 12:00 | Manikganj | 133 | 02:00 | 121 | 12:00
Bangabhaban | 140 | 04:00 | 130 | 12:00 | Maniknagar | 141 | 04:00 | 129 | 13:00
Barapukuria | 139 | 06:00 | 128 | 08:00 | Matarbari | 128 | 03:00 | 121 | 21:00
Barguna | 137 | 06:00 | 134 | 12:00 | Matuail | 141 | 06:00 | 134 | 12:00
Barishal | 142 | 05:00 | 135 | 12:00 | Metrorail_Motijheel | 141 | 04:00 | 129 | 13:00
Barishal-230 | 142 | 05:00 | 136 | 12:00 | Metrorail_Uttara | 137 | 03:00 | 127 | 12:00
Baroaulia | 136 | 04:00 | 131 | 16:00 | Millgate | 137 | 03:00 | 125 | 12:00
Baroirhat | 137 | 04:00 | 130 | 13:00 | Mirpur | 138 | 05:00 | 127 | 12:00
Bashundhara | 138 | 02:00 | 129 | 12:00 | Mirzapur | 136 | 04:00 | 126 | 12:00
BashundharaCement | 138 | 00:00 | 134 | 13:00 | Mithapukur | 137 | 05:00 | 125 | 09:00
Beanibazar | 137 | 02:00 | 131 | 12:00 | MI_Cement | 139.8 | 05:00 | 127 | 12:00
Benapole | 135 | 02:00 | 118 | 13:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 136 | 05:00 | 127 | 18:00 | Mogbazar | 139 | 03:00 | 130 | 12:00
Bhandaria | 140 | 02:00 | 135 | 12:00 | Mongla | 131 | 06:00 | 124 | 18:00
Bhangura | 140 | 02:00 | 133 | 08:00 | Motijheel | 140 | 04:00 | 130 | 12:00
Bheramara | 139 | 03:00 | 129 | 09:00 | Muktagacha | 132 | 10:00 | 123 | 18:30
Bheramara(GK) | 139 | 05:00 | 129 | 09:00 | Munshiganj | 140 | 03:00 | 132 | 12:00
Bhulta | 132 | 07:00 | 124 | 16:00 | Muradnagar | 140 | 04:00 | 130 | 13:00
Bog-Sherpur | 139 | 04:00 | 130 | 12:00 | Mymensingh | 133 | 03:00 | 122 | 18:00
Bogura | 140 | 05:00 | 131 | 09:00 | Naogaon | 136 | 01:00 | 127 | 09:00
Bogura-230 | 139 | 03:00 | 131 | 12:00 | Narail | 139 | 04:00 | 126 | 13:00
Brahmanbaria | 137 | 06:00 | 129 | 13:00 | Narinda | 141 | 04:00 | 129 | 13:00
Cantonment | 139 | 04:00 | 129 | 12:00 | Narshingdi | 139 | 03:00 | 127 | 12:00
Chandina | 141 | 03:00 | 133 | 13:00 | Natore | 138 | 15:00 | 129 | 09:00
Chandpur | 139 | 04:00 | 133 | 13:00 | Nawabganj | 138 | 05:00 | 127 | 12:00
Chandraghona | 138 | 03:00 | 133 | 12:00 | Netrakona | 132 | 23:00 | 122 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 04:00 | 134 | 08:00 | New | 138 | 06:00 | 126 | 11:00
Charsaidpur | 141 | 04:00 | 132 | 13:00 | Niamatpur | 140 | 01:00 | 135 | 12:00
Chauddagram | 139 | 03:00 | 131 | 13:00 | Noapara | 136 | 05:00 | 120 | 13:00
Chhatak | 135 | 04:00 | 130 | 12:00 | Pabna | 140 | 06:00 | 131 | 09:00
Chowmuhani | 135 | 03:00 | 128 | 16:00 | Palashbari | 134 | 04:00 | 124 | 08:00
Chuadanga | 140 | 04:00 | 125 | 18:00 | Panchagarh | 139 | 04:00 | 124 | 08:00
Coxsbazar | 128 | 03:00 | 120 | 21:00 | Patiya | 134 | 00:00 | 130 | 13:00
Cumilla(N) | 141 | 05:00 | 133 | 12:00 | Patuakhali | 136 | 05:00 | 133 | 00:00
Cumilla(S) | 138 | 00:00 | 125 | 11:00 | Payra | 138 | 04:00 | 135 | 12:00
Daganbhuiyan | 138 | 05:00 | 130 | 10:00 | PHP | 137 | 04:00 | 130 | 12:00
Daudkandi | 138 | 02:00 | 129 | 12:00 | Postogola | 141 | 05:00 | 129 | 12:00
DhakaUniversity | 138 | 05:00 | 129 | 12:00 | Purbachal | 138 | 03:00 | 128 | 13:00
Dhamrai | 137 | 03:00 | 127 | 12:00 | Purbasadipur | 133 | 03:00 | 119 | 09:00
Dhanmondi | 143 | 04:00 | 135 | 12:00 | Rahanpur | 140 | 00:00 | 135 | 18:00
Dohazari | 134 | 04:00 | 127 | 16:00 | Rahanpur-400 | 142 | 04:00 | 136 | 13:00
Faridpur | 140 | 02:00 | 134 | 12:00 | Rahim | 142 | 05:00 | 134 | 12:00
Fatullah | 139 | 03:00 | 127 | 12:00 | Rajbari | 141 | 03:00 | 134 | 12:00
Fenchuganj | 139 | 02:00 | 135 | 12:00 | Rajendrapur | 136 | 04:00 | 129 | 12:00
Feni | 136 | 06:00 | 130 | 13:00 | Rajshahi | 138 | 01:00 | 129 | 11:00
Feni-230 | 137 | 02:00 | 130 | 12:00 | Rajshahi-230 | 137 | 03:00 | 129 | 09:00
Ghatail | 132 | 03:00 | 120 | 18:00 | Ramganj | 136 | 01:00 | 128 | 13:00
Ghorashal | 136 | 04:00 | 127 | 12:00 | Rampur | 137 | 05:00 | 130 | 12:00
Goalpara | 135 | 04:00 | 127 | 13:00 | Rampura | 138 | 04:00 | 128 | 12:00
Gollamari | 136 | 03:00 | 128 | 18:00 | Rangamati | 138 | 05:00 | 132 | 12:00
Gopalganj | 140 | 04:00 | 132 | 12:00 | Rangpur | 134 | 04:00 | 124 | 09:00
Gopalganj-400 | 143 | 05:00 | 135 | 13:00 | Ruppur | 140 | 03:00 | 131 | 09:00
Gulshan | 137 | 05:00 | 128 | 12:00 | Saidpur | 135 | 04:00 | 122 | 12:00
Halishahar | 138 | 06:00 | 131 | 12:00 | Satkhira | 135 | 04:00 | 124 | 18:00
Haripur | 142 | 04:00 | 134 | 12:00 | Satmasjid | 138 | 04:00 | 127 | 13:00
HaripurSBU | 142 | 04:00 | 134 | 12:00 | Savar | 137 | 03:00 | 126 | 12:00
Hasnabad | 139 | 03:00 | 131 | 11:00 | SevenRings | 137 | 04:00 | 126 | 12:00
Hathazari | 137 | 02:00 | 133 | 12:00 | ShahCement | 141 | 04:00 | 132 | 13:00
Hatirjheel | 138 | 05:00 | 128 | 13:00 | Shahjadpur | 140 | 03:00 | 135 | 21:00
Ishurdi | 141 | 03:00 | 132 | 18:00 | Shahjibazar | 137 | 06:00 | 130 | 12:00
Jaldhaka | 133 | 05:00 | 120 | 12:00 | Shahmirpur | 138 | 03:00 | 132 | 12:00
Jamalpur | 132 | 09:00 | 120 | 01:00 | Shariatpur | 142 | 04:00 | 134 | 13:00
Jashore | 133 | 00:00 | 121 | 13:00 | Sherpur | 131 | 09:00 | 117 | 00:00
Jhenaidah | 140 | 03:00 | 115 | 18:00 | Shikalbaha | 127 | 01:00 | 121 | 12:00
Jhenaidah-230 | 140 | 03:00 | 128 | 13:00 | Shikalbaha-230 | 139 | 05:00 | 132 | 13:00
Joydebpur | 136 | 03:00 | 122 | 12:00 | Shitalakhya | 139.8 | 05:00 | 127 | 12:00
Joypurhat | 135 | 01:00 | 126 | 09:00 | Sholosohor | 138 | 04:00 | 132 | 12:00
Juldah | 137 | 01:00 | 132 | 12:00 | Shyampur | 137 | 07:00 | 130 | 12:00
Kabirpur | 139 | 04:00 | 121 | 12:00 | Shyampur-230 | 140 | 04:00 | 130 | 12:00
Kachua | 141 | 05:00 | 134 | 13:00 | Siddhirganj | 142 | 06:00 | 134 | 12:00
Kaliakoir | 142 | 05:00 | 131 | 16:00 | Sirajganj | 138 | 03:00 | 129 | 18:00
Kallyanpur | 139 | 01:00 | 129 | 12:00 | Sonargaon | 139 | 07:00 | 132 | 12:00
Kalurghat | 136 | 03:00 | 133 | 12:00 | Sreemongol | 137 | 03:00 | 132 | 12:00
Kamrangirchar | 136 | 05:00 | 127 | 12:00 | Sreepur | 138 | 02:00 | 132 | 12:00
Kaptai | 140 | 4:00 | 135 | 13:00 | Srinagar | 138 | 04:00 | 127 | 12:00
Kasba | 140 | 05:00 | 130 | 13:00 | SSM | 140 | 01:00 | 136 | 13:00
Kazla | 136 | 05:00 | 129 | 13:00 | Sunamganj | 134 | 03:00 | 129 | 12:00
Keranigonj | 138 | 04:00 | 127 | 12:00 | Sylhet | 136 | 04:00 | 131 | 13:00
Khagrachori | 137 | 04:00 | 132 | 12:00 | Sylhet-132 | 135 | 00:00 | 133 | 13:00
Khulna | 133 | 01:00 | 126 | 18:00 | Tangail | 130 | 03:00 | 122 | 18:00
Khulna(S) | 137 | 04:00 | 127 | 18:00 | Taraganj | 134 | 06:00 | 123 | 09:00
Khulshi | 136 | 03:00 | 129 | 13:00 | Tasnim | 141 | 04:00 | 132 | 12:00
Kishoreganj | 135 | 06:00 | 128 | 18:00 | Thakurgaon | 136 | 04:00 | 119 | 08:00
Kodda | 135 | 03:00 | 123 | 12:00 | TK | 138 | 04:00 | 133 | 14:00
KSRM | 137 | 00:00 | 132 | 12:00 | Tongi | 139 | 04:00 | 128 | 13:00
Kulaura | 139 | 04:00 | 134 | 12:00 | Ullahpara | 140 | 05:00 | 131 | 09:00
Kurigram | 133 | 05:00 | 119 | 08:00 | Ullon | 138 | 03:00 | 129 | 12:00
Kushtia | 136 | 05:00 | 123 | 18:30 | Uttara | 138 | 05:00 | 128 | 12:00
Zigatola | 139 | 04:00 | 127 | 12:00 | UttaraNew | 137 | 03:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division