## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-12-2025 | during | 27-12-2025 | during | 27-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 346 | 355 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 250 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 0 | 0 | ps availability is less
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 49 | 49 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14 | 8 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | ST maint & Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 410 | 415 | 583 | 583 | 450 | 450 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1078 | 1050 | 5564.22 | 5548.22 | 2437.37 | 2421.37
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 230 | 0 | 220 | 220 | 0 | 0 | Under Maintenance
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 56 | 48 | 64 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 33 | 33 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 42 | 38 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1026 | 1158 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 600 | 515 | 518 | 518 | 518 | 518 | Plant availability less
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1956 | 1751 | 3327.72 | 3328.72 | 2643.5 | 2644.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 130 | 189 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 387 | 260 | 353.35 | 353.35 | 320 | 320 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0.01 | 0.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 230 | 393 | 393 | 340 | 340 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 110 | 110 | 163 | 163 | 112 | 112 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 84 | 76 | 160 | 160 | 110 | 110 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1047 | 935 | 2780.56 | 2725.56 | 1857.71 | 1802.71
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-12-2025 | during | 27-12-2025 | during | 27-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 70 | 70 | 157.5 | 157.5 | 55 | 55 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 25 | 20 | 20 | 20 | 70 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 18 | 60 | 60 | 60 | 60 | Machine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 9 | 0 | 20 | 0 | 20 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 114 | 113 | 335.5 | 314 | 168.5 | 197
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 35 | 35 | 35 | 35 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 160 | 0 | 0 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 212 | 212 | 210 | 210 | 210 | 210 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 546 | 541 | 413 | 413 | 598 | 598
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 434 | 422 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 73 | 0 | 73 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 892 | 1101 | 0 | 0 | 1118 | 1118 | FGMO, plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1394 | 1523 | 2345 | 2272 | 2298.1 | 2225.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 400 | 450 | 0 | 0 | 500 | 500 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 140 | 140 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 686 | 860 | 1085.32 | 1085.32 | 1025 | 1025 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1446 | 1670 | 2009.32 | 2009.32 | 2316 | 2316
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 39 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 179 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 283 | 358 | 413.79 | 413.79 | 0 | 0 | Maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 2 | 0 | 2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1023.14 | 1273 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 6 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 80 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1610.14 | 1810 | 3048.87 | 2885.87 | 2175.08 | 2012.08
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | plant availability zero
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 54 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 8 | 0 | 12 | 0 | 12 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 35 | 0 | 75.23 | 0 | 75.23 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 102 | 54 | 373.43 | 283 | 373.43 | 283
System Total |  |  |  |  | 28823.2 | 28379.108 | 9293.14 | 9447 | 20197.62 | 19779.69 | 14867.69 | 14499.76
Forecast Scenario (27-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8480 |  | 0 |  | 8480
|  |  |  | 1:00 | 7980 |  | 0 |  | 7980
|  |  |  | 2:00 | 7560 |  | 0 |  | 7560
|  |  |  | 3:00 | 7320 |  | 0 |  | 7320
|  |  |  | 4:00 | 7140 |  | 0 |  | 7140
|  |  |  | 5:00 | 6950 |  | 0 |  | 6950
|  |  |  | 6:00 | 7480 |  | 0 |  | 7480
|  |  |  | 7:00 | 8020 |  | 0 |  | 8020
|  |  |  | 8:00 | 8780 |  | 0 |  | 8780
|  |  |  | 9:00 | 9340 |  | 0 |  | 9340
|  |  |  | 10:00 | 9230 |  | 0 |  | 9230
|  |  |  | 11:00 | 9350 |  | 0 |  | 9350
|  |  |  | 12:00 | 9750 |  | 0 |  | 9750
|  |  |  | 13:00 | 10180 |  | 0 |  | 10180
|  |  |  | 14:00 | 9730 |  | 0 |  | 9730
|  |  |  | 15:00 | 9500 |  | 0 |  | 9500
|  |  |  | 16:00 | 9400 |  | 0 |  | 9400
|  |  |  | 17:00 | 9720 |  | 0 |  | 9720
|  |  |  | 18:00 | 10880 |  | 0 |  | 10880
|  |  |  | 18:30 | 10700 |  | 0 |  | 10700
|  |  |  | 19:00 | 10640 |  | 0 |  | 10640
|  |  |  | 19:30 | 10560 |  | 0 |  | 10560
|  |  |  | 20:00 | 10440 |  | 0 |  | 10440
|  |  |  | 21:00 | 10360 |  | 0 |  | 10360
|  |  |  | 22:00 | 9920 |  | 0 |  | 9920
|  |  |  | 23:00 | 9270 |  | 0 |  | 9270
Probable Maximum Temperature: |  |  | 24.00°C
Probable Maximum Demand at Day Peak: |  |  | 9750.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10880.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10880.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 217.42 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:52 hrs on 27-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-12-2025 | [28 empty] | Date: | 26-12-2025 | [28 empty] | Date: | 26-12-2025 | [28 empty] | Date: | 26-12-2025 | [28 empty] | Date: | 26-12-2025 | [17 empty] | Date: | 26-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 13.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 775 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 112 | 0 | 0 | 20 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 4553.5 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796 | 0 | 0 | 0 | 870.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 180 | 0 | 250 | 800 | 0 | 4054.56 | 8608.06 | 98.24
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 715 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 230 | 280 | 0 | 51 | 0 | 180 | 0 | 0 | 114 | 0 | 0 | 14 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 5 | 0 | 5 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 4358.5 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 831.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 180 | 0 | 250 | 600 | 0 | 3762.6 | 8121.1 | 98.24
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 665 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 3812.5 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 836.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 550 | 0 | 3694.18 | 7506.68 | 98.24
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 610 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 3558 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 0 | 0 | 857.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3537.33 | 7095.33 | 98.23
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 220 | 270 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 143 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 3442 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 832.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3350.74 | 6792.74 | 98.23
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 220 | 270 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 143 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 3396 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 0 | 0 | 0 | 831.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3400.54 | 6796.54 | 98.23
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 220 | 270 | 0 | 0 | 0 | 203 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 211 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 3498 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 840.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3484.81 | 6982.81 | 98.23
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 220 | 270 | 0 | 0 | 0 | 213 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 66 | 0 | 1 | 0 | 0 | 0 | 211 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 3536.07 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 737 | 0 | 0 | 0 | 830.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0.55 | 0 | 0 | 179 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 500 | 0 | 3491.82 | 7027.89 | 98.22
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 230 | 0 | 0 | 2 | 0 | 10 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 660 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 654 | 2 | 0 | 0 | 270 | 300 | 0 | 0 | 0 | 197 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 64 | 0 | 4 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 1 | 0 | 0 | 40 | 30 | 0 | 0 | 158 | 0 | 0 | 0 | 62 | 0 | 1.37 | 0 | 4064.37 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 757 | 0 | 0 | 0 | 830.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.46 | 12 | 0 | 0 | 2.57 | 0 | 0 | 195 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 53 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 8 | 0 | 0 | 0 | 120 | 220 | 0 | 250 | 510 | 0 | 3749.98 | 7814.35 | 98.22
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 5 | 0 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 660 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 655 | 4 | 0 | 0 | 300 | 343 | 0 | 10 | 0 | 198 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 76 | 0 | 11 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 1 | 17 | 0 | 42 | 30 | 0 | 0 | 158 | 0 | 0 | 12 | 110 | 0 | 3.25 | 0 | 4293.25 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 810 | 0 | 0 | 0 | 824.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 0 | 0 | 4.29 | 0 | 0 | 187 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 53 | 0 | 4 | 0 | 0 | 0 | 0 | 1.2 | 14 | 0 | 0 | 0 | 140 | 220 | 0 | 250 | 600 | 0 | 3961.15 | 8254.4 | 98.22
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 250 | 0 | 0 | 9 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 600 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 817 | 16 | 0 | 0 | 300 | 396 | 0 | 10 | 0 | 191 | 0 | 0 | 110 | 0 | 0 | 11 | 0 | 76 | 0 | 14 | 0 | 0 | 0 | 213 | 35 | 0 | 0 | 2 | 17 | 0 | 42 | 30 | 0 | 0 | 158 | 0 | 0 | 35 | 103 | 0 | 6 | 0 | 4386 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 806 | 0 | 0 | 0 | 825.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 52 | 0 | 0 | 6.29 | 0 | 0 | 190 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 53 | 0 | 5 | 0 | 0 | 0 | 0 | 3 | 26 | 0.02 | 0 | 0 | 140 | 220 | 0 | 250 | 560 | 0 | 3943.9 | 8329.9 | 98.22
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 600 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 893 | 18 | 0 | 0 | 230 | 397 | 0 | 25 | 0 | 140 | 0 | 0 | 110 | 0 | 0 | 6 | 0 | 70 | 0 | 22 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 10 | 17 | 0 | 72 | 30 | 0 | 0 | 159 | 0 | 0 | 35 | 91 | 0 | 8 | 0 | 4536 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 790 | 0 | 0 | 0 | 860.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 68 | 0 | 0 | 5 | 0 | 0 | 177 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 53 | 0 | 8 | 0 | 0 | 0 | 0 | 4 | 32 | 0 | 0 | 0 | 140 | 220 | 0 | 300 | 570 | 0 | 4053.19 | 8589.19 | 98.21
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 600 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 1026 | 18 | 0 | 0 | 215 | 387 | 0 | 51 | 0 | 130 | 0 | 0 | 110 | 0 | 0 | 6 | 0 | 84 | 0 | 64 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 35 | 70 | 0 | 9 | 0 | 4741 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 892 | 0 | 0 | 0 | 1023.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 80 | 0 | 0 | 6 | 0 | 0 | 179 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 54 | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 35 | 0 | 0 | 0 | 140 | 220 | 0 | 400 | 686 | 0 | 4552.14 | 9293.14 | 98.21
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 335 | 0 | 0 | 13 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 575 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1142 | 16 | 0 | 0 | 215 | 354 | 0 | 51 | 0 | 130 | 0 | 0 | 110 | 0 | 0 | 6 | 0 | 110 | 0 | 57 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 64 | 70 | 1 | 8 | 0 | 4901 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1063 | 0 | 0 | 0 | 1283.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 74 | 0 | 0 | 7 | 0 | 0 | 183 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 54 | 0 | 20 | 0 | 0 | 0 | 0 | 4 | 53 | 0 | 0 | 0 | 140 | 220 | 0 | 502 | 914 | 0 | 5306.49 | 10207.49 | 98.21
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 17 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.49 | 40 | 0 | 4 | 480 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 928 | 15 | 0 | 0 | 215 | 280 | 0 | 5 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 6 | 0 | 86 | 0 | 49 | 0 | 0 | 0 | 212 | 36 | 0 | 0 | 8 | 5 | 0 | 5 | 20 | 0 | 0 | 159 | 0 | 0 | 65 | 70 | 0 | 11.05 | 0 | 4011.54 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 968 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.6 | 56 | 0 | 0 | 10.08 | 0 | 0 | 140 | 0 | 0 | 0 | 220 | 0 | 0.84 | 0 | 53 | 0 | 18 | 0 | 0 | 0 | 0 | 3.7 | 58 | 0.09 | 0 | 0 | 100 | 180 | 0 | 250 | 850 | 0 | 4613.31 | 8624.85 | 98.21
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 250 | 0 | 0 | 12 | 0 | 14.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.64 | 40 | 0 | 5 | 480 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 785 | 11 | 0 | 0 | 215 | 260 | 0 | 5 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 6 | 0 | 74 | 0 | 33 | 0 | 0 | 0 | 212 | 36 | 0 | 0 | 4 | 5 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 0 | 65 | 66 | 0 | 15.81 | 0 | 3774.95 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 775 | 0 | 0 | 0 | 968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.37 | 35 | 0 | 0 | 9.78 | 0 | 0 | 157 | 0 | 0 | 0 | 220 | 0 | 0.86 | 0 | 54 | 0 | 13 | 0 | 0 | 0 | 0 | 2.4 | 72 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 700 | 0 | 4020.41 | 7795.36 | 98.2
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 250 | 0 | 0 | 5 | 0 | 14.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 40 | 0 | 5 | 480 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 708 | 6 | 0 | 0 | 230 | 260 | 0 | 5 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 6 | 0 | 68 | 0 | 14 | 0 | 0 | 0 | 212 | 36 | 0 | 0 | 1 | 5 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 0 | 68 | 67 | 0 | 7.77 | 0 | 3706.01 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 798 | 0 | 0 | 0 | 937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.31 | 18 | 0 | 0 | 4.14 | 0 | 0 | 174 | 0 | 0 | 0 | 230 | 0 | 0.35 | 0 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 30 | 0.01 | 0 | 0 | 100 | 180 | 0 | 256 | 610 | 0 | 3847.81 | 7553.82 | 98.2
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 40 | 0 | 5 | 515 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 890 | 0 | 0 | 0 | 230 | 260 | 0 | 5 | 0 | 186 | 0 | 0 | 50 | 0 | 0 | 6 | 0 | 78 | 0 | 1 | 0 | 0 | 0 | 212 | 36 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | 0 | 0 | 160 | 0 | 5 | 68 | 67 | 0 | 0.76 | 0 | 3967.81 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 829 | 0 | 0 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 | 2 | 0 | 0 | 0.32 | 0 | 0 | 173 | 0 | 0 | 0 | 230 | 0 | 0.05 | 0 | 53 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 2 | 0 | 0 | 0 | 100 | 180 | 0 | 350 | 710 | 0 | 3974.44 | 7942.25 | 98.2
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 11.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 519 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 230 | 260 | 0 | 20 | 0 | 200 | 0 | 0 | 110 | 0 | 0 | 6 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 18 | 68 | 70 | 0 | 0 | 0 | 4549.5 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958 | 0 | 0 | 0 | 1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 400 | 895 | 0 | 4744 | 9293.5 | 98.2
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 517 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1159 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 193 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 18 | 25 | 73 | 0 | 0 | 0 | 4596 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 340 | 925 | 0 | 4791 | 9387 | 98.19
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1159 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 193 | 0 | 0 | 110 | 0 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 18 | 25 | 72 | 0 | 0 | 0 | 4385 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 391 | 860 | 0 | 4870 | 9255
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1158 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 189 | 0 | 0 | 110 | 0 | 0 | 19 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 18 | 25 | 70 | 0 | 0 | 0 | 4390 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 0 | 0 | 1273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 450 | 860 | 0 | 5057 | 9447 | 98.19
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1149 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 189 | 0 | 0 | 111 | 0 | 0 | 20 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 18 | 25 | 70 | 0 | 0 | 0 | 4372 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 450 | 880 | 0 | 5055 | 9427 | 98.19
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1147 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 194 | 0 | 0 | 112 | 0 | 0 | 20 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 21 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 18 | 16 | 71 | 0 | 0 | 0 | 4336 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 0 | 0 | 0 | 1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 281 | 940 | 0 | 4763 | 9099 | 98.19
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 188 | 0 | 0 | 111 | 0 | 0 | 20 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 18 | 0 | 72 | 0 | 0 | 0 | 4149 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912 | 0 | 0 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 180 | 0 | 250 | 920 | 0 | 4361 | 8510 | 98.18
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8200800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8608636 | 0 | 0 | 5870857 | 0 | 0 | 76492 | 0 | 286200 | 433440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17641 | 656000 | 0 | 569280 | 13912727.27 | 0 | 0 | 0 | 0 | 0 | 4131522 | 0 | 0 | 0 | 20678180 | 98280 | 0 | 0 | 5730000 | 7306900 | 0 | 621424 | 0 | 4331000 | 0 | 0 | 2022480 | 0 | 0 | 271410 | 0 | 1760640 | 0 | 268473 | 0 | 0 | 0 | 5153000 | 834000 | 117420 | 0 | 42150 | 248112 | 0 | 963840 | 578304 | 0 | 0 | 3704510 | 0 | 122400 | 633600 | 1540800 | 2650 | 71000 | 0 | 99864168.27 | 9766545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408240 | 20800000 | 0 | 0 | 0 | 23068153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203868 | 432030 | 0 | 0 | 60752 | 0 | 0 | 4377591 | 0 | 0 | 0 | 7433600 | 0 | 5520 | 0 | 1234472 | 0 | 80561 | 0 | 0 | 0 | 0 | 26809.68 | 336960 | 1026 | 0 | 0 | 2905000 | 5076505 | 0 | 7352727.27 | 17712000 | 0 | 101282359.95 | 201146528.22

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9293.14 | MW | 12:00 Hr. | Energy Generated |  |  | 201.1465 |  | MKWHr.
| Day Peak Demand |  |  | 9293.14 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9447 | MW | 20:00 Hr. | Energy Demand |  |  | 201.1465 |  | MKWHr.
| Evening Peak Demand |  |  | 9447 | MW | 20:00 Hr. | Maximum Temperature |  |  | 20.8 |  | °C
| Minimum Generation of the Day |  |  | 6792.74 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 562.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 10207.49 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.4195 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.3999 | 0 | 0 | 0 | 0 | 0.076492 | 0 | 0 | 23.4764 | Gas | 81.3166 | Gas | 282257822.7
| Chattogram Zone |  |  | 4.7008 | 34.5909 | 0 | 0 | 0.656 | 0.11592 | 0 | 0 | 40.0636 | Coal | 81.6901 | Coal | 545049495.1356
| Cumilla Zone |  |  | 20.2832 | 0 | 0 | 0 | 0 | 0.26847 | 1.7606 | 0 | 22.3123 | HFO | 0.756 | HFO | 14256432
| Mymensingh Zone |  |  | 1.5408 | 0 | 0.756 | 0 | 0 | 0.07365 | 0 | 0 | 2.3704 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 11.5992 | 0 | 0 | 0 | 0 | 0.04215 | 0 | 0 | 11.6413 | Hydro | 0.656 | Hydro | 65600
| Khulna Zone |  |  | 0 | 20.8 | 0 | 0 | 0 | 0.40824 | 9.7665 | 0 | 30.9748 | Solar | 2.1325 | Solar | 32625713.076
| Barishal Zone |  |  | 7.9815 | 25.0647 | 0 | 0 | 0 | 0.001026 | 0 | 0 | 33.0473 | Import | 34.5953 | Import | 215855292.72
| Rajshahi Zone |  |  | 11.8112 | 0 | 0 | 0 | 0 | 0.70217 | 23.0682 | 0 | 35.5815 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 1.2345 | 0 | 0 | 0 | 0.44433 | 0 | 0 | 1.6788
| Total |  |  | 81.3166 | 81.6901 | 0.756 | 0 | 0.656 | 2.1325 | 34.5953 | 0 | 201.1465
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 282257822.7 |  | Hydro | 65600
|  |  |  | Coal | 545049495.1356 |  | Solar | 32625713.076
|  |  |  | HFO | 14256432 |  | Import | 215855292.72
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 109,01,10,355 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 9.7665 | Peak Hr Flow | 422.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34001654.55 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.0682 | Peak Hr Flow | 1273.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1924 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7606 | Peak Hr Flow | 76.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2219 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 34.5953 | Peak Hr Flow | 1771.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3051
|  |  |  | Chattogram |  | 0 |  | 1029
|  |  |  | Cumilla |  | 0 |  | 857
|  |  |  | Mymensingh |  | 0 |  | 782
|  |  |  | Sylhet |  | 0 |  | 374
|  |  |  | Khulna |  | 0 |  | 1115
|  |  |  | Barishal |  | 0 |  | 301
|  |  |  | Rajshahi |  | 0 |  | 891
|  |  |  | Rangpur |  | 0 |  | 639
|  |  |  | Total |  | 0 |  | 9039
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Baghabari 100 MW GTPP |  |  | 100 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 730
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 17:05 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Project Work S/D from Rangpur 132/33kV end
Due to Re-Conducting
| 08:21 | 16:01 | Rajbari 132/33kV S/S Faridpur -1 Scheduled S/D Due to For annual maintenance.
| 08:23 | 16:00 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-1 Scheduled S/D Due to Annual maintenance
| 08:29 | 18:13 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Due to roads and highway braidge installation work.
| 08:31 | 09:59 | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Rampura 230/132kV end Due to Bhulta-04
(230 kV) line was shut down for removal of an unwanted rope from Tower No. 40–41. and
from Bhulta 400/230kVend.
| 08:38 | 18:19 | Maniknagar-Narinda 132kV Ckt-1 Scheduled S/D from Maniknagar 132/33kV end Due to Annual
Maintenance
| 08:52 |  | Ashuganj-Ghorasal 132kV Ckt-2 Project Work S/D from Ashuganj 230/132/33kV end.
| 09:43 |  | Kishoreganj-Mymensingh 132kV Ckt-2 Project Work S/D from Kishoreganj 132/33kV end.
| 09:50 | 10:17 | Kodda 132/33kV S/S Tr-1 (406T) LT Tripped showing Over current relay relays Due to Due to | [7 empty] | 75.0MW load
|  |  | 33kV L-19 feeder triping | [7 empty] | interrup.
| 09:50 | 10:17 | Kodda 132/33kV S/S Tr-3 (426T) LT Tripped showing Over current realy relays Due to Due to | [7 empty] | 75.0MW load
|  |  | 33kV L-19 feeder triping | [7 empty] | interrup.
| 09:50 | 10:17 | Kodda 132/33kV S/S Tr-5 (446T) LT Tripped showing Over current relay relays Due to Due to | [7 empty] | 75.0MW load
|  |  | 33kV L-19 feeder triping | [7 empty] | interrup.
| 09:58 |  | Kishoreganj-Mymensingh 132kV Ckt-2 Project Work S/D from Mymensingh 132/33kV end Due to
Project Work
| 10:13 |  | 400kV reactor of Adani- Rahanpur 400kV ckt-2 was openned.
|  | 10:27 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
|  | 10:27 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
|  | 10:38 | Sonargaon 132/33kV S/S Tr-2 HT is restored.
|  | 10:40 | Sonargaon 132/33kV S/S Tr-2 LT is restored.
|  | 10:41 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT is restored.
|  | 10:42 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT is restored.
| 11:10 |  | Baropukuria PS 230Kv Bus-1 S/D[Busbar Stability Test, EEGBPS Project]
|  | 11:10 | Jaldhaka 132/33kV S/S 406T-1 LT is restored.
|  | 11:10 | Jaldhaka 132/33kV S/S 406T-1 HT is restored.
| 11:13 | 12:09 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to Due to Auxiliary Transformer fuse Cut | [7 empty] | 35.0MW load
|  |  | and loop Y,B phase attached. | [7 empty] | interrup.
| 11:14 | 12:08 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to Due to Auxiliary Transformer fuse Cut | [7 empty] | 35.0MW load
|  |  | and loop Y,B phase attached. | [7 empty] | interrup.
| 12:00 |  | Day Peak Generation: 9293 MW.
| 12:16 | 15:19 | Haripur 230/132kV S/S 132kV Main Bus Sec-2 Tripped showing O/C & E/F relays.
| 12:16 | 15:19 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-2 Tripped showing O/C & E/F relays.
|  | 12:20 | Natore 132/33kV S/S 132 KV MAIN BUS is restored.
|  | 12:20 | Bogura-Natore 132 kV Ckt-2 is restored.
|  | 12:20 | Bogura-Natore 132 kV Ckt-2 is restored.
|  | 12:20 | Bogura-Natore 132 kV Ckt-1 is restored.
|  | 12:22 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
|  | 12:23 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
|  | 12:25 | Natore-Rajshahi 132kV Ckt-1 is restored.
|  | 12:26 | Natore-Rajshahi 132kV Ckt-2 is restored.
|  | 12:27 | Ishwardi-Natore 132kV Ckt-1 is restored.
|  | 12:27 | Ishwardi-Natore 132kV Ckt-1 is restored.
|  | 12:28 | Ishwardi-Natore 132kV Ckt-2 is restored.
|  | 12:30 | Natore 132/33kV S/S TR-4 (435 T) HT is restored.
|  | 12:31 | Natore 132/33kV S/S TR-3 (425 T) HT is restored.
|  | 12:31 | Natore 132/33kV S/S TR-3 (425 T) LT is restored.
|  | 12:31 | Natore 132/33kV S/S TR-4 (435 T) LT is restored.
|  | 12:34 | Natore 132/33kV S/S Rajlanka is restored.
|  | 12:34 | Natore 132/33kV S/S Rajlanka is restored.
|  | 12:36 | Natore 132/33kV S/S TR-2 (415 T) HT is restored.
|  | 12:37 | Natore 132/33kV S/S TR-2 (415 T) LT is restored.
|  | 14:01 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
| 15:20 | 16:27 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to PBS Side 33kV Red Hot | [7 empty] | 12.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 15:24 | 16:25 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to PBS 33kV Red Hot | [7 empty] | 12.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 15:26 | 15:30 | Barishal 230/132kV S/S T-5 HT Tripped showing Differtial -2, REF relays Due to Differtial
trip due to Mehendigang 33kv feeder trip
| 15:26 |  | Barishal 230/132kV S/S T-5 LT Tripped showing Lockout relays Due to Trip due to
Mehendigang 33kv feeder trip
| 15:31 | 19:46 | Barishal 230/132kV S/S T-5 HT Forced S/D Due to For checking due to diferential trip
| 15:33 |  | Baropukuria-Purbasadipur 230 KV ckt-2 S/D.
|  | 17:03 | BIPTC S/S Block-01, Trafo-02 HT is restored.
| 17:15 |  | Baropukuria-Purbasadipur 230 KV ckt-2 charge from Purbasadipur end .
| 18:26 |  | Baropukuria PS 230Kv Bus-1 Syn.
| 20:00 |  | Evening Peak generation: 9447 MW
| 04:26 |  | Bhulta-Haripur 230 kV Ckt-1 Forced S/D from Haripur 230/132kV end.
| 06:07 | 06:20 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Tripped showing Lockout Relay K861 Trip, | [7 empty] | 12.0MW load
|  |  | Lockout Relay K862 Trip, 33KV (SIEMENS) Relay, 132KV (SIEMENS) Relay, relays Due to | [7 empty] | interrup.
Patiya 33kv Feeder
| 06:30 |  | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to P/W | [7 empty] | 4.0MW load
interrup.
| 06:31 |  | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to P/W | [7 empty] | 4.0MW load
interrup.
| 06:33 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- ST
| 06:42 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- GT
| 06:42 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown
| 07:03 |  | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Project Work S/D from Rangpur 132/33kV
end.
| 07:23 |  | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to Annual Maintenance
| 07:24 |  | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to Annual Maintenance
| 07:45 |  | Jaldhaka 132/33kV S/S 406T-1 LT Scheduled S/D Due to Purpose of switching: 132/33kV Tr-1 | [7 empty] | 14.0MW load
|  |  | Shutdown due to new 33kV Feeder(Nilphamari PBS) connection on 33kV Bus section-1. | [7 empty] | interrup.
| 07:46 |  | Jaldhaka 132/33kV S/S 406T-1 HT Scheduled S/D Due to Purpose of switching: 132/33kV Tr-1 | [7 empty] | 14.0MW load
|  |  | Shutdown due to new 33kV Feeder(Nilphamari PBS) connection on 33kV Bus section-1. | [7 empty] | interrup.
| 07:58 |  | Naogaon-Niyamatpur 132kV Ckt-1 Forced S/D from Niamatpur 132/33kV end Due to Guidance of
ALDC
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Grid fault
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 8200800 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 5870857 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8 | 286200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 433440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 76492 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 415 | 8608636 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1050 | 23476425
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 98280 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 656000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 4131522 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 38 | 569280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1158 | 20678180 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 515 | 13912727.27 | -
Chattogram Area Total |  |  |  |  | 4895.723 | 1751 | 40063630.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 189 | 4331000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 260 | 7306900 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 5730000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 621424 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 110 | 2022480 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1760640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 271410 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 268473 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 935 | 22312327
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 70 | 1540800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 2650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 25 | 633600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 18 | 122400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 71000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 113 | 2370450
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 42150 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 35 | 834000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 117420 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 578304 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 963840 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3704510 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 248112 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 212 | 5153000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 541 | 11641336
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 422 | 9766545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 408240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1101 | 20800000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1523 | 30974785
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 450 | 7352727.27 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2905000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 860 | 17712000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5076505 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | Plant is on standby as per NLDC instruction
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1026 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1670 | 33047258.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 203868 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 179 | 4377591 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 358 | 7433600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 5520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1273 | 23068153 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 60752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 432030 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1810 | 35581514
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1234472 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 26809.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 80561 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 336960 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 54 | 1678802.68
Eastern Grid Total |  |  |  |  | 17395.105 | 4390 | 99864168.27
Western Grid Total |  |  |  |  | 10984.003 | 5057 | 101282359.95
National Grid Total |  |  |  |  | 28379.108 | 9447 | 201146528.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-12-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6093.37 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 2946 | MW
i) Dhaka area |  |  | 3051.37 |  | MW | i) Khulna area |  |  |  | 1115 | MW
ii) Chattogram area |  |  | 1029 |  | MW | ii) Barishal area |  |  |  | 300.8 | MW
iii) Cumilla area |  |  | 857 |  | MW | iii) Rajshahi area |  |  |  | 891.2 | MW
iv) Mymensingh area |  |  | 782 |  | MW | iv) Rangpur area |  |  |  | 639 | MW
v) Sylhet area |  |  | 374 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9039.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 64 | 13:00 | 133 | Netrakona | 106 | 18:00
2 | AKSML | 98 | 10:00 | 68 | Hathazari | 64 | 13:00 | 134 | New | 52 | 12:00
3 | Aftabnagar | 26 | 13:00 | 69 | Hatirjheel | 24 | 18:00 | 135 | Niamatpur | 50 | 08:00
4 | Agargaon | 80 | 13:00 | 70 | Ishurdi | 44 | 19:30 | 136 | Noapara | 30 | 18:00
5 | Agrabad | 36 | 18:30 | 71 | Jaldhaka | 50 | 18:00 | 137 | PHP | 7 | 01:00
6 | Amnura | 23 | 09:00 | 72 | Jamalpur | 89 | 18:30 | 138 | Pabna | 62 | 18:00
7 | Ashuganj | 56 | 13:00 | 73 | Jashore | 116 | 13:00 | 139 | Palashbari | 72 | 18:00
8 | BSRM | 195 | 02:00 | 74 | Jhenaidah | 91 | 18:00 | 140 | Panchagarh | 45 | 18:30
9 | Bagerhat | 60 | 18:00 | 75 | Joydebpur | 79 | 13:00 | 141 | Patiya | 6 | 18:00
10 | Bajitpur | 59 | 18:00 | 76 | Joypurhat | 41 | 18:00 | 142 | Patuakhali | 41 | 21:00
11 | Bakerganj | 0 | 10:00 | 77 | Juldah | 13.5 | 01:00 | 143 | Payra | 22 | 18:00
12 | Bakulia | 50 | 13:00 | 78 | KSRM | 10 | 07:00 | 144 | Postogola | 33 | 14:00
13 | Banani | 14.2 | 12:00 | 79 | Kabirpur | 140 | 13:00 | 145 | Purbachal | 19 | 13:00
14 | Bangabhaban | 4 | 12:00 | 80 | Kachua | 57 | 13:00 | 146 | Purbasadipur | 111 | 12:00
15 | Barapukuria | 46 | 13:00 | 81 | Kallyanpur | 75 | 13:00 | 147 | Rahanpur | 22 | 11:00
16 | Barguna | 14 | 19:30 | 82 | Kalurghat | 18 | 00:00 | 148 | Rahim | 26 | 15:00
17 | Barishal | 80 | 13:00 | 83 | Kamrangirchar | 43 | 00:00 | 149 | Rajbari | 54 | 18:00
18 | Barishal-230 | 66 | 13:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 105 | 13:00
19 | Baroaulia | 47 | 17:00 | 85 | Kasba | 26 | 13:00 | 151 | Rajshahi | 79 | 13:00
20 | Baroirhat | 55 | 13:00 | 86 | Kazla | 74 | 01:00 | 152 | Rajshahi-230 | 60 | 13:00
21 | Bashundhara | 122 | 13:00 | 87 | Keranigonj | 44 | 13:00 | 153 | Ramganj | 88 | 13:00
22 | BashundharaCement | 7 | 00:00 | 88 | Khagrachori | 22 | 13:00 | 154 | Rampur | 25 | 13:00
23 | Beanibazar | 46 | 13:00 | 89 | Khulna | 49 | 13:00 | 155 | Rangamati | 12 | 17:00
24 | Benapole | 40 | 13:00 | 90 | Khulshi | 149 | 20:00 | 156 | Rangpur | 96 | 13:00
25 | Bhaluka | 103 | 13:00 | 91 | Kishoreganj | 94 | 12:00 | 157 | Ruppur | 2.2 | 08:00
26 | Bhandaria | 35 | 20:00 | 92 | Kodda | 177 | 12:00 | 158 | SSM | 0 | 00:00
27 | Bhangura | 23 | 18:00 | 93 | Kulaura | 32 | 13:00 | 159 | Saidpur | 79 | 10:00
28 | Bheramara(GK) | 39 | 18:00 | 94 | Kurigram | 46 | 18:00 | 160 | Satkhira | 89 | 18:00
29 | Bhulta | 172 | 23:00 | 95 | Kushtia | 98 | 13:00 | 161 | Satmasjid | 67 | 13:00
30 | Bog-Sherpur | 50 | 18:00 | 96 | Laksam | 23 | 12:00 | 162 | Savar | 116 | 12:00
31 | Bogura | 102 | 19:30 | 97 | Lakshmipur | 23 | 19:30 | 163 | SevenRings | 15.21 | 00:00
32 | Borhanuddin | 66 | 13:00 | 98 | Lalbag | 47 | 00:00 | 164 | ShahCement | 36 | 02:00
33 | Brahmanbaria | 84 | 18:00 | 99 | Lalmonirhat | 42 | 18:30 | 165 | Shahjadpur | 45 | 18:00
34 | Cantonment | 80 | 12:00 | 100 | MI_Cement | 15.8 | 00:00 | 166 | Shahjibazar | 73 | 21:00
35 | Chandina | 11 | 13:00 | 101 | Madanganj | 39 | 13:00 | 167 | Shahmirpur | 29 | 00:00
36 | Chandpur | 56 | 13:00 | 102 | Madaripur | 73 | 13:00 | 168 | Shariatpur | 60 | 13:00
37 | Chandraghona | 25 | 18:00 | 103 | Madartek | 59 | 13:00 | 169 | Sherpur | 108 | 18:00
38 | Chapai | 51 | 08:00 | 104 | Madunaghat | 33 | 13:00 | 170 | Shikalbaha | 21.5 | 13:00
39 | Charsaidpur | 42 | 19:00 | 105 | Magura | 44 | 13:00 | 171 | Shitalakhya | 40.5 | 13:00
40 | Chauddagram | 56 | 13:00 | 106 | Mahasthangarh | 44 | 18:00 | 172 | Sholosohor | 25 | 12:00
41 | Chhatak | 23 | 13:00 | 107 | Maijdee | 28 | 20:00 | 173 | Shyampur | 124 | 02:00
42 | Chowmuhani | 119 | 13:00 | 108 | Manikganj | 82 | 19:30 | 174 | Siddhirganj | 71 | 12:00
43 | Chuadanga | 73 | 13:00 | 109 | Maniknagar | 46 | 13:00 | 175 | Sirajganj | 60 | 18:30
44 | Coxsbazar | 93 | 13:00 | 110 | Matarbari | 35 | 18:00 | 176 | Sonargaon | 111 | 01:00
45 | Cumilla(N) | 94 | 13:00 | 111 | Matuail | 34 | 00:00 | 177 | Sreemongol | 50 | 18:00
46 | Cumilla(S) | 107 | 13:00 | 112 | Metrorail_Motijheel | 12 | 18:00 | 178 | Sreepur | 69 | 00:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 5 | 19:30 | 179 | Srinagar | 33.8 | 13:00
48 | Daudkandi | 94 | 20:00 | 114 | Millgate | 56 | 11:00 | 180 | Sunamganj | 38 | 19:00
49 | DhakaUniversity | 26 | 12:00 | 115 | Mirpur | 99 | 13:00 | 181 | Sylhet | 38 | 13:00
50 | Dhamrai | 74 | 12:00 | 116 | Mirsorai | 41 | 13:00 | 182 | Sylhet-132 | 73 | 13:00
51 | Dhanmondi | 66 | 13:00 | 117 | Mirzapur | 34 | 13:00 | 183 | TK | 16 | 13:00
52 | Dohazari | 68 | 13:00 | 118 | Mithapukur | 44 | 09:00 | 184 | Tangail | 114 | 12:00
53 | Faridpur | 97 | 19:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 27 | 10:00
54 | Fatullah | 77 | 00:00 | 120 | Mogbazar | 50 | 11:00 | 186 | Tasnim | 24 | 08:00
55 | Fenchuganj | 25 | 13:00 | 121 | Mongla | 24 | 18:00 | 187 | Thakurgaon | 76 | 18:00
56 | Feni | 75 | 13:00 | 122 | Motijheel | 24 | 13:00 | 188 | Tongi | 76 | 13:00
57 | GPH | 83 | 04:00 | 123 | Muktagacha | 31 | 13:00 | 189 | Ullahpara | 22 | 18:00
58 | Ghatail | 58 | 18:00 | 124 | Munshiganj | 80 | 13:00 | 190 | Ullon | 53 | 13:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 24 | 13:00 | 191 | Uttara | 55 | 13:00
60 | Ghorashal-230 | 71 | 10:00 | 126 | Mymensingh | 154 | 13:00 | 192 | UttaraNew | 42 | 13:00
61 | Goalpara | 24 | 12:00 | 127 | Naogaon | 80 | 18:00 | 193 | Zigatola | 70 | 13:00
62 | Gollamari | 72 | 13:00 | 128 | Narail | 38 | 13:00
63 | Gopalganj | 75 | 18:30 | 129 | Narinda | 40 | 13:00
64 | Gulshan | 56 | 13:00 | 130 | Narshingdi | 126 | 19:30
65 | Halishahar | 26 | 18:00 | 131 | Natore | 96 | 18:00
66 | HaripurSBU | 81 | 01:00 | 132 | Nawabganj | 43.8 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8608.06 | 0 |  | 8608.06
1:00 | 8121.1 | 0 |  | 8121.1
2:00 | 7506.68 | 0 |  | 7506.68
3:00 | 7095.33 | 0 |  | 7095.33
4:00 | 6792.74 | 0 |  | 6792.74
5:00 | 6796.54 | 0 |  | 6796.54
6:00 | 6982.81 | 0 |  | 6982.81
7:00 | 7027.89 | 0 |  | 7027.89
8:00 | 7814.35 | 0 |  | 7814.35
9:00 | 8254.4 | 0 |  | 8254.4
10:00 | 8329.9 | 0 |  | 8329.9
11:00 | 8589.19 | 0 |  | 8589.19
12:00 | 9293.14 | 0 |  | 9293.14
13:00 | 10207.49 | 0 |  | 10207.49
14:00 | 8624.85 | 0 |  | 8624.85
15:00 | 7795.36 | 0 |  | 7795.36
16:00 | 7553.82 | 0 |  | 7553.82
17:00 | 7942.25 | 0 |  | 7942.25
18:00 | 9293.5 | 0 |  | 9293.5
19:00 | 9387 | 0 |  | 9387
19:30 | 9255 | 0 |  | 9255
20:00 | 9447 | 0 |  | 9447
21:00 | 9427 | 0 |  | 9427
22:00 | 9099 | 0 |  | 9099
23:00 | 8510 | 0 |  | 8510
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4553.5 | 4054.56 | 8608.06 | DAILY GENERATION CURVE
00:30 | 4456 | 3908.58 | 8364.58
01:00 | 4358.5 | 3762.6 | 8121.1 | 26-12-2025
01:30 | 4085.5 | 3728.39 | 7813.89
02:00 | 3812.5 | 3694.18 | 7506.68
02:30 | 3685.25 | 3615.755 | 7301.005
03:00 | 3558 | 3537.33 | 7095.33
03:30 | 3500 | 3444.035 | 6944.035
04:00 | 3442 | 3350.74 | 6792.74
04:30 | 3419 | 3375.64 | 6794.64
05:00 | 3396 | 3400.54 | 6796.54
05:30 | 3447 | 3442.675 | 6889.675
06:00 | 3498 | 3484.81 | 6982.81
06:30 | 3517.035 | 3488.315 | 7005.35
07:00 | 3536.07 | 3491.82 | 7027.89
07:30 | 3800.22 | 3620.9 | 7421.12
08:00 | 4064.37 | 3749.98 | 7814.35
08:30 | 4178.81 | 3855.565 | 8034.375
09:00 | 4293.25 | 3961.15 | 8254.4
09:30 | 4339.625 | 3952.525 | 8292.15
10:00 | 4386 | 3943.9 | 8329.9
10:30 | 4461 | 3998.545 | 8459.545
11:00 | 4536 | 4053.19 | 8589.19
11:30 | 4638.5 | 4302.665 | 8941.165
12:00 | 4741 | 4552.14 | 9293.14
12:30 | 4821 | 4929.315 | 9750.315
13:00 | 4901 | 5306.49 | 10207.49
13:30 | 4456.27 | 4959.9 | 9416.17
14:00 | 4011.54 | 4613.31 | 8624.85
14:30 | 3893.245 | 4316.86 | 8210.105
15:00 | 3774.95 | 4020.41 | 7795.36
15:30 | 3740.48 | 3934.11 | 7674.59
16:00 | 3706.01 | 3847.81 | 7553.82
16:30 | 3836.91 | 3911.125 | 7748.035
17:00 | 3967.81 | 3974.44 | 7942.25
17:30 | 4258.655 | 4359.22 | 8617.875
18:00 | 4549.5 | 4744 | 9293.5
18:30 | 4572.75 | 4767.5 | 9340.25
19:00 | 4596 | 4791 | 9387
19:30 | 4385 | 4870 | 9255
20:00 | 4390 | 5057 | 9447
20:30 | 4381 | 5056 | 9437 |  | Executive Engineer
21:00 | 4372 | 5055 | 9427 |  | Network Operation Division
21:30 | 4354 | 4909 | 9263
22:00 | 4336 | 4763 | 9099
22:30 | 4242.5 | 4562 | 8804.5
23:00 | 4149 | 4361 | 8510

## En-Curve
QF-LDC-12
Date | 26-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2843 | 825.5 | 433 | 0 | 76 | 870.56 | 40 | 3520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2835.5 | 758 | 433 | 0 | 74 | 851.08 | 40 | 3373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26-12-2025
01:00 | 2828 | 690.5 | 433 | 0 | 72 | 831.6 | 40 | 3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2744.5 | 611 | 433 | 0 | 73 | 833.89 | 40 | 3078.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 201.1465 |  | MKWHr
02:00 | 2661 | 531.5 | 433 | 0 | 74 | 836.18 | 40 | 2931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2519.5 | 524.75 | 433 | 0 | 73 | 846.755 | 40 | 2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 201.1465 |  | MKWHr
03:00 | 2378 | 518 | 433 | 0 | 72 | 857.33 | 40 | 2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2369 | 507 | 362.5 | 0 | 68 | 845.035 | 20 | 2772.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2360 | 496 | 292 | 0 | 64 | 832.74 | 0 | 2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2362.5 | 505.5 | 291.5 | 0 | 61 | 832.14 | 0 | 2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2365 | 515 | 291 | 0 | 58 | 831.54 | 0 | 2736 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2438.5 | 527.5 | 291 | 0 | 60 | 836.175 | 0 | 2736.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2512 | 540 | 291 | 0 | 62 | 840.81 | 0 | 2737 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2531 | 540.5 | 291 | 0 | 64 | 835.6 | 0 | 2741.5 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0
07:00 | 2550 | 541 | 291 | 0 | 66 | 830.39 | 0 | 2746 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 2695.5 | 624.5 | 362 | 0 | 65 | 830.52 | 0 | 2815 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0
08:00 | 2841 | 708 | 433 | 0 | 64 | 830.65 | 0 | 2884 | 53.7 | 0 | 0 | 0 | 0 | 0 | 0
08:30 | 2912 | 739 | 433 | 0 | 70 | 827.655 | 0 | 2956 | 90.72 | 0 | 6 | 0 | 0 | 0 | 0
09:00 | 2983 | 770 | 433 | 0 | 76 | 824.66 | 0 | 3028 | 127.74 | 0 | 12 | 0 | 0 | 0 | 0
09:30 | 2941 | 764.5 | 433 | 0 | 76 | 825.125 | 0 | 3057 | 172.025 | 0 | 23.5 | 0 | 0 | 0 | 0
10:00 | 2899 | 759 | 433 | 0 | 76 | 825.59 | 0 | 3086 | 216.31 | 0 | 35 | 0 | 0 | 0 | 0
10:30 | 2881 | 781 | 433 | 0 | 73 | 842.89 | 20 | 3146 | 247.655 | 0 | 35 | 0 | 0 | 0 | 0
11:00 | 2863 | 803 | 433 | 0 | 70 | 860.19 | 40 | 3206 | 279 | 0 | 35 | 0 | 0 | 0 | 0
11:30 | 2834.5 | 834 | 433.5 | 0 | 77 | 941.665 | 40 | 3432 | 313.5 | 0 | 35 | 0 | 0 | 0 | 0
12:00 | 2806 | 865 | 434 | 0 | 84 | 1023.14 | 40 | 3658 | 348 | 0 | 35 | 0 | 0 | 0 | 0
12:30 | 2804 | 869 | 428 | 0 | 97 | 1153.315 | 40 | 3954 | 355.5 | 0 | 49.5 | 0 | 0 | 0 | 0
13:00 | 2802 | 873 | 422 | 0 | 110 | 1283.49 | 40 | 4250 | 363 | 0 | 64 | 0 | 0 | 0 | 0
13:30 | 2604 | 708.5 | 422 | 0 | 98 | 1242.745 | 40 | 3889.5 | 346.925 | 0 | 64.5 | 0 | 0 | 0 | 0
14:00 | 2406 | 544 | 422 | 0 | 86 | 1202 | 40 | 3529 | 330.85 | 0 | 65 | 0 | 0 | 0 | 0
14:30 | 2400.5 | 529.75 | 422 | 0 | 80 | 1085 | 40 | 3286.5 | 301.355 | 0 | 65 | 0 | 0 | 0 | 0
15:00 | 2395 | 515.5 | 422 | 0 | 74 | 968 | 40 | 3044 | 271.86 | 0 | 65 | 0 | 0 | 0 | 0
15:30 | 2440.5 | 510.5 | 422 | 0 | 71 | 952.5 | 40 | 2975 | 196.59 | 0 | 66.5 | 0 | 0 | 0 | 0
16:00 | 2486 | 505.5 | 422 | 0 | 68 | 937 | 40 | 2906 | 121.32 | 0 | 68 | 0 | 0 | 0 | 0
16:30 | 2495.5 | 526.25 | 422 | 0 | 73 | 928 | 40 | 3126.5 | 66.285 | 0 | 70.5 | 0 | 0 | 0 | 0
17:00 | 2505 | 547 | 422 | 0 | 78 | 919 | 40 | 3347 | 11.25 | 0 | 73 | 0 | 0 | 0 | 0
17:30 | 2656 | 669.25 | 422 | 0 | 81 | 1023 | 40 | 3641.5 | 5.625 | 0 | 79.5 | 0 | 0 | 0 | 0
18:00 | 2807 | 791.5 | 422 | 0 | 84 | 1127 | 40 | 3936 | 0 | 0 | 86 | 0 | 0 | 0 | 0
18:30 | 2788 | 825.25 | 422 | 0 | 83 | 1128.5 | 40 | 3989 | 0 | 0 | 64.5 | 0 | 0 | 0 | 0
19:00 | 2769 | 859 | 422 | 0 | 82 | 1130 | 40 | 4042 | 0 | 0 | 43 | 0 | 0 | 0 | 0
19:30 | 2568 | 871 | 422 | 0 | 80 | 1175 | 40 | 4056 | 0 | 0 | 43 | 0 | 0 | 0 | 0
20:00 | 2578 | 877 | 422 | 0 | 76 | 1273 | 40 | 4138 | 0 | 0 | 43 | 0 | 0 | 0 | 0
20:30 | 2561 | 876 | 422 | 0 | 77 | 1269 | 40 | 4149 | 0 | 0 | 43 | 0 | 0 | 0 | 0
21:00 | 2544 | 875 | 422 | 0 | 78 | 1265 | 40 | 4160 | 0 | 0 | 43 | 0 | 0 | 0 | 0
21:30 | 2521 | 868.5 | 422 | 0 | 76 | 1220 | 40 | 4077 | 0 | 0 | 38.5 | 0 | 0 | 0 | 0
22:00 | 2498 | 862 | 422 | 0 | 74 | 1175 | 40 | 3994 | 0 | 0 | 34 | 0 | 0 | 0 | 0
22:30 | 2487 | 817.5 | 422 | 0 | 72 | 1098 | 40 | 3842 | 0 | 0 | 26 | 0 | 0 | 0 | 0
23:00 | 2476 | 773 | 422 | 0 | 70 | 1021 | 40 | 3690 | 0 | 0 | 18 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 415 | 05:00 | 401 | 13:00 | Meghnaghat | 416 | 05:00 | 398 | 13:00
Ashuganj | 422 | 5:00 | 401 | 13:00 | Payra | 419 | 02:00 | 414 | 18:00
Bhulta | 419 | 05:00 | 398 | 12:00 | Rahanpur | 420 | 05:00 | 403 | 13:00
Bibiana | 408 | 05:00 | 393 | 13:00 | Rampal | 417 | 05:00 | 400 | 13:00
BIPTC | 407 | 04:00 | 391 | 11:00
Bogura | 417 | 05:00 | 392 | 13:00
Gopalganj | 418 | 05:00 | 400 | 13:00
Kaliakoir | 408 | 05:00 | 386 | 13:00
Korerhat | 416 | 05:00 | 401 | 13:00
Madunaghat | 411 | 05:00 | 403 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 05:00 | 232 | 13:00 | Kachua | 241 | 04:00 | 232 | 12:00
AKSML | 238 | 03:00 | 231 | 12:00 | Kaliakoir | 246 | 05:00 | 232 | 12:00
Aminbazar | 243 | 05:00 | 232 | 13:00 | Keranigonj | 244 | 05:00 | 230 | 13:00
Ashuganj | 242 | 04:00 | 231 | 13:00 | Khulna(S) | 244 | 05:00 | 230 | 13:00
Ashuganj-400 | 242 | 04:00 | 231 | 13:00 | Korerhat | 242 | 05:00 | 232 | 13:00
Baghabari | 240 | 03:00 | 232 | 12:00 | Madunaghat | 237 | 05:00 | 231 | 13:00
Barapukuria | 230 | 05:00 | 215 | 13:00 | Madunaghat-400 | 238 | 05:00 | 232 | 13:00
Barapukuria-230 | 230 | 05:00 | 215 | 13:00 | Maniknagar | 242 | 05:00 | 233 | 13:00
Barishal | 247 | 05:00 | 239 | 13:00 | Meghnaghat | 247 | 09:00 | 238 | 03:00
Bheramara | 239 | 05:00 | 222 | 12:00 | Meghnaghat-400 | 245 | 05:00 | 234 | 13:00
Bhulta | 246 | 05:00 | 235 | 13:00 | Mirsorai | 242 | 05:00 | 231 | 13:00
Bibiana | 242 | 05:00 | 232 | 13:00 | Rajshahi | 239 | 05:00 | 220 | 12:00
BIPTC | 240 | 05:00 | 222 | 12:00 | Rampal | 241 | 04:00 | 229 | 13:00
Bogura | 243 | 05:00 | 230 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 244 | 05:00 | 229 | 13:00 | Rampura | 245 | 06:00 | 234 | 13:00
Borhanuddin | 247 | 01:00 | 242 | 10:00 | Shikalbaha | 237 | 23:00 | 231 | 13:00
BSRM | 241 | 05:00 | 232 | 13:00 | Shyampur | 244 | 05:00 | 232 | 13:00
Cumilla(N) | 243 | 06:00 | 232 | 13:00 | Siddhirganj | 245 | 05:00 | 236 | 12:00
Faridpur | 247 | 04:00 | 237 | 13:00 | Sirajgonj | 246 | 06:00 | 237 | 13:00
Fenchuganj | 240 | 01:00 | 234 | 13:00 | Sreepur | 240 | 04:00 | 227 | 13:00
Feni | 242 | 05:00 | 232 | 13:00 | Tongi | 268 | 03:00 | 226 | 22:00
Ghorashal | 246 | 07:00 | 238 | 13:00
Ghorashal-230 | 235 | 05:00 | 216 | 12:00
Gopalganj | 247 | 05:00 | 237 | 13:00
GPH | 239 | 05:00 | 231 | 13:00
Haripur | 245 | 05:00 | 234 | 13:00
Hasnabad | 244 | 04:00 | 233 | 13:00
Hathazari | 236 | 04:00 | 231 | 19:00
Ishurdi | 241 | 05:00 | 225 | 12:00
Jhenaidah | 241 | 05:00 | 223 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 131 | 13:00 | Lakshmipur | 136 | 05:00 | 130 | 13:00
Agargaon | 141 | 05:00 | 133 | 13:00 | Lalbag | 138 | 17:00 | 131 | 08:00
Agrabad | 138 | 06:00 | 134 | 13:00 | Lalmonirhat | 133 | 15:00 | 121 | 18:00
AKS | 136 | 05:00 | 132 | 12:00 | Madanganj | 142 | 06:00 | 136 | 13:00
Aminbazar | 140 | 05:00 | 132 | 13:00 | Madaripur | 141 | 06:00 | 136 | 13:00
Amnura | 138 | 00:00 | 127 | 12:00 | Madartek | 137 | 05:00 | 131 | 12:00
Ashuganj | 143 | 03:00 | 138 | 12:00 | Madunaghat | 139 | 03:00 | 128 | 02:00
Bagerhat | 135 | 05:00 | 124 | 13:00 | Magura | 139 | 06:00 | 126 | 13:00
Bajitpur | 138 | 02:00 | 131 | 11:00 | Mahasthangarh | 138 | 05:00 | 129 | 18:00
Bakerganj | 137 | 06:00 | 135 | 11:00 | Maijdee | 137 | 05:00 | 130 | 13:00
Bakulia | 138 | 01:00 | 134 | 13:00 | Manikganj | 135 | 07:00 | 122 | 13:00
Banani | 138 | 05:00 | 131 | 13:00 | Maniknagar | 142 | 04:00 | 135 | 13:00
Bangabhaban | 142 | 04:00 | 135 | 13:00 | Matarbari | 130 | 04:00 | 122 | 13:00
Barapukuria | 138 | 04:00 | 128 | 13:00 | Matuail | 144 | 06:00 | 139 | 12:00
Barguna | 137 | 00:00 | 134 | 12:00 | Metrorail_Motijheel | 142 | 05:00 | 135 | 13:00
Barishal | 141 | 01:00 | 138 | 12:00 | Metrorail_Uttara | 140 | 01:00 | 132 | 13:00
Barishal-230 | 142 | 02:00 | 137 | 12:00 | Millgate | 139 | 04:00 | 130 | 12:00
Baroaulia | 139 | 05:00 | 134 | 13:00 | Mirpur | 141 | 05:00 | 132 | 13:00
Baroirhat | 138 | 05:00 | 132 | 13:00 | Mirzapur | 139 | 05:00 | 132 | 12:00
Bashundhara | 138 | 04:00 | 131 | 13:00 | Mithapukur | 136 | 03:00 | 126 | 18:00
BashundharaCement | 142 | 06:00 | 136 | 13:00 | MI_Cement | 140 | 03:00 | 131 | 12:00
Beanibazar | 136 | 06:00 | 132 | 13:00 | Modern | N/A | N/A | N/A | N/A
Benapole | 136 | 04:00 | 119 | 13:00 | Mogbazar | 139 | 00:00 | 133 | 13:00
Bhaluka | 136 | 03:00 | 127 | 13:00 | Mongla | 135 | 02:00 | 128 | 13:00
Bhandaria | 141 | 05:00 | 136 | 20:00 | Motijheel | 142 | 04:00 | 135 | 13:00
Bhangura | 140 | 04:00 | 133 | 18:00 | Muktagacha | 137 | 15:00 | 128 | 08:00
Bheramara | 140 | 05:00 | 129 | 18:00 | Munshiganj | 141 | 02:00 | 136 | 13:00
Bheramara(GK) | 140 | 04:00 | 129 | 18:00 | Muradnagar | 142 | 05:00 | 134 | 13:00
Bhulta | 137 | 02:00 | 131 | 12:00 | Mymensingh | 137 | 15:00 | 123 | 12:00
Bog-Sherpur | 139 | 05:00 | 132 | 12:00 | Naogaon | 135 | 04:00 | 127 | 13:00
Bogura | 138 | 04:00 | 132 | 12:00 | Narail | 139 | 05:00 | 125 | 13:00
Bogura-230 | 139 | 05:00 | 131 | 13:00 | Narinda | 142 | 04:00 | 135 | 13:00
Brahmanbaria | 136 | 01:00 | 131 | 12:00 | Narshingdi | 141 | 04:00 | 130 | 13:00
Cantonment | 141 | 05:00 | 133 | 12:00 | Natore | 137 | 03:00 | 129 | 13:00
Chandina | 143 | 05:00 | 124 | 06:00 | Nawabganj | 139 | 05:00 | 131 | 13:00
Chandpur | 139 | 01:00 | 134 | 13:00 | Netrakona | 131 | 05:00 | 118 | 11:00
Chandraghona | 139 | 03:00 | 135 | 12:00 | New | 140 | 06:00 | 131 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 01:00 | 133 | 12:00 | Niamatpur | 140 | 00:00 | 134 | 13:00
Charsaidpur | 143 | 04:00 | 138 | 12:00 | Noapara | 135 | 03:00 | 120 | 13:00
Chauddagram | 139 | 02:00 | 133 | 23:00 | Pabna | 138 | 02:00 | 130 | 18:00
Chhatak | 135 | 05:00 | 130 | 13:00 | Palashbari | 133 | 05:00 | 125 | 18:00
Chowmuhani | 135 | 15:00 | 129 | 13:00 | Panchagarh | 137 | 05:00 | 126 | 18:00
Chuadanga | 139 | 05:00 | 124 | 13:00 | Patiya | 138 | 04:00 | 133 | 18:30
Coxsbazar | 129 | 10:00 | 123 | 13:00 | Patuakhali | 136 | 03:00 | 134 | 13:00
Cumilla(N) | 142 | 05:00 | 136 | 13:00 | Payra | 138 | 02:00 | 135 | 12:00
Cumilla(S) | 143 | 05:00 | 126 | 13:00 | PHP | 138 | 04:00 | 131 | 13:00
Daganbhuiyan | 138 | 03:00 | 132 | 12:00 | Postogola | 143 | 05:00 | 133 | 12:00
Daudkandi | 141 | 06:00 | 135 | 13:00 | Purbachal | 138 | 03:00 | 132 | 12:00
DhakaUniversity | 138 | 04:00 | 132 | 12:00 | Purbasadipur | 131 | 03:00 | 121 | 12:00
Dhamrai | 141 | 06:00 | 134 | 12:00 | Rahanpur | 140 | 01:00 | 136 | 12:00
Dhanmondi | 144.7 | 06:00 | 139 | 13:00 | Rahanpur-400 | 141 | 03:00 | 135 | 13:00
Dohazari | 135 | 04:00 | 130 | 12:00 | Rahim | 144 | 05:00 | 138 | 12:00
Faridpur | 141 | 04:00 | 136 | 13:00 | Rajbari | 142 | 05:00 | 134 | 13:00
Fatullah | 142 | 05:00 | 131 | 13:00 | Rajendrapur | 139 | 16:00 | 128 | 13:00
Fenchuganj | 140 | 02:00 | 136 | 13:00 | Rajshahi | 138 | 06:00 | 127 | 12:00
Feni | 136 | 03:00 | 129 | 19:00 | Rajshahi-230 | 138 | 05:00 | 126 | 12:00
Feni-230 | 138 | 03:00 | 132 | 13:00 | Ramganj | 137 | 07:00 | 131 | 13:00
Ghatail | 135 | 15:00 | 126 | 13:00 | Rampur | 138 | 08:00 | 133 | 13:00
Ghorashal | 139 | 06:00 | 130 | 13:00 | Rampura | 138 | 06:00 | 131 | 13:00
Goalpara | 139 | 05:00 | 130 | 13:00 | Rangamati | 138 | 02:00 | 134 | 13:00
Gollamari | 137 | 05:00 | 130 | 12:00 | Rangpur | 135 | 03:00 | 125 | 12:00
Gopalganj | 140 | 04:00 | 134 | 13:00 | Ruppur | 140 | 05:00 | 131 | 13:00
Gopalganj-400 | 171 | 14:00 | 136 | 13:00 | Saidpur | 137 | 05:00 | 124 | 13:00
Gulshan | 137 | 04:00 | 131 | 13:00 | Satkhira | 136 | 04:00 | 126 | 13:00
Halishahar | 138 | 02:00 | 134 | 16:00 | Satmasjid | 140 | 04:00 | 131 | 13:00
Haripur | 144 | 05:00 | 138 | 13:00 | Savar | 139 | 04:00 | 131 | 13:00
HaripurSBU | 143 | 03:00 | 139 | 12:00 | SevenRings | 139 | 05:00 | 129 | 12:00
Hasnabad | 140 | 06:00 | 131 | 12:00 | ShahCement | 143 | 04:00 | 131 | 10:00
Hathazari | 139 | 04:00 | 136 | 12:00 | Shahjadpur | 142 | 01:00 | 136 | 09:00
Hatirjheel | 138 | 05:00 | 131 | 13:00 | Shahjibazar | 137 | 03:00 | 132 | 13:00
Ishurdi | 141 | 05:00 | 132 | 13:00 | Shahmirpur | 138 | 08:00 | 132 | 01:00
Jaldhaka | 133 | 05:00 | 121 | 13:00 | Shariatpur | 142 | 04:00 | 135 | 13:00
Jamalpur | 137 | 16:00 | 122 | 00:00 | Sherpur | 134 | 16:00 | 119 | 08:00
Jashore | 136 | 06:00 | 120 | 13:00 | Shikalbaha | 128 | 04:00 | 122 | 13:00
Jhenaidah | 140 | 05:00 | 115 | 13:00 | Shikalbaha-230 | 140 | 23:00 | 136 | 18:00
Jhenaidah-230 | 140 | 04:00 | 126 | 01:00 | Shitalakhya | 140 | 03:00 | 131 | 12:00
Joydebpur | 140 | 05:00 | 128 | 13:00 | Sholosohor | 139 | 05:00 | 134 | 13:00
Joypurhat | 135 | 04:00 | 127 | 18:00 | Shyampur | 138 | 09:00 | 135 | 12:00
Juldah | 138 | 04:00 | 134 | 12:00 | Shyampur-230 | 141 | 04:00 | 134 | 13:00
Kabirpur | 141 | 06:00 | 129 | 13:00 | Siddhirganj | 144 | 06:00 | 138 | 12:00
Kachua | 142 | 04:00 | 137 | 12:00 | Sirajganj | 138 | 04:00 | 131 | 12:00
Kaliakoir | 143 | 05:00 | 135 | 13:00 | Sonargaon | 143 | 05:00 | 138 | 00:00
Kallyanpur | 141 | 06:00 | 132 | 13:00 | Sreemongol | 138 | 05:00 | 133 | 12:00
Kalurghat | 139 | 03:00 | 134 | 13:00 | Sreepur | 141 | 06:00 | 132 | 13:00
Kamrangirchar | 139 | 07:00 | 131 | 13:00 | Srinagar | 139 | 03:00 | 132 | 13:00
Kaptai | 137 | 1:00 | 133 | 13:00 | SSM | 141 | 09:00 | 138 | 00:00
Kasba | 140 | 07:00 | 135 | 13:00 | Sunamganj | 134 | 02:00 | 130 | 13:00
Kazla | 141 | 05:00 | 136 | 13:00 | Sylhet | 136 | 01:00 | 127 | 17:00
Keranigonj | 140 | 05:00 | 131 | 13:00 | Sylhet-132 | 135 | 00:00 | 134 | 12:00
Khagrachori | 138 | 02:00 | 134 | 12:00 | Tangail | 134 | 15:00 | 127 | 13:00
Khulna | 135 | 03:00 | 128 | 12:00 | Taraganj | 133 | 03:00 | 124 | 12:00
Khulna(S) | 138 | 05:00 | 129 | 13:00 | Tasnim | 142 | 04:00 | 138 | 12:00
Khulshi | 137 | 07:00 | 132 | 13:00 | Thakurgaon | 136 | 05:00 | 123 | 18:00
Kishoreganj | 136 | 03:00 | 129 | 12:00 | TK | 138 | 04:00 | 135 | 12:00
Kodda | 137 | 07:00 | 128 | 12:00 | Tongi | 140 | 07:00 | 134 | 11:00
KSRM | 138 | 01:00 | 135 | 12:00 | Ullahpara | 139 | 05:00 | 132 | 18:00
Kulaura | 140 | 05:00 | 135 | 13:00 | Ullon | 137 | 03:00 | 131 | 13:00
Kurigram | 134 | 03:00 | 119 | 18:00 | Uttara | 139 | 06:00 | 131 | 13:00
Kushtia | 137 | 05:00 | 122 | 13:00 | UttaraNew | 140 | 01:00 | 132 | 13:00
Laksam | 141 | 07:00 | 126 | 13:00 | Zigatola | 140 | 06:00 | 130 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division