## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-12-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-12-2025 | during | 28-12-2025 | during | 28-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 349 | 412 | 412 | 392 | 392 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 270 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 0 | 0 | ps availability is less
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 46 | 53.97 | 53.97 | 49 | 49 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 54 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 23 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 0 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 125 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 1 | 78 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 127 | 162 | 162 | 146 | 146 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 420 | 420 | 0 | 0 | Gas Shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 380 | 385 | 583 | 583 | 450 | 450 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1039.5 | 1492 | 5772.35 | 5756.35 | 2437.36 | 2439.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 80 | 40 | 40 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 152 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 56 | 105 | 105 | 95 | 95 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 13 | 29 | 5 | 9 | 5 | 9 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.07 | 0 | 3.27 | 0 | 3.27 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 988 | 1162 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 518 | 518 | 830 | 830 | 830 | 830 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 1568.07 | 2030 | 3597.99 | 3595.72 | 3118.77 | 3116.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 185 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 280 | 353.35 | 353.35 | 320 | 320 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 325 | 210 | 393 | 393 | 340 | 340 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 46.7 | 46.7 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 85 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 111 | 109 | 163 | 163 | 112 | 112 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 84 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 74 | 96 | 100 | 90 | 100 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 40 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1154 | 1136 | 2720.56 | 2655.56 | 1847.71 | 1782.71
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-12-2025 | during | 28-12-2025 | during | 28-12-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 52 | 81 | 157.5 | 157.5 | 55 | 55 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 20 | 20 | 20 | 70 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 59 | 60 | 60 | 60 | 60 | Machine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.44 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 178.44 | 171 | 350.5 | 314 | 183.5 | 197
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 35 | 37 | 35 | 35 | 42 | 42 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 156 | 159 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 212 | 212 | 210 | 210 | 210 | 210 | due to GBC problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 544 | 568 | 571 | 571 | 598 | 598
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 422 | 422 | 500 | 500 | 500 | 500 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 26 | 0 | 68 | 0 | 68 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 921 | 1109 | 1148.28 | 1148.28 | 1108 | 1108 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1369 | 1531 | 2988.28 | 2920.28 | 1783.1 | 1715.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 250 | 503 | 622 | 622 | 622 | 622 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 140 | 140 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 950 | 1048 | 1085.32 | 1085.32 | 1085.32 | 1085.32 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Plant is on standby as per NLDC instruction
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.73 | 0 | 1 | 1 | 1 | 1 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1560.73 | 1911 | 2631.32 | 2631.32 | 2191.32 | 2191.32
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 8.97 | 0 | 39 | 0 | 39 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 115 | 214 | 214 | 193 | 193 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 166 | 182 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 33 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 2 | 0 | 2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1159.77 | 1450 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.81 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 84 | 0 | 95 | 0 | 95 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1460.55 | 1780 | 2701.08 | 2504.08 | 2322.2 | 2125.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 54 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 60 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.8 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 10 | 0 | 10 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 55 | 0 | 82.39 | 0 | 82.39 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 117.8 | 184 | 378.59 | 283 | 378.59 | 283
System Total |  |  |  |  | 28823.2 | 28379.108 | 8992.09 | 10803 | 21711.67 | 21231.31 | 14860.55 | 14448.19
Forecast Scenario (28-12-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9040 |  | 0 |  | 9040
|  |  |  | 1:00 | 8560 |  | 0 |  | 8560
|  |  |  | 2:00 | 8100 |  | 0 |  | 8100
|  |  |  | 3:00 | 7790 |  | 0 |  | 7790
|  |  |  | 4:00 | 7570 |  | 0 |  | 7570
|  |  |  | 5:00 | 7460 |  | 0 |  | 7460
|  |  |  | 6:00 | 7920 |  | 0 |  | 7920
|  |  |  | 7:00 | 8430 |  | 0 |  | 8430
|  |  |  | 8:00 | 9160 |  | 0 |  | 9160
|  |  |  | 9:00 | 9690 |  | 0 |  | 9690
|  |  |  | 10:00 | 9660 |  | 0 |  | 9660
|  |  |  | 11:00 | 9720 |  | 0 |  | 9720
|  |  |  | 12:00 | 10230 |  | 0 |  | 10230
|  |  |  | 13:00 | 10610 |  | 0 |  | 10610
|  |  |  | 14:00 | 10170 |  | 0 |  | 10170
|  |  |  | 15:00 | 9780 |  | 0 |  | 9780
|  |  |  | 16:00 | 9640 |  | 0 |  | 9640
|  |  |  | 17:00 | 9880 |  | 0 |  | 9880
|  |  |  | 18:00 | 11140 |  | 0 |  | 11140
|  |  |  | 18:30 | 11080 |  | 0 |  | 11080
|  |  |  | 19:00 | 11020 |  | 0 |  | 11020
|  |  |  | 19:30 | 10780 |  | 0 |  | 10780
|  |  |  | 20:00 | 10780 |  | 0 |  | 10780
|  |  |  | 21:00 | 10570 |  | 0 |  | 10570
|  |  |  | 22:00 | 9920 |  | 0 |  | 9920
|  |  |  | 23:00 | 9510 |  | 0 |  | 9510
Probable Maximum Temperature: |  |  | 23.50°C
Probable Maximum Demand at Day Peak: |  |  | 10230.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11140.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11140.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 226.35 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:38 hrs on 28-12-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-12-2025 | [28 empty] | Date: | 27-12-2025 | [28 empty] | Date: | 27-12-2025 | [28 empty] | Date: | 27-12-2025 | [28 empty] | Date: | 27-12-2025 | [17 empty] | Date: | 27-12-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 202 | 0 | 0 | 112 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 4054 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 0 | 0 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 180 | 0 | 250 | 860 | 0 | 4150 | 8204 | 98.18
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853 | 0 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 160 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 17 | 0 | 5 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 3711 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 750 | 0 | 3797 | 7508 | 98.18
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 230 | 260 | 0 | 5 | 0 | 140 | 0 | 0 | 90 | 0 | 0 | 11 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 158 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 3505 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 600 | 0 | 3609 | 7114 | 98.18
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705 | 0 | 0 | 0 | 230 | 260 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 153 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 3320 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 600 | 0 | 3559 | 6879 | 98.17
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625 | 0 | 0 | 0 | 230 | 260 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 153 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 3216 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 600 | 0 | 3389 | 6605 | 98.17
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 230 | 260 | 0 | 0 | 0 | 201 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 153 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 3293 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 250 | 580 | 0 | 3329 | 6622 | 98.17
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 0 | 0 | 230 | 260 | 0 | 0 | 0 | 176 | 0 | 0 | 114 | 0 | 0 | 5 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 212 | 36 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 0 | 0 | 153 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 3515 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 0 | 0 | 0 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 300 | 620 | 0 | 3525 | 7040 | 98.17
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 40 | 0 | 28 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 1 | 0 | 0 | 230 | 260 | 0 | 42 | 0 | 186 | 0 | 0 | 113 | 0 | 0 | 5 | 0 | 62 | 0 | 1 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 0 | 17 | 0 | 83 | 20 | 0 | 0 | 153 | 0 | 0 | 0 | 52 | 0 | 0.04 | 0 | 3772.08 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 883 | 0 | 0 | 0 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 190 | 0 | 300 | 700 | 0 | 3615.04 | 7387.12 | 98.16
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 250 | 0 | 0 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 40 | 0 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054 | 5 | 0 | 0 | 230 | 260 | 0 | 51 | 0 | 198 | 0 | 0 | 114 | 0 | 0 | 13 | 0 | 72 | 0 | 6 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 1 | 0 | 0 | 83 | 30 | 0 | 0 | 153 | 0 | 16 | 0 | 52 | 0 | 2.28 | 0 | 4001.53 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 998 | 0 | 0 | 0 | 1140.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 6 | 0 | 0 | 1.61 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 7 | 0 | 0 | 0 | 120 | 220 | 0 | 300 | 855 | 0 | 4313.66 | 8315.19 | 98.16
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 40 | 0 | 6 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 360 | 330 | 0 | 51 | 0 | 181 | 0 | 0 | 112 | 0 | 0 | 13 | 0 | 58 | 0 | 18 | 0 | 15 | 0 | 212 | 35 | 0 | 0 | 2 | 8 | 0 | 83 | 30 | 0 | 0 | 155 | 0 | 18 | 19 | 52 | 0 | 5.92 | 0 | 4169.53 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1067 | 0 | 0 | 0 | 1230.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.48 | 14 | 0 | 0 | 3.63 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0.7 | 19 | 0.06 | 0 | 0 | 140 | 180 | 0 | 250 | 1000 | 0 | 4573.56 | 8743.09 | 98.16
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 40 | 0 | 5 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 15 | 0 | 0 | 360 | 300 | 0 | 51 | 0 | 196 | 0 | 0 | 70 | 0 | 0 | 13 | 0 | 64 | 0 | 18 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 4 | 17 | 0 | 83 | 30 | 0 | 0 | 155 | 0 | 57 | 19 | 52 | 0 | 9.91 | 0 | 4063.33 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 968 | 0 | 0 | 0 | 1132.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.92 | 57 | 0 | 0 | 6.87 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 3 | 0 | 0 | 0 | 0 | 1.5 | 24 | 0.16 | 0 | 0 | 100 | 180 | 0 | 250 | 950 | 0 | 4320.61 | 8383.94 | 98.16
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 40 | 0 | 10 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 17 | 0 | 0 | 335 | 330 | 0 | 51 | 0 | 198 | 0 | 0 | 70 | 0 | 0 | 13 | 0 | 64 | 0 | 24 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 155 | 0 | 57 | 19 | 52 | 1 | 17.47 | 4 | 4320.24 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 920 | 0 | 0 | 0 | 1134.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 75 | 0 | 0 | 11.77 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 37 | 0.41 | 0 | 0 | 100 | 220 | 0 | 250 | 950 | 0 | 4358.03 | 8678.27 | 98.15
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 40 | 0 | 13 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 6 | 0 | 0 | 325 | 355 | 0 | 51 | 0 | 185 | 0 | 0 | 111 | 0 | 0 | 13 | 0 | 74 | 0 | 40 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 11 | 17 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 57 | 19 | 52 | 1 | 43.44 | 6 | 4484.01 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 921 | 0 | 0 | 0 | 1159.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.97 | 84 | 0 | 0 | 41.81 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 7 | 0 | 0 | 0 | 0 | 2.8 | 55 | 0.73 | 0 | 0 | 140 | 220 | 0 | 250 | 950 | 0 | 4508.08 | 8992.09 | 98.15
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 17 | 39 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 80 | 0 | 10 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 11 | 0 | 0 | 230 | 355 | 0 | 51 | 0 | 177 | 0 | 0 | 109 | 0 | 0 | 13 | 0 | 86 | 0 | 31 | 0 | 0 | 0 | 212 | 35 | 0 | 0 | 10 | 17 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 59 | 19 | 51 | 2 | 41.39 | 11 | 4586.24 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 995 | 0 | 0 | 0 | 1320.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.73 | 85 | 0 | 0 | 52.23 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 7 | 0 | 0 | 0 | 0 | 4.2 | 96 | 0.49 | 0 | 0 | 140 | 220 | 0 | 286 | 995 | 0 | 4916.6 | 9502.84 | 98.15
14:00 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.14 | 80 | 0 | 10 | 518 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1100 | 14 | 0 | 0 | 225 | 300 | 0 | 51 | 0 | 172 | 0 | 0 | 108 | 0 | 0 | 13 | 0 | 78 | 0 | 48 | 0 | 0 | 0 | 212 | 36 | 20 | 0 | 8 | 17 | 0 | 83 | 30 | 0 | 0 | 156 | 0 | 59 | 19 | 58 | 2 | 33.87 | 9 | 4490.01 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 1034 | 0 | 0 | 0 | 1223.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.78 | 53 | 0 | 0 | 42.39 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 6 | 0 | 0 | 0 | 0 | 3.5 | 93 | 0.37 | 0 | 0 | 100 | 180 | 0 | 250 | 1036 | 0 | 4734.93 | 9224.94 | 98.14
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 80 | 0 | 9 | 518 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1039 | 9 | 0 | 0 | 225 | 270 | 0 | 51 | 0 | 191 | 0 | 0 | 108 | 0 | 0 | 14 | 0 | 92 | 0 | 32 | 0 | 0 | 0 | 212 | 36 | 20 | 0 | 4 | 17 | 0 | 83 | 20 | 0 | 0 | 155 | 0 | 59 | 19 | 103 | 1 | 22.16 | 6 | 4562.84 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 925 | 0 | 0 | 0 | 1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.96 | 34 | 0 | 0 | 24.55 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 4 | 0 | 0 | 0 | 0 | 2.5 | 34 | 0.28 | 0 | 0 | 100 | 180 | 0 | 250 | 940 | 0 | 4353.29 | 8916.13 | 98.14
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 80 | 0 | 13 | 518 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1027 | 0 | 0 | 0 | 210 | 270 | 0 | 51 | 0 | 204 | 0 | 0 | 108 | 0 | 0 | 14 | 0 | 98 | 0 | 13 | 0 | 0 | 0 | 212 | 36 | 20 | 0 | 1 | 17 | 0 | 83 | 20 | 0 | 0 | 156 | 0 | 59 | 19 | 91 | 0 | 8.81 | 6 | 4564.15 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 855 | 0 | 0 | 0 | 1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.86 | 19 | 0 | 0 | 9.88 | 39 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 53 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 26 | 0.14 | 0 | 0 | 100 | 220 | 0 | 264 | 850 | 0 | 4122.68 | 8686.83 | 98.14
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0.5 | 0 | 43 | 0 | 30 | 0 | 5 | 15 | 0 | 0 | 0 | 395 | 0 | 5 | 270 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0.02 | 80 | 0 | 19 | 518 | 0 | 0 | 0 | 0 | 1 | 152 | 0 | 0 | 0 | 1160 | 0 | 7 | 0 | 210 | 270 | 0 | 51 | 0 | 195 | 0 | 0 | 108 | 0 | 0 | 14 | 0 | 100 | 0 | 1 | 0 | 0 | 0 | 213 | 35 | 20 | 0 | 0 | 17 | 0 | 83 | 20 | 0 | 0 | 158 | 0 | 59 | 19 | 91 | 0 | 0.77 | 10 | 4797.29 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 870 | 0 | 0 | 0 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 2 | 0 | 0 | 1.09 | 102 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 53 | 35 | 0 | 20 | 0 | 0 | 0 | 0.1 | 2 | 0.02 | 0 | 0 | 140 | 220 | 0 | 400 | 858 | 0 | 4495.73 | 9293.02 | 98.13
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 16 | 0 | 58 | 0 | 80 | 0 | 30 | 68 | 0 | 0 | 0 | 385 | 0 | 35 | 335 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 18 | 25 | 0 | 80 | 0 | 22 | 518 | 0 | 0 | 0 | 0 | 25 | 152 | 0 | 0 | 0 | 1166 | 0 | 43 | 0 | 250 | 310 | 0 | 51 | 0 | 203 | 0 | 0 | 108 | 26 | 0 | 18 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 212 | 37 | 20 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 59 | 19 | 91 | 0 | 0 | 12 | 5318 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 0 | 0 | 0 | 1446 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 65 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 504 | 978 | 0 | 5249 | 10567 | 98.13
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 46 | 0 | 78 | 0 | 125 | 0 | 54 | 127 | 0 | 0 | 0 | 385 | 0 | 35 | 270 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 25 | 0 | 80 | 0 | 29 | 518 | 0 | 0 | 0 | 0 | 56 | 152 | 0 | 0 | 0 | 1162 | 0 | 85 | 0 | 210 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 109 | 84 | 0 | 20 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 212 | 37 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 59 | 19 | 81 | 0 | 0 | 12 | 5397 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 70 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 503 | 1048 | 0 | 5406 | 10803 | 98.13
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 46 | 0 | 78 | 0 | 125 | 0 | 55 | 125 | 0 | 0 | 0 | 349 | 0 | 35 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 80 | 0 | 29 | 518 | 0 | 0 | 0 | 0 | 76 | 152 | 0 | 0 | 0 | 1150 | 0 | 90 | 0 | 210 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 109 | 123 | 0 | 20 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 212 | 37 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 59 | 19 | 81 | 0 | 0 | 0 | 5363 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 70 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 503 | 1074 | 0 | 5391 | 10754 | 98.13
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 47 | 0 | 78 | 0 | 60 | 0 | 55 | 129 | 0 | 0 | 0 | 350 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 80 | 0 | 30 | 518 | 0 | 0 | 0 | 0 | 80 | 152 | 0 | 0 | 0 | 1160 | 0 | 15 | 0 | 210 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 109 | 126 | 0 | 20 | 0 | 88 | 0 | 0 | 0 | 5 | 0 | 212 | 38 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 59 | 19 | 81 | 0 | 0 | 0 | 5242 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 0 | 0 | 1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 70 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 503 | 1068 | 0 | 5381 | 10623 | 98.12
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 49.5 | 0 | 40 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 325 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 80 | 0 | 30 | 518 | 0 | 0 | 0 | 0 | 101 | 152 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 210 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 110 | 51 | 0 | 20 | 0 | 90 | 0 | 0 | 0 | 10 | 0 | 212 | 38 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 59 | 0 | 81 | 0 | 0 | 0 | 5050.5 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 504 | 1072 | 0 | 5355 | 10405.5 | 98.12
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 355 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 30 | 518 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 210 | 280 | 0 | 51 | 0 | 201 | 0 | 0 | 110 | 48 | 0 | 20 | 0 | 84 | 0 | 0 | 0 | 12 | 0 | 212 | 38 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 59 | 0 | 82 | 0 | 0 | 0 | 4780 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 0 | 0 | 1453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 503 | 1068 | 0 | 5271 | 10051 | 98.12
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 30 | 518 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 210 | 280 | 0 | 51 | 0 | 206 | 0 | 0 | 110 | 0 | 0 | 20 | 0 | 80 | 0 | 0 | 0 | 20 | 0 | 212 | 38 | 30 | 0 | 0 | 17 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 58 | 0 | 80 | 0 | 0 | 0 | 4508 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1072 | 0 | 0 | 0 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 220 | 0 | 300 | 1000 | 0 | 4727 | 9235 | 98.11
Total KWH | 0 | 73920 | 0 | 0 | 0 | 0 | 0 | 0 | 8460000 | 0 | 0 | 172.8 | 88200 | 515232 | 22560 | 292309 | 0 | 156487 | 524160 | 0 | 0 | 0 | 8865909 | 0 | 85687 | 6371212 | 0 | 0 | 1065 | 0 | 334800 | 236520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64048 | 0 | 24960 | 114240 | 12359 | 1446360 | 0 | 444480 | 10807272.73 | 0 | 0 | 0 | 0 | 313636 | 1355218 | 0 | 0 | 0 | 23629088 | 95580 | 214109 | 0 | 5919200 | 7187300 | 0 | 1012904 | 0 | 4639000 | 0 | 0 | 2329857 | 377280 | 0 | 311190 | 0 | 1783680 | 0 | 234809 | 0 | 70080 | 0 | 5163000 | 854000 | 248040 | 0 | 50670 | 288240 | 0 | 1472640 | 617381 | 0 | 0 | 4377050 | 0 | 883200 | 223200 | 1563840 | 7000 | 187690 | 81360 | 104432195.53 | 9569454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241200 | 22683640 | 0 | 0 | 0 | 27325653 | 0 | 0 | 0 | 0 | 42624 | 0 | 0 | 0 | 0 | 94668 | 435630 | 0 | 0 | 190496 | 773636 | 0 | 4240927 | 0 | 0 | 0 | 29270 | 0 | 1080 | 0 | 1224436 | 240489 | 34124 | 264556 | 0 | 0 | 0 | 17121.84 | 413280 | 2464 | 0 | 0 | 2917000 | 5093667 | 0 | 7869090 | 22017454.55 | 0 | 105721960.39 | 210154155.92

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-12-2025
Power Supply Scenario
| Day Peak Generation |  |  | 8992.09 | MW | 12:00 Hr. | Energy Generated |  |  | 210.1542 |  | MKWHr.
| Day Peak Demand |  |  | 8992.09 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10803 | MW | 19:00 Hr. | Energy Demand |  |  | 210.1542 |  | MKWHr.
| Evening Peak Demand |  |  | 10803 | MW | 19:00 Hr. | Maximum Temperature |  |  | 23 |  | °C
| Minimum Generation of the Day |  |  | 6605 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 607.09 |  | MMCFD
| Maximum Generation of the Day |  |  | 10803 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.7282 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 24.2684 | 0 | 1.7587 | 0 | 0 | 0.001065 | 0 | 0 | 26.0282 | Gas | 75.1764 | Gas | 264064525.86
| Chattogram Zone |  |  | 1.7997 | 34.4364 | 0.51688 | 0 | 1.4464 | 0.10794 | 0 | 0 | 38.3072 | Coal | 88.231 | Coal | 588123194.8459
| Cumilla Zone |  |  | 21.3995 | 0 | 0.59139 | 0 | 0 | 0.23481 | 1.7837 | 0 | 24.0093 | HFO | 4.6024 | HFO | 76018276.268
| Mymensingh Zone |  |  | 1.5638 | 0 | 1.1878 | 0 | 0 | 0.19469 | 0 | 0 | 2.9463 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 13.0904 | 0 | 0 | 0 | 0 | 0.05067 | 0 | 0 | 13.1411 | Hydro | 1.4464 | Hydro | 144636
| Khulna Zone |  |  | 0 | 22.6836 | 0 | 0 | 0 | 0.2412 | 9.5695 | 0 | 32.4943 | Solar | 2.0192 | Solar | 31101895.208
| Barishal Zone |  |  | 8.0107 | 29.8865 | 0 | 0 | 0 | 0.002464 | 0 | 0 | 37.8997 | Import | 38.6788 | Import | 244345932.84
| Rajshahi Zone |  |  | 5.0438 | 0 | 0.042624 | 0 | 0 | 0.72187 | 27.3257 | 0 | 33.134 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 1.2244 | 0.50504 | 0 | 0 | 0.46453 | 0 | 0 | 2.194
| Total |  |  | 75.1764 | 88.231 | 4.6024 | 0 | 1.4464 | 2.0192 | 38.6788 | 0 | 210.1542
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 264064525.86 |  | Hydro | 144636
|  |  |  | Coal | 588123194.8459 |  | Solar | 31101895.208
|  |  |  | HFO | 76018276.268 |  | Import | 244345932.84
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 120,37,98,461 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 9.5695 | Peak Hr Flow | 422.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35139454.55 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.3257 | Peak Hr Flow | 1450.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1987 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7837 | Peak Hr Flow | 96.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2165 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 38.6788 | Peak Hr Flow | 1968.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3839
|  |  |  | Chattogram |  | 0 |  | 1175
|  |  |  | Cumilla |  | 0 |  | 916
|  |  |  | Mymensingh |  | 0 |  | 861
|  |  |  | Sylhet |  | 0 |  | 391
|  |  |  | Khulna |  | 0 |  | 1231
|  |  |  | Barishal |  | 0 |  | 314
|  |  |  | Rajshahi |  | 0 |  | 993
|  |  |  | Rangpur |  | 0 |  | 732
|  |  |  | Total |  | 0 |  | 10452
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Baghabari 100 MW GTPP |  |  | 100 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 730
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 | 11:44 | Bogura(New)-Naogaon 132 kV Ckt-2 Project Work S/D from Bogura 230/132kV end Due to
Naogaon 132kv Main Bus S/D
| 08:21 | 11:50 | Naogaon 132/33kV S/S Main Bus Scheduled S/D Due to 132kV Main BUS Loop change
Maintenance
| 08:25 | 11:51 | Naogaon 132/33kV S/S Nao-SPPP Ckt-1 Scheduled S/D Due to 132kV Main BUS Loop change
Maintenance
| 08:28 | 16:21 | Shahjibazar-Sreemangal 132kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to
Annul Maintenance. and from Sreemongol 132/33kV end Due to Annual Maintenance
| 08:28 | 15:42 | Chowmuhani-Ramganj 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to Annual
Maintenance.
| 08:30 | 11:45 | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to Annual | [7 empty] | 10.0MW load
|  |  | Maintenance. and from Daganbhuiyan 132/33kV end Due to Shutdown taken by Chowmuhuni S/S | [7 empty] | interrup.
|  |  | for Main Bus maintenance purpose | [7 empty] | Chowmuhani 132/33kV
end and 10.0MW load
interrup.
Daganbhuiyan
132/33kV end
| 08:33 | 13:28 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Maintenance works by PBS | [7 empty] | 27.0MW load
interrup.
| 08:34 | 13:22 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Maintenance works by PBS | [7 empty] | 27.0MW load
interrup.
| 08:39 | 14:55 | Rajbari 132/33kV S/S Faridpur -1 Scheduled S/D Due to Annual maintenance.
| 08:39 | 11:49 | Chowmuhani 132/33kV S/S Main Bus Scheduled S/D Due to Annual maintenance | [7 empty] | 30.0MW load
interrup.
| 08:40 | 14:55 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-1 Scheduled S/D Due to Annual maintenance.
| 08:40 | 18:31 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline Checking
| 08:42 | 16:26 | Agargaon 230/132kV S/S Auxiliary Tr-2 LT Scheduled S/D Due to Annual maintenance.
| 08:42 | 16:26 | Agargaon 230/132kV S/S Auxiliary Tr-2 HT Scheduled S/D Due to Annual maintenance.
| 08:43 | 16:25 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT Scheduled S/D Due to Annual
maintenance.
| 08:43 | 16:21 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT Scheduled S/D Due to Annual
maintenance.
| 08:48 | 15:59 | Bogura-Mahasthangar (New)) 132 kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due
to Annual Maintenance and from Bogura 132/33kV end Due to Annual Maintenance.
| 08:52 | 15:21 | Ashuganj-Kishoreganj 132kV Ckt-2 Project Work S/D from Ashuganj 230/132/33kV end Due to
shutdown by PGCB, OFCN
| 08:54 | 16:30 | Rahanpur 400/132kV S/S Rahanpur-Niamatpur 132 KV Line Ckt-02 Scheduled S/D
| 08:54 | 17:37 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Scheduled S/D
| 08:54 | 16:34 | Niamatpur 132/33kV S/S 132 kV Rahanpur Ckt-2 Scheduled S/D Due to Annual Maintenance
| 08:56 | 12:17 | Sylhet-Sylhet (South) 132KV Ckt-2 Project Work S/D from Sylhet 132/33kV end Due to EEGBPS
Project work purpose.
| 09:01 | 12:32 | Meghnaghat 400/230kV S/S ATR -03 HT Forced S/D Due to ATR- 03 shutdown instructed by
NLDC.
| 09:07 | 15:36 | Goalpara- Khulna (C) 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Annual
Maintenance work and from Khulna (C) end Due to For A/M
| 09:11 |  | Mogbazar 132/33kV S/S GT-1 LT Scheduled S/D
| 09:11 | 18:42 | Madanganj 132/33kV S/S GT-2 LT Scheduled S/D
| 09:13 | 18:38 | Madanganj 132/33kV S/S GT-2 HT Scheduled S/D Due to Annual Maintenance
| 09:14 | 16:56 | Baghabari-Bangura 132 kV Ckt-1 Scheduled S/D from Bhangura 132/33kV end Due to Annual | [7 empty] | 10.0MW load
|  |  | Maintenance | [7 empty] | interrup. Bhangura
132/33kV end
| 09:16 | 17:20 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) LT Scheduled S/D Due to Annual
maintenance.
| 09:16 | 17:31 | Mongla 132/33kV S/S T-2 HT Scheduled S/D Due to Yearly Mentanance
| 09:16 | 17:31 | Mongla 132/33kV S/S T-2 LT Scheduled S/D Due to Yearly Mentanance
| 09:17 | 17:18 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) HT Scheduled S/D Due to Annual
maintenance.
| 09:19 | 16:40 | Shikalbaha 230/132kV S/S Hathazari-02 Scheduled S/D
| 09:19 | 16:40 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-2 Scheduled S/D Due to Annual
Maintenance
| 09:21 | 17:37 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
Works for RHD department.
| 09:24 | 14:32 | Maniknagar-Narinda 132kV Ckt-2 Scheduled S/D from Maniknagar 132/33kV end Due to Annual
Maintenance
| 09:27 | 16:01 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning and Dead line check
| 09:28 |  | Magura 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to Annual maintenance of T-3
| 09:29 | 17:00 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-1 Scheduled S/D Due to Annual
Maintenance
| 09:29 | 17:42 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D Due to Annual maintenance work | [7 empty] | 30.0MW load
interrup.
| 09:29 | 17:42 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to Annual maintenance work | [7 empty] | 30.0MW load
interrup.
| 09:29 | 17:43 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Annual maintenance work | [7 empty] | 20.0MW load
interrup.
| 09:29 | 17:43 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D Due to Annual maintenance work | [7 empty] | 20.0MW load
interrup.
| 09:30 | 16:27 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Scheduled S/D Due to Annual maintenance
| 09:30 | 16:25 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Scheduled S/D Due to Annual maintenance
| 09:30 | 16:09 | Jamalpur United(20MW)-Sherpur 132kV Ckt-1 Scheduled S/D from Sherpur 132/33kV end Due to
Annual Maintenace
| 09:31 | 17:41 | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Satkhira 132/33kV end Due to Annual
maintenance work and from Khulna(S) 230/132kVend.
| 09:31 | 18:27 | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Satkhira 132/33kV end Due to Annual
maintenance work and from Khulna(S) 230/132kVend.
| 09:38 | 16:50 | Tongi 230/132/33kV S/S T-02 HT Scheduled S/D Due to Annual maintenance
| 09:38 | 16:50 | Tongi 230/132/33kV S/S T-02 LT Scheduled S/D Due to Annual maintenance
| 09:46 | 17:48 | Ashuganj-Ghorasal 132kV Ckt-1 Project Work S/D from Ashuganj 230/132/33kV end Due to
shutdown by PGCB, OFCN
| 09:47 | 16:22 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end.
| 09:48 | 15:54 | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to Annual Maintenance
| 09:53 | 17:32 | Tangail 132/33kV S/S Kaliakair-2 Project Work S/D
| 09:54 | 17:31 | Mirzapur 132/33kV S/S Mirzapur-Kaliakair-ckt-2A(E08) Project Work S/D Due to LILO
condutor changing work. Stringing ACCC instead ACSR condutor.
| 09:54 | 17:31 | Mirzapur 132/33kV S/S Mirzapur-Kaliakoir ckt-2B(E-09) Project Work S/D Due to LILO | [7 empty] | 167.0MW load
|  |  | condutor changing work. Stringing ACCC instead ACSR condutor. | [7 empty] | interrup.
| 09:56 | 17:00 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-1 Scheduled S/D from Jamalpur 132/33kV end Due
to Annual Maintenance work
| 09:57 | 17:33 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Project Work S/D Due to LILO condutor | [7 empty] | 10.0MW load
|  |  | changing work. Stringing ACCC instead ACSR condutor. | [7 empty] | interrup.
| 09:58 | 18:32 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Project Work S/D Due to LILO condutor
changing work. Stringing ACCC instead ACSR condutor.
| 09:58 | 18:32 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Project Work S/D Due to LILO condutor | [7 empty] | 140.0MW load
|  |  | changing work. Stringing ACCC instead ACSR condutor. | [7 empty] | interrup.
| 09:58 | 17:38 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Project Work S/D Due to LILO condutor | [7 empty] | 18.0MW load
|  |  | changing work. Stringing ACCC instead ACSR condutor. | [7 empty] | interrup.
| 09:59 | 17:37 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Project Work S/D Due to LILO condutor | [7 empty] | 18.0MW load
|  |  | changing work. Stringing ACCC instead ACSR condutor. | [7 empty] | interrup.
| 10:08 | 15:59 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Ghatail 132/33kV end Due to
Annual Maintenance
| 10:08 | 15:59 | Tangail 132/33kV S/S RPCL-1 Scheduled S/D Due to Annual Maintenance
| 10:19 | 17:01 | BIPTC S/S 400kV Bus-1 Scheduled S/D Due to Annual Maintenance
| 10:24 | 17:23 | Baghabari-Sirajganj 230 kV Ckt-1 Scheduled S/D from Baghabari 230/132kV end Due to Annual
Maintenance
|  | 10:44 | Jaldhaka 132/33kV S/S 406T-1 HT is restored.
|  | 10:45 | Jaldhaka 132/33kV S/S 406T-1 LT is restored.
| 11:09 | 16:30 | Kodda-Rajendrapur 132kV Ckt-2 Forced S/D from Rajendrapur 132/33kV end Due to For red
hot maintenance work at sreepur end. Load continued by Kodda -1 line.
| 11:25 | 16:36 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Forced S/D Due to Redhot Mintenance
|  | 11:47 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
|  | 11:51 | Bhulta-Haripur 230 kV Ckt-1 is restored.
| 12:00 |  | Day Peak Generation: 8987 MW.
|  | 12:15 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 12:16 | Meghnaghat 400/230kV S/S ATR -03 LT is restored.
|  | 12:17 | Naogaon 132/33kV S/S T-3 LT is restored.
| 12:34 |  | Kaptai-1 was sync.
| 13:49 |  | Sikalbaha 225 MW GT was sync
| 14:14 | 17:26 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to Tan-Delta test
| 14:15 | 17:25 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to Tan-Delta test
|  | 14:29 | Naogaon 132/33kV S/S T-1 HT is restored.
|  | 14:30 | Naogaon 132/33kV S/S T-2 HT is restored.
|  | 14:31 | Naogaon 132/33kV S/S T-2 LT is restored.
|  | 14:32 | Naogaon 132/33kV S/S T-1 LT is restored.
| 15:12 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by Ghorashal end via NLDC
| 15:43 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
|  | 15:48 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 15:49 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
|  | 17:01 | BIPTC S/S 11T01 HT is restored.
|  | 17:15 | Rajendrapur 132/33kV S/S MTR-2 HT is restored.
|  | 17:17 | Rajendrapur 132/33kV S/S MTR-2 LT is restored.
|  | 17:24 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 is restored.
| 17:29 | 20:01 | Bhandaria 132/33kV S/S Transformer-2 LT Forced S/D Due to Tan delta test
| 17:30 | 20:01 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to Tan delta test
| 17:45 | 17:57 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Tripped showing Lockout Relay K861 Trip, | [7 empty] | 11.0MW load
|  |  | Lockout Relay K862 Trip. 33KV (SIEMENS) Relay. 132KV (SIEMENS) Relay. relays Due to | [7 empty] | interrup.
Patiya 33Kv Feeder
|  | 18:03 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 18:04 | Khulna (C) S/S TR-1 425T LT is restored.
| 18:28 | 19:14 | Khulna (C) S/S Tr-2 415 T HT Tripped showing No relay relays Due to For 33 kv PBS feeder
fault
| 18:28 | 19:14 | Khulna (C) S/S TR-1 425T LT Tripped showing Over current relays Due to For 33 PBS feeder | [7 empty] | 14.0MW load
|  |  | fault | [7 empty] | interrup.
| 18:28 | 19:14 | Khulna (C) S/S Tr-2 415 T LT Tripped showing Inst. Over current relays Due to For 33 kv | [7 empty] | 7.0MW load
|  |  | PBS feeder fault | [7 empty] | interrup.
| 19:00 |  | Day Peak Generation: 10803 MW.
| 19:55 |  | Summit Bibiyana-2 CCPP GT was sync.
| 22:26 |  | Summit Bibiyana-2 CCPP ST was sync.
| 04:32 |  | Sirajganj unit-4 GT & ST were sync. at 04:32hr and 06:16hr respectively.
| 04:32 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- GT
| 05:00 |  | Minimum Generation: 7153 MW.
| 05:49 |  | Ashuganj 225 MW CCPP ST tripped at 05:49hr due to flash tank level high.
| 05:49 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
| 05:50 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT (False)
|  | 05:55 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 06:16 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 06:22 |  | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to Piling work safety purpose. | [7 empty] | 4.0MW load
interrup.
| 06:23 |  | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to Piling work safety purpose. | [7 empty] | 4.0MW load
interrup.
| 06:44 |  | Mongla 132/33kV S/S 100MW ERBL Solar PS Project Work S/D Due to Project work
| 06:46 |  | Bagerhat-Mongla 132 kV Ckt-1 Project Work S/D from Mongla 132/33kV end Due to Project | [7 empty] | 10.0MW load
|  |  | work | [7 empty] | interrup. Mongla
132/33kV end
| 06:48 |  | Bagerhat-Mongla 132 kV Ckt-2 Project Work S/D from Mongla 132/33kV end Due to Project | [7 empty] | 10.0MW load
interrup. Mongla
132/33kV end
| 06:49 |  | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Annual | [7 empty] | 28.0MW load
|  |  | maintenance work | [7 empty] | interrup. Bagerhat
132/33kV end
| 06:51 |  | Mongla 132/33kV S/S T-2 LT Project Work S/D Due to Project work&yearly mentanance
| 06:51 |  | Mongla 132/33kV S/S T-1 LT Project Work S/D Due to Project work | [7 empty] | 10.0MW load
interrup.
| 06:51 |  | Mongla 132/33kV S/S T-2 HT Project Work S/D Due to Project work&yearly mentanance
| 06:51 |  | Mongla 132/33kV S/S T-1 HT Project Work S/D Due to Project Work | [7 empty] | 10.0MW load
interrup.
| 06:53 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
|  |  | work. | [7 empty] | interrup.
| 06:53 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
|  |  | work | [7 empty] | interrup.
| 06:55 |  | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Project Work S/D from Rangpur 132/33kV end
Due to Re conductig
| 06:55 | 06:55 | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bhandaria 132/33kV end Due to Purpose
aldc
| 07:01 |  | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:01 |  | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
|  |  | work | [7 empty] | interrup.
| 07:03 |  | Bagerhat 132/33kV S/S 132 kV BUS Scheduled S/D Due to Phase sequence change of TR-3 | [7 empty] | 40.0MW load
interrup.
| 07:03 |  | Bagerhat-Goalpara 132 kV Ckt-1 Forced S/D from Goalpara 132/33kV end Due to Work done by | [7 empty] | and 36.0MW load
|  |  | bagerhat ss and from Bagerhat 132/33kV end Due to Annual maintenance work | [7 empty] | interrup. Bagerhat
132/33kV end
| 07:30 |  | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to Annual maintenance
| 07:30 |  | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to Annual maintenance
| 07:43 |  | Rajbari 132/33kV S/S Faridpur -1 Scheduled S/D Due to Annual maintenance
| 07:44 |  | Faridpur 132/33kV S/S 132 KV Rajbari ckt-1 Scheduled S/D Due to Annual mentenance
| 07:51 |  | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Dead line checking
| 08:00 |  | Kachua 230/132/33kV S/S TR-2 LT Scheduled S/D Due to for annual maintenance.
| 08:00 |  | Kachua 230/132/33kV S/S TR-2 HT Scheduled S/D Due to for annual maintenance.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-12-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8460000 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6371212 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | ps availability is less
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46 | 172.8 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 22560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 54 | 156487 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 85687 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 334800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 236520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 125 | 292309 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 78 | 515232 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 73920 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 127 | 524160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 1065 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 88200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 385 | 8865909 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 0 | Engine Problem
Dhaka Area Total |  |  |  |  | 6667.111 | 1492 | 26028233.8
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 95580 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1446360 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 152 | 1355218 | Under Maintenance
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 56 | 313636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 64048 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 24960 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 444480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 12359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 114240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1162 | 23629088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 518 | 10807272.73 | Plant availability less
Chattogram Area Total |  |  |  |  | 4895.723 | 2030 | 38307241.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 201 | 4639000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 280 | 7187300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 210 | 5919200 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1012904 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 85 | 214109 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 109 | 2329857 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 84 | 377280 | -
| Import (Tripura) |  | Import | 0 | 160 | 96 | 1783680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 311190 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 234809 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1136 | 24009329
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 81 | 1563840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 223200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 883200 | Machine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 187690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 81360 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 171 | 2946290
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 50670 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 37 | 854000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 248040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 617381 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1472640 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 159 | 4377050 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 288240 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 70080 | shutdown due to Schedule Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 212 | 5163000 | due to GBC problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 568 | 13141101
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 422 | 9569454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 241200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1109 | 22683640 | FGMO, plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1531 | 32494294
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 503 | 7869090 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2917000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 1048 | 22017454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5093667 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2464 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1911 | 37899675.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 94668 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 115 | 773636 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 182 | 4240927 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 29270 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 33 | 42624 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 1080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1450 | 27325653 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 190496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 435630 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1780 | 33133984
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | plant availability zero
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1224436 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 60 | 264556 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 17121.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 240489 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 34124 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 413280 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 184 | 2194006.84
Eastern Grid Total |  |  |  |  | 17395.105 | 5397 | 104432195.53
Western Grid Total |  |  |  |  | 10984.003 | 5406 | 105721960.39
National Grid Total |  |  |  |  | 28379.108 | 10803 | 210154155.92
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-12-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7182.04 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3270.9 | MW
i) Dhaka area |  |  | 3839.34 |  | MW | i) Khulna area |  |  |  | 1231 | MW
ii) Chattogram area |  |  | 1174.7 |  | MW | ii) Barishal area |  |  |  | 314.5 | MW
iii) Cumilla area |  |  | 916 |  | MW | iii) Rajshahi area |  |  |  | 993.4 | MW
iv) Mymensingh area |  |  | 861 |  | MW | iv) Rangpur area |  |  |  | 732 | MW
v) Sylhet area |  |  | 391 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10452.94 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 72 | 21:00 | 133 | Netrakona | 103 | 18:00
2 | AKSML | 113 | 07:00 | 68 | Hathazari | 61 | 13:00 | 134 | New | 65.2 | 14:00
3 | Aftabnagar | 24 | 13:00 | 69 | Hatirjheel | 26 | 18:00 | 135 | Niamatpur | 48 | 09:00
4 | Agargaon | 79 | 13:00 | 70 | Ishurdi | 51 | 18:00 | 136 | Noapara | 39 | 19:30
5 | Agrabad | 38 | 18:00 | 71 | Jaldhaka | 56 | 18:00 | 137 | PHP | 9 | 23:00
6 | Amnura | 27 | 08:00 | 72 | Jamalpur | 88 | 19:00 | 138 | Pabna | 76 | 17:00
7 | Ashuganj | 56 | 18:00 | 73 | Jashore | 98 | 18:00 | 139 | Palashbari | 82 | 18:00
8 | BSRM | 200 | 22:00 | 74 | Jhenaidah | 97 | 18:00 | 140 | Panchagarh | 49 | 18:00
9 | Bagerhat | 64 | 18:00 | 75 | Joydebpur | 103 | 18:00 | 141 | Patiya | 6 | 18:00
10 | Bajitpur | 60 | 18:00 | 76 | Joypurhat | 46 | 09:00 | 142 | Patuakhali | 43 | 19:30
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 15 | 14:00 | 143 | Payra | 22 | 18:00
12 | Bakulia | 62 | 15:00 | 78 | KSRM | 11 | 17:00 | 144 | Postogola | 38 | 13:00
13 | Banani | 16 | 12:00 | 79 | Kabirpur | 172 | 10:00 | 145 | Purbachal | 23 | 18:00
14 | Bangabhaban | 5 | 10:00 | 80 | Kachua | 55 | 20:00 | 146 | Purbasadipur | 114 | 18:30
15 | Barapukuria | 52 | 18:30 | 81 | Kallyanpur | 69 | 14:00 | 147 | Rahanpur | 18 | 18:30
16 | Barguna | 14 | 18:00 | 82 | Kalurghat | 28 | 12:00 | 148 | Rahim | 30 | 07:00
17 | Barishal | 80 | 13:00 | 83 | Kamrangirchar | 59 | 13:00 | 149 | Rajbari | 62 | 18:00
18 | Barishal-230 | 64 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 124 | 12:00
19 | Baroaulia | 63 | 17:00 | 85 | Kasba | 22 | 19:30 | 151 | Rajshahi | 77 | 18:30
20 | Baroirhat | 47 | 13:00 | 86 | Kazla | 86 | 13:00 | 152 | Rajshahi-230 | 57 | 13:00
21 | Bashundhara | 119 | 13:00 | 87 | Keranigonj | 49 | 18:30 | 153 | Ramganj | 72 | 18:00
22 | BashundharaCement | 7 | 03:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 28 | 12:00
23 | Beanibazar | 46 | 18:00 | 89 | Khulna | 44 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 52 | 18:00 | 90 | Khulshi | 164 | 14:00 | 156 | Rangpur | 103 | 18:30
25 | Bhaluka | 114 | 18:00 | 91 | Kishoreganj | 86 | 19:00 | 157 | Ruppur | 1.4 | 00:00
26 | Bhandaria | 37 | 21:00 | 92 | Kodda | 238 | 11:00 | 158 | SSM | 0 | 00:00
27 | Bhangura | 28 | 18:00 | 93 | Kulaura | 27 | 13:00 | 159 | Saidpur | 94 | 18:00
28 | Bheramara(GK) | 41 | 18:00 | 94 | Kurigram | 50 | 17:00 | 160 | Satkhira | 102 | 19:00
29 | Bhulta | 180 | 21:00 | 95 | Kushtia | 114 | 18:00 | 161 | Satmasjid | 74 | 18:30
30 | Bog-Sherpur | 56 | 18:00 | 96 | Laksam | 22 | 11:00 | 162 | Savar | 143 | 19:00
31 | Bogura | 108 | 19:00 | 97 | Lakshmipur | 24 | 18:00 | 163 | SevenRings | 9.08 | 00:00
32 | Borhanuddin | 65 | 21:00 | 98 | Lalbag | 54 | 13:00 | 164 | ShahCement | 34 | 16:00
33 | Brahmanbaria | 86 | 19:30 | 99 | Lalmonirhat | 48 | 18:00 | 165 | Shahjadpur | 56 | 18:00
34 | Cantonment | 74 | 13:00 | 100 | MI_Cement | 13.8 | 08:00 | 166 | Shahjibazar | 86 | 18:00
35 | Chandina | 11 | 03:00 | 101 | Madanganj | 30 | 18:00 | 167 | Shahmirpur | 36 | 18:00
36 | Chandpur | 50 | 18:30 | 102 | Madaripur | 68 | 18:30 | 168 | Shariatpur | 67 | 14:00
37 | Chandraghona | 26 | 17:00 | 103 | Madartek | 56 | 13:00 | 169 | Sherpur | 128 | 18:30
38 | Chapai | 49 | 09:00 | 104 | Madunaghat | 34 | 12:00 | 170 | Shikalbaha | 21 | 12:00
39 | Charsaidpur | 41 | 00:00 | 105 | Magura | 46 | 18:00 | 171 | Shitalakhya | 60.9 | 11:00
40 | Chauddagram | 48 | 13:00 | 106 | Mahasthangarh | 48 | 18:30 | 172 | Sholosohor | 37 | 12:00
41 | Chhatak | 23 | 18:30 | 107 | Maijdee | 30 | 21:00 | 173 | Shyampur | 144 | 12:00
42 | Chowmuhani | 108 | 18:00 | 108 | Manikganj | 95 | 18:00 | 174 | Siddhirganj | 84 | 12:00
43 | Chuadanga | 78 | 18:00 | 109 | Maniknagar | 46 | 13:00 | 175 | Sirajganj | 78 | 18:30
44 | Coxsbazar | 113 | 18:00 | 110 | Matarbari | 40 | 18:00 | 176 | Sonargaon | 138 | 17:00
45 | Cumilla(N) | 91 | 13:00 | 111 | Matuail | 42 | 10:00 | 177 | Sreemongol | 55 | 18:30
46 | Cumilla(S) | 97 | 16:00 | 112 | Metrorail_Motijheel | 23 | 12:00 | 178 | Sreepur | 83 | 19:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 6 | 13:00 | 179 | Srinagar | 31.83 | 13:00
48 | Daudkandi | 106 | 18:00 | 114 | Millgate | 71 | 12:00 | 180 | Sunamganj | 39 | 19:00
49 | DhakaUniversity | 42 | 13:00 | 115 | Mirpur | 102 | 13:00 | 181 | Sylhet | 38 | 13:00
50 | Dhamrai | 102 | 18:00 | 116 | Mirsorai | 44 | 16:00 | 182 | Sylhet-132 | 76 | 18:00
51 | Dhanmondi | 66 | 13:00 | 117 | Mirzapur | 44 | 18:00 | 183 | TK | 15.5 | 22:00
52 | Dohazari | 67 | 18:30 | 118 | Mithapukur | 52 | 18:00 | 184 | Tangail | 126 | 18:00
53 | Faridpur | 110 | 19:30 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 18:00
54 | Fatullah | 88 | 15:00 | 120 | Mogbazar | 32.3 | 12:00 | 186 | Tasnim | 17 | 01:00
55 | Fenchuganj | 27 | 17:00 | 121 | Mongla | 33 | 17:00 | 187 | Thakurgaon | 83 | 18:30
56 | Feni | 68 | 21:00 | 122 | Motijheel | 25 | 13:00 | 188 | Tongi | 78 | 15:00
57 | GPH | 84 | 03:00 | 123 | Muktagacha | 29 | 18:00 | 189 | Ullahpara | 26 | 18:00
58 | Ghatail | 58 | 18:00 | 124 | Munshiganj | 68 | 19:30 | 190 | Ullon | 47 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 24 | 20:00 | 191 | Uttara | 58 | 18:30
60 | Ghorashal-230 | 80 | 19:30 | 126 | Mymensingh | 152 | 18:00 | 192 | UttaraNew | 35 | 13:00
61 | Goalpara | 27 | 19:00 | 127 | Naogaon | 91 | 19:00 | 193 | Zigatola | 68 | 13:00
62 | Gollamari | 82 | 20:00 | 128 | Narail | 43.5 | 18:00
63 | Gopalganj | 82 | 18:00 | 129 | Narinda | 48 | 18:30
64 | Gulshan | 60 | 13:00 | 130 | Narshingdi | 147 | 19:00
65 | Halishahar | 46 | 12:00 | 131 | Natore | 100 | 18:30
66 | HaripurSBU | 85 | 15:00 | 132 | Nawabganj | 30.4 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-12-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8204 | 0 |  | 8204
1:00 | 7508 | 0 |  | 7508
2:00 | 7114 | 0 |  | 7114
3:00 | 6879 | 0 |  | 6879
4:00 | 6605 | 0 |  | 6605
5:00 | 6622 | 0 |  | 6622
6:00 | 7040 | 0 |  | 7040
7:00 | 7387.12 | 0 |  | 7387.12
8:00 | 8315.19 | 0 |  | 8315.19
9:00 | 8743.09 | 0 |  | 8743.09
10:00 | 8383.94 | 0 |  | 8383.94
11:00 | 8678.27 | 0 |  | 8678.27
12:00 | 8992.09 | 0 |  | 8992.09
13:00 | 9502.84 | 0 |  | 9502.84
14:00 | 9224.94 | 0 |  | 9224.94
15:00 | 8916.13 | 0 |  | 8916.13
16:00 | 8686.83 | 0 |  | 8686.83
17:00 | 9293.02 | 0 |  | 9293.02
18:00 | 10567 | 0 |  | 10567
19:00 | 10803 | 0 |  | 10803
19:30 | 10754 | 0 |  | 10754
20:00 | 10623 | 0 |  | 10623
21:00 | 10405.5 | 0 |  | 10405.5
22:00 | 10051 | 0 |  | 10051
23:00 | 9235 | 0 |  | 9235
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-12-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4054 | 4150 | 8204 | DAILY GENERATION CURVE
00:30 | 3882.5 | 3973.5 | 7856
01:00 | 3711 | 3797 | 7508 | 27-12-2025
01:30 | 3608 | 3703 | 7311
02:00 | 3505 | 3609 | 7114
02:30 | 3412.5 | 3584 | 6996.5
03:00 | 3320 | 3559 | 6879
03:30 | 3268 | 3474 | 6742
04:00 | 3216 | 3389 | 6605
04:30 | 3254.5 | 3359 | 6613.5
05:00 | 3293 | 3329 | 6622
05:30 | 3404 | 3427 | 6831
06:00 | 3515 | 3525 | 7040
06:30 | 3643.54 | 3570.02 | 7213.56
07:00 | 3772.08 | 3615.04 | 7387.12
07:30 | 3886.805 | 3964.35 | 7851.155
08:00 | 4001.53 | 4313.66 | 8315.19
08:30 | 4085.53 | 4443.61 | 8529.14
09:00 | 4169.53 | 4573.56 | 8743.09
09:30 | 4116.43 | 4447.085 | 8563.515
10:00 | 4063.33 | 4320.61 | 8383.94
10:30 | 4191.785 | 4339.32 | 8531.105
11:00 | 4320.24 | 4358.03 | 8678.27
11:30 | 4402.125 | 4433.055 | 8835.18
12:00 | 4484.01 | 4508.08 | 8992.09
12:30 | 4535.125 | 4712.34 | 9247.465
13:00 | 4586.24 | 4916.6 | 9502.84
13:30 | 4538.125 | 4825.765 | 9363.89
14:00 | 4490.01 | 4734.93 | 9224.94
14:30 | 4526.425 | 4544.11 | 9070.535
15:00 | 4562.84 | 4353.29 | 8916.13
15:30 | 4563.495 | 4237.985 | 8801.48
16:00 | 4564.15 | 4122.68 | 8686.83
16:30 | 4680.72 | 4309.205 | 8989.925
17:00 | 4797.29 | 4495.73 | 9293.02
17:30 | 5057.645 | 4872.365 | 9930.01
18:00 | 5318 | 5249 | 10567
18:30 | 5357.5 | 5327.5 | 10685
19:00 | 5397 | 5406 | 10803
19:30 | 5363 | 5391 | 10754
20:00 | 5242 | 5381 | 10623
20:30 | 5146.25 | 5368 | 10514.25 |  | Executive Engineer
21:00 | 5050.5 | 5355 | 10405.5 |  | Network Operation Division
21:30 | 4915.25 | 5313 | 10228.25
22:00 | 4780 | 5271 | 10051
22:30 | 4644 | 4999 | 9643
23:00 | 4508 | 4727 | 9235

## En-Curve
QF-LDC-12
Date | 27-12-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2486 | 733 | 422 | 0 | 68 | 914 | 40 | 3541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2444 | 699.5 | 422 | 0 | 65 | 870.5 | 40 | 3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27-12-2025
01:00 | 2402 | 666 | 422 | 0 | 62 | 827 | 40 | 3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 2341.5 | 631 | 422 | 0 | 61 | 829.5 | 40 | 2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 210.1542 |  | MKWHr
02:00 | 2281 | 596 | 422 | 0 | 60 | 832 | 40 | 2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2229 | 588 | 422 | 0 | 59 | 835.5 | 40 | 2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Energy Requirement | 210.1542 |  | MKWHr
03:00 | 2177 | 580 | 422 | 0 | 58 | 839 | 40 | 2763 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2163 | 592.5 | 351 | 0 | 56 | 842 | 40 | 2697.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2149 | 605 | 280 | 0 | 54 | 845 | 40 | 2632 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2163.5 | 623.5 | 280 | 0 | 55 | 840 | 40 | 2611.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2178 | 642 | 280 | 0 | 56 | 835 | 40 | 2591 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2219.5 | 682 | 280 | 0 | 58 | 835.5 | 40 | 2716 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2261 | 722 | 280 | 0 | 60 | 836 | 40 | 2841 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2202 | 756 | 280 | 0 | 61 | 877 | 40 | 2996 | 1.56 | 0 | 0 | 0 | 0 | 0 | 0
07:00 | 2143 | 790 | 280 | 0 | 62 | 918 | 40 | 3151 | 3.12 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 2161 | 811 | 351 | 0 | 67 | 1029.32 | 40 | 3363.5 | 20.335 | 0 | 8 | 0 | 0 | 0 | 0
08:00 | 2179 | 832 | 422 | 0 | 72 | 1140.64 | 40 | 3576 | 37.55 | 0 | 16 | 0 | 0 | 0 | 0
08:30 | 2277 | 796.5 | 422 | 0 | 65 | 1185.665 | 40 | 3658.5 | 57.975 | 0 | 26.5 | 0 | 0 | 0 | 0
09:00 | 2375 | 761 | 422 | 0 | 58 | 1230.69 | 40 | 3741 | 78.4 | 0 | 37 | 0 | 0 | 0 | 0
09:30 | 2311 | 713.75 | 422 | 0 | 61 | 1181.425 | 40 | 3656.5 | 120.34 | 0 | 57.5 | 0 | 0 | 0 | 0
10:00 | 2247 | 666.5 | 422 | 0 | 64 | 1132.16 | 40 | 3572 | 162.28 | 0 | 78 | 0 | 0 | 0 | 0
10:30 | 2268 | 708 | 422 | 0 | 64 | 1133.085 | 40 | 3617.5 | 191.02 | 0 | 87.5 | 0 | 0 | 0 | 0
11:00 | 2289 | 749.5 | 422 | 0 | 64 | 1134.01 | 40 | 3663 | 219.76 | 0 | 97 | 0 | 0 | 0 | 0
11:30 | 2338.5 | 773.5 | 422 | 0 | 69 | 1146.89 | 40 | 3671.5 | 275.29 | 0 | 98.5 | 0 | 0 | 0 | 0
12:00 | 2388 | 797.5 | 422 | 0 | 74 | 1159.77 | 40 | 3680 | 330.82 | 0 | 100 | 0 | 0 | 0 | 0
12:30 | 2326 | 809.25 | 422 | 0 | 80 | 1240.36 | 60 | 3806 | 373.355 | 8 | 122.5 | 0 | 0 | 0 | 0
13:00 | 2264 | 821 | 422 | 0 | 86 | 1320.95 | 80 | 3932 | 415.89 | 16 | 145 | 0 | 0 | 0 | 0
13:30 | 2245 | 756 | 413 | 0 | 82 | 1272.42 | 80 | 3961.5 | 399.47 | 8.5 | 146 | 0 | 0 | 0 | 0
14:00 | 2226 | 691 | 404 | 0 | 78 | 1223.89 | 80 | 3991 | 383.05 | 1 | 147 | 0 | 0 | 0 | 0
14:30 | 2287 | 706.5 | 413 | 0 | 85 | 1191.445 | 80 | 3858 | 303.59 | 9 | 137 | 0 | 0 | 0 | 0
15:00 | 2348 | 722 | 422 | 0 | 92 | 1159 | 80 | 3725 | 224.13 | 17 | 127 | 0 | 0 | 0 | 0
15:30 | 2383 | 754 | 422 | 0 | 95 | 1111.5 | 80 | 3646 | 165.98 | 17 | 127 | 0 | 0 | 0 | 0
16:00 | 2418 | 786 | 422 | 0 | 98 | 1064 | 80 | 3567 | 107.83 | 17 | 127 | 0 | 0 | 0 | 0
16:30 | 2478 | 804 | 422 | 0 | 99 | 1116 | 80 | 3713 | 59.675 | 30 | 188.25 | 0 | 0 | 0 | 0
17:00 | 2538 | 822 | 422 | 0 | 100 | 1168 | 80 | 3859 | 11.52 | 43 | 249.5 | 0 | 0 | 0 | 0
17:30 | 2643 | 820.5 | 422 | 0 | 98 | 1307 | 80 | 4065 | 5.76 | 49 | 439.75 | 0 | 0 | 0 | 0
18:00 | 2748 | 819 | 422 | 0 | 96 | 1446 | 80 | 4271 | 0 | 55 | 630 | 0 | 0 | 0 | 0
18:30 | 2652.5 | 823.5 | 422 | 0 | 96 | 1448 | 80 | 4332.5 | 0 | 31.5 | 799 | 0 | 0 | 0 | 0
19:00 | 2557 | 828 | 422 | 0 | 96 | 1450 | 80 | 4394 | 0 | 8 | 968 | 0 | 0 | 0 | 0
19:30 | 2546 | 769 | 422 | 0 | 94 | 1455 | 80 | 4402 | 0 | 0 | 986 | 0 | 0 | 0 | 0
20:00 | 2555 | 803 | 421 | 0 | 88 | 1448 | 80 | 4405 | 0 | 0 | 823 | 0 | 0 | 0 | 0
20:30 | 2577 | 796 | 421.5 | 0 | 89 | 1448 | 80 | 4415 | 0 | 0 | 687.75 | 0 | 0 | 0 | 0
21:00 | 2599 | 789 | 422 | 0 | 90 | 1448 | 80 | 4425 | 0 | 0 | 552.5 | 0 | 0 | 0 | 0
21:30 | 2583 | 805.5 | 422 | 0 | 87 | 1450.5 | 83 | 4418.5 | 0 | 0 | 378.75 | 0 | 0 | 0 | 0
22:00 | 2567 | 822 | 422 | 0 | 84 | 1453 | 86 | 4412 | 0 | 0 | 205 | 0 | 0 | 0 | 0
22:30 | 2508.5 | 800 | 422 | 0 | 82 | 1388.5 | 86 | 4224.5 | 0 | 0 | 131.5 | 0 | 0 | 0 | 0
23:00 | 2450 | 778 | 422 | 0 | 80 | 1324 | 86 | 4037 | 0 | 0 | 58 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-12-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 421 | 05:00 | 395 | 13:00 | Meghnaghat | 426 | 04:00 | 402 | 13:00
Ashuganj | 416 | 6:00 | 398 | 13:00 | Payra | 420 | 03:00 | 407 | 13:00
Bhulta | 411 | 05:00 | 390 | 13:00 | Rahanpur | 420 | 05:00 | 397 | 18:00
Bibiana | 408 | 04:00 | 393 | 13:00 | Rampal | 417 | 04:00 | 398 | 13:00
BIPTC | 407 | 04:00 | 396 | 11:00
Bogura | 417 | 05:00 | 388 | 18:00
Gopalganj | 420 | 04:00 | 397 | 13:00
Kaliakoir | 412 | 05:00 | 386 | 12:00
Korerhat | 422 | 04:00 | 400 | 13:00
Madunaghat | 416 | 06:00 | 401 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 04:00 | 229 | 13:00 | Kachua | 240 | 03:00 | 230 | 13:00
AKSML | 241 | 01:00 | 230 | 12:00 | Kaliakoir | 248 | 04:00 | 232 | 12:00
Aminbazar | 244 | 05:00 | 229 | 13:00 | Keranigonj | 245 | 05:00 | 227 | 13:00
Ashuganj | 242 | 05:00 | 230 | 13:00 | Khulna(S) | 246 | 04:00 | 232 | 13:00
Ashuganj-400 | 242 | 05:00 | 230 | 13:00 | Korerhat | 242 | 05:00 | 231 | 13:00
Baghabari | 240 | 04:00 | 230 | 18:00 | Madunaghat | 241 | 05:00 | 231 | 14:00
Barapukuria | 233 | 05:00 | 216 | 08:00 | Madunaghat-400 | 242 | 05:00 | 231 | 13:00
Barapukuria-230 | 233 | 05:00 | 216 | 08:00 | Maniknagar | 242 | 02:00 | 230 | 13:00
Barishal | 249 | 05:00 | 237 | 13:00 | Meghnaghat | 246 | 03:00 | 235 | 14:00
Bheramara | 239 | 04:00 | 224 | 08:00 | Meghnaghat-400 | 243 | 04:00 | 229 | 13:00
Bhulta | 246 | 05:00 | 231 | 13:00 | Mirsorai | 244 | 02:00 | 231 | 13:00
Bibiana | 240 | 04:00 | 231 | 13:00 | Rajshahi | 240 | 05:00 | 223 | 08:00
BIPTC | 240 | 05:00 | 223 | 08:00 | Rampal | 241 | 03:00 | 228 | 18:00
Bogura | 244 | 05:00 | 229 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 244 | 05:00 | 226 | 18:00 | Rampura | 246 | 05:00 | 232 | 13:00
Borhanuddin | 249 | 06:00 | 241 | 13:00 | Shikalbaha | 240 | 03:00 | 229 | 16:00
BSRM | 245 | 06:00 | 231 | 13:00 | Shyampur | 243 | 05:00 | 227 | 13:00
Cumilla(N) | 242 | 04:00 | 230 | 13:00 | Siddhirganj | 242 | 03:00 | 231 | 13:00
Faridpur | 250 | 04:00 | 236 | 13:00 | Sirajgonj | 248 | 05:00 | 235 | 18:00
Fenchuganj | 242 | 04:00 | 231 | 13:00 | Sreepur | 240 | 05:00 | 226 | 18:30
Feni | 244 | 04:00 | 230 | 13:00 | Tongi | 242 | 04:00 | 231 | 15:00
Ghorashal | 245 | 01:00 | 234 | 11:00
Ghorashal-230 | 237 | 06:00 | 215 | 09:00
Gopalganj | 249 | 04:00 | 235 | 13:00
GPH | 243 | 04:00 | 231 | 13:00
Haripur | 243 | 04:00 | 231 | 13:00
Hasnabad | 243 | 06:00 | 227 | 13:00
Hathazari | 241 | 04:00 | 230 | 13:00
Ishurdi | 242 | 05:00 | 226 | 08:00
Jhenaidah | 242 | 05:00 | 226 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 129 | 13:00 | Laksam | 146 | 06:00 | 136 | 13:00
Agargaon | 140 | 01:00 | 128 | 13:00 | Lakshmipur | 137 | 02:00 | 130 | 13:00
Agrabad | 140 | 04:00 | 132 | 16:00 | Lalbag | 141 | 02:00 | 128 | 13:00
AKS | 136 | 01:00 | 131 | 14:00 | Lalmonirhat | 131 | 00:00 | 123 | 13:00
Aminbazar | 139 | 03:00 | 130 | 12:00 | Madanganj | 140 | 02:00 | 131 | 13:00
Amnura | 138 | 00:00 | 128 | 08:00 | Madaripur | 141 | 03:00 | 136 | 13:00
Ashuganj | 144 | 03:00 | 138 | 17:00 | Madartek | 137 | 06:00 | 128 | 13:00
Bagerhat | 136 | 04:00 | 124 | 18:00 | Madunaghat | 141 | 02:00 | 135 | 15:00
Bajitpur | 139 | 04:00 | 131 | 13:00 | Magura | 139 | 05:00 | 128 | 18:00
Bakerganj | 138 | 05:00 | 133 | 12:00 | Mahasthangarh | 139 | 05:00 | 130 | 18:00
Bakulia | 141 | 05:00 | 133 | 14:00 | Maijdee | 137 | 02:00 | 130 | 13:00
Banani | 138 | 03:00 | 129 | 13:00 | Manikganj | 136 | 02:00 | 126 | 14:00
Bangabhaban | 140 | 01:00 | 131 | 13:00 | Maniknagar | 141 | 02:00 | 132 | 13:00
Barapukuria | 140 | 04:00 | 129 | 08:00 | Matarbari | 135 | 08:00 | 119 | 18:00
Barguna | 137 | 00:00 | 133 | 13:00 | Matuail | 143 | 03:00 | 133.6 | 13:00
Barishal | 142 | 04:00 | 136 | 13:00 | Metrorail_Motijheel | 142 | 07:00 | 132 | 13:00
Barishal-230 | 144 | 04:00 | 136 | 13:00 | Metrorail_Uttara | 140 | 05:00 | 129 | 14:00
Baroaulia | 141 | 05:00 | 133 | 14:00 | Millgate | 141 | 03:00 | 129 | 12:00
Baroirhat | 137 | 00:00 | 132 | 13:00 | Mirpur | 140 | 04:00 | 128 | 13:00
Bashundhara | 138 | 04:00 | 129 | 13:00 | Mirzapur | 140 | 05:00 | 132 | 08:00
BashundharaCement | 140 | 02:00 | 133 | 14:00 | Mithapukur | 137 | 05:00 | 127 | 18:00
Beanibazar | 136 | 01:00 | 132 | 13:00 | MI_Cement | 138.9 | 05:00 | 124 | 13:00
Benapole | 137 | 04:00 | 120 | 18:00 | Modern | N/A | N/A | N/A | N/A
Bhaluka | 137 | 05:00 | 126 | 18:00 | Mogbazar | 140 | 04:00 | 130 | 13:00
Bhandaria | 142 | 05:00 | 135 | 13:00 | Mongla | 138 | 04:00 | 126 | 18:00
Bhangura | 141 | 03:00 | 132 | 18:00 | Motijheel | 140 | 01:00 | 131 | 13:00
Bheramara | 140 | 04:00 | 130 | 08:00 | Muktagacha | 136 | 15:00 | 127 | 8:00
Bheramara(GK) | 139 | 04:00 | 130 | 08:00 | Munshiganj | 141 | 02:00 | 131 | 13:00
Bhulta | 133 | 03:00 | 128 | 13:00 | Muradnagar | 141 | 02:00 | 133 | 12:00
Bog-Sherpur | 139 | 04:00 | 130 | 18:00 | Mymensingh | 139 | 15:00 | 121 | 18:00
Bogura | 139 | 06:00 | 132 | 17:00 | Naogaon | 136 | 06:00 | 125 | 18:00
Bogura-230 | 139 | 04:00 | 131 | 18:00 | Narail | 139 | 04:00 | 126 | 18:00
Brahmanbaria | 138 | 06:00 | 130 | 20:00 | Narinda | 141 | 02:00 | 132 | 13:00
Cantonment | 141 | 01:00 | 127 | 13:00 | Narshingdi | 141 | 05:00 | 128 | 18:00
Chandina | 143 | 04:00 | 135 | 13:00 | Natore | 138 | 03:00 | 128 | 18:00
Chandpur | 140 | 09:00 | 136 | 13:00 | Nawabganj | 139 | 02:00 | 129 | 12:00
Chandraghona | 140 | 01:00 | 134 | 13:00 | Netrakona | 130 | 03:00 | 118 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 139 | 04:00 | 133 | 12:00 | New | 142 | 04:00 | 131 | 14:00
Charsaidpur | 143 | 05:00 | 132 | 13:00 | Niamatpur | 140 | 01:00 | 132 | 18:00
Chauddagram | 141 | 04:00 | 132 | 13:00 | Noapara | 137 | 05:00 | 122 | 18:00
Chhatak | 136 | 04:00 | 131 | 11:00 | Pabna | 140 | 04:00 | 131 | 08:00
Chowmuhani | 137 | 05:00 | 125 | 13:00 | Palashbari | 135 | 05:00 | 124 | 18:00
Chuadanga | 140 | 04:00 | 126 | 13:00 | Panchagarh | 140 | 04:00 | 125 | 08:00
Coxsbazar | 134 | 09:00 | 119 | 18:00 | Patiya | 139 | 08:00 | 133 | 13:00
Cumilla(N) | 143 | 05:00 | 135 | 12:00 | Patuakhali | 137 | 03:00 | 132 | 14:00
Cumilla(S) | 141 | 04:00 | 126 | 16:00 | Payra | 138 | 03:00 | 134 | 12:00
Daganbhuiyan | 140 | 06:00 | 130 | 13:00 | PHP | 139 | 02:00 | 130 | 13:00
Daudkandi | 140 | 02:00 | 132 | 13:00 | Postogola | 139 | 04:00 | 126 | 13:00
DhakaUniversity | 137 | 04:00 | 129 | 13:00 | Purbachal | 138 | 05:00 | 129 | 13:00
Dhamrai | 143 | 05:00 | 133 | 12:00 | Purbasadipur | 132 | 04:00 | 124 | 17:00
Dhanmondi | 143.6 | 06:00 | 134.5 | 13:00 | Rahanpur | 140 | 01:00 | 134 | 18:00
Dohazari | 137 | 06:00 | 130 | 17:00 | Rahanpur-400 | 141 | 03:00 | 133 | 18:00
Faridpur | 142 | 06:00 | 134 | 13:00 | Rahim | 141 | 02:00 | 133 | 13:00
Fatullah | 141 | 04:00 | 124 | 13:00 | Rajbari | 143 | 04:00 | 134 | 13:00
Fenchuganj | 141 | 05:00 | 136 | 11:00 | Rajendrapur | 139 | 01:00 | 123 | 12:00
Feni | 137 | 02:00 | 129 | 12:00 | Rajshahi | 138 | 05:00 | 130 | 08:00
Feni-230 | 139 | 02:00 | 131 | 13:00 | Rajshahi-230 | 138 | 04:00 | 129 | 08:00
Ghatail | 134 | 15:00 | 126 | 08:00 | Ramganj | 139 | 06:00 | 133 | 16:00
Ghorashal | 138 | 02:00 | 132 | 13:00 | Rampur | 140 | 02:00 | 133 | 13:00
Goalpara | 140 | 06:00 | 129 | 18:00 | Rampura | 138 | 05:00 | 130 | 12:00
Gollamari | 138 | 04:00 | 129 | 18:00 | Rangamati | 140 | 03:00 | 134 | 13:00
Gopalganj | 141 | 04:00 | 132 | 18:00 | Rangpur | 137 | 05:00 | 127 | 13:00
Gopalganj-400 | 144 | 03:00 | 136 | 13:00 | Ruppur | 140 | 04:00 | 131 | 11:00
Gulshan | 137 | 04:00 | 128 | 13:00 | Saidpur | 134 | 02:00 | 125 | 08:00
Halishahar | 141 | 06:00 | 133 | 13:00 | Satkhira | 136 | 04:00 | 118 | 18:00
Haripur | 143 | 04:00 | 133 | 13:00 | Satmasjid | 140 | 01:00 | 128 | 14:00
HaripurSBU | 143 | 04:00 | 130 | 22:00 | Savar | 138 | 02:00 | 127 | 14:00
Hasnabad | 138 | 00:00 | 126 | 12:00 | SevenRings | 139 | 04:00 | 128 | 17:00
Hathazari | 142 | 04:00 | 135 | 13:00 | ShahCement | 143 | 05:00 | 132 | 13:00
Hatirjheel | 138 | 05:00 | 129 | 13:00 | Shahjadpur | 141 | 04:00 | 136 | 11:00
Ishurdi | 142 | 05:00 | 132 | 08:00 | Shahjibazar | 138 | 06:00 | 132 | 13:00
Jaldhaka | 134 | 06:00 | 122 | 08:00 | Shahmirpur | 140 | 06:00 | 134 | 14:00
Jamalpur | 139 | 15:00 | 118 | 08:00 | Shariatpur | 143 | 04:00 | 134 | 14:00
Jashore | 137 | 03:00 | 122 | 18:00 | Sherpur | 135 | 15:00 | 115 | 08:00
Jhenaidah | 139 | 06:00 | 114 | 18:00 | Shikalbaha | 129 | 01:00 | 123 | 14:00
Jhenaidah-230 | 141 | 05:00 | 129 | 13:00 | Shikalbaha-230 | 141 | 02:00 | 135 | 13:00
Joydebpur | 135 | 00:00 | 127 | 17:00 | Shitalakhya | 138.8 | 05:00 | 123.6 | 13:00
Joypurhat | 136 | 04:00 | 127 | 09:00 | Sholosohor | 141 | 06:00 | 134 | 13:00
Juldah | 140 | 05:00 | 134 | 15:00 | Shyampur | 140 | 05:00 | 128 | 13:00
Kabirpur | 141 | 03:00 | 129 | 12:00 | Shyampur-230 | 141 | 03:00 | 131 | 13:00
Kachua | 143 | 03:00 | 136 | 13:00 | Siddhirganj | 142 | 02:00 | 133 | 13:00
Kaliakoir | 144 | 03:00 | 134 | 12:00 | Sirajganj | 139 | 04:00 | 130 | 17:00
Kallyanpur | 138 | 00:00 | 129 | 14:00 | Sonargaon | 143 | 05:00 | 132 | 12:00
Kalurghat | 140 | 03:00 | 134 | 12:00 | Sreemongol | 138 | 05:00 | 132 | 17:00
Kamrangirchar | 140 | 05:00 | 129 | 13:00 | Sreepur | 141 | 05:00 | 129 | 18:30
Kaptai | 142 | 2:00 | 137 | 16:00 | Srinagar | 140 | 03:00 | 128 | 13:00
Kasba | 142 | 05:00 | 132 | 13:00 | SSM | 142 | 03:00 | 140 | 00:00
Kazla | 140 | 03:00 | 131 | 13:00 | Sunamganj | 135 | 06:00 | 130 | 13:00
Keranigonj | 140 | 04:00 | 129 | 13:00 | Sylhet | 137 | 05:00 | 132 | 12:00
Khagrachori | 140 | 04:00 | 133 | 13:00 | Sylhet-132 | 136 | 00:00 | 133 | 12:00
Khulna | 136 | 04:00 | 127 | 18:00 | Tangail | 135 | 04:00 | 127 | 08:00
Khulna(S) | 138 | 04:00 | 130 | 13:00 | Taraganj | 136 | 04:00 | 123 | 15:00
Khulshi | 139 | 06:00 | 131 | 14:00 | Tasnim | 142 | 03:00 | 132 | 13:00
Kishoreganj | 136 | 03:00 | 128 | 13:00 | Thakurgaon | 138 | 04:00 | 122 | 08:00
Kodda | 138 | 01:00 | 126 | 12:00 | TK | 140 | 05:00 | 135 | 13:00
KSRM | 141 | 05:00 | 133 | 18:30 | Tongi | 142 | 04:00 | 132 | 15:00
Kulaura | 140 | 04:00 | 134 | 13:00 | Ullahpara | 140 | 05:00 | 131 | 17:00
Kurigram | 134 | 04:00 | 121 | 08:00 | Ullon | 138 | 06:00 | 129 | 14:00
Kushtia | 137 | 02:00 | 120 | 18:30 | Uttara | 140 | 03:00 | 130 | 12:00
Zigatola | 140 | 04:00 | 129 | 13:00 | UttaraNew | 140 | 05:00 | 128 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division