## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-01-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-01-2026 | during | 02-01-2026 | during | 02-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 366 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 225 | 225 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 300 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 67 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 33.7 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 29 | 7 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 2 | 17 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 365 | 390 | 583 | 583 | 524 | 524 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6667.111 | 1153 | 1368.7 | 5364.35 | 5336.35 | 2794.33 | 2766.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 46 | 46 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 160 | 173 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 40 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 10 | 10 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 21 | 35 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.31 | 0 | 3.04 | 0 | 3.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 45 | 45 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 20 | 20 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 840 | 1150 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 6 | 5 | 16 | 5 | 16 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 745 | 745 | 625 | 625 | 625 | 625 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1839.31 | 2155 | 3397.9 | 3430.86 | 2935.54 | 2968.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 330 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 360 | 325 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 40 | 46.7 | 46.7 | 0 | 0 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 46 | 55 | 55 | 0 | 0 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 7 | 38 | 195 | 195 | 195 | 195 | Transformer overload
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 110 | 109 | 163 | 163 | 115 | 115 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 92 | 100 | 84 | 76 | 110 | 110 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 11 | 20.84 | 20.84 | 20.84 | 20.84 | Machine Schedule Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 31 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1075 | 1076 | 2474.9 | 2416.9 | 1898.39 | 1848.39
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-01-2026 | during | 02-01-2026 | during | 02-01-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 128 | 166 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 57 | 60 | 60 | 60 | 60 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 11 | 19 | 20 | 20 | 20 | 20 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 8.93 | 0 | 20 | 0 | 20 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 212.93 | 259 | 336.1 | 314 | 326.1 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 50 | 60 | 60 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 34 | 0 | 113 | 113 | 113 | 113 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 84 | 84 | 84 | 84 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 159 | 158 | 158 | 158 | 158 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 719 | 698 | 852 | 852 | 818 | 818
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 892 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 787 | 900 | 1148.28 | 1148.28 | 1108 | 1108 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 1757 | 1792 | 3495.28 | 3420.28 | 2290.1 | 2215.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 256 | 345 | 622 | 622 | 622 | 622 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 140 | 140 | 136 | 136 | 136 | 136 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1085.32 | 350 | 455 | 605 | 605 | 575 | 575 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 181 | 280 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2699.32 | 1147.54 | 1440 | 2150 | 2150 | 1967 | 1967
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 53.17 | 0 | 53.17 | 0 | 53.17 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 192 | 214 | 214 | 194 | 194 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.13 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 842.07 | 1162.52 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.42 | 0 | 40 | 0 | 40 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1638.79 | 1768.52 | 3117.14 | 2918.87 | 2505.88 | 2307.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 3.2 | 0 | 3.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 12 | 0 | 12 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 113 | 0 | 115.66 | 0 | 115.66 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 141.1 | 35 | 378.86 | 248 | 358.86 | 228
System Total |  |  |  |  | 28823.2 | 28382.248 | 9683.67 | 10592.22 | 21566.53 | 21087.26 | 15894.2 | 15422.93
Forecast Scenario (02-01-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8700 |  | 0 |  | 8700
|  |  |  | 1:00 | 8220 |  | 0 |  | 8220
|  |  |  | 2:00 | 7600 |  | 0 |  | 7600
|  |  |  | 3:00 | 7190 |  | 0 |  | 7190
|  |  |  | 4:00 | 6890 |  | 0 |  | 6890
|  |  |  | 5:00 | 6890 |  | 0 |  | 6890
|  |  |  | 6:00 | 7080 |  | 0 |  | 7080
|  |  |  | 7:00 | 7120 |  | 0 |  | 7120
|  |  |  | 8:00 | 7910 |  | 0 |  | 7910
|  |  |  | 9:00 | 8350 |  | 0 |  | 8350
|  |  |  | 10:00 | 8430 |  | 0 |  | 8430
|  |  |  | 11:00 | 8680 |  | 0 |  | 8680
|  |  |  | 12:00 | 9390 |  | 0 |  | 9390
|  |  |  | 13:00 | 10300 |  | 0 |  | 10300
|  |  |  | 14:00 | 8720 |  | 0 |  | 8720
|  |  |  | 15:00 | 7890 |  | 0 |  | 7890
|  |  |  | 16:00 | 7650 |  | 0 |  | 7650
|  |  |  | 17:00 | 8040 |  | 0 |  | 8040
|  |  |  | 18:00 | 9390 |  | 0 |  | 9390
|  |  |  | 18:30 | 9420 |  | 0 |  | 9420
|  |  |  | 19:00 | 9480 |  | 0 |  | 9480
|  |  |  | 19:30 | 9350 |  | 0 |  | 9350
|  |  |  | 20:00 | 9540 |  | 0 |  | 9540
|  |  |  | 21:00 | 9520 |  | 0 |  | 9520
|  |  |  | 22:00 | 9190 |  | 0 |  | 9190
|  |  |  | 23:00 | 8610 |  | 0 |  | 8610
Probable Maximum Temperature: |  |  | 24.20°C
Probable Maximum Demand at Day Peak: |  |  | 9390.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 9540.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9540.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 200.78 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:49 hrs on 02-01-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-01-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9683.67 | MW | 12:00 Hr. | Energy Generated |  |  | 216.8221 |  | MKWHr.
| Day Peak Demand |  |  | 9683.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 10592.22 | MW | 18:00 Hr. | Energy Demand |  |  | 216.8221 |  | MKWHr.
| Evening Peak Demand |  |  | 10592.22 | MW | 18:00 Hr. | Maximum Temperature |  |  | 23.4 |  | °C
| Minimum Generation of the Day |  |  | 6599.78 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 701.35 |  | MMCFD
| Maximum Generation of the Day |  |  | 10592.22 | MW | 18:00 Hr. | Production Cost per KWHr |  |  | 5.508 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 23.4872 | 0 | 2.2583 | 0 | 0 | 0.18053 | 0 | 0 | 25.9261 | Gas | 89.9615 | Gas | 318050264.76
| Chattogram Zone |  |  | 4.5206 | 36.1945 | 0 | 0 | 1.1007 | 0.11868 | 0 | 0.33408 | 42.2686 | Coal | 77.4981 | Coal | 515166904.2168
| Cumilla Zone |  |  | 21.2337 | 0 | 0 | 0 | 0 | 0.25697 | 1.9277 | 0 | 23.4184 | HFO | 3.4572 | HFO | 64802270.58
| Mymensingh Zone |  |  | 3.313 | 0 | 1.1335 | 0 | 0 | 0.08845 | 0 | 0 | 4.5349 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 16.5103 | 0 | 0 | 0 | 0 | 0.01654 | 0 | 0 | 16.5269 | Hydro | 1.1007 | Hydro | 110070
| Khulna Zone |  |  | 0 | 20.0727 | 0 | 0 | 0 | 0.48168 | 17.7469 | 0 | 38.3013 | Solar | 3.1632 | Solar | 49478358.814
| Barishal Zone |  |  | 8.1781 | 21.2308 | 0 | 0 | 0 | 0.003213 | 0 | 0 | 29.4121 | Import | 41.3073 | Import | 241736386.4
| Rajshahi Zone |  |  | 12.7186 | 0 | 0 | 0 | 0 | 1.2042 | 21.6327 | 0 | 35.5555 | Wind | 0.33408 | Wind | 4914316.8
| Rangpur Zone |  |  | 0 | 0 | 0.065316 | 0 | 0 | 0.81299 | 0 | 0 | 0.8783
| Total |  |  | 89.9615 | 77.4981 | 3.4572 | 0 | 1.1007 | 3.1632 | 41.3073 | 0.33408 | 216.8221
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 318050264.76 |  | Hydro | 110070
|  |  |  | Coal | 515166904.2168 |  | Solar | 49478358.814
|  |  |  | HFO | 64802270.58 |  | Import | 241736386.4
|  |  |  | HSD | 0 |  | Wind | 4914316.8
[5 empty] | Total: | 119,42,58,571 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.7469 | Peak Hr Flow | 892.00 MW at 18:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33016490.92 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.6327 | Peak Hr Flow | 1162.52 MW at 18:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1783 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.9277 | Peak Hr Flow | 100.00 MW at 18:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2012 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.3073 | Peak Hr Flow | 2154.52 MW at 18:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3812
|  |  |  | Chattogram |  | 0 |  | 1123
|  |  |  | Cumilla |  | 0 |  | 903
|  |  |  | Mymensingh |  | 0 |  | 863
|  |  |  | Sylhet |  | 0 |  | 403
|  |  |  | Khulna |  | 0 |  | 1283
|  |  |  | Barishal |  | 0 |  | 312
|  |  |  | Rajshahi |  | 0 |  | 979
|  |  |  | Rangpur |  | 0 |  | 766
|  |  |  | Total |  | 0 |  | 10444
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bheramara 410 MW CCPP GT |  |  | 278
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Bheramara 410 MW CCPP ST |  |  | 132
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 410
|  |  |  | Total Unavailable Capacity |  |  |  | 710
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 15:25 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to Ten dalta test
| 08:07 | 15:24 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to Ten dalta test
| 08:18 | 09:46 | Sonargaon 132/33kV S/S Tr-1 LT Scheduled S/D Due to Cable heat shrink of 33KV side | [7 empty] | 45.0MW load
|  |  | underground cable | [7 empty] | interrup.
| 08:19 | 09:46 | Sonargaon 132/33kV S/S Tr-1 HT Scheduled S/D Due to Cable heat shrink of 33KV side | [7 empty] | 45.0MW load
|  |  | underground cable. | [7 empty] | interrup.
| 08:36 | 18:33 | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to OPGW
Stringing work.
| 08:39 | 17:22 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Scheduled S/D Due to Annual Maintenance
| 08:45 | 13:35 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to Annual maintenance
| 08:45 | 13:35 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Annual maintenance
| 08:47 | 16:58 | Baghabari 230/132kV S/S T-2 Bank HT Forced S/D Due to T-02 Bank এর B-ফেজের Oil লিকেজ বন্ধ
করার জন্য।
| 08:47 | 16:58 | Baghabari 230/132kV S/S T-2 Bank LT Forced S/D Due to T-02 Bank এর B-ফেজের Oil লিকেজ বন্ধ
করার জন্য।
| 08:49 | 16:02 | Benapole-Jashore 132 kV Ckt-2 Scheduled S/D from Benapole 132/33kV end Due to annual
maintenance work. and from Jashore 132/33kV end Due to Annual Maintenance
| 08:52 | 16:08 | Gulsan-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
Maintenance and from Gulshan 132/33kVend.
| 08:55 | 15:02 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Deadline Checking and Disc Cleaning and from Keranigonj 230/132/33kV end Due to Annual
maintenance work
| 09:08 | 14:54 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to
Shutdown for annual maintenance and from Brahmanbaria 132/33kVend.
| 09:14 | 17:39 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Daganbhuiyan 132/33kV end Due to Deadline
Checkout and from Chowmuhani 132/33kV end Due to Annual Maintenance
| 09:18 | 18:51 | Tongi 230/132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to bus extension work by PSDC
| 09:31 | 14:24 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Scheduled S/D Due to DS maintenance work
| 09:32 | 17:53 | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end.
| 09:34 | 12:38 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Scheduled S/D Due to Shutdown taken by Shripur grid | [7 empty] | 30.0MW load
interrup.
| 09:35 | 17:40 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual | [7 empty] | 10.0MW load
|  |  | Maintenance | [7 empty] | interrup. Dohazari
132/33kV end
| 09:35 | 17:06 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Ghatail 132/33kV end Due to
annual maintenance
| 09:35 | 09:59 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Bus section -C and Mehendigonj feeder | [7 empty] | 30.0MW load
|  |  | source DS repair by BPBS-1 | [7 empty] | interrup.
| 09:35 | 10:58 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Bus section -C and Mehendigonj feeder | [7 empty] | 30.0MW load
|  |  | source DS repair by BPBS-1 | [7 empty] | interrup.
| 09:36 | 12:36 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Scheduled S/D Due to DS Repair
| 09:36 | 17:05 | Tangail 132/33kV S/S RPCL-2 Scheduled S/D Due to Schedule S/D
| 09:38 | 14:53 | Rampura 230/132kV S/S Auto Transformer - 03 HT Scheduled S/D Due to shutdown taken by
SPMD to relay work.
| 09:40 | 14:54 | Rampura 230/132kV S/S Auto Transformer - 03 LT Scheduled S/D Due to shutdown taken by
SPMD to relay work.
| 09:40 | 18:11 | Chapai 132/33kV S/S T-2 (415T) HT Project Work S/D Due to T-02 CB change S/D exact
time 28/12/2025 at 9:40
| 09:45 | 16:12 | Bogura-Mahasthangar (New)) 132 kV Ckt-2 Scheduled S/D from Mahasthangarh 132/33kV end Due
to Due to Annual Maintenance work. and from Bogura 132/33kV end Due to ALDC shutdown.
| 09:45 | 16:02 | Madartek-Rampura 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to shutdown
taken by NLDC to Madertek end SS works.
| 09:50 | 17:38 | Baghabari-Sirajganj 230 kV Ckt-2 Scheduled S/D from Sirajgonj 230 end Due to Annual
Maintenance and from Baghabari 230/132kV end Due to সিরাজগঞ্জ পান্তে কাজ করার জন্য।
| 09:58 | 17:33 | Tongi 230/132/33kV S/S 230 kV Bus-1 Scheduled S/D Due to Annual maintenance work
| 09:58 | 17:28 | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Only HV side shutdown CB-822B open
only
| 10:00 | 14:22 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Forced S/D Due to T3 33KV Redhot Maintenance
| 10:00 | 11:52 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to DS repair work.
| 10:01 | 14:22 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Forced S/D Due to T3 33KV Redhot Maintenance
| 10:08 | 12:47 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT Forced S/D Due to Due to High voltage in
B-Phase.
| 10:08 | 12:47 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Forced S/D Due to Due to High voltage in
B-Phase.
| 10:22 | 17:23 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual Maintenance
| 10:42 | 11:32 | BIPTC S/S 20DF24 Scheduled S/D Due to Corrective maintenance
| 11:06 | 13:28 | BIPTC S/S 10CF16 Scheduled S/D Due to for corrective maintenance
| 12:00 |  | Day peak generation: 9684 MW
| 12:08 |  | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to Sreepur Bay extension work at
busbar-01
| 12:09 |  | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Sreepur Bay extension work at
busbar-01
| 12:14 |  | Rajendrapur 132/33kV S/S 132 kV BUS-1 Project Work S/D Due to Sreepur Bay extension work
at busbar-01
| 13:05 | 15:25 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to None
| 13:16 | 14:02 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Project Work S/D Due to PSDC ATR-3
Installation work
| 13:20 | 17:45 | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintanance work
| 13:30 | 17:46 | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to Disc
Cleaning
| 14:15 |  | Kushiara 163MW CCPP GT tripped.
| 14:41 | 15:48 | Sonargaon 132/33kV S/S Tr-1 LT Scheduled S/D Due to PBS 33KV side heat shrink work of | [7 empty] | 45.0MW load
|  |  | underground cable. | [7 empty] | interrup.
| 14:41 | 15:47 | Sonargaon 132/33kV S/S Tr-1 HT Scheduled S/D Due to PBS 33KV side heat shrink work of | [7 empty] | 45.0MW load
|  |  | underground cable | [7 empty] | interrup.
| 14:44 | 16:01 | Kodda-Rajendrapur 132kV Ckt-1 Tripped from Rajendrapur 132/33kV end showing EF 67N | [7 empty] | 110.0MW load
|  |  | relays Due to Project work fault in Bus 1 & 2. Suspected mis operation in new bay | [7 empty] | interrup.
|  |  | extension part. | [7 empty] | Rajendrapur
132/33kV end
| 14:44 | 16:03 | Rajendrapur 132/33kV S/S MTR-1 HT Tripped showing No relay signal, only breaker trip due | [7 empty] | 48.0MW load
|  |  | to BBP trip signal relays Due to Project work fault in Bus 1 & 2. Suspected mis operation | [7 empty] | interrup.
in new bay extension part.
| 14:44 | 16:06 | Rajendrapur 132/33kV S/S MTR-3 HT Tripped showing No relay shown except BBP trip relays | [7 empty] | 62.0MW load
|  |  | Due to Project work fault in Bus 1 & 2. Suspected mis operation in new bay extension | [7 empty] | interrup.
part.
|  | 16:07 | Savar 132/33kV S/S T-1 HT is restored.
|  | 16:22 | Savar 132/33kV S/S T-1 LT is restored.
|  | 16:55 | Chattak-Sylhet 132 kV Ckt-1 is restored.
|  | 17:18 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 is restored.
| 18:00 |  | Day Peak Generation: 10591 MW.
|  | 18:02 | Aminbazar-Meghnaghat 400kV Ckt-2 is restored.
|  | 18:06 | Khulna (C) S/S Tr-2 415 T HT is restored.
|  | 18:06 | Daganbhuiyan 132/33kV S/S Transformer-2 HT is restored.
|  | 18:07 | Khulna (C) S/S Tr-2 415 T LT is restored.
| 20:05 | 20:42 | Ashuganj-Brahmanbaria 132kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Distance
Relay relays.
| 20:22 |  | Kushiara 163MW CCPP GT was sync.
| 23:13 |  | Siddhirganj 335 MW CCPP was shutdown due to the borescope inspection.
| 00:10 |  | Siddhirganj 230/132kV S/S 335MW EGCB 1 Scheduled S/D Due to emergency maintence work
perform by egcb side
| 00:22 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2
| 01:01 |  | Meghnaghat-Shyampur 230kV Ckt-2 Tripped from Meghnaghat 400/230kV end showing DFDR
relays Due to None
| 03:29 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- ST
| 04:12 | 04:24 | Meghnaghat-Shyampur 230kV Ckt-1 Tripped from Meghnaghat 400/230kV end showing DFDR | [7 empty] | 290.0MW load
|  |  | relays Due to None | [7 empty] | interrup.
Meghnaghat
400/230kV end
| 05:00 |  | Minimum Generation = 6976 MW.
| 07:10 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Forced S/D Due to due to intermittent flashing
at R-phase CT.
| 07:12 |  | Mymensingh 132/33kV S/S 50 MW Solar Plant Scheduled S/D Due to Project work.
| 07:13 |  | Khulna (C) S/S Tr-2 415 T HT Project Work S/D Due to G TO G project work piling.
| 07:13 |  | Khulna (C) S/S Tr-2 415 T LT Project Work S/D Due to G TO G project work piling G.
| 07:20 |  | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to Disc
Cleaning at Tower No 22 & 23
| 07:22 |  | Rampura 230/132kV S/S Auto Transformer - 02 LT Scheduled S/D
| 07:23 |  | Rampura 230/132kV S/S Auto Transformer - 02 HT Scheduled S/D
| 07:23 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to OPGW
wire stringing.
| 07:46 |  | Mymensingh 132/33kV S/S Bus A Scheduled S/D Due to Project work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-01-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 366 | 7952400 | FGMO, Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 47016 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 5841584 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 67 | 468576 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.7 | 186516 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 145710 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 7 | 408600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 359640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 188928 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | -
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 180526 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Schedule Outage Ongoing
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 390 | 8925001 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1221600 | -
Dhaka Area Total |  |  |  |  | 6667.111 | 1368.7 | 25926097
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 101115 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1100700 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 173 | 3953230 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 567360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17563 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 20034543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 334080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 745 | 16160000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2155 | 42268591
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 206000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8071400 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 325 | 7654200 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 840600 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 864480 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 38 | 451636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 827691 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 109 | 2081083 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 100 | 1927680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 236630 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 256973 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1076 | 23418373
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 166 | 3312960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 57 | 602400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 382800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 79250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 148320 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 259 | 4534930
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 16540 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 966000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 1086600 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 530673 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 611232 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1311360 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 159 | 4394550 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 299424 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7310500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 698 | 16526879
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 17746909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 481680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 900 | 20072726 | FGMO, plant availability zero
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1792 | 38301315
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 345 | 7047272 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2952000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1085.32 | 455 | 9798545.46 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5226080 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 4385000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3213 | -
Barishal Area Total |  |  |  |  | 2699.32 | 1440 | 29412110.46
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 294076 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 192 | 4169273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8549309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1162.52 | 21632727 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 316496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 566800 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 1768.52 | 35555501
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30138.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 65316 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 150687 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 632160 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 35 | 878301.72
Eastern Grid Total |  |  |  |  | 17398.245 | 5556.7 | 112674870
Western Grid Total |  |  |  |  | 10984.003 | 5035.52 | 104147228.18
National Grid Total |  |  |  |  | 28382.248 | 10592.22 | 216822098.18
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-01-2026
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7103.33 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3339.8 | MW
i) Dhaka area |  |  | 3811.73 |  | MW | i) Khulna area |  |  |  | 1283 | MW
ii) Chattogram area |  |  | 1122.6 |  | MW | ii) Barishal area |  |  |  | 312 | MW
iii) Cumilla area |  |  | 903 |  | MW | iii) Rajshahi area |  |  |  | 978.8 | MW
iv) Mymensingh area |  |  | 863 |  | MW | iv) Rangpur area |  |  |  | 766 | MW
v) Sylhet area |  |  | 403 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10443.13 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 94 | 13:00 | 133 | Netrakona | 104 | 18:30
2 | AKSML | 139 | 05:00 | 68 | Hathazari | 66 | 13:00 | 134 | New | 60 | 16:00
3 | Aftabnagar | 24 | 13:00 | 69 | Hatirjheel | 27 | 13:00 | 135 | Niamatpur | 51 | 13:00
4 | Agargaon | 77 | 14:00 | 70 | Ishurdi | 53 | 18:30 | 136 | Noapara | 38 | 18:00
5 | Agrabad | 36 | 18:00 | 71 | Jaldhaka | 57 | 18:00 | 137 | PHP | 8 | 19:30
6 | Amnura | 30 | 13:00 | 72 | Jamalpur | 89 | 18:00 | 138 | Pabna | 68 | 18:00
7 | Ashuganj | 60 | 13:00 | 73 | Jashore | 113 | 13:00 | 139 | Palashbari | 83 | 18:00
8 | BSRM | 185 | 18:30 | 74 | Jhenaidah | 96 | 18:00 | 140 | Panchagarh | 44 | 18:00
9 | Bagerhat | 64 | 18:30 | 75 | Joydebpur | 88 | 08:00 | 141 | Patiya | 6.7 | 22:00
10 | Bajitpur | 69 | 19:30 | 76 | Joypurhat | 43 | 18:30 | 142 | Patuakhali | 39 | 19:30
11 | Bakerganj | 0 | 00:00 | 77 | Juldah | 12 | 00:00 | 143 | Payra | 28 | 18:00
12 | Bakulia | 69 | 12:00 | 78 | KSRM | 30 | 09:00 | 144 | Postogola | 38 | 13:00
13 | Banani | 17.2 | 14:00 | 79 | Kabirpur | 147 | 18:00 | 145 | Purbachal | 19 | 18:00
14 | Bangabhaban | 9 | 11:00 | 80 | Kachua | 57 | 18:00 | 146 | Purbasadipur | 107 | 09:00
15 | Barapukuria | 47 | 19:00 | 81 | Kallyanpur | 69 | 12:00 | 147 | Rahanpur | 24 | 20:00
16 | Barguna | 14 | 18:00 | 82 | Kalurghat | 24 | 17:00 | 148 | Rahim | 31 | 10:00
17 | Barishal | 85 | 14:00 | 83 | Kamrangirchar | 59 | 13:00 | 149 | Rajbari | 61 | 18:00
18 | Barishal-230 | 66 | 18:00 | 84 | Kaptai | N/A | N/A | 150 | Rajendrapur | 118 | 19:30
19 | Baroaulia | 52 | 11:00 | 85 | Kasba | 22 | 13:00 | 151 | Rajshahi | 71 | 21:00
20 | Baroirhat | 64 | 13:00 | 86 | Kazla | 97 | 13:00 | 152 | Rajshahi-230 | 68 | 13:00
21 | Bashundhara | 113 | 13:00 | 87 | Keranigonj | 43 | 13:00 | 153 | Ramganj | 70 | 13:00
22 | BashundharaCement | 9 | 16:00 | 88 | Khagrachori | 24 | 18:00 | 154 | Rampur | 24 | 17:00
23 | Beanibazar | 42 | 18:00 | 89 | Khulna | 45 | 13:00 | 155 | Rangamati | 13 | 18:00
24 | Benapole | 50 | 19:00 | 90 | Khulshi | 155 | 21:00 | 156 | Rangpur | 110 | 18:00
25 | Bhaluka | 120 | 18:00 | 91 | Kishoreganj | 89 | 18:00 | 157 | Ruppur | 0.8 | 00:00
26 | Bhandaria | 38 | 13:00 | 92 | Kodda | 219 | 16:00 | 158 | SSM | 0 | 00:00
27 | Bhangura | 24 | 18:00 | 93 | Kulaura | 28 | 18:00 | 159 | Saidpur | 88 | 18:00
28 | Bheramara(GK) | 41 | 13:00 | 94 | Kurigram | 49 | 18:00 | 160 | Satkhira | 89 | 18:00
29 | Bhulta | 184 | 19:00 | 95 | Kushtia | 108 | 18:00 | 161 | Satmasjid | 73 | 13:00
30 | Bog-Sherpur | 54 | 18:00 | 96 | Laksam | 23 | 20:00 | 162 | Savar | 154 | 12:00
31 | Bogura | 105 | 18:30 | 97 | Lakshmipur | 27 | 15:00 | 163 | SevenRings | 14.67 | 20:00
32 | Borhanuddin | 65 | 19:30 | 98 | Lalbag | 51 | 18:00 | 164 | ShahCement | 16 | 19:30
33 | Brahmanbaria | 88 | 18:30 | 99 | Lalmonirhat | 43 | 18:00 | 165 | Shahjadpur | 53 | 18:00
34 | Cantonment | 82 | 13:00 | 100 | MI_Cement | 15.8 | 06:00 | 166 | Shahjibazar | 85 | 18:00
35 | Chandina | 20 | 09:00 | 101 | Madanganj | 42 | 12:00 | 167 | Shahmirpur | 36 | 18:00
36 | Chandpur | 50 | 18:00 | 102 | Madaripur | 73 | 13:00 | 168 | Shariatpur | 57 | 20:00
37 | Chandraghona | 26 | 18:00 | 103 | Madartek | 50 | 20:00 | 169 | Sherpur | 110 | 18:00
38 | Chapai | 47 | 07:00 | 104 | Madunaghat | 33 | 12:00 | 170 | Shikalbaha | 17.5 | 00:00
39 | Charsaidpur | 46 | 15:00 | 105 | Magura | 49 | 18:00 | 171 | Shitalakhya | 61.6 | 12:00
40 | Chauddagram | 43 | 19:30 | 106 | Mahasthangarh | 48 | 18:30 | 172 | Sholosohor | 28 | 10:00
41 | Chhatak | 23 | 18:00 | 107 | Maijdee | 25 | 18:00 | 173 | Shyampur | 138 | 12:00
42 | Chowmuhani | 107 | 18:30 | 108 | Manikganj | 90 | 21:00 | 174 | Siddhirganj | 87 | 14:00
43 | Chuadanga | 78 | 18:00 | 109 | Maniknagar | 48 | 13:00 | 175 | Sirajganj | 78 | 19:00
44 | Coxsbazar | 105 | 18:00 | 110 | Matarbari | 46 | 18:00 | 176 | Sonargaon | 118 | 19:00
45 | Cumilla(N) | 89 | 22:00 | 111 | Matuail | 43 | 12:00 | 177 | Sreemongol | 52 | 19:00
46 | Cumilla(S) | 103 | 14:00 | 112 | Metrorail_Motijheel | 16 | 18:00 | 178 | Sreepur | 84 | 18:00
47 | Daganbhuiyan | 0 | 00:00 | 113 | Metrorail_Uttara | 8 | 09:00 | 179 | Srinagar | 33 | 13:00
48 | Daudkandi | 112 | 19:00 | 114 | Millgate | 67 | 12:00 | 180 | Sunamganj | 39 | 18:00
49 | DhakaUniversity | 48 | 13:00 | 115 | Mirpur | 101 | 13:00 | 181 | Sylhet | 35 | 13:00
50 | Dhamrai | 96 | 15:00 | 116 | Mirsorai | 9 | 11:00 | 182 | Sylhet-132 | 77 | 18:00
51 | Dhanmondi | 72.4 | 14:00 | 117 | Mirzapur | 33 | 19:00 | 183 | TK | 19 | 18:00
52 | Dohazari | 67 | 18:00 | 118 | Mithapukur | 46 | 18:00 | 184 | Tangail | 120 | 18:00
53 | Faridpur | 117 | 18:00 | 119 | Modern | N/A | N/A | 185 | Taraganj | 16 | 08:00
54 | Fatullah | 88 | 12:00 | 120 | Mogbazar | 35.2 | 14:00 | 186 | Tasnim | 25 | 16:00
55 | Fenchuganj | 24 | 18:00 | 121 | Mongla | 26 | 18:00 | 187 | Thakurgaon | 79 | 18:00
56 | Feni | 67 | 18:00 | 122 | Motijheel | 25 | 13:00 | 188 | Tongi | 97 | 11:00
57 | GPH | 92 | 04:00 | 123 | Muktagacha | 26 | 08:00 | 189 | Ullahpara | 25 | 18:00
58 | Ghatail | 58 | 18:00 | 124 | Munshiganj | 70 | 20:00 | 190 | Ullon | 49 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Muradnagar | 23 | 18:00 | 191 | Uttara | 56 | 13:00
60 | Ghorashal-230 | 74 | 09:00 | 126 | Mymensingh | 135 | 19:30 | 192 | UttaraNew | 41 | 13:00
61 | Goalpara | 30 | 13:00 | 127 | Naogaon | 88 | 13:00 | 193 | Zigatola | 68 | 13:00
62 | Gollamari | 78 | 13:00 | 128 | Narail | 40 | 18:00
63 | Gopalganj | 80 | 18:30 | 129 | Narinda | 53 | 13:00
64 | Gulshan | 68 | 14:00 | 130 | Narshingdi | 134 | 20:00
65 | Halishahar | 36 | 10:00 | 131 | Natore | 103 | 18:30
66 | HaripurSBU | 85 | 00:00 | 132 | Nawabganj | 32.6 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-01-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 8270.25 | 0 |  | 8270.25
1:00 | 7718.04 | 0 |  | 7718.04
2:00 | 7244.76 | 0 |  | 7244.76
3:00 | 6888.95 | 0 |  | 6888.95
4:00 | 6626.96 | 0 |  | 6626.96
5:00 | 6599.78 | 0 |  | 6599.78
6:00 | 6944.56 | 0 |  | 6944.56
7:00 | 7677.61 | 0 |  | 7677.61
8:00 | 8638.99 | 0 |  | 8638.99
9:00 | 9459.43 | 0 |  | 9459.43
10:00 | 9112.21 | 0 |  | 9112.21
11:00 | 9294.54 | 0 |  | 9294.54
12:00 | 9683.67 | 0 |  | 9683.67
13:00 | 10330.39 | 0 |  | 10330.39
14:00 | 10157.11 | 0 |  | 10157.11
15:00 | 9243.48 | 0 |  | 9243.48
16:00 | 8849.51 | 0 |  | 8849.51
17:00 | 9344.22 | 0 |  | 9344.22
18:00 | 10592.22 | 0 |  | 10592.22
19:00 | 10563.07 | 0 |  | 10563.07
19:30 | 10552.07 | 0 |  | 10552.07
20:00 | 10478.39 | 0 |  | 10478.39
21:00 | 10260 | 0 |  | 10260
22:00 | 9891 | 0 |  | 9891
23:00 | 9305 | 0 |  | 9305
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-01-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4177 | 4093.25 | 8270.25 | DAILY GENERATION CURVE
00:30 | 4041.5 | 3952.645 | 7994.145
01:00 | 3906 | 3812.04 | 7718.04 | 01-01-2026
01:30 | 3783 | 3698.4 | 7481.4
02:00 | 3660 | 3584.76 | 7244.76
02:30 | 3611.5 | 3455.355 | 7066.855
03:00 | 3563 | 3325.95 | 6888.95
03:30 | 3527.5 | 3230.455 | 6757.955
04:00 | 3492 | 3134.96 | 6626.96
04:30 | 3441.5 | 3171.87 | 6613.37
05:00 | 3391 | 3208.78 | 6599.78
05:30 | 3471.5 | 3300.67 | 6772.17
06:00 | 3552 | 3392.56 | 6944.56
06:30 | 3870.05 | 3441.035 | 7311.085
07:00 | 4188.1 | 3489.51 | 7677.61
07:30 | 4373.94 | 3784.36 | 8158.3
08:00 | 4559.78 | 4079.21 | 8638.99
08:30 | 4708.235 | 4340.975 | 9049.21
09:00 | 4856.69 | 4602.74 | 9459.43
09:30 | 4786.5 | 4499.32 | 9285.82
10:00 | 4716.31 | 4395.9 | 9112.21
10:30 | 4744.495 | 4458.88 | 9203.375
11:00 | 4772.68 | 4521.86 | 9294.54
11:30 | 4885.96 | 4603.145 | 9489.105
12:00 | 4999.24 | 4684.43 | 9683.67
12:30 | 5200.47 | 4806.56 | 10007.03
13:00 | 5401.7 | 4928.69 | 10330.39
13:30 | 5343.42 | 4900.33 | 10243.75
14:00 | 5285.14 | 4871.97 | 10157.11
14:30 | 5119.22 | 4581.075 | 9700.295
15:00 | 4953.3 | 4290.18 | 9243.48
15:30 | 4809.645 | 4236.85 | 9046.495
16:00 | 4665.99 | 4183.52 | 8849.51
16:30 | 4835.365 | 4261.5 | 9096.865
17:00 | 5004.74 | 4339.48 | 9344.22
17:30 | 5280.72 | 4687.5 | 9968.22
18:00 | 5556.7 | 5035.52 | 10592.22
18:30 | 5382.5 | 5195.145 | 10577.645
19:00 | 5208.3 | 5354.77 | 10563.07
19:30 | 5288 | 5264.07 | 10552.07
20:00 | 5272 | 5206.39 | 10478.39
20:30 | 5268.5 | 5100.695 | 10369.195 |  | Executive Engineer
21:00 | 5265 | 4995 | 10260 |  | Network Operation Division
21:30 | 5224 | 4851.5 | 10075.5
22:00 | 5183 | 4708 | 9891
22:30 | 5008 | 4590 | 9598
23:00 | 4833 | 4472 | 9305

## En-Curve
QF-LDC-12
Date | 01-01-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2727 | 985 | 892 | 0 | 76 | 840.25 | 46 | 2680 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | DAILY ENERGY CURVE
00:30 | 2596.5 | 962 | 835.5 | 0 | 71 | 840.145 | 46 | 2618 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 01-01-2026
01:00 | 2466 | 939 | 779 | 0 | 66 | 840.04 | 46 | 2556 | 0 | 0 | 0 | 0 | 0 | 26 | 0
01:30 | 2336 | 877 | 716.5 | 0 | 63 | 842.4 | 46 | 2571 | 0 | 0 | 0 | 0 | 0 | 29.5 | 0 | Energy Generated | 216.8221 |  | MKWHr
02:00 | 2206 | 815 | 654 | 0 | 60 | 844.76 | 46 | 2586 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2171.5 | 784.5 | 516 | 0 | 61 | 843.855 | 46 | 2613 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | Total Energy Requirement | 216.8221 |  | MKWHr
03:00 | 2137 | 754 | 378 | 0 | 62 | 842.95 | 46 | 2640 | 0 | 0 | 0 | 0 | 0 | 29 | 0
03:30 | 2098.5 | 764 | 277.5 | 0 | 61 | 840.955 | 46 | 2640.5 | 0 | 0 | 0 | 0 | 0 | 29.5 | 0
04:00 | 2060 | 774 | 177 | 0 | 60 | 838.96 | 46 | 2641 | 0 | 0 | 0 | 0 | 0 | 30 | 0
04:30 | 2023.5 | 766 | 208.5 | 0 | 61 | 839.37 | 46 | 2642.5 | 0 | 0 | 0 | 0 | 0 | 26.5 | 0
05:00 | 1987 | 758 | 240 | 0 | 62 | 839.78 | 46 | 2644 | 0 | 0 | 0 | 0 | 0 | 23 | 0
05:30 | 2122 | 787.5 | 240 | 0 | 64 | 842.67 | 46 | 2654 | 0 | 0 | 0 | 0 | 0 | 16 | 0
06:00 | 2257 | 817 | 240 | 0 | 66 | 845.56 | 46 | 2664 | 0 | 0 | 0 | 0 | 0 | 9 | 0
06:30 | 2409 | 970.5 | 239.5 | 0 | 65 | 839.68 | 46 | 2728 | 3.905 | 0 | 0 | 0 | 0 | 9.5 | 0
07:00 | 2561 | 1124 | 239 | 0 | 64 | 833.8 | 46 | 2792 | 7.81 | 0 | 0 | 0 | 0 | 10 | 0
07:30 | 2650 | 1158.75 | 471.5 | 0 | 70 | 841.95 | 46 | 2858.5 | 48.1 | 0 | 5 | 0 | 0 | 8.5 | 0
08:00 | 2739 | 1193.5 | 704 | 0 | 76 | 850.1 | 46 | 2925 | 88.39 | 0 | 10 | 0 | 0 | 7 | 0
08:30 | 2728 | 1213 | 798 | 0 | 78 | 887.99 | 46 | 3094 | 147.22 | 26 | 24 | 0 | 0 | 7 | 0
09:00 | 2717 | 1232.5 | 892 | 0 | 80 | 925.88 | 46 | 3263 | 206.05 | 52 | 38 | 0 | 0 | 7 | 0
09:30 | 2647.5 | 1146 | 892 | 0 | 84 | 881.61 | 46 | 3211 | 261.71 | 52 | 57 | 0 | 0 | 7 | 0
10:00 | 2578 | 1059.5 | 892 | 0 | 88 | 837.34 | 46 | 3159 | 317.37 | 52 | 76 | 0 | 0 | 7 | 0
10:30 | 2576.5 | 1072.75 | 892 | 0 | 87 | 838.805 | 46 | 3163 | 369.32 | 76 | 76 | 0 | 0 | 6 | 0
11:00 | 2575 | 1086 | 892 | 0 | 86 | 840.27 | 46 | 3167 | 421.27 | 100 | 76 | 0 | 0 | 5 | 0
11:30 | 2651 | 1142.5 | 892 | 0 | 89 | 841.17 | 46 | 3163 | 470.435 | 104 | 85 | 0 | 0 | 5 | 0
12:00 | 2727 | 1199 | 892 | 0 | 92 | 842.07 | 46 | 3159 | 519.6 | 108 | 94 | 0 | 0 | 5 | 0
12:30 | 2747 | 1251.5 | 892 | 0 | 96 | 885.435 | 46 | 3293 | 543.095 | 116.5 | 130.5 | 0 | 0 | 6 | 0
13:00 | 2767 | 1304 | 892 | 0 | 100 | 928.8 | 46 | 3427 | 566.59 | 125 | 167 | 0 | 0 | 7 | 0
13:30 | 2727 | 1295 | 892 | 0 | 101 | 905.735 | 46 | 3426.5 | 521.515 | 125 | 199.5 | 0 | 0 | 4.5 | 0
14:00 | 2687 | 1286 | 892 | 0 | 102 | 882.67 | 46 | 3426 | 476.44 | 125 | 232 | 0 | 0 | 2 | 0
14:30 | 2565 | 1196 | 862 | 0 | 98 | 863.3 | 46 | 3268 | 412.245 | 125 | 263.75 | 0 | 0 | 1 | 0
15:00 | 2443 | 1106 | 832 | 0 | 94 | 843.93 | 46 | 3110 | 348.05 | 125 | 295.5 | 0 | 0 | 0 | 0
15:30 | 2481 | 1055 | 862 | 0 | 94 | 839.665 | 46 | 3048.5 | 253.73 | 97.5 | 265.6 | 0 | 0 | 3.5 | 0
16:00 | 2519 | 1004 | 892 | 0 | 94 | 835.4 | 46 | 2987 | 159.41 | 70 | 235.7 | 0 | 0 | 7 | 0
16:30 | 2555 | 1092.5 | 892 | 0 | 91 | 883.93 | 46 | 3144 | 90.185 | 70 | 226.25 | 0 | 0 | 6 | 0
17:00 | 2591 | 1181 | 892 | 0 | 88 | 932.46 | 46 | 3301 | 20.96 | 70 | 216.8 | 0 | 0 | 5 | 0
17:30 | 2726 | 1205.5 | 892 | 0 | 94 | 1047.49 | 46 | 3588 | 10.48 | 106 | 247.25 | 0 | 0 | 5.5 | 0
18:00 | 2861 | 1230 | 892 | 0 | 100 | 1162.52 | 46 | 3875 | 0 | 142 | 277.7 | 0 | 0 | 6 | 0
18:30 | 2782 | 1227 | 892 | 0 | 95 | 1193.645 | 46 | 3988.5 | 0 | 142 | 202 | 0 | 0 | 9.5 | 0
19:00 | 2703 | 1224 | 892 | 0 | 90 | 1224.77 | 46 | 4102 | 0 | 142 | 126.3 | 0 | 0 | 13 | 0
19:30 | 2798 | 1256 | 891 | 0 | 90 | 1130.07 | 46 | 4096 | 0 | 125 | 106 | 0 | 0 | 14 | 0
20:00 | 2813 | 1265 | 891 | 0 | 90 | 1128.39 | 46 | 4071 | 0 | 90 | 71 | 0 | 0 | 13 | 0
20:30 | 2838.5 | 1287 | 891.5 | 0 | 88 | 1054.195 | 46 | 4012.5 | 0 | 62.5 | 71 | 0 | 0 | 18 | 0
21:00 | 2864 | 1309 | 892 | 0 | 86 | 980 | 46 | 3954 | 0 | 35 | 71 | 0 | 0 | 23 | 0
21:30 | 2858 | 1345.5 | 892 | 0 | 85 | 906.5 | 46 | 3842 | 0 | 17.5 | 57 | 0 | 0 | 26 | 0
22:00 | 2852 | 1382 | 892 | 0 | 84 | 833 | 46 | 3730 | 0 | 0 | 43 | 0 | 0 | 29 | 0
22:30 | 2752.5 | 1352 | 892 | 0 | 82 | 835.5 | 46 | 3579.5 | 0 | 0 | 35 | 0 | 0 | 23.5 | 0
23:00 | 2653 | 1322 | 892 | 0 | 80 | 838 | 46 | 3429 | 0 | 0 | 27 | 0 | 0 | 18 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-01-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 424 | 03:00 | 396 | 12:00 | Meghnaghat | 427 | 05:00 | 404 | 12:00
Ashuganj | 423 | 03:00 | 401 | 13:00 | Payra | 422 | 02:00 | 413 | 13:00
Bhulta | 407 | 04:00 | 386 | 13:00 | Rahanpur | 419 | 02:00 | 403 | 18:00
Bibiana | 421 | 02:00 | 402 | 13:00 | Rampal | 420 | 03:00 | 399 | 13:00
BIPTC | 410 | 04:00 | 390 | 13:00
Bogura | 416 | 03:00 | 394 | 18:30
Gopalganj | 423 | 03:00 | 401 | 13:00
Kaliakoir | 421 | 01:00 | 388 | 12:00
Korerhat | 421 | 02:00 | 405 | 12:00
Madunaghat | 414 | 04:00 | 403 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 248 | 05:00 | 36 | 20:00 | Kachua | 242 | 02:00 | 233 | 18:00
AKSML | 240.1 | 23:00 | 232.8 | 13:00 | Kaliakoir | 247 | 03:00 | 227 | 12:00
Aminbazar | 246 | 02:00 | 229 | 12:00 | Keranigonj | 245 | 03:00 | 227 | 12:00
Ashuganj | 239 | 02:00 | 230 | 12:00 | Khulna(S) | 247 | 05:00 | 230 | 13:00
Ashuganj-400 | 239 | 02:00 | 230 | 12:00 | Korerhat | 243 | 00:00 | 235 | 12:00
Baghabari | 241 | 00:00 | 230 | 12:00 | Madunaghat | 239 | 03:00 | 232 | 18:00
Barapukuria | 233 | 04:00 | 213 | 18:00 | Madunaghat-400 | 240 | 04:00 | 233 | 13:00
Barapukuria-230 | 233 | 04:00 | 213 | 18:00 | Maniknagar | 242 | 01:00 | 229 | 13:00
Barishal | 240 | 01:00 | 229 | 13:00 | Meghnaghat | 242 | 21:00 | 234 | 12:00
Bheramara | 242 | 04:00 | 222 | 12:00 | Meghnaghat-400 | 244 | 03:00 | 229 | 12:00
Bhulta | 245 | 03:00 | 231 | 12:00 | Mirsorai | 244 | 04:00 | 234 | 13:00
Bibiana | 248 | 05:00 | 236 | 12:00 | Rajshahi | 242 | 04:00 | 221 | 18:00
BIPTC | 243 | 04:00 | 222 | 18:00 | Rampal | 243 | 03:00 | 228 | 12:00
Bogura | 243 | 02:00 | 229 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Bogura-400 | 243 | 02:00 | 229 | 18:30 | Rampura | 244 | 05:00 | 230 | 13:00
Borhanuddin | 243 | 04:00 | 236 | 12:00 | Shikalbaha | 237 | 00:00 | 230 | 13:00
BSRM | 243 | 03:00 | 234 | 13:00 | Shyampur | 245 | 05:00 | 228 | 12:00
Cumilla(N) | 241 | 00:00 | 231 | 12:00 | Siddhirganj | 244 | 02:00 | 231 | 12:00
Faridpur | 241 | 05:00 | 227 | 13:00 | Sirajgonj | 247 | 02:00 | 237 | 18:00
Fenchuganj | 245 | 00:00 | 239 | 16:00 | Sreepur | 240 | 05:00 | 228 | 18:00
Feni | 244 | 05:00 | 233 | 13:00 | Tongi | 241 | 04:00 | 225 | 11:00
Ghorashal | 242 | 01:00 | 235 | 13:00
Ghorashal-230 | 238 | 05:00 | 214 | 12:00
Gopalganj | 239 | 05:00 | 226 | 12:00
GPH | 241 | 02:00 | 24 | 04:00
Haripur | 245 | 05:00 | 231 | 12:00
Hasnabad | 243 | 03:00 | 227 | 12:00
Hathazari | 238 | 00:00 | 228 | 13:00
Ishurdi | 244 | 05:00 | 225 | 12:00
Jhenaidah | 244 | 04:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 126 | 12:00 | Laksam | 143 | 02:00 | 137 | 13:00 | UttaraNew | 139 | 02:00 | 127 | 13:00
Agargaon | 141 | 03:00 | 129 | 12:00 | Lakshmipur | 137 | 02:00 | 131 | 13:00 | Zigatola | 140 | 03:00 | 127 | 12:00
Agrabad | 140 | 03:00 | 135 | 11:00 | Lalbag | 140 | 06:00 | 128 | 12:00
AKS | 136 | 00:00 | 132 | 13:00 | Lalmonirhat | 132 | 02:00 | 122 | 08:00
Aminbazar | 141 | 04:00 | 129 | 12:00 | Madanganj | 138 | 02:00 | 134 | 09:00
Amnura | 138 | 00:00 | 128 | 18:00 | Madaripur | 142 | 05:00 | 135 | 13:00
Ashuganj | 143 | 04:00 | 137 | 12:00 | Madartek | 137 | 02:00 | 126 | 12:00
Bagerhat | 136 | 01:00 | 125 | 18:00 | Madunaghat | 141 | 05:00 | 135 | 18:00
Bajitpur | 138 | 02:00 | 130 | 09:00 | Magura | 139 | 05:00 | 124 | 13:00
Bakerganj | 138 | 04:00 | 135 | 13:00 | Mahasthangarh | 138 | 02:00 | 127 | 18:00
Bakulia | 139 | 02:00 | 134 | 13:00 | Maijdee | 137 | 02:00 | 131 | 13:00
Banani | 138 | 02:00 | 125 | 13:00 | Manikganj | 137 | 02:00 | 124 | 13:00
Bangabhaban | 141 | 02:00 | 131 | 13:00 | Maniknagar | 141 | 02:00 | 131 | 13:00
Barapukuria | 139 | 04:00 | 127 | 18:00 | Matarbari | 132 | 00:00 | 114 | 13:00
Barguna | 138 | 01:00 | 135 | 10:00 | Matuail | 140 | 03:00 | 133 | 12:00
Barishal | 142 | 06:00 | 133 | 13:00 | Metrorail_Motijheel | 141 | 04:00 | 131 | 13:00
Barishal-230 | 142 | 03:00 | 133 | 13:00 | Metrorail_Uttara | 139 | 02:00 | 127 | 13:00
Baroaulia | 138 | 22:00 | 135 | 13:00 | Millgate | 140 | 01:00 | 126 | 12:00
Baroirhat | 137 | 00:00 | 133 | 12:00 | Mirpur | 138 | 00:00 | 128 | 12:00
Bashundhara | 138 | 03:00 | 125 | 13:00 | Mirzapur | 140 | 04:00 | 126 | 12:00
BashundharaCement | 138 | 02:00 | 134 | 09:00 | Mithapukur | 137 | 03:00 | 125 | 18:00
Beanibazar | 138 | 06:00 | 133 | 12:00 | MI_Cement | 138 | 02:00 | 127 | 11:00
Benapole | 137 | 03:00 | 117 | 13:00 | Modern | 0 | 00:00 | 0 | 00:00
Bhaluka | 137 | 15:00 | 130 | 08:00 | Mogbazar | 139 | 03:00 | 130 | 14:00
Bhandaria | 140 | 02:00 | 132 | 13:00 | Mongla | 138 | 03:00 | 126 | 13:00
Bhangura | 141 | 02:00 | 14 | 05:00 | Motijheel | 141 | 02:00 | 131 | 13:00
Bheramara | 141 | 02:00 | 128 | 12:00 | Muktagacha | 136 | 15:00 | 126 | 08:00
Bheramara(GK) | 139 | 04:00 | 128 | 12:00 | Munshiganj | 138 | 04:00 | 131 | 12:00
Bhulta | 133 | 00:00 | 126 | 13:00 | Muradnagar | 142 | 03:00 | 133 | 13:00
Bog-Sherpur | 140 | 04:00 | 129 | 18:00 | Mymensingh | 136 | 15:00 | 124 | 06:00
Bogura | 140 | 04:00 | 130 | 18:00 | Naogaon | 135 | 03:00 | 125 | 13:00
Bogura-230 | 139 | 02:00 | 130 | 18:00 | Narail | 142 | 03:00 | 123 | 13:00
Brahmanbaria | 136 | 02:00 | 129 | 11:00 | Narinda | 141 | 02:00 | 131 | 13:00
Cantonment | 141 | 04:00 | 128 | 12:00 | Narshingdi | 139 | 04:00 | 126 | 12:00
Chandina | 143 | 03:00 | 135 | 12:00 | Natore | 138 | 01:00 | 128 | 17:00
Chandpur | 141 | 07:00 | 136 | 13:00 | Nawabganj | 140 | 02:00 | 126 | 13:00
Chandraghona | 140 | 00:00 | 135 | 13:00 | Netrakona | 131 | 01:00 | 123 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chapai | 140 | 01:00 | 133 | 18:00 | New | 161 | 13:00 | 127 | 12:00
Charsaidpur | 140 | 03:00 | 132 | 12:00 | Niamatpur | 139 | 00:00 | 133 | 18:00
Chauddagram | 140 | 00:00 | 134 | 11:00 | Noapara | 138 | 05:00 | 116 | 13:00
Chhatak | 136 | 00:00 | 130 | 16:00 | Pabna | 141 | 02:00 | 129 | 12:00
Chowmuhani | 136 | 23:00 | 131 | 11:00 | Palashbari | 132 | 00:00 | 123 | 18:00
Chuadanga | 142 | 04:00 | 124 | 13:00 | Panchagarh | 137 | 00:00 | 123 | 08:00
Coxsbazar | 131 | 00:00 | 117 | 12:00 | Patiya | 140 | 03:00 | 133 | 18:00
Cumilla(N) | 142 | 04:00 | 135 | 13:00 | Patuakhali | 137 | 02:00 | 134 | 12:00
Cumilla(S) | 143 | 02:00 | 126 | 08:00 | Payra | 139 | 02:00 | 136 | 12:00
Daganbhuiyan | 139 | 03:00 | 133 | 13:00 | PHP | 140 | 04:00 | 132 | 13:00
Daudkandi | 139 | 02:00 | 131 | 12:00 | Postogola | 140 | 04:00 | 129 | 11:00
DhakaUniversity | 139 | 04:00 | 126 | 12:00 | Purbachal | 139 | 03:00 | 126 | 12:00
Dhamrai | 140 | 01:00 | 128 | 12:00 | Purbasadipur | 132 | 02:00 | 122 | 08:00
Dhanmondi | 141 | 04:00 | 134 | 11:00 | Rahanpur | 141 | 02:00 | 134 | 10:00
Dohazari | 137 | 00:00 | 130 | 18:00 | Rahanpur-400 | 141 | 02:00 | 135 | 18:00
Faridpur | 140 | 03:00 | 131 | 13:00 | Rahim | 139 | 02:00 | 132 | 13:00
Fatullah | 142 | 05:00 | 127 | 11:00 | Rajbari | 139 | 02:00 | 130 | 13:00
Fenchuganj | 142 | 00:00 | 137 | 11:00 | Rajendrapur | 139 | 03:00 | 117 | 12:00
Feni | 137 | 04:00 | 131 | 19:00 | Rajshahi | 138 | 01:00 | 128 | 13:00
Feni-230 | 139 | 02:00 | 133 | 13:00 | Rajshahi-230 | 139 | 03:00 | 127 | 13:00
Ghatail | 134 | 03:00 | 126 | 08:00 | Ramganj | 139 | 06:00 | 121 | 04:00
Ghorashal | 137 | 01:00 | 127 | 13:00 | Rampur | 139 | 01:00 | 134 | 12:00
Goalpara | 138 | 05:00 | 129 | 12:00 | Rampura | 137 | 04:00 | 125 | 13:00
Gollamari | 139 | 04:00 | 129 | 13:00 | Rangamati | 140 | 03:00 | 134 | 13:00
Gopalganj | 142 | 05:00 | 132 | 13:00 | Rangpur | 136 | 02:00 | 125 | 08:00
Gopalganj-400 | 144 | 02:00 | 136 | 12:00 | Ruppur | 141 | 05:00 | 130 | 12:00
Gulshan | 137 | 06:00 | 125 | 12:00 | Saidpur | 134 | 01:00 | 124 | 18:00
Halishahar | 140 | 01:00 | 134 | 13:00 | Satkhira | 138 | 02:00 | 125 | 13:00
Haripur | 141 | 05:00 | 132 | 12:00 | Satmasjid | 139 | 01:00 | 129 | 13:00
HaripurSBU | 141 | 05:00 | 132 | 13:00 | Savar | 138 | 02:00 | 127 | 12:00
Hasnabad | 138 | 01:00 | 129 | 12:00 | SevenRings | 139 | 05:00 | 127 | 11:00
Hathazari | 140 | 00:00 | 136 | 11:00 | ShahCement | 140 | 03:00 | 132 | 12:00
Hatirjheel | 139 | 05:00 | 126 | 12:00 | Shahjadpur | 142 | 00:00 | 135 | 12:00
Ishurdi | 143 | 02:00 | 131 | 12:00 | Shahjibazar | 137 | 02:00 | 132 | 12:00
Jaldhaka | 133 | 03:00 | 121 | 18:00 | Shahmirpur | 140 | 02:00 | 135 | 12:00
Jamalpur | 135 | 15:00 | 122 | 08:00 | Shariatpur | 143 | 02:00 | 134 | 13:00
Jashore | 138 | 04:00 | 117 | 13:00 | Sherpur | 133 | 15:00 | 118 | 07:00
Jhenaidah | 140 | 00:00 | 112 | 13:00 | Shikalbaha | 129 | 00:00 | 123 | 13:00
Jhenaidah-230 | 141 | 02:00 | 126 | 18:30 | Shikalbaha-230 | 140 | 00:00 | 135 | 13:00
Joydebpur | 135 | 03:00 | 119 | 12:00 | Shitalakhya | 138 | 02:00 | 127 | 11:00
Joypurhat | 136 | 03:00 | 127 | 13:00 | Sholosohor | 140 | 02:00 | 135 | 12:00
Juldah | 139 | 00:00 | 134 | 17:00 | Shyampur | 138 | 03:00 | 133 | 10:00
Kabirpur | 141 | 03:00 | 125 | 13:00 | Shyampur-230 | 142 | 05:00 | 132 | 12:00
Kachua | 143 | 02:00 | 137 | 13:00 | Siddhirganj | 140 | 02:00 | 133 | 12:00
Kaliakoir | 143 | 03:00 | 129 | 12:00 | Sirajganj | 138 | 00:00 | 131 | 13:00
Kallyanpur | 139 | 01:00 | 130 | 12:00 | Sonargaon | 139 | 02:00 | 132 | 12:00
Kalurghat | 140 | 05:00 | 136 | 11:00 | Sreemongol | 139 | 03:00 | 133 | 12:00
Kamrangirchar | 140 | 01:00 | 126 | 13:00 | Sreepur | 141 | 02:00 | 132 | 17:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 139 | 01:00 | 127 | 12:00
Kasba | 142 | 03:00 | 133 | 12:00 | SSM | 141 | 23:00 | 138 | 15:00
Kazla | 141 | 03:00 | 131 | 13:00 | Sunamganj | 136 | 04:00 | 131 | 12:00
Keranigonj | 140 | 02:00 | 126 | 13:00 | Sylhet | 138 | 03:00 | 133 | 12:00
Khagrachori | 139 | 00:00 | 134 | 12:00 | Sylhet-132 | 138 | 02:00 | 134 | 11:00
Khulna | 139 | 04:00 | 127 | 13:00 | Tangail | 135 | 05:00 | 124 | 12:00
Khulna(S) | 139 | 02:00 | 129 | 13:00 | Taraganj | 134 | 03:00 | 124 | 18:30
Khulshi | 138 | 01:00 | 133 | 13:00 | Tasnim | 140 | 03:00 | 132 | 12:00
Kishoreganj | 134 | 00:00 | 128 | 18:00 | Thakurgaon | 135 | 00:00 | 122 | 08:00
Kodda | 138 | 01:00 | 120 | 12:00 | TK | 139 | 05:00 | 135 | 00:00
KSRM | 139 | 01:00 | 19 | 04:00 | Tongi | 141 | 04:00 | 131 | 11:00
Kulaura | 142 | 03:00 | 136 | 12:00 | Ullahpara | 139 | 00:00 | 130 | 18:00
Kurigram | 133 | 03:00 | 121 | 08:00 | Ullon | 137 | 02:00 | 125 | 13:00
Kushtia | 136 | 04:00 | 120 | 18:00 | Uttara | 140 | 02:00 | 127 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-01-2026 | [28 empty] | Date: | 01-01-2026 | [28 empty] | Date: | 01-01-2026 | [28 empty] | Date: | 01-01-2026 | [28 empty] | Date: | 01-01-2026 | [17 empty] | Date: | 01-01-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1085.320 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 535 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 300 | 300 | 0 | 51 | 0 | 189 | 0 | 0 | 112 | 0 | 0 | 11 | 0 | 76 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 60 | 0 | 0 | 17 | 0 | 5 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 4177 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 0 | 0 | 840.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 180 | 0 | 256 | 500 | 0 | 4093.25 | 8270.25 | 97.72
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 550 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 260 | 300 | 0 | 0 | 0 | 74 | 13 | 0 | 50 | 0 | 0 | 11 | 0 | 66 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 40 | 0 | 0 | 17 | 0 | 5 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 3906 | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 840.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 100 | 180 | 0 | 258 | 300 | 0 | 3812.04 | 7718.04 | 97.71
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 550 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 230 | 290 | 0 | 0 | 7 | 40 | 25 | 0 | 50 | 0 | 0 | 11 | 0 | 60 | 0 | 0 | 0 | 260 | 0 | 0 | 41 | 40 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 147 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 3660 | 654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 844.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 100 | 180 | 0 | 258 | 300 | 0 | 3584.76 | 7244.76 | 97.71
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 565 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 230 | 290 | 0 | 0 | 15 | 0 | 25 | 0 | 50 | 0 | 0 | 5 | 0 | 62 | 0 | 0 | 0 | 260 | 0 | 0 | 41 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 149 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3563 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 0 | 0 | 0 | 842.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 100 | 180 | 0 | 259 | 297 | 0 | 3325.95 | 6888.95 | 97.7
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 572 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 230 | 290 | 0 | 0 | 20 | 0 | 25 | 0 | 50 | 0 | 0 | 5 | 0 | 60 | 0 | 0 | 0 | 260 | 0 | 0 | 41 | 40 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 147 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3492 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 0 | 0 | 838.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 100 | 180 | 0 | 260 | 280 | 0 | 3134.96 | 6626.96 | 97.7
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 545 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 230 | 280 | 0 | 0 | 14 | 0 | 25 | 0 | 50 | 0 | 0 | 5 | 0 | 62 | 0 | 0 | 0 | 255 | 0 | 0 | 41 | 36 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 149 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3391 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 0 | 0 | 839.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 100 | 180 | 0 | 262 | 280 | 0 | 3208.78 | 6599.78 | 97.69
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 553 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 320 | 280 | 0 | 0 | 13 | 0 | 36 | 0 | 50 | 0 | 0 | 5 | 0 | 66 | 0 | 0 | 0 | 255 | 0 | 0 | 41 | 36 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 150 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 3552 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 0 | 0 | 0 | 845.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 100 | 180 | 0 | 252 | 287 | 0 | 3392.56 | 6944.56 | 97.69
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.1 | 46 | 0 | 24 | 577 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 653 | 1 | 0 | 0 | 350 | 355 | 0 | 0 | 24 | 0 | 37 | 0 | 114 | 0 | 0 | 0 | 0 | 64 | 0 | 1 | 0 | 310 | 0 | 0 | 41 | 36 | 0 | 0 | 8 | 0 | 61 | 20 | 0 | 0 | 153 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4188.1 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 816 | 0 | 0 | 0 | 833.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0 | 0 | 0 | 0.65 | 148 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 153 | 110 | 220 | 0 | 273 | 320 | 0 | 3489.51 | 7677.61 | 97.69
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0.45 | 46 | 0 | 26 | 590 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 790 | 8 | 0 | 0 | 365 | 360 | 0 | 35 | 32 | 0 | 40 | 0 | 114 | 0 | 0 | 0 | 0 | 76 | 0 | 6 | 0 | 315 | 0 | 0 | 41 | 50 | 0 | 1 | 10 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 10 | 0 | 109 | 0 | 1.83 | 0 | 4559.78 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 809 | 0 | 0 | 0 | 850.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.88 | 11 | 0 | 0 | 9.4 | 172 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0.82 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.9 | 15 | 0.11 | 0 | 155 | 140 | 220 | 0 | 251 | 330 | 0 | 4079.21 | 8638.99 | 97.68
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 280 | 0 | 0 | 14 | 52 | 22.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.03 | 46 | 0 | 24 | 720 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 850 | 14 | 0 | 0 | 320 | 360 | 0 | 51 | 36 | 0 | 40 | 0 | 114 | 0 | 0 | 3 | 0 | 80 | 0 | 11 | 0 | 310 | 0 | 0 | 41 | 50 | 0 | 1 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 38 | 0 | 110 | 1 | 4.16 | 0 | 4856.69 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 861 | 0 | 0 | 0 | 925.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.34 | 31 | 0 | 0 | 25.43 | 172 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 2.33 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 2.5 | 32 | 0.26 | 0 | 169 | 140 | 220 | 0 | 298 | 365 | 0 | 4602.74 | 9459.43 | 97.67
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 22 | 52 | 27.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.7 | 46 | 0 | 23 | 745 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 330 | 330 | 0 | 51 | 42 | 0 | 40 | 0 | 112 | 0 | 0 | 3 | 0 | 88 | 0 | 13 | 0 | 310 | 0 | 0 | 41 | 50 | 0 | 2 | 17 | 0 | 78 | 30 | 0 | 0 | 158 | 0 | 57 | 19 | 110 | 1 | 6.11 | 0 | 4716.31 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 793 | 0 | 0 | 0 | 837.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.19 | 72 | 0 | 0 | 40.56 | 172 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 3.62 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 3.8 | 32 | 0.39 | 0 | 172 | 120 | 180 | 0 | 264 | 350 | 0 | 4395.9 | 9112.21 | 97.67
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 250 | 0 | 0 | 28 | 100 | 28 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3.1 | 46 | 0 | 24 | 745 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 845 | 20 | 0 | 0 | 355 | 300 | 0 | 51 | 45 | 0 | 40 | 0 | 50 | 0 | 0 | 8 | 0 | 86 | 0 | 20 | 0 | 315 | 0 | 0 | 41 | 50 | 5 | 2 | 17 | 0 | 79 | 30 | 0 | 0 | 158 | 0 | 11 | 65 | 110 | 2 | 7.58 | 0 | 4772.68 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 787 | 0 | 0 | 0 | 840.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.21 | 90 | 0 | 0 | 49.1 | 175 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 3.99 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 4.8 | 42 | 0.49 | 0 | 174 | 140 | 180 | 0 | 266 | 350 | 0 | 4521.86 | 9294.54 | 97.66
12:00 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 250 | 0 | 0 | 29 | 108 | 29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3.31 | 46 | 0 | 21 | 745 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 840 | 19 | 0 | 7 | 360 | 330 | 0 | 51 | 46 | 0 | 40 | 0 | 110 | 0 | 0 | 8 | 0 | 92 | 0 | 31 | 0 | 310 | 0 | 0 | 41 | 50 | 34 | 2 | 17 | 0 | 77 | 30 | 0 | 0 | 158 | 0 | 11 | 65 | 128 | 0 | 8.93 | 0 | 4999.24 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 787 | 0 | 0 | 0 | 842.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.17 | 96 | 0 | 0 | 54.42 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.13 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 5.1 | 113 | 0.54 | 0 | 181 | 140 | 220 | 0 | 256 | 350 | 0 | 4684.43 | 9683.67 | 97.66
13:00 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 250 | 0 | 0 | 28 | 125 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 3.11 | 46 | 0 | 27 | 745 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 950 | 18 | 0 | 46 | 345 | 360 | 0 | 51 | 46 | 0 | 40 | 0 | 108 | 0 | 0 | 15 | 0 | 100 | 0 | 61 | 0 | 310 | 0 | 0 | 41 | 50 | 44 | 2 | 17 | 0 | 81 | 30 | 0 | 0 | 158 | 0 | 15 | 65 | 164 | 2 | 13.59 | 0 | 5401.7 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 843 | 0 | 0 | 0 | 928.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.94 | 92 | 0 | 0 | 54.26 | 194 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 5.19 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 5 | 138 | 0.5 | 0 | 198 | 140 | 220 | 0 | 311 | 380 | 0 | 4928.69 | 10330.39 | 97.65
14:00 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 20 | 250 | 0 | 0 | 25 | 125 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.58 | 46 | 0 | 23 | 665 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 930 | 0 | 0 | 73 | 360 | 300 | 0 | 51 | 48 | 0 | 40 | 0 | 108 | 0 | 0 | 15 | 0 | 102 | 0 | 54 | 0 | 315 | 0 | 0 | 41 | 50 | 41 | 2 | 17 | 0 | 81 | 30 | 0 | 0 | 158 | 8 | 22 | 46 | 167 | 1 | 11.56 | 0 | 5285.14 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 906 | 0 | 0 | 0 | 882.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.85 | 77 | 0 | 0 | 41.87 | 178 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 4.07 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.1 | 123 | 0.41 | 0 | 195 | 140 | 220 | 0 | 310 | 420 | 0 | 4871.97 | 10157.11 | 97.65
15:00 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 43.5 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 55 | 230 | 0 | 0 | 17 | 125 | 29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.79 | 46 | 0 | 22 | 665 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 850 | 0 | 0 | 15 | 300 | 320 | 0 | 10 | 46 | 0 | 36 | 0 | 50 | 0 | 0 | 15 | 0 | 94 | 0 | 38 | 0 | 305 | 0 | 0 | 41 | 50 | 0 | 3 | 17 | 0 | 78 | 20 | 0 | 0 | 158 | 17 | 26 | 45 | 165 | 0 | 20.01 | 0 | 4953.3 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 797 | 0 | 0 | 0 | 843.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.22 | 55 | 0 | 0 | 28.89 | 171 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.72 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3.1 | 86 | 0.32 | 0 | 169 | 100 | 180 | 0 | 259 | 370 | 0 | 4290.18 | 9243.48 | 97.64
16:00 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 40.7 | 0 | 32 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 17 | 230 | 0 | 0 | 8 | 70 | 29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0.79 | 46 | 0 | 22 | 665 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 810 | 6 | 0 | 8 | 330 | 280 | 0 | 10 | 47 | 0 | 40 | 0 | 50 | 0 | 0 | 15 | 0 | 94 | 0 | 18 | 0 | 305 | 0 | 0 | 41 | 50 | 0 | 1 | 17 | 0 | 42 | 20 | 0 | 0 | 158 | 17 | 23 | 32 | 165 | 0 | 8.5 | 0 | 4665.99 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 787 | 0 | 0 | 0 | 835.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.28 | 25 | 0 | 0 | 12.07 | 174 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 1.12 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.5 | 39 | 0.15 | 0 | 175 | 100 | 180 | 0 | 250 | 300 | 0 | 4183.52 | 8849.51 | 97.64
17:00 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 32.8 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 17 | 230 | 0 | 0 | 1 | 70 | 29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.07 | 46 | 0 | 33 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 950 | 1 | 0 | 8 | 300 | 280 | 0 | 30 | 50 | 0 | 40 | 0 | 108 | 0 | 0 | 15 | 0 | 88 | 0 | 2 | 0 | 315 | 0 | 0 | 41 | 50 | 0 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 159 | 17 | 19 | 32 | 165 | 0 | 0.87 | 0 | 5004.74 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | 807 | 0 | 0 | 0 | 932.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.67 | 4 | 0 | 0 | 1.14 | 202 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0.16 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 4 | 0.02 | 0 | 199 | 130 | 220 | 0 | 260 | 340 | 0 | 4339.48 | 9344.22 | 97.63
18:00 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 33.7 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 7 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 35 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1150 | 0 | 0 | 38 | 325 | 356 | 0 | 51 | 46 | 0 | 40 | 0 | 109 | 0 | 0 | 11 | 0 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 0 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 17 | 19 | 57 | 166 | 0 | 0 | 0 | 5556.7 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 1162.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 140 | 220 | 0 | 345 | 455 | 0 | 5035.52 | 10592.22 | 97.63
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 7 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 37 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1040 | 0 | 0 | 41 | 295 | 356 | 0 | 51 | 45 | 0 | 40 | 0 | 109 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 0 | 41 | 50 | 0 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 17 | 19 | 35 | 166 | 0 | 0 | 0 | 5208.3 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1027 | 0 | 0 | 0 | 1224.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 140 | 220 | 0 | 494 | 520 | 0 | 5354.77 | 10563.07 | 97.62
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 7 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1060 | 0 | 0 | 43 | 340 | 357 | 0 | 51 | 49 | 0 | 40 | 0 | 110 | 0 | 0 | 11 | 0 | 90 | 0 | 0 | 0 | 315 | 0 | 0 | 41 | 50 | 0 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 17 | 19 | 35 | 166 | 0 | 0 | 0 | 5288 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 1130.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 140 | 220 | 0 | 439 | 545 | 0 | 5264.07 | 10552.07 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 38 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1060 | 0 | 0 | 45 | 350 | 356 | 0 | 51 | 47 | 0 | 40 | 0 | 111 | 0 | 0 | 15 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 0 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 17 | 19 | 35 | 167 | 0 | 0 | 0 | 5272 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 1128.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 140 | 220 | 0 | 436 | 545 | 0 | 5206.39 | 10478.39 | 97.62
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 10 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 1057 | 0 | 0 | 45 | 345 | 356 | 0 | 51 | 49 | 0 | 37 | 0 | 111 | 0 | 0 | 18 | 0 | 86 | 0 | 0 | 0 | 320 | 0 | 0 | 41 | 50 | 47 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 17 | 19 | 35 | 167 | 0 | 0 | 0 | 5265 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 140 | 220 | 0 | 366 | 545 | 0 | 4995 | 10260 | 97.61
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 39 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 971 | 0 | 0 | 45 | 340 | 357 | 0 | 51 | 49 | 0 | 40 | 0 | 111 | 0 | 0 | 17 | 0 | 84 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 107 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 0 | 19 | 24 | 166 | 0 | 0 | 0 | 5183 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 140 | 220 | 0 | 325 | 545 | 0 | 4708 | 9891 | 97.61
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 745 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 860 | 0 | 0 | 45 | 350 | 355 | 0 | 43 | 49 | 0 | 40 | 0 | 111 | 0 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 0 | 41 | 50 | 106 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 159 | 0 | 19 | 8 | 166 | 0 | 0 | 0 | 4833 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 140 | 220 | 0 | 279 | 544 | 0 | 4472 | 9305 | 97.6
Total KWH | 468576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7952400 | 0 | 0 | 186516 | 0 | 188928 | 0 | 0 | 47016 | 0 | 0 | 0 | 0 | 0 | 8925001 | 0 | 145710 | 5841584 | 0 | 0 | 180526 | 1221600 | 408600 | 359640 | 0 | 0 | 0 | 0 | 0 | 0 | 334080 | 0 | 0 | 0 | 0 | 0 | 17563 | 1100700 | 0 | 567360 | 16160000 | 0 | 0 | 0 | 0 | 0 | 3953230 | 0 | 0 | 0 | 20034543 | 101115 | 0 | 451636 | 7654200 | 8071400 | 0 | 827691 | 864480 | 206000 | 840600 | 0 | 2081083 | 0 | 0 | 236630 | 0 | 1927680 | 0 | 256973 | 0 | 7310500 | 0 | 0 | 966000 | 1086600 | 530673 | 16540 | 299424 | 0 | 1311360 | 611232 | 0 | 0 | 4394550 | 148320 | 382800 | 602400 | 3312960 | 9200 | 79250 | 0 | 112674870 | 17746909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481680 | 20072726 | 0 | 0 | 0 | 21632727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294076 | 566800 | 0 | 0 | 316496 | 4169273 | 0 | 0 | 0 | 0 | 0 | 8549309 | 0 | 26820 | 0 | 0 | 65316 | 150687 | 0 | 0 | 0 | 0 | 30138.72 | 632160 | 3213 | 0 | 4385000 | 2952000 | 5226080 | 0 | 7047272 | 9798545.46 | 0 | 104147228.18 | 216822098.18